## Summary
SSR target (%) | Min BESS Power (MW) | Min BESS Energy (MWh) | BESS duration (h) | Peak grid import (MW) | Simulated SSR Model R (%) | Simulated SCR (%) | Simulated unmet (MWh) | Deliverable BESS (MWh) | Physics valid | Viable in simulation | Detail sheet
5 | 0 | 0 | 0 | 88.5 | 39.6 | 72.6 | 0 | 0 | ok | YES | Sim_NoBESS
10 | 0 | 0 | 0 | 88.5 | 39.6 | 72.6 | 0 | 0 | ok | YES | Sim_NoBESS
15 | 0 | 0 | 0 | 88.5 | 39.6 | 72.6 | 0 | 0 | ok | YES | Sim_NoBESS
20 | 0 | 0 | 0 | 88.5 | 39.6 | 72.6 | 0 | 0 | ok | YES | Sim_NoBESS
25 | 0 | 0 | 0 | 88.2 | 39.6 | 72.6 | 0 | 0 | ok | YES | Sim_NoBESS
30 | 0 | 0 | 0 | 88.2 | 39.6 | 72.6 | 0 | 0 | ok | YES | Sim_NoBESS
35 | 0 | 0 | 0 | 88.2 | 39.6 | 72.6 | 0 | 0 | ok | YES | Sim_NoBESS
40 | 3.4 | 6.8 | 2 | 82.2 | 40 | 73.4 | 0 | 6.8 | ok | YES | Sim_SSR40pct
45 | 62.5 | 125.1 | 2 | 82.2 | 45 | 83.5 | 0 | 125 | ok | YES | Sim_SSR45pct
50 | 76.4 | 324.5 | 4.2 | 82.2 | 50 | 93.7 | 0 | 323.7 | ok | YES | Sim_SSR50pct

## Sim_NoBESS
Timestamp | Load (MW) | PV available (MW) | PV used on-site (MW) | Grid import (MW) | BESS charge (MW) | BESS discharge (MW) | BESS state of charge (MWh) | PV curtailed (MW) | Unmet load (MW)
2025-01-01 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0 | 0 | 0
2025-01-01 01:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 0 | 0 | 0
2025-01-01 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-01-01 03:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0 | 0 | 0
2025-01-01 04:00 | 37.77 | 0 | 0 | 37.77 | 0 | 0 | 0 | 0 | 0
2025-01-01 05:00 | 37.73 | 0 | 0 | 37.73 | 0 | 0 | 0 | 0 | 0
2025-01-01 06:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0 | 0 | 0
2025-01-01 07:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 0 | 0 | 0
2025-01-01 08:00 | 40.47 | 0.35 | 0.35 | 40.12 | 0 | 0 | 0 | 0 | 0
2025-01-01 09:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 0 | 0 | 0
2025-01-01 10:00 | 43.25 | 39.6 | 39.6 | 3.65 | 0 | 0 | 0 | 0 | 0
2025-01-01 11:00 | 42.95 | 51.11 | 42.95 | 0 | 0 | 0 | 0 | 8.16 | 0
2025-01-01 12:00 | 42.89 | 47.41 | 42.89 | 0 | 0 | 0 | 0 | 4.52 | 0
2025-01-01 13:00 | 45.35 | 15.24 | 15.24 | 30.11 | 0 | 0 | 0 | 0 | 0
2025-01-01 14:00 | 44.73 | 17.49 | 17.49 | 27.24 | 0 | 0 | 0 | 0 | 0
2025-01-01 15:00 | 45.16 | 7.79 | 7.79 | 37.36 | 0 | 0 | 0 | 0 | 0
2025-01-01 16:00 | 45.62 | 0.73 | 0.73 | 44.89 | 0 | 0 | 0 | 0 | 0
2025-01-01 17:00 | 43.75 | 0 | 0 | 43.75 | 0 | 0 | 0 | 0 | 0
2025-01-01 18:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 0 | 0 | 0
2025-01-01 19:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 0 | 0 | 0
2025-01-01 20:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 0 | 0 | 0
2025-01-01 21:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 0 | 0 | 0
2025-01-01 22:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 0 | 0 | 0
2025-01-01 23:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0 | 0 | 0
2025-01-02 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 0 | 0 | 0
2025-01-02 01:00 | 36.51 | 0 | 0 | 36.51 | 0 | 0 | 0 | 0 | 0
2025-01-02 02:00 | 37.33 | 0 | 0 | 37.33 | 0 | 0 | 0 | 0 | 0
2025-01-02 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-01-02 04:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0 | 0 | 0
2025-01-02 05:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0 | 0 | 0
2025-01-02 06:00 | 38.3 | 0 | 0 | 38.3 | 0 | 0 | 0 | 0 | 0
2025-01-02 07:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 0 | 0 | 0
2025-01-02 08:00 | 39.84 | 3.35 | 3.35 | 36.49 | 0 | 0 | 0 | 0 | 0
2025-01-02 09:00 | 40.79 | 0.73 | 0.73 | 40.07 | 0 | 0 | 0 | 0 | 0
2025-01-02 10:00 | 40.93 | 11.93 | 11.93 | 29 | 0 | 0 | 0 | 0 | 0
2025-01-02 11:00 | 41.86 | 40.23 | 40.23 | 1.63 | 0 | 0 | 0 | 0 | 0
2025-01-02 12:00 | 42.58 | 49.61 | 42.58 | 0 | 0 | 0 | 0 | 7.03 | 0
2025-01-02 13:00 | 43.28 | 52.12 | 43.28 | 0 | 0 | 0 | 0 | 8.84 | 0
2025-01-02 14:00 | 42.91 | 35.75 | 35.75 | 7.17 | 0 | 0 | 0 | 0 | 0
2025-01-02 15:00 | 43.45 | 53.79 | 43.45 | 0 | 0 | 0 | 0 | 10.34 | 0
2025-01-02 16:00 | 42.98 | 6.95 | 6.95 | 36.02 | 0 | 0 | 0 | 0 | 0
2025-01-02 17:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 0 | 0 | 0
2025-01-02 18:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 0 | 0 | 0
2025-01-02 19:00 | 40.95 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0
2025-01-02 20:00 | 40.64 | 0 | 0 | 40.64 | 0 | 0 | 0 | 0 | 0
2025-01-02 21:00 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 0 | 0 | 0
2025-01-02 22:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 0 | 0 | 0
2025-01-02 23:00 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 0 | 0 | 0
2025-01-03 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 0 | 0 | 0
2025-01-03 01:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 0 | 0 | 0
2025-01-03 02:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 0 | 0 | 0
2025-01-03 03:00 | 37.67 | 0 | 0 | 37.67 | 0 | 0 | 0 | 0 | 0
2025-01-03 04:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 0 | 0 | 0
2025-01-03 05:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 0 | 0 | 0
2025-01-03 06:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 0 | 0 | 0
2025-01-03 07:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0 | 0 | 0
2025-01-03 08:00 | 39.56 | 5.56 | 5.56 | 34 | 0 | 0 | 0 | 0 | 0
2025-01-03 09:00 | 40.75 | 58.94 | 40.75 | 0 | 0 | 0 | 0 | 18.19 | 0
2025-01-03 10:00 | 41.4 | 61.46 | 41.4 | 0 | 0 | 0 | 0 | 20.06 | 0
2025-01-03 11:00 | 42.74 | 45.74 | 42.74 | 0 | 0 | 0 | 0 | 3 | 0
2025-01-03 12:00 | 43.93 | 43.72 | 43.72 | 0.22 | 0 | 0 | 0 | 0 | 0
2025-01-03 13:00 | 45.24 | 53.25 | 45.24 | 0 | 0 | 0 | 0 | 8.01 | 0
2025-01-03 14:00 | 46.16 | 56.05 | 46.16 | 0 | 0 | 0 | 0 | 9.89 | 0
2025-01-03 15:00 | 44.76 | 59.27 | 44.76 | 0 | 0 | 0 | 0 | 14.51 | 0
2025-01-03 16:00 | 45.49 | 2.76 | 2.76 | 42.73 | 0 | 0 | 0 | 0 | 0
2025-01-03 17:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 0 | 0 | 0
2025-01-03 18:00 | 44.35 | 0 | 0 | 44.35 | 0 | 0 | 0 | 0 | 0
2025-01-03 19:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0 | 0 | 0
2025-01-03 20:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 0 | 0 | 0
2025-01-03 21:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 0 | 0 | 0
2025-01-03 22:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 0 | 0 | 0
2025-01-03 23:00 | 38.76 | 0 | 0 | 38.76 | 0 | 0 | 0 | 0 | 0
2025-01-04 | 37.64 | 0 | 0 | 37.64 | 0 | 0 | 0 | 0 | 0
2025-01-04 01:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 0 | 0 | 0
2025-01-04 02:00 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 0 | 0 | 0
2025-01-04 03:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 0 | 0 | 0
2025-01-04 04:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 0 | 0 | 0
2025-01-04 05:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0 | 0 | 0
2025-01-04 06:00 | 38.84 | 0 | 0 | 38.84 | 0 | 0 | 0 | 0 | 0
2025-01-04 07:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0 | 0 | 0
2025-01-04 08:00 | 39.21 | 5.61 | 5.61 | 33.61 | 0 | 0 | 0 | 0 | 0
2025-01-04 09:00 | 41.56 | 63.95 | 41.56 | 0 | 0 | 0 | 0 | 22.38 | 0
2025-01-04 10:00 | 41.98 | 65.08 | 41.98 | 0 | 0 | 0 | 0 | 23.1 | 0
2025-01-04 11:00 | 43.79 | 50.17 | 43.79 | 0 | 0 | 0 | 0 | 6.38 | 0
2025-01-04 12:00 | 44.38 | 45.3 | 44.38 | 0 | 0 | 0 | 0 | 0.92 | 0
2025-01-04 13:00 | 44.88 | 44.2 | 44.2 | 0.68 | 0 | 0 | 0 | 0 | 0
2025-01-04 14:00 | 45.6 | 40.92 | 40.92 | 4.68 | 0 | 0 | 0 | 0 | 0
2025-01-04 15:00 | 46.56 | 17.8 | 17.8 | 28.77 | 0 | 0 | 0 | 0 | 0
2025-01-04 16:00 | 46.46 | 2.17 | 2.17 | 44.29 | 0 | 0 | 0 | 0 | 0
2025-01-04 17:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0 | 0 | 0
2025-01-04 18:00 | 44.27 | 0 | 0 | 44.27 | 0 | 0 | 0 | 0 | 0
2025-01-04 19:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 0 | 0 | 0
2025-01-04 20:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 0 | 0 | 0
2025-01-04 21:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 0 | 0 | 0
2025-01-04 22:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 0 | 0 | 0
2025-01-04 23:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0 | 0 | 0
2025-01-05 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0 | 0 | 0
2025-01-05 01:00 | 36.72 | 0 | 0 | 36.72 | 0 | 0 | 0 | 0 | 0
2025-01-05 02:00 | 36.13 | 0 | 0 | 36.13 | 0 | 0 | 0 | 0 | 0
2025-01-05 03:00 | 36.48 | 0 | 0 | 36.48 | 0 | 0 | 0 | 0 | 0
2025-01-05 04:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-01-05 05:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 0 | 0 | 0
2025-01-05 06:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 0 | 0 | 0
2025-01-05 07:00 | 39.24 | 0 | 0 | 39.24 | 0 | 0 | 0 | 0 | 0
2025-01-05 08:00 | 38.89 | 5.6 | 5.6 | 33.29 | 0 | 0 | 0 | 0 | 0
2025-01-05 09:00 | 40.19 | 69.74 | 40.19 | 0 | 0 | 0 | 0 | 29.55 | 0
2025-01-05 10:00 | 40.38 | 56.56 | 40.38 | 0 | 0 | 0 | 0 | 16.19 | 0
2025-01-05 11:00 | 40.89 | 41.29 | 40.89 | 0 | 0 | 0 | 0 | 0.4 | 0
2025-01-05 12:00 | 41.45 | 37.95 | 37.95 | 3.5 | 0 | 0 | 0 | 0 | 0
2025-01-05 13:00 | 41.88 | 35.68 | 35.68 | 6.2 | 0 | 0 | 0 | 0 | 0
2025-01-05 14:00 | 41.52 | 22.65 | 22.65 | 18.87 | 0 | 0 | 0 | 0 | 0
2025-01-05 15:00 | 42.25 | 33.53 | 33.53 | 8.72 | 0 | 0 | 0 | 0 | 0
2025-01-05 16:00 | 41.11 | 5.31 | 5.31 | 35.81 | 0 | 0 | 0 | 0 | 0
2025-01-05 17:00 | 41.57 | 0 | 0 | 41.57 | 0 | 0 | 0 | 0 | 0
2025-01-05 18:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 0 | 0 | 0
2025-01-05 19:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0 | 0 | 0
2025-01-05 20:00 | 41.3 | 0 | 0 | 41.3 | 0 | 0 | 0 | 0 | 0
2025-01-05 21:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 0 | 0 | 0
2025-01-05 22:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 0 | 0 | 0
2025-01-05 23:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 0 | 0 | 0
2025-01-06 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 0 | 0 | 0
2025-01-06 01:00 | 37.09 | 0 | 0 | 37.09 | 0 | 0 | 0 | 0 | 0
2025-01-06 02:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 0 | 0 | 0
2025-01-06 03:00 | 36.58 | 0 | 0 | 36.58 | 0 | 0 | 0 | 0 | 0
2025-01-06 04:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 0 | 0 | 0
2025-01-06 05:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0 | 0 | 0
2025-01-06 06:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0 | 0 | 0
2025-01-06 07:00 | 38.54 | 0 | 0 | 38.54 | 0 | 0 | 0 | 0 | 0
2025-01-06 08:00 | 39.65 | 1.65 | 1.65 | 38 | 0 | 0 | 0 | 0 | 0
2025-01-06 09:00 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 0 | 0 | 0
2025-01-06 10:00 | 41.31 | 31.52 | 31.52 | 9.79 | 0 | 0 | 0 | 0 | 0
2025-01-06 11:00 | 40.51 | 40.66 | 40.51 | 0 | 0 | 0 | 0 | 0.15 | 0
2025-01-06 12:00 | 41.72 | 35.39 | 35.39 | 6.33 | 0 | 0 | 0 | 0 | 0
2025-01-06 13:00 | 41.22 | 32.44 | 32.44 | 8.78 | 0 | 0 | 0 | 0 | 0
2025-01-06 14:00 | 41.67 | 25.68 | 25.68 | 15.99 | 0 | 0 | 0 | 0 | 0
2025-01-06 15:00 | 43.16 | 4.26 | 4.26 | 38.91 | 0 | 0 | 0 | 0 | 0
2025-01-06 16:00 | 42.86 | 1.43 | 1.43 | 41.44 | 0 | 0 | 0 | 0 | 0
2025-01-06 17:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 0 | 0 | 0
2025-01-06 18:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0 | 0 | 0
2025-01-06 19:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 0 | 0 | 0
2025-01-06 20:00 | 40.57 | 0 | 0 | 40.57 | 0 | 0 | 0 | 0 | 0
2025-01-06 21:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 0 | 0 | 0
2025-01-06 22:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 0 | 0 | 0
2025-01-06 23:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 0 | 0 | 0
2025-01-07 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0 | 0 | 0
2025-01-07 01:00 | 36.66 | 0 | 0 | 36.66 | 0 | 0 | 0 | 0 | 0
2025-01-07 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-01-07 03:00 | 37.02 | 0 | 0 | 37.02 | 0 | 0 | 0 | 0 | 0
2025-01-07 04:00 | 37.04 | 0 | 0 | 37.04 | 0 | 0 | 0 | 0 | 0
2025-01-07 05:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 0 | 0 | 0
2025-01-07 06:00 | 38.18 | 0 | 0 | 38.18 | 0 | 0 | 0 | 0 | 0
2025-01-07 07:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 0 | 0 | 0
2025-01-07 08:00 | 39.28 | 0 | 0 | 39.28 | 0 | 0 | 0 | 0 | 0
2025-01-07 09:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0 | 0 | 0
2025-01-07 10:00 | 42.32 | 2.3 | 2.3 | 40.01 | 0 | 0 | 0 | 0 | 0
2025-01-07 11:00 | 41.9 | 6.14 | 6.14 | 35.76 | 0 | 0 | 0 | 0 | 0
2025-01-07 12:00 | 42.7 | 5.59 | 5.59 | 37.12 | 0 | 0 | 0 | 0 | 0
2025-01-07 13:00 | 44.4 | 41.59 | 41.59 | 2.81 | 0 | 0 | 0 | 0 | 0
2025-01-07 14:00 | 44.01 | 44.55 | 44.01 | 0 | 0 | 0 | 0 | 0.54 | 0
2025-01-07 15:00 | 44.93 | 49.89 | 44.93 | 0 | 0 | 0 | 0 | 4.96 | 0
2025-01-07 16:00 | 43.88 | 3.06 | 3.06 | 40.82 | 0 | 0 | 0 | 0 | 0
2025-01-07 17:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0 | 0 | 0
2025-01-07 18:00 | 43.21 | 0 | 0 | 43.21 | 0 | 0 | 0 | 0 | 0
2025-01-07 19:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 0 | 0 | 0
2025-01-07 20:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0 | 0 | 0
2025-01-07 21:00 | 40.38 | 0 | 0 | 40.38 | 0 | 0 | 0 | 0 | 0
2025-01-07 22:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0 | 0 | 0
2025-01-07 23:00 | 38.53 | 0 | 0 | 38.53 | 0 | 0 | 0 | 0 | 0
2025-01-08 | 38.18 | 0 | 0 | 38.18 | 0 | 0 | 0 | 0 | 0
2025-01-08 01:00 | 36.62 | 0 | 0 | 36.62 | 0 | 0 | 0 | 0 | 0
2025-01-08 02:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 0 | 0 | 0
2025-01-08 03:00 | 36.66 | 0 | 0 | 36.66 | 0 | 0 | 0 | 0 | 0
2025-01-08 04:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0 | 0 | 0
2025-01-08 05:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 0 | 0 | 0
2025-01-08 06:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 0 | 0 | 0
2025-01-08 07:00 | 37.83 | 0 | 0 | 37.83 | 0 | 0 | 0 | 0 | 0
2025-01-08 08:00 | 39.08 | 2.87 | 2.87 | 36.2 | 0 | 0 | 0 | 0 | 0
2025-01-08 09:00 | 40.48 | 54.59 | 40.48 | 0 | 0 | 0 | 0 | 14.1 | 0
2025-01-08 10:00 | 41.12 | 46.52 | 41.12 | 0 | 0 | 0 | 0 | 5.4 | 0
2025-01-08 11:00 | 41.87 | 40.62 | 40.62 | 1.24 | 0 | 0 | 0 | 0 | 0
2025-01-08 12:00 | 42.58 | 30.81 | 30.81 | 11.77 | 0 | 0 | 0 | 0 | 0
2025-01-08 13:00 | 43.26 | 30.82 | 30.82 | 12.45 | 0 | 0 | 0 | 0 | 0
2025-01-08 14:00 | 42.97 | 21.02 | 21.02 | 21.95 | 0 | 0 | 0 | 0 | 0
2025-01-08 15:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 0 | 0 | 0
2025-01-08 16:00 | 43.81 | 0.49 | 0.49 | 43.31 | 0 | 0 | 0 | 0 | 0
2025-01-08 17:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 0 | 0 | 0
2025-01-08 18:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0 | 0 | 0
2025-01-08 19:00 | 42.14 | 0 | 0 | 42.14 | 0 | 0 | 0 | 0 | 0
2025-01-08 20:00 | 42.23 | 0 | 0 | 42.23 | 0 | 0 | 0 | 0 | 0
2025-01-08 21:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 0 | 0 | 0
2025-01-08 22:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0 | 0 | 0
2025-01-08 23:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 0 | 0 | 0
2025-01-09 | 37.41 | 0 | 0 | 37.41 | 0 | 0 | 0 | 0 | 0
2025-01-09 01:00 | 36.75 | 0 | 0 | 36.75 | 0 | 0 | 0 | 0 | 0
2025-01-09 02:00 | 36.57 | 0 | 0 | 36.57 | 0 | 0 | 0 | 0 | 0
2025-01-09 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 0 | 0 | 0
2025-01-09 04:00 | 37.19 | 0 | 0 | 37.19 | 0 | 0 | 0 | 0 | 0
2025-01-09 05:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 0 | 0 | 0
2025-01-09 06:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 0 | 0 | 0
2025-01-09 07:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 0 | 0 | 0
2025-01-09 08:00 | 39.86 | 4.53 | 4.53 | 35.33 | 0 | 0 | 0 | 0 | 0
2025-01-09 09:00 | 40.32 | 54.25 | 40.32 | 0 | 0 | 0 | 0 | 13.94 | 0
2025-01-09 10:00 | 40.97 | 63.39 | 40.97 | 0 | 0 | 0 | 0 | 22.42 | 0
2025-01-09 11:00 | 42.41 | 53.19 | 42.41 | 0 | 0 | 0 | 0 | 10.78 | 0
2025-01-09 12:00 | 42.95 | 50.69 | 42.95 | 0 | 0 | 0 | 0 | 7.74 | 0
2025-01-09 13:00 | 42.69 | 61.34 | 42.69 | 0 | 0 | 0 | 0 | 18.65 | 0
2025-01-09 14:00 | 43.73 | 72.15 | 43.73 | 0 | 0 | 0 | 0 | 28.42 | 0
2025-01-09 15:00 | 44.01 | 74.05 | 44.01 | 0 | 0 | 0 | 0 | 30.03 | 0
2025-01-09 16:00 | 43.31 | 11.39 | 11.39 | 31.92 | 0 | 0 | 0 | 0 | 0
2025-01-09 17:00 | 43.51 | 0 | 0 | 43.51 | 0 | 0 | 0 | 0 | 0
2025-01-09 18:00 | 42.13 | 0 | 0 | 42.13 | 0 | 0 | 0 | 0 | 0
2025-01-09 19:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 0 | 0 | 0
2025-01-09 20:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 0 | 0 | 0
2025-01-09 21:00 | 40.27 | 0 | 0 | 40.27 | 0 | 0 | 0 | 0 | 0
2025-01-09 22:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0 | 0 | 0
2025-01-09 23:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 0 | 0 | 0
2025-01-10 | 37.29 | 0 | 0 | 37.29 | 0 | 0 | 0 | 0 | 0
2025-01-10 01:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 0 | 0 | 0
2025-01-10 02:00 | 36.45 | 0 | 0 | 36.45 | 0 | 0 | 0 | 0 | 0
2025-01-10 03:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 0 | 0 | 0
2025-01-10 04:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 0 | 0 | 0
2025-01-10 05:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 0 | 0 | 0
2025-01-10 06:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0 | 0 | 0
2025-01-10 07:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 0 | 0 | 0
2025-01-10 08:00 | 40.11 | 1.65 | 1.65 | 38.46 | 0 | 0 | 0 | 0 | 0
2025-01-10 09:00 | 39.47 | 23.38 | 23.38 | 16.09 | 0 | 0 | 0 | 0 | 0
2025-01-10 10:00 | 40.95 | 35.23 | 35.23 | 5.72 | 0 | 0 | 0 | 0 | 0
2025-01-10 11:00 | 42.4 | 16.56 | 16.56 | 25.83 | 0 | 0 | 0 | 0 | 0
2025-01-10 12:00 | 41.2 | 23.28 | 23.28 | 17.92 | 0 | 0 | 0 | 0 | 0
2025-01-10 13:00 | 41.79 | 36.62 | 36.62 | 5.17 | 0 | 0 | 0 | 0 | 0
2025-01-10 14:00 | 42.46 | 10.28 | 10.28 | 32.18 | 0 | 0 | 0 | 0 | 0
2025-01-10 15:00 | 42.5 | 0.06 | 0.06 | 42.44 | 0 | 0 | 0 | 0 | 0
2025-01-10 16:00 | 43.08 | 0.33 | 0.33 | 42.75 | 0 | 0 | 0 | 0 | 0
2025-01-10 17:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 0 | 0 | 0
2025-01-10 18:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0 | 0 | 0
2025-01-10 19:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0 | 0 | 0
2025-01-10 20:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 0 | 0 | 0
2025-01-10 21:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 0 | 0 | 0
2025-01-10 22:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0 | 0 | 0
2025-01-10 23:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 0 | 0 | 0
2025-01-11 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0 | 0 | 0
2025-01-11 01:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0 | 0 | 0
2025-01-11 02:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 0 | 0 | 0
2025-01-11 03:00 | 36 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0
2025-01-11 04:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 0 | 0 | 0
2025-01-11 05:00 | 36.79 | 0 | 0 | 36.79 | 0 | 0 | 0 | 0 | 0
2025-01-11 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 0 | 0 | 0
2025-01-11 07:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 0 | 0 | 0
2025-01-11 08:00 | 39.78 | 5.3 | 5.3 | 34.47 | 0 | 0 | 0 | 0 | 0
2025-01-11 09:00 | 40.17 | 72.35 | 40.17 | 0 | 0 | 0 | 0 | 32.18 | 0
2025-01-11 10:00 | 40.98 | 70.19 | 40.98 | 0 | 0 | 0 | 0 | 29.21 | 0
2025-01-11 11:00 | 43 | 58.87 | 43 | 0 | 0 | 0 | 0 | 15.87 | 0
2025-01-11 12:00 | 43.66 | 51.69 | 43.66 | 0 | 0 | 0 | 0 | 8.03 | 0
2025-01-11 13:00 | 43.94 | 56.66 | 43.94 | 0 | 0 | 0 | 0 | 12.72 | 0
2025-01-11 14:00 | 45.42 | 67.69 | 45.42 | 0 | 0 | 0 | 0 | 22.26 | 0
2025-01-11 15:00 | 44.63 | 69.51 | 44.63 | 0 | 0 | 0 | 0 | 24.88 | 0
2025-01-11 16:00 | 44.71 | 6.98 | 6.98 | 37.73 | 0 | 0 | 0 | 0 | 0
2025-01-11 17:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 0 | 0 | 0
2025-01-11 18:00 | 43.23 | 0 | 0 | 43.23 | 0 | 0 | 0 | 0 | 0
2025-01-11 19:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 0 | 0 | 0
2025-01-11 20:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 0 | 0 | 0
2025-01-11 21:00 | 40.37 | 0 | 0 | 40.37 | 0 | 0 | 0 | 0 | 0
2025-01-11 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 0 | 0 | 0
2025-01-11 23:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-01-12 | 36.64 | 0 | 0 | 36.64 | 0 | 0 | 0 | 0 | 0
2025-01-12 01:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0 | 0 | 0
2025-01-12 02:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0 | 0 | 0
2025-01-12 03:00 | 36.61 | 0 | 0 | 36.61 | 0 | 0 | 0 | 0 | 0
2025-01-12 04:00 | 35.96 | 0 | 0 | 35.96 | 0 | 0 | 0 | 0 | 0
2025-01-12 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 0 | 0 | 0
2025-01-12 06:00 | 37.7 | 0 | 0 | 37.7 | 0 | 0 | 0 | 0 | 0
2025-01-12 07:00 | 38.5 | 0 | 0 | 38.5 | 0 | 0 | 0 | 0 | 0
2025-01-12 08:00 | 38.94 | 5.94 | 5.94 | 32.99 | 0 | 0 | 0 | 0 | 0
2025-01-12 09:00 | 40.78 | 56.69 | 40.78 | 0 | 0 | 0 | 0 | 15.91 | 0
2025-01-12 10:00 | 41.79 | 54.06 | 41.79 | 0 | 0 | 0 | 0 | 12.27 | 0
2025-01-12 11:00 | 41.77 | 52.16 | 41.77 | 0 | 0 | 0 | 0 | 10.39 | 0
2025-01-12 12:00 | 43.74 | 56.79 | 43.74 | 0 | 0 | 0 | 0 | 13.05 | 0
2025-01-12 13:00 | 45.1 | 63.13 | 45.1 | 0 | 0 | 0 | 0 | 18.04 | 0
2025-01-12 14:00 | 44.59 | 74.02 | 44.59 | 0 | 0 | 0 | 0 | 29.43 | 0
2025-01-12 15:00 | 44.49 | 76.46 | 44.49 | 0 | 0 | 0 | 0 | 31.98 | 0
2025-01-12 16:00 | 44.43 | 14.19 | 14.19 | 30.24 | 0 | 0 | 0 | 0 | 0
2025-01-12 17:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 0 | 0 | 0
2025-01-12 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0 | 0 | 0
2025-01-12 19:00 | 42.6 | 0 | 0 | 42.6 | 0 | 0 | 0 | 0 | 0
2025-01-12 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0 | 0 | 0
2025-01-12 21:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0 | 0 | 0
2025-01-12 22:00 | 39.41 | 0 | 0 | 39.41 | 0 | 0 | 0 | 0 | 0
2025-01-12 23:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 0 | 0 | 0
2025-01-13 | 37.24 | 0 | 0 | 37.24 | 0 | 0 | 0 | 0 | 0
2025-01-13 01:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 0 | 0 | 0
2025-01-13 02:00 | 37.07 | 0 | 0 | 37.07 | 0 | 0 | 0 | 0 | 0
2025-01-13 03:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 0 | 0 | 0
2025-01-13 04:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 0 | 0 | 0
2025-01-13 05:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0 | 0 | 0
2025-01-13 06:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0 | 0 | 0
2025-01-13 07:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0 | 0 | 0
2025-01-13 08:00 | 39.33 | 3.52 | 3.52 | 35.81 | 0 | 0 | 0 | 0 | 0
2025-01-13 09:00 | 39.78 | 36.98 | 36.98 | 2.8 | 0 | 0 | 0 | 0 | 0
2025-01-13 10:00 | 40.96 | 30.12 | 30.12 | 10.84 | 0 | 0 | 0 | 0 | 0
2025-01-13 11:00 | 41.93 | 21.09 | 21.09 | 20.84 | 0 | 0 | 0 | 0 | 0
2025-01-13 12:00 | 41.84 | 13.28 | 13.28 | 28.56 | 0 | 0 | 0 | 0 | 0
2025-01-13 13:00 | 42.44 | 38.06 | 38.06 | 4.38 | 0 | 0 | 0 | 0 | 0
2025-01-13 14:00 | 43.83 | 61.2 | 43.83 | 0 | 0 | 0 | 0 | 17.37 | 0
2025-01-13 15:00 | 43.45 | 70.5 | 43.45 | 0 | 0 | 0 | 0 | 27.05 | 0
2025-01-13 16:00 | 42.31 | 15.81 | 15.81 | 26.5 | 0 | 0 | 0 | 0 | 0
2025-01-13 17:00 | 43.64 | 0 | 0 | 43.64 | 0 | 0 | 0 | 0 | 0
2025-01-13 18:00 | 42.82 | 0 | 0 | 42.82 | 0 | 0 | 0 | 0 | 0
2025-01-13 19:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 0 | 0 | 0
2025-01-13 20:00 | 40.47 | 0 | 0 | 40.47 | 0 | 0 | 0 | 0 | 0
2025-01-13 21:00 | 40.65 | 0 | 0 | 40.65 | 0 | 0 | 0 | 0 | 0
2025-01-13 22:00 | 39.51 | 0 | 0 | 39.51 | 0 | 0 | 0 | 0 | 0
2025-01-13 23:00 | 39.7 | 0 | 0 | 39.7 | 0 | 0 | 0 | 0 | 0
2025-01-14 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0
2025-01-14 01:00 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 0 | 0 | 0
2025-01-14 02:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 0 | 0 | 0
2025-01-14 03:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 0 | 0 | 0
2025-01-14 04:00 | 37.2 | 0 | 0 | 37.2 | 0 | 0 | 0 | 0 | 0
2025-01-14 05:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0 | 0 | 0
2025-01-14 06:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0 | 0 | 0
2025-01-14 07:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0 | 0 | 0
2025-01-14 08:00 | 39.24 | 2.1 | 2.1 | 37.14 | 0 | 0 | 0 | 0 | 0
2025-01-14 09:00 | 40.91 | 0 | 0 | 40.91 | 0 | 0 | 0 | 0 | 0
2025-01-14 10:00 | 42.35 | 23.81 | 23.81 | 18.54 | 0 | 0 | 0 | 0 | 0
2025-01-14 11:00 | 42.42 | 7.58 | 7.58 | 34.84 | 0 | 0 | 0 | 0 | 0
2025-01-14 12:00 | 43.38 | 17.48 | 17.48 | 25.9 | 0 | 0 | 0 | 0 | 0
2025-01-14 13:00 | 44.48 | 31.4 | 31.4 | 13.08 | 0 | 0 | 0 | 0 | 0
2025-01-14 14:00 | 44.67 | 56.66 | 44.67 | 0 | 0 | 0 | 0 | 11.99 | 0
2025-01-14 15:00 | 45.44 | 67.78 | 45.44 | 0 | 0 | 0 | 0 | 22.35 | 0
2025-01-14 16:00 | 43.67 | 15.89 | 15.89 | 27.78 | 0 | 0 | 0 | 0 | 0
2025-01-14 17:00 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 0 | 0 | 0
2025-01-14 18:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 0 | 0 | 0
2025-01-14 19:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-01-14 20:00 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 0 | 0 | 0
2025-01-14 21:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 0 | 0 | 0
2025-01-14 22:00 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 0 | 0 | 0
2025-01-14 23:00 | 39.11 | 0 | 0 | 39.11 | 0 | 0 | 0 | 0 | 0
2025-01-15 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0 | 0 | 0
2025-01-15 01:00 | 36.69 | 0 | 0 | 36.69 | 0 | 0 | 0 | 0 | 0
2025-01-15 02:00 | 36.83 | 0 | 0 | 36.83 | 0 | 0 | 0 | 0 | 0
2025-01-15 03:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 0 | 0 | 0
2025-01-15 04:00 | 36.37 | 0 | 0 | 36.37 | 0 | 0 | 0 | 0 | 0
2025-01-15 05:00 | 36.75 | 0 | 0 | 36.75 | 0 | 0 | 0 | 0 | 0
2025-01-15 06:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 0 | 0 | 0
2025-01-15 07:00 | 38.37 | 0 | 0 | 38.37 | 0 | 0 | 0 | 0 | 0
2025-01-15 08:00 | 39.66 | 5.23 | 5.23 | 34.43 | 0 | 0 | 0 | 0 | 0
2025-01-15 09:00 | 40.27 | 59.3 | 40.27 | 0 | 0 | 0 | 0 | 19.03 | 0
2025-01-15 10:00 | 41.59 | 59.44 | 41.59 | 0 | 0 | 0 | 0 | 17.85 | 0
2025-01-15 11:00 | 41.64 | 52.05 | 41.64 | 0 | 0 | 0 | 0 | 10.41 | 0
2025-01-15 12:00 | 42.95 | 44.11 | 42.95 | 0 | 0 | 0 | 0 | 1.16 | 0
2025-01-15 13:00 | 43.47 | 52.23 | 43.47 | 0 | 0 | 0 | 0 | 8.77 | 0
2025-01-15 14:00 | 43.36 | 36.92 | 36.92 | 6.44 | 0 | 0 | 0 | 0 | 0
2025-01-15 15:00 | 43.32 | 50.39 | 43.32 | 0 | 0 | 0 | 0 | 7.07 | 0
2025-01-15 16:00 | 44.31 | 9.01 | 9.01 | 35.3 | 0 | 0 | 0 | 0 | 0
2025-01-15 17:00 | 43.4 | 0 | 0 | 43.4 | 0 | 0 | 0 | 0 | 0
2025-01-15 18:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0 | 0 | 0
2025-01-15 19:00 | 42.11 | 0 | 0 | 42.11 | 0 | 0 | 0 | 0 | 0
2025-01-15 20:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 0 | 0 | 0
2025-01-15 21:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0 | 0 | 0
2025-01-15 22:00 | 38.59 | 0 | 0 | 38.59 | 0 | 0 | 0 | 0 | 0
2025-01-15 23:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0 | 0 | 0
2025-01-16 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0 | 0 | 0
2025-01-16 01:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0 | 0 | 0
2025-01-16 02:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 0 | 0 | 0
2025-01-16 03:00 | 36.16 | 0 | 0 | 36.16 | 0 | 0 | 0 | 0 | 0
2025-01-16 04:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 0 | 0 | 0
2025-01-16 05:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 0 | 0 | 0
2025-01-16 06:00 | 37.72 | 0 | 0 | 37.72 | 0 | 0 | 0 | 0 | 0
2025-01-16 07:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 0 | 0 | 0
2025-01-16 08:00 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
2025-01-16 09:00 | 39.98 | 0.01 | 0.01 | 39.97 | 0 | 0 | 0 | 0 | 0
2025-01-16 10:00 | 40.65 | 5.61 | 5.61 | 35.04 | 0 | 0 | 0 | 0 | 0
2025-01-16 11:00 | 41.6 | 8.51 | 8.51 | 33.09 | 0 | 0 | 0 | 0 | 0
2025-01-16 12:00 | 42.14 | 9.57 | 9.57 | 32.57 | 0 | 0 | 0 | 0 | 0
2025-01-16 13:00 | 41.31 | 42.62 | 41.31 | 0 | 0 | 0 | 0 | 1.31 | 0
2025-01-16 14:00 | 41.24 | 53.03 | 41.24 | 0 | 0 | 0 | 0 | 11.79 | 0
2025-01-16 15:00 | 42.94 | 35.77 | 35.77 | 7.18 | 0 | 0 | 0 | 0 | 0
2025-01-16 16:00 | 42.96 | 10.06 | 10.06 | 32.89 | 0 | 0 | 0 | 0 | 0
2025-01-16 17:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 0 | 0 | 0
2025-01-16 18:00 | 40.8 | 0 | 0 | 40.8 | 0 | 0 | 0 | 0 | 0
2025-01-16 19:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 0 | 0 | 0
2025-01-16 20:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 0 | 0 | 0
2025-01-16 21:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 0 | 0 | 0
2025-01-16 22:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 0 | 0 | 0
2025-01-16 23:00 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 0 | 0 | 0
2025-01-17 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 0 | 0 | 0
2025-01-17 01:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 0 | 0 | 0
2025-01-17 02:00 | 36.68 | 0 | 0 | 36.68 | 0 | 0 | 0 | 0 | 0
2025-01-17 03:00 | 36.21 | 0 | 0 | 36.21 | 0 | 0 | 0 | 0 | 0
2025-01-17 04:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0 | 0 | 0
2025-01-17 05:00 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 0 | 0 | 0
2025-01-17 06:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-01-17 07:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 0 | 0 | 0
2025-01-17 08:00 | 39.7 | 0.79 | 0.79 | 38.91 | 0 | 0 | 0 | 0 | 0
2025-01-17 09:00 | 40.51 | 0.09 | 0.09 | 40.42 | 0 | 0 | 0 | 0 | 0
2025-01-17 10:00 | 41.35 | 9.46 | 9.46 | 31.89 | 0 | 0 | 0 | 0 | 0
2025-01-17 11:00 | 42.64 | 23.66 | 23.66 | 18.98 | 0 | 0 | 0 | 0 | 0
2025-01-17 12:00 | 43.1 | 26.35 | 26.35 | 16.76 | 0 | 0 | 0 | 0 | 0
2025-01-17 13:00 | 43.76 | 25.24 | 25.24 | 18.52 | 0 | 0 | 0 | 0 | 0
2025-01-17 14:00 | 44.08 | 26.75 | 26.75 | 17.33 | 0 | 0 | 0 | 0 | 0
2025-01-17 15:00 | 44.06 | 15.7 | 15.7 | 28.36 | 0 | 0 | 0 | 0 | 0
2025-01-17 16:00 | 42.87 | 3.54 | 3.54 | 39.33 | 0 | 0 | 0 | 0 | 0
2025-01-17 17:00 | 43.43 | 0 | 0 | 43.43 | 0 | 0 | 0 | 0 | 0
2025-01-17 18:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 0 | 0 | 0
2025-01-17 19:00 | 41.38 | 0 | 0 | 41.38 | 0 | 0 | 0 | 0 | 0
2025-01-17 20:00 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 0 | 0 | 0
2025-01-17 21:00 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 0 | 0 | 0
2025-01-17 22:00 | 39.95 | 0 | 0 | 39.95 | 0 | 0 | 0 | 0 | 0
2025-01-17 23:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 0 | 0 | 0
2025-01-18 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0 | 0 | 0
2025-01-18 01:00 | 37.15 | 0 | 0 | 37.15 | 0 | 0 | 0 | 0 | 0
2025-01-18 02:00 | 36.92 | 0 | 0 | 36.92 | 0 | 0 | 0 | 0 | 0
2025-01-18 03:00 | 36.15 | 0 | 0 | 36.15 | 0 | 0 | 0 | 0 | 0
2025-01-18 04:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 0 | 0 | 0
2025-01-18 05:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 0 | 0 | 0
2025-01-18 06:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 0 | 0 | 0
2025-01-18 07:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-01-18 08:00 | 38.99 | 0.3 | 0.3 | 38.69 | 0 | 0 | 0 | 0 | 0
2025-01-18 09:00 | 40.67 | 3.59 | 3.59 | 37.08 | 0 | 0 | 0 | 0 | 0
2025-01-18 10:00 | 40.92 | 7.21 | 7.21 | 33.7 | 0 | 0 | 0 | 0 | 0
2025-01-18 11:00 | 41.09 | 8.96 | 8.96 | 32.13 | 0 | 0 | 0 | 0 | 0
2025-01-18 12:00 | 41.71 | 10.82 | 10.82 | 30.9 | 0 | 0 | 0 | 0 | 0
2025-01-18 13:00 | 41.98 | 11.55 | 11.55 | 30.43 | 0 | 0 | 0 | 0 | 0
2025-01-18 14:00 | 42.08 | 8.37 | 8.37 | 33.71 | 0 | 0 | 0 | 0 | 0
2025-01-18 15:00 | 41.72 | 4.23 | 4.23 | 37.48 | 0 | 0 | 0 | 0 | 0
2025-01-18 16:00 | 42.11 | 0.33 | 0.33 | 41.78 | 0 | 0 | 0 | 0 | 0
2025-01-18 17:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 0 | 0 | 0
2025-01-18 18:00 | 40.96 | 0 | 0 | 40.96 | 0 | 0 | 0 | 0 | 0
2025-01-18 19:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 0 | 0 | 0
2025-01-18 20:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 0 | 0 | 0
2025-01-18 21:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 0 | 0 | 0
2025-01-18 22:00 | 38.97 | 0 | 0 | 38.97 | 0 | 0 | 0 | 0 | 0
2025-01-18 23:00 | 38.8 | 0 | 0 | 38.8 | 0 | 0 | 0 | 0 | 0
2025-01-19 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 0 | 0 | 0
2025-01-19 01:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0 | 0 | 0
2025-01-19 02:00 | 36.82 | 0 | 0 | 36.82 | 0 | 0 | 0 | 0 | 0
2025-01-19 03:00 | 36.27 | 0 | 0 | 36.27 | 0 | 0 | 0 | 0 | 0
2025-01-19 04:00 | 36.26 | 0 | 0 | 36.26 | 0 | 0 | 0 | 0 | 0
2025-01-19 05:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0 | 0 | 0
2025-01-19 06:00 | 37.88 | 0 | 0 | 37.88 | 0 | 0 | 0 | 0 | 0
2025-01-19 07:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0 | 0 | 0
2025-01-19 08:00 | 39.87 | 0 | 0 | 39.87 | 0 | 0 | 0 | 0 | 0
2025-01-19 09:00 | 40.24 | 2.24 | 2.24 | 38 | 0 | 0 | 0 | 0 | 0
2025-01-19 10:00 | 40.7 | 4.22 | 4.22 | 36.49 | 0 | 0 | 0 | 0 | 0
2025-01-19 11:00 | 42.15 | 5.37 | 5.37 | 36.78 | 0 | 0 | 0 | 0 | 0
2025-01-19 12:00 | 43.29 | 6.56 | 6.56 | 36.73 | 0 | 0 | 0 | 0 | 0
2025-01-19 13:00 | 43.76 | 6.23 | 6.23 | 37.53 | 0 | 0 | 0 | 0 | 0
2025-01-19 14:00 | 44.01 | 5.3 | 5.3 | 38.71 | 0 | 0 | 0 | 0 | 0
2025-01-19 15:00 | 44.57 | 2.67 | 2.67 | 41.9 | 0 | 0 | 0 | 0 | 0
2025-01-19 16:00 | 44.05 | 0.15 | 0.15 | 43.9 | 0 | 0 | 0 | 0 | 0
2025-01-19 17:00 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 0 | 0 | 0
2025-01-19 18:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 0 | 0 | 0
2025-01-19 19:00 | 42.11 | 0 | 0 | 42.11 | 0 | 0 | 0 | 0 | 0
2025-01-19 20:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 0 | 0 | 0
2025-01-19 21:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 0 | 0 | 0
2025-01-19 22:00 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 0 | 0 | 0
2025-01-19 23:00 | 38.19 | 0 | 0 | 38.19 | 0 | 0 | 0 | 0 | 0
2025-01-20 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 0 | 0 | 0
2025-01-20 01:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 0 | 0 | 0
2025-01-20 02:00 | 35.74 | 0 | 0 | 35.74 | 0 | 0 | 0 | 0 | 0
2025-01-20 03:00 | 35.75 | 0 | 0 | 35.75 | 0 | 0 | 0 | 0 | 0
2025-01-20 04:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 0 | 0 | 0
2025-01-20 05:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 0 | 0 | 0
2025-01-20 06:00 | 37.6 | 0 | 0 | 37.6 | 0 | 0 | 0 | 0 | 0
2025-01-20 07:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0 | 0 | 0
2025-01-20 08:00 | 37.81 | 9.17 | 9.17 | 28.65 | 0 | 0 | 0 | 0 | 0
2025-01-20 09:00 | 40.21 | 69.34 | 40.21 | 0 | 0 | 0 | 0 | 29.14 | 0
2025-01-20 10:00 | 41.65 | 61.8 | 41.65 | 0 | 0 | 0 | 0 | 20.16 | 0
2025-01-20 11:00 | 41.1 | 52.27 | 41.1 | 0 | 0 | 0 | 0 | 11.17 | 0
2025-01-20 12:00 | 42.15 | 46.79 | 42.15 | 0 | 0 | 0 | 0 | 4.64 | 0
2025-01-20 13:00 | 42.49 | 53.41 | 42.49 | 0 | 0 | 0 | 0 | 10.92 | 0
2025-01-20 14:00 | 42.75 | 67.67 | 42.75 | 0 | 0 | 0 | 0 | 24.93 | 0
2025-01-20 15:00 | 43.14 | 74.01 | 43.14 | 0 | 0 | 0 | 0 | 30.87 | 0
2025-01-20 16:00 | 43.91 | 27.56 | 27.56 | 16.35 | 0 | 0 | 0 | 0 | 0
2025-01-20 17:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0 | 0 | 0
2025-01-20 18:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 0 | 0 | 0
2025-01-20 19:00 | 42.61 | 0 | 0 | 42.61 | 0 | 0 | 0 | 0 | 0
2025-01-20 20:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 0 | 0 | 0
2025-01-20 21:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 0 | 0 | 0
2025-01-20 22:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 0 | 0 | 0
2025-01-20 23:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 0 | 0 | 0
2025-01-21 | 37.83 | 0 | 0 | 37.83 | 0 | 0 | 0 | 0 | 0
2025-01-21 01:00 | 38.71 | 0 | 0 | 38.71 | 0 | 0 | 0 | 0 | 0
2025-01-21 02:00 | 37.21 | 0 | 0 | 37.21 | 0 | 0 | 0 | 0 | 0
2025-01-21 03:00 | 36.32 | 0 | 0 | 36.32 | 0 | 0 | 0 | 0 | 0
2025-01-21 04:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 0 | 0 | 0
2025-01-21 05:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-01-21 06:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 0 | 0 | 0
2025-01-21 07:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0 | 0 | 0
2025-01-21 08:00 | 39.13 | 9.68 | 9.68 | 29.45 | 0 | 0 | 0 | 0 | 0
2025-01-21 09:00 | 40.1 | 58.65 | 40.1 | 0 | 0 | 0 | 0 | 18.55 | 0
2025-01-21 10:00 | 40.79 | 67.45 | 40.79 | 0 | 0 | 0 | 0 | 26.65 | 0
2025-01-21 11:00 | 41.72 | 56.06 | 41.72 | 0 | 0 | 0 | 0 | 14.34 | 0
2025-01-21 12:00 | 42.42 | 49.51 | 42.42 | 0 | 0 | 0 | 0 | 7.09 | 0
2025-01-21 13:00 | 41.74 | 57.79 | 41.74 | 0 | 0 | 0 | 0 | 16.04 | 0
2025-01-21 14:00 | 43.36 | 65.14 | 43.36 | 0 | 0 | 0 | 0 | 21.78 | 0
2025-01-21 15:00 | 42.64 | 69.7 | 42.64 | 0 | 0 | 0 | 0 | 27.07 | 0
2025-01-21 16:00 | 42.3 | 24.93 | 24.93 | 17.37 | 0 | 0 | 0 | 0 | 0
2025-01-21 17:00 | 42.68 | 0 | 0 | 42.68 | 0 | 0 | 0 | 0 | 0
2025-01-21 18:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 0 | 0 | 0
2025-01-21 19:00 | 41.21 | 0 | 0 | 41.21 | 0 | 0 | 0 | 0 | 0
2025-01-21 20:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 0 | 0 | 0
2025-01-21 21:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0 | 0 | 0
2025-01-21 22:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 0 | 0 | 0
2025-01-21 23:00 | 38.04 | 0 | 0 | 38.04 | 0 | 0 | 0 | 0 | 0
2025-01-22 | 37.6 | 0 | 0 | 37.6 | 0 | 0 | 0 | 0 | 0
2025-01-22 01:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 0 | 0 | 0
2025-01-22 02:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 0 | 0 | 0
2025-01-22 03:00 | 37.03 | 0 | 0 | 37.03 | 0 | 0 | 0 | 0 | 0
2025-01-22 04:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 0 | 0 | 0
2025-01-22 05:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 0 | 0 | 0
2025-01-22 06:00 | 36.65 | 0 | 0 | 36.65 | 0 | 0 | 0 | 0 | 0
2025-01-22 07:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-01-22 08:00 | 38.92 | 10.55 | 10.55 | 28.37 | 0 | 0 | 0 | 0 | 0
2025-01-22 09:00 | 39.75 | 52.26 | 39.75 | 0 | 0 | 0 | 0 | 12.51 | 0
2025-01-22 10:00 | 40.53 | 40.74 | 40.53 | 0 | 0 | 0 | 0 | 0.21 | 0
2025-01-22 11:00 | 41.32 | 32.04 | 32.04 | 9.28 | 0 | 0 | 0 | 0 | 0
2025-01-22 12:00 | 42.24 | 52.65 | 42.24 | 0 | 0 | 0 | 0 | 10.41 | 0
2025-01-22 13:00 | 41.62 | 55.13 | 41.62 | 0 | 0 | 0 | 0 | 13.51 | 0
2025-01-22 14:00 | 41.85 | 40.08 | 40.08 | 1.77 | 0 | 0 | 0 | 0 | 0
2025-01-22 15:00 | 41.97 | 53.58 | 41.97 | 0 | 0 | 0 | 0 | 11.6 | 0
2025-01-22 16:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 0 | 0 | 0
2025-01-22 17:00 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 0 | 0 | 0
2025-01-22 18:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 0 | 0 | 0
2025-01-22 19:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 0 | 0 | 0
2025-01-22 20:00 | 39.69 | 0 | 0 | 39.69 | 0 | 0 | 0 | 0 | 0
2025-01-22 21:00 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 0 | 0 | 0
2025-01-22 22:00 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 0 | 0 | 0
2025-01-22 23:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0 | 0 | 0
2025-01-23 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0 | 0 | 0
2025-01-23 01:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 0 | 0 | 0
2025-01-23 02:00 | 37.31 | 0 | 0 | 37.31 | 0 | 0 | 0 | 0 | 0
2025-01-23 03:00 | 36.33 | 0 | 0 | 36.33 | 0 | 0 | 0 | 0 | 0
2025-01-23 04:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 0 | 0 | 0
2025-01-23 05:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 0 | 0 | 0
2025-01-23 06:00 | 36.91 | 0 | 0 | 36.91 | 0 | 0 | 0 | 0 | 0
2025-01-23 07:00 | 38.62 | 0 | 0 | 38.62 | 0 | 0 | 0 | 0 | 0
2025-01-23 08:00 | 39.39 | 9.01 | 9.01 | 30.38 | 0 | 0 | 0 | 0 | 0
2025-01-23 09:00 | 40.29 | 23.77 | 23.77 | 16.52 | 0 | 0 | 0 | 0 | 0
2025-01-23 10:00 | 42.24 | 43 | 42.24 | 0 | 0 | 0 | 0 | 0.77 | 0
2025-01-23 11:00 | 42.18 | 57.82 | 42.18 | 0 | 0 | 0 | 0 | 15.64 | 0
2025-01-23 12:00 | 44.46 | 53.02 | 44.46 | 0 | 0 | 0 | 0 | 8.56 | 0
2025-01-23 13:00 | 44.05 | 61.04 | 44.05 | 0 | 0 | 0 | 0 | 16.99 | 0
2025-01-23 14:00 | 44 | 36.19 | 36.19 | 7.81 | 0 | 0 | 0 | 0 | 0
2025-01-23 15:00 | 44.84 | 35.58 | 35.58 | 9.26 | 0 | 0 | 0 | 0 | 0
2025-01-23 16:00 | 44.1 | 0 | 0 | 44.1 | 0 | 0 | 0 | 0 | 0
2025-01-23 17:00 | 43.79 | 0 | 0 | 43.79 | 0 | 0 | 0 | 0 | 0
2025-01-23 18:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 0 | 0 | 0
2025-01-23 19:00 | 42.77 | 0 | 0 | 42.77 | 0 | 0 | 0 | 0 | 0
2025-01-23 20:00 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 0 | 0 | 0
2025-01-23 21:00 | 40.86 | 0 | 0 | 40.86 | 0 | 0 | 0 | 0 | 0
2025-01-23 22:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0
2025-01-23 23:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0 | 0 | 0
2025-01-24 | 37.9 | 0 | 0 | 37.9 | 0 | 0 | 0 | 0 | 0
2025-01-24 01:00 | 37.79 | 0 | 0 | 37.79 | 0 | 0 | 0 | 0 | 0
2025-01-24 02:00 | 35.84 | 0 | 0 | 35.84 | 0 | 0 | 0 | 0 | 0
2025-01-24 03:00 | 36.51 | 0 | 0 | 36.51 | 0 | 0 | 0 | 0 | 0
2025-01-24 04:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 0 | 0 | 0
2025-01-24 05:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 0 | 0 | 0
2025-01-24 06:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 0 | 0 | 0
2025-01-24 07:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0 | 0 | 0
2025-01-24 08:00 | 40.05 | 1.02 | 1.02 | 39.03 | 0 | 0 | 0 | 0 | 0
2025-01-24 09:00 | 39.87 | 5.67 | 5.67 | 34.2 | 0 | 0 | 0 | 0 | 0
2025-01-24 10:00 | 41 | 22.28 | 22.28 | 18.72 | 0 | 0 | 0 | 0 | 0
2025-01-24 11:00 | 41.45 | 36.59 | 36.59 | 4.85 | 0 | 0 | 0 | 0 | 0
2025-01-24 12:00 | 42.26 | 30.02 | 30.02 | 12.24 | 0 | 0 | 0 | 0 | 0
2025-01-24 13:00 | 42.73 | 17.07 | 17.07 | 25.66 | 0 | 0 | 0 | 0 | 0
2025-01-24 14:00 | 43.26 | 16.56 | 16.56 | 26.7 | 0 | 0 | 0 | 0 | 0
2025-01-24 15:00 | 43.73 | 0.72 | 0.72 | 43.01 | 0 | 0 | 0 | 0 | 0
2025-01-24 16:00 | 43.86 | 2 | 2 | 41.87 | 0 | 0 | 0 | 0 | 0
2025-01-24 17:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 0 | 0 | 0
2025-01-24 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0 | 0 | 0
2025-01-24 19:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 0 | 0 | 0
2025-01-24 20:00 | 40.75 | 0 | 0 | 40.75 | 0 | 0 | 0 | 0 | 0
2025-01-24 21:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0 | 0 | 0
2025-01-24 22:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 0 | 0 | 0
2025-01-24 23:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0 | 0 | 0
2025-01-25 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0 | 0 | 0
2025-01-25 01:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 0 | 0 | 0
2025-01-25 02:00 | 37.38 | 0 | 0 | 37.38 | 0 | 0 | 0 | 0 | 0
2025-01-25 03:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 0 | 0 | 0
2025-01-25 04:00 | 36.61 | 0 | 0 | 36.61 | 0 | 0 | 0 | 0 | 0
2025-01-25 05:00 | 37.28 | 0 | 0 | 37.28 | 0 | 0 | 0 | 0 | 0
2025-01-25 06:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 0 | 0 | 0
2025-01-25 07:00 | 38.5 | 0 | 0 | 38.5 | 0 | 0 | 0 | 0 | 0
2025-01-25 08:00 | 37.25 | 5.03 | 5.03 | 32.21 | 0 | 0 | 0 | 0 | 0
2025-01-25 09:00 | 39.01 | 57.95 | 39.01 | 0 | 0 | 0 | 0 | 18.94 | 0
2025-01-25 10:00 | 40.89 | 49.89 | 40.89 | 0 | 0 | 0 | 0 | 9 | 0
2025-01-25 11:00 | 41.62 | 38.85 | 38.85 | 2.77 | 0 | 0 | 0 | 0 | 0
2025-01-25 12:00 | 41.41 | 42.63 | 41.41 | 0 | 0 | 0 | 0 | 1.23 | 0
2025-01-25 13:00 | 42.09 | 57.38 | 42.09 | 0 | 0 | 0 | 0 | 15.29 | 0
2025-01-25 14:00 | 43.41 | 37.26 | 37.26 | 6.15 | 0 | 0 | 0 | 0 | 0
2025-01-25 15:00 | 42.58 | 5.07 | 5.07 | 37.51 | 0 | 0 | 0 | 0 | 0
2025-01-25 16:00 | 43.85 | 0 | 0 | 43.85 | 0 | 0 | 0 | 0 | 0
2025-01-25 17:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0 | 0 | 0
2025-01-25 18:00 | 42.19 | 0 | 0 | 42.19 | 0 | 0 | 0 | 0 | 0
2025-01-25 19:00 | 42.19 | 0 | 0 | 42.19 | 0 | 0 | 0 | 0 | 0
2025-01-25 20:00 | 40.73 | 0 | 0 | 40.73 | 0 | 0 | 0 | 0 | 0
2025-01-25 21:00 | 39.37 | 0 | 0 | 39.37 | 0 | 0 | 0 | 0 | 0
2025-01-25 22:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0
2025-01-25 23:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 0 | 0 | 0
2025-01-26 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 0 | 0 | 0
2025-01-26 01:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 0 | 0 | 0
2025-01-26 02:00 | 36.42 | 0 | 0 | 36.42 | 0 | 0 | 0 | 0 | 0
2025-01-26 03:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 0 | 0 | 0
2025-01-26 04:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 0 | 0 | 0
2025-01-26 05:00 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 0 | 0 | 0
2025-01-26 06:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 0 | 0 | 0
2025-01-26 07:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0 | 0 | 0
2025-01-26 08:00 | 39.4 | 3.54 | 3.54 | 35.85 | 0 | 0 | 0 | 0 | 0
2025-01-26 09:00 | 39.41 | 11.53 | 11.53 | 27.88 | 0 | 0 | 0 | 0 | 0
2025-01-26 10:00 | 40.19 | 12.3 | 12.3 | 27.88 | 0 | 0 | 0 | 0 | 0
2025-01-26 11:00 | 42 | 25.7 | 25.7 | 16.29 | 0 | 0 | 0 | 0 | 0
2025-01-26 12:00 | 41.86 | 34.22 | 34.22 | 7.64 | 0 | 0 | 0 | 0 | 0
2025-01-26 13:00 | 41.83 | 44.39 | 41.83 | 0 | 0 | 0 | 0 | 2.56 | 0
2025-01-26 14:00 | 43.05 | 69.02 | 43.05 | 0 | 0 | 0 | 0 | 25.97 | 0
2025-01-26 15:00 | 43.16 | 72.81 | 43.16 | 0 | 0 | 0 | 0 | 29.65 | 0
2025-01-26 16:00 | 42.06 | 33.43 | 33.43 | 8.64 | 0 | 0 | 0 | 0 | 0
2025-01-26 17:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 0 | 0 | 0
2025-01-26 18:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 0 | 0 | 0
2025-01-26 19:00 | 41.63 | 0 | 0 | 41.63 | 0 | 0 | 0 | 0 | 0
2025-01-26 20:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 0 | 0 | 0
2025-01-26 21:00 | 39.2 | 0 | 0 | 39.2 | 0 | 0 | 0 | 0 | 0
2025-01-26 22:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 0 | 0 | 0
2025-01-26 23:00 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 0 | 0 | 0
2025-01-27 | 37.43 | 0 | 0 | 37.43 | 0 | 0 | 0 | 0 | 0
2025-01-27 01:00 | 37.57 | 0 | 0 | 37.57 | 0 | 0 | 0 | 0 | 0
2025-01-27 02:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0 | 0 | 0
2025-01-27 03:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0 | 0 | 0
2025-01-27 04:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0 | 0 | 0
2025-01-27 05:00 | 37.08 | 0 | 0 | 37.08 | 0 | 0 | 0 | 0 | 0
2025-01-27 06:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0 | 0 | 0
2025-01-27 07:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0 | 0 | 0
2025-01-27 08:00 | 39.31 | 2.52 | 2.52 | 36.79 | 0 | 0 | 0 | 0 | 0
2025-01-27 09:00 | 40.25 | 36.71 | 36.71 | 3.54 | 0 | 0 | 0 | 0 | 0
2025-01-27 10:00 | 41.55 | 71.4 | 41.55 | 0 | 0 | 0 | 0 | 29.85 | 0
2025-01-27 11:00 | 42.03 | 48.64 | 42.03 | 0 | 0 | 0 | 0 | 6.62 | 0
2025-01-27 12:00 | 42.49 | 31.4 | 31.4 | 11.09 | 0 | 0 | 0 | 0 | 0
2025-01-27 13:00 | 43.27 | 14.53 | 14.53 | 28.74 | 0 | 0 | 0 | 0 | 0
2025-01-27 14:00 | 44.19 | 8.6 | 8.6 | 35.59 | 0 | 0 | 0 | 0 | 0
2025-01-27 15:00 | 44.01 | 6.22 | 6.22 | 37.79 | 0 | 0 | 0 | 0 | 0
2025-01-27 16:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 0 | 0 | 0
2025-01-27 17:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 0 | 0 | 0
2025-01-27 18:00 | 42.67 | 0 | 0 | 42.67 | 0 | 0 | 0 | 0 | 0
2025-01-27 19:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 0 | 0 | 0
2025-01-27 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0 | 0 | 0
2025-01-27 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0 | 0 | 0
2025-01-27 22:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 0 | 0 | 0
2025-01-27 23:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 0 | 0 | 0
2025-01-28 | 36.85 | 0 | 0 | 36.85 | 0 | 0 | 0 | 0 | 0
2025-01-28 01:00 | 36.62 | 0 | 0 | 36.62 | 0 | 0 | 0 | 0 | 0
2025-01-28 02:00 | 36.29 | 0 | 0 | 36.29 | 0 | 0 | 0 | 0 | 0
2025-01-28 03:00 | 36.71 | 0 | 0 | 36.71 | 0 | 0 | 0 | 0 | 0
2025-01-28 04:00 | 36.67 | 0 | 0 | 36.67 | 0 | 0 | 0 | 0 | 0
2025-01-28 05:00 | 36.97 | 0 | 0 | 36.97 | 0 | 0 | 0 | 0 | 0
2025-01-28 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 0 | 0 | 0
2025-01-28 07:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 0 | 0 | 0
2025-01-28 08:00 | 39.39 | 24.32 | 24.32 | 15.07 | 0 | 0 | 0 | 0 | 0
2025-01-28 09:00 | 40.35 | 69.08 | 40.35 | 0 | 0 | 0 | 0 | 28.72 | 0
2025-01-28 10:00 | 41.39 | 33.94 | 33.94 | 7.45 | 0 | 0 | 0 | 0 | 0
2025-01-28 11:00 | 40.91 | 24.24 | 24.24 | 16.67 | 0 | 0 | 0 | 0 | 0
2025-01-28 12:00 | 42.55 | 28.78 | 28.78 | 13.77 | 0 | 0 | 0 | 0 | 0
2025-01-28 13:00 | 42.23 | 21.07 | 21.07 | 21.16 | 0 | 0 | 0 | 0 | 0
2025-01-28 14:00 | 43.72 | 25.41 | 25.41 | 18.31 | 0 | 0 | 0 | 0 | 0
2025-01-28 15:00 | 43.83 | 45.56 | 43.83 | 0 | 0 | 0 | 0 | 1.74 | 0
2025-01-28 16:00 | 44.22 | 14.25 | 14.25 | 29.97 | 0 | 0 | 0 | 0 | 0
2025-01-28 17:00 | 43.92 | 0 | 0 | 43.92 | 0 | 0 | 0 | 0 | 0
2025-01-28 18:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 0 | 0 | 0
2025-01-28 19:00 | 41.71 | 0 | 0 | 41.71 | 0 | 0 | 0 | 0 | 0
2025-01-28 20:00 | 41.32 | 0 | 0 | 41.32 | 0 | 0 | 0 | 0 | 0
2025-01-28 21:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0 | 0 | 0
2025-01-28 22:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0
2025-01-28 23:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 0 | 0 | 0
2025-01-29 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 0 | 0 | 0
2025-01-29 01:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 0 | 0 | 0
2025-01-29 02:00 | 37.15 | 0 | 0 | 37.15 | 0 | 0 | 0 | 0 | 0
2025-01-29 03:00 | 36.22 | 0 | 0 | 36.22 | 0 | 0 | 0 | 0 | 0
2025-01-29 04:00 | 37.3 | 0 | 0 | 37.3 | 0 | 0 | 0 | 0 | 0
2025-01-29 05:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 0 | 0 | 0
2025-01-29 06:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 0 | 0 | 0
2025-01-29 07:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 0 | 0 | 0
2025-01-29 08:00 | 38.83 | 21.81 | 21.81 | 17.02 | 0 | 0 | 0 | 0 | 0
2025-01-29 09:00 | 39.91 | 72.61 | 39.91 | 0 | 0 | 0 | 0 | 32.7 | 0
2025-01-29 10:00 | 41.4 | 61.64 | 41.4 | 0 | 0 | 0 | 0 | 20.24 | 0
2025-01-29 11:00 | 41.54 | 59.08 | 41.54 | 0 | 0 | 0 | 0 | 17.54 | 0
2025-01-29 12:00 | 43.01 | 52.21 | 43.01 | 0 | 0 | 0 | 0 | 9.2 | 0
2025-01-29 13:00 | 42.78 | 57.38 | 42.78 | 0 | 0 | 0 | 0 | 14.6 | 0
2025-01-29 14:00 | 43.68 | 41.32 | 41.32 | 2.36 | 0 | 0 | 0 | 0 | 0
2025-01-29 15:00 | 43.97 | 40.72 | 40.72 | 3.25 | 0 | 0 | 0 | 0 | 0
2025-01-29 16:00 | 45.01 | 12.53 | 12.53 | 32.47 | 0 | 0 | 0 | 0 | 0
2025-01-29 17:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0 | 0 | 0
2025-01-29 18:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0 | 0 | 0
2025-01-29 19:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0 | 0 | 0
2025-01-29 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0 | 0 | 0
2025-01-29 21:00 | 40.24 | 0 | 0 | 40.24 | 0 | 0 | 0 | 0 | 0
2025-01-29 22:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 0 | 0 | 0
2025-01-29 23:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0 | 0 | 0
2025-01-30 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 0 | 0 | 0
2025-01-30 01:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-01-30 02:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 0 | 0 | 0
2025-01-30 03:00 | 36.39 | 0 | 0 | 36.39 | 0 | 0 | 0 | 0 | 0
2025-01-30 04:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 0 | 0 | 0
2025-01-30 05:00 | 36.63 | 0 | 0 | 36.63 | 0 | 0 | 0 | 0 | 0
2025-01-30 06:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0
2025-01-30 07:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0 | 0 | 0
2025-01-30 08:00 | 39.24 | 14.56 | 14.56 | 24.69 | 0 | 0 | 0 | 0 | 0
2025-01-30 09:00 | 40.11 | 25.94 | 25.94 | 14.17 | 0 | 0 | 0 | 0 | 0
2025-01-30 10:00 | 40.6 | 49.76 | 40.6 | 0 | 0 | 0 | 0 | 9.15 | 0
2025-01-30 11:00 | 41.94 | 49.77 | 41.94 | 0 | 0 | 0 | 0 | 7.82 | 0
2025-01-30 12:00 | 42.05 | 44.9 | 42.05 | 0 | 0 | 0 | 0 | 2.85 | 0
2025-01-30 13:00 | 43 | 53.23 | 43 | 0 | 0 | 0 | 0 | 10.24 | 0
2025-01-30 14:00 | 43.95 | 53.8 | 43.95 | 0 | 0 | 0 | 0 | 9.85 | 0
2025-01-30 15:00 | 44.63 | 65.15 | 44.63 | 0 | 0 | 0 | 0 | 20.52 | 0
2025-01-30 16:00 | 45.24 | 36.99 | 36.99 | 8.26 | 0 | 0 | 0 | 0 | 0
2025-01-30 17:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 0 | 0 | 0
2025-01-30 18:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0 | 0 | 0
2025-01-30 19:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 0 | 0 | 0
2025-01-30 20:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 0 | 0 | 0
2025-01-30 21:00 | 40.43 | 0 | 0 | 40.43 | 0 | 0 | 0 | 0 | 0
2025-01-30 22:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 0 | 0 | 0
2025-01-30 23:00 | 38.48 | 0 | 0 | 38.48 | 0 | 0 | 0 | 0 | 0
2025-01-31 | 37.57 | 0 | 0 | 37.57 | 0 | 0 | 0 | 0 | 0
2025-01-31 01:00 | 36.49 | 0 | 0 | 36.49 | 0 | 0 | 0 | 0 | 0
2025-01-31 02:00 | 36.07 | 0 | 0 | 36.07 | 0 | 0 | 0 | 0 | 0
2025-01-31 03:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 0 | 0 | 0
2025-01-31 04:00 | 36.71 | 0 | 0 | 36.71 | 0 | 0 | 0 | 0 | 0
2025-01-31 05:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 0 | 0 | 0
2025-01-31 06:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0 | 0 | 0
2025-01-31 07:00 | 38.98 | 0 | 0 | 38.98 | 0 | 0 | 0 | 0 | 0
2025-01-31 08:00 | 39.68 | 27.73 | 27.73 | 11.95 | 0 | 0 | 0 | 0 | 0
2025-01-31 09:00 | 40.43 | 79.33 | 40.43 | 0 | 0 | 0 | 0 | 38.9 | 0
2025-01-31 10:00 | 42.63 | 77.95 | 42.63 | 0 | 0 | 0 | 0 | 35.32 | 0
2025-01-31 11:00 | 44.05 | 68.62 | 44.05 | 0 | 0 | 0 | 0 | 24.57 | 0
2025-01-31 12:00 | 44.64 | 61.77 | 44.64 | 0 | 0 | 0 | 0 | 17.13 | 0
2025-01-31 13:00 | 45.79 | 57.65 | 45.79 | 0 | 0 | 0 | 0 | 11.87 | 0
2025-01-31 14:00 | 46.51 | 41.5 | 41.5 | 5.01 | 0 | 0 | 0 | 0 | 0
2025-01-31 15:00 | 46.66 | 17.34 | 17.34 | 29.32 | 0 | 0 | 0 | 0 | 0
2025-01-31 16:00 | 46.2 | 19.84 | 19.84 | 26.35 | 0 | 0 | 0 | 0 | 0
2025-01-31 17:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 0 | 0 | 0
2025-01-31 18:00 | 44.65 | 0 | 0 | 44.65 | 0 | 0 | 0 | 0 | 0
2025-01-31 19:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0 | 0 | 0
2025-01-31 20:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 0 | 0 | 0
2025-01-31 21:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 0 | 0 | 0
2025-01-31 22:00 | 39.19 | 0 | 0 | 39.19 | 0 | 0 | 0 | 0 | 0
2025-01-31 23:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0
2025-02-01 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0 | 0 | 0
2025-02-01 01:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0
2025-02-01 02:00 | 36.73 | 0 | 0 | 36.73 | 0 | 0 | 0 | 0 | 0
2025-02-01 03:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 0 | 0 | 0
2025-02-01 04:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 0 | 0 | 0
2025-02-01 05:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 0 | 0 | 0
2025-02-01 06:00 | 37.77 | 0 | 0 | 37.77 | 0 | 0 | 0 | 0 | 0
2025-02-01 07:00 | 38.98 | 0 | 0 | 38.98 | 0 | 0 | 0 | 0 | 0
2025-02-01 08:00 | 39.01 | 23.06 | 23.06 | 15.96 | 0 | 0 | 0 | 0 | 0
2025-02-01 09:00 | 40.19 | 68.7 | 40.19 | 0 | 0 | 0 | 0 | 28.51 | 0
2025-02-01 10:00 | 40.33 | 69.47 | 40.33 | 0 | 0 | 0 | 0 | 29.15 | 0
2025-02-01 11:00 | 41.78 | 48.34 | 41.78 | 0 | 0 | 0 | 0 | 6.56 | 0
2025-02-01 12:00 | 42.18 | 44.42 | 42.18 | 0 | 0 | 0 | 0 | 2.25 | 0
2025-02-01 13:00 | 42.27 | 53.73 | 42.27 | 0 | 0 | 0 | 0 | 11.46 | 0
2025-02-01 14:00 | 42.82 | 62.52 | 42.82 | 0 | 0 | 0 | 0 | 19.7 | 0
2025-02-01 15:00 | 42.94 | 74.18 | 42.94 | 0 | 0 | 0 | 0 | 31.23 | 0
2025-02-01 16:00 | 42.8 | 40.83 | 40.83 | 1.97 | 0 | 0 | 0 | 0 | 0
2025-02-01 17:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0 | 0 | 0
2025-02-01 18:00 | 42.12 | 0 | 0 | 42.12 | 0 | 0 | 0 | 0 | 0
2025-02-01 19:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 0 | 0 | 0
2025-02-01 20:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 0 | 0 | 0
2025-02-01 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0 | 0 | 0
2025-02-01 22:00 | 39.06 | 0 | 0 | 39.06 | 0 | 0 | 0 | 0 | 0
2025-02-01 23:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 0 | 0 | 0
2025-02-02 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 0 | 0 | 0
2025-02-02 01:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 0 | 0 | 0
2025-02-02 02:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0 | 0 | 0
2025-02-02 03:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 0 | 0 | 0
2025-02-02 04:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 0 | 0 | 0
2025-02-02 05:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 0 | 0 | 0
2025-02-02 06:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 0 | 0 | 0
2025-02-02 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0 | 0 | 0
2025-02-02 08:00 | 38.04 | 36.21 | 36.21 | 1.83 | 0 | 0 | 0 | 0 | 0
2025-02-02 09:00 | 39.01 | 85.37 | 39.01 | 0 | 0 | 0 | 0 | 46.36 | 0
2025-02-02 10:00 | 40.53 | 79.06 | 40.53 | 0 | 0 | 0 | 0 | 38.52 | 0
2025-02-02 11:00 | 41.53 | 15.34 | 15.34 | 26.19 | 0 | 0 | 0 | 0 | 0
2025-02-02 12:00 | 42.47 | 38.81 | 38.81 | 3.66 | 0 | 0 | 0 | 0 | 0
2025-02-02 13:00 | 42.81 | 62.9 | 42.81 | 0 | 0 | 0 | 0 | 20.09 | 0
2025-02-02 14:00 | 42.66 | 72.15 | 42.66 | 0 | 0 | 0 | 0 | 29.48 | 0
2025-02-02 15:00 | 43.46 | 56.47 | 43.46 | 0 | 0 | 0 | 0 | 13.01 | 0
2025-02-02 16:00 | 43.37 | 45.51 | 43.37 | 0 | 0 | 0 | 0 | 2.14 | 0
2025-02-02 17:00 | 42.67 | 0 | 0 | 42.67 | 0 | 0 | 0 | 0 | 0
2025-02-02 18:00 | 42.6 | 0 | 0 | 42.6 | 0 | 0 | 0 | 0 | 0
2025-02-02 19:00 | 41.66 | 0 | 0 | 41.66 | 0 | 0 | 0 | 0 | 0
2025-02-02 20:00 | 40.52 | 0 | 0 | 40.52 | 0 | 0 | 0 | 0 | 0
2025-02-02 21:00 | 40.36 | 0 | 0 | 40.36 | 0 | 0 | 0 | 0 | 0
2025-02-02 22:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 0 | 0 | 0
2025-02-02 23:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0 | 0 | 0
2025-02-03 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 0 | 0 | 0
2025-02-03 01:00 | 36.02 | 0 | 0 | 36.02 | 0 | 0 | 0 | 0 | 0
2025-02-03 02:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 0 | 0 | 0
2025-02-03 03:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 0 | 0 | 0
2025-02-03 04:00 | 36.72 | 0 | 0 | 36.72 | 0 | 0 | 0 | 0 | 0
2025-02-03 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 0 | 0 | 0
2025-02-03 06:00 | 37.02 | 0 | 0 | 37.02 | 0 | 0 | 0 | 0 | 0
2025-02-03 07:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 0 | 0 | 0
2025-02-03 08:00 | 38.76 | 1.4 | 1.4 | 37.35 | 0 | 0 | 0 | 0 | 0
2025-02-03 09:00 | 41.19 | 8.34 | 8.34 | 32.85 | 0 | 0 | 0 | 0 | 0
2025-02-03 10:00 | 41.6 | 11.46 | 11.46 | 30.14 | 0 | 0 | 0 | 0 | 0
2025-02-03 11:00 | 41.15 | 28.92 | 28.92 | 12.23 | 0 | 0 | 0 | 0 | 0
2025-02-03 12:00 | 41.72 | 31.18 | 31.18 | 10.54 | 0 | 0 | 0 | 0 | 0
2025-02-03 13:00 | 41.73 | 38.39 | 38.39 | 3.34 | 0 | 0 | 0 | 0 | 0
2025-02-03 14:00 | 41.59 | 28.73 | 28.73 | 12.86 | 0 | 0 | 0 | 0 | 0
2025-02-03 15:00 | 42.57 | 22.59 | 22.59 | 19.98 | 0 | 0 | 0 | 0 | 0
2025-02-03 16:00 | 42.05 | 44.68 | 42.05 | 0 | 0 | 0 | 0 | 2.63 | 0
2025-02-03 17:00 | 42.26 | 0.56 | 0.56 | 41.7 | 0 | 0 | 0 | 0 | 0
2025-02-03 18:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 0 | 0 | 0
2025-02-03 19:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 0 | 0 | 0
2025-02-03 20:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 0 | 0 | 0
2025-02-03 21:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 0 | 0 | 0
2025-02-03 22:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 0 | 0 | 0
2025-02-03 23:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0 | 0 | 0
2025-02-04 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 0 | 0 | 0
2025-02-04 01:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 0 | 0 | 0
2025-02-04 02:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 0 | 0 | 0
2025-02-04 03:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 0 | 0 | 0
2025-02-04 04:00 | 36.24 | 0 | 0 | 36.24 | 0 | 0 | 0 | 0 | 0
2025-02-04 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 0 | 0 | 0
2025-02-04 06:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0 | 0 | 0
2025-02-04 07:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 0 | 0 | 0
2025-02-04 08:00 | 39.4 | 4.79 | 4.79 | 34.61 | 0 | 0 | 0 | 0 | 0
2025-02-04 09:00 | 41.21 | 25.48 | 25.48 | 15.73 | 0 | 0 | 0 | 0 | 0
2025-02-04 10:00 | 41.95 | 40.94 | 40.94 | 1.01 | 0 | 0 | 0 | 0 | 0
2025-02-04 11:00 | 42.27 | 15.3 | 15.3 | 26.98 | 0 | 0 | 0 | 0 | 0
2025-02-04 12:00 | 43.61 | 27.48 | 27.48 | 16.14 | 0 | 0 | 0 | 0 | 0
2025-02-04 13:00 | 44.86 | 20.15 | 20.15 | 24.71 | 0 | 0 | 0 | 0 | 0
2025-02-04 14:00 | 45.29 | 22.48 | 22.48 | 22.81 | 0 | 0 | 0 | 0 | 0
2025-02-04 15:00 | 43.84 | 12.55 | 12.55 | 31.29 | 0 | 0 | 0 | 0 | 0
2025-02-04 16:00 | 43.85 | 9.39 | 9.39 | 34.46 | 0 | 0 | 0 | 0 | 0
2025-02-04 17:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 0 | 0 | 0
2025-02-04 18:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0 | 0 | 0
2025-02-04 19:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0 | 0 | 0
2025-02-04 20:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 0 | 0 | 0
2025-02-04 21:00 | 40.65 | 0 | 0 | 40.65 | 0 | 0 | 0 | 0 | 0
2025-02-04 22:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0 | 0 | 0
2025-02-04 23:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 0 | 0 | 0
2025-02-05 | 37.55 | 0 | 0 | 37.55 | 0 | 0 | 0 | 0 | 0
2025-02-05 01:00 | 36.95 | 0 | 0 | 36.95 | 0 | 0 | 0 | 0 | 0
2025-02-05 02:00 | 36.52 | 0 | 0 | 36.52 | 0 | 0 | 0 | 0 | 0
2025-02-05 03:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 0 | 0 | 0
2025-02-05 04:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 0 | 0 | 0
2025-02-05 05:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 0 | 0 | 0
2025-02-05 06:00 | 37.64 | 0 | 0 | 37.64 | 0 | 0 | 0 | 0 | 0
2025-02-05 07:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 0 | 0 | 0
2025-02-05 08:00 | 39.24 | 12.08 | 12.08 | 27.16 | 0 | 0 | 0 | 0 | 0
2025-02-05 09:00 | 39.32 | 13.84 | 13.84 | 25.48 | 0 | 0 | 0 | 0 | 0
2025-02-05 10:00 | 41.06 | 36.55 | 36.55 | 4.51 | 0 | 0 | 0 | 0 | 0
2025-02-05 11:00 | 41.91 | 36.66 | 36.66 | 5.25 | 0 | 0 | 0 | 0 | 0
2025-02-05 12:00 | 42.64 | 43.01 | 42.64 | 0 | 0 | 0 | 0 | 0.37 | 0
2025-02-05 13:00 | 43.92 | 42.44 | 42.44 | 1.48 | 0 | 0 | 0 | 0 | 0
2025-02-05 14:00 | 45.66 | 37.58 | 37.58 | 8.08 | 0 | 0 | 0 | 0 | 0
2025-02-05 15:00 | 45.14 | 29.01 | 29.01 | 16.13 | 0 | 0 | 0 | 0 | 0
2025-02-05 16:00 | 45.64 | 40.98 | 40.98 | 4.67 | 0 | 0 | 0 | 0 | 0
2025-02-05 17:00 | 44.72 | 1.01 | 1.01 | 43.71 | 0 | 0 | 0 | 0 | 0
2025-02-05 18:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 0 | 0 | 0
2025-02-05 19:00 | 42.37 | 0 | 0 | 42.37 | 0 | 0 | 0 | 0 | 0
2025-02-05 20:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 0 | 0 | 0
2025-02-05 21:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0 | 0 | 0
2025-02-05 22:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 0 | 0 | 0
2025-02-05 23:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 0 | 0 | 0
2025-02-06 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 0 | 0 | 0
2025-02-06 01:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 0 | 0 | 0
2025-02-06 02:00 | 36.43 | 0 | 0 | 36.43 | 0 | 0 | 0 | 0 | 0
2025-02-06 03:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 0 | 0 | 0
2025-02-06 04:00 | 37.03 | 0 | 0 | 37.03 | 0 | 0 | 0 | 0 | 0
2025-02-06 05:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 0 | 0 | 0
2025-02-06 06:00 | 37.49 | 0 | 0 | 37.49 | 0 | 0 | 0 | 0 | 0
2025-02-06 07:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0 | 0 | 0
2025-02-06 08:00 | 39.71 | 41.09 | 39.71 | 0 | 0 | 0 | 0 | 1.38 | 0
2025-02-06 09:00 | 40.62 | 89.38 | 40.62 | 0 | 0 | 0 | 0 | 48.76 | 0
2025-02-06 10:00 | 41.97 | 84.52 | 41.97 | 0 | 0 | 0 | 0 | 42.55 | 0
2025-02-06 11:00 | 42.64 | 75.48 | 42.64 | 0 | 0 | 0 | 0 | 32.84 | 0
2025-02-06 12:00 | 42.2 | 67.93 | 42.2 | 0 | 0 | 0 | 0 | 25.73 | 0
2025-02-06 13:00 | 44.08 | 72.02 | 44.08 | 0 | 0 | 0 | 0 | 27.94 | 0
2025-02-06 14:00 | 43.3 | 81.8 | 43.3 | 0 | 0 | 0 | 0 | 38.49 | 0
2025-02-06 15:00 | 44.21 | 88.01 | 44.21 | 0 | 0 | 0 | 0 | 43.81 | 0
2025-02-06 16:00 | 43.6 | 62.85 | 43.6 | 0 | 0 | 0 | 0 | 19.25 | 0
2025-02-06 17:00 | 43.03 | 0.62 | 0.62 | 42.41 | 0 | 0 | 0 | 0 | 0
2025-02-06 18:00 | 41.8 | 0 | 0 | 41.8 | 0 | 0 | 0 | 0 | 0
2025-02-06 19:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 0 | 0 | 0
2025-02-06 20:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0 | 0 | 0
2025-02-06 21:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0 | 0 | 0
2025-02-06 22:00 | 40.19 | 0 | 0 | 40.19 | 0 | 0 | 0 | 0 | 0
2025-02-06 23:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0 | 0 | 0
2025-02-07 | 38.05 | 0 | 0 | 38.05 | 0 | 0 | 0 | 0 | 0
2025-02-07 01:00 | 37 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0
2025-02-07 02:00 | 36.7 | 0 | 0 | 36.7 | 0 | 0 | 0 | 0 | 0
2025-02-07 03:00 | 37.29 | 0 | 0 | 37.29 | 0 | 0 | 0 | 0 | 0
2025-02-07 04:00 | 37 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0
2025-02-07 05:00 | 38.23 | 0 | 0 | 38.23 | 0 | 0 | 0 | 0 | 0
2025-02-07 06:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0 | 0 | 0
2025-02-07 07:00 | 39.08 | 0 | 0 | 39.08 | 0 | 0 | 0 | 0 | 0
2025-02-07 08:00 | 39.4 | 40.97 | 39.4 | 0 | 0 | 0 | 0 | 1.58 | 0
2025-02-07 09:00 | 40.53 | 68.45 | 40.53 | 0 | 0 | 0 | 0 | 27.91 | 0
2025-02-07 10:00 | 40.66 | 15.93 | 15.93 | 24.73 | 0 | 0 | 0 | 0 | 0
2025-02-07 11:00 | 41.53 | 48.48 | 41.53 | 0 | 0 | 0 | 0 | 6.95 | 0
2025-02-07 12:00 | 42.05 | 63 | 42.05 | 0 | 0 | 0 | 0 | 20.95 | 0
2025-02-07 13:00 | 42.09 | 79.24 | 42.09 | 0 | 0 | 0 | 0 | 37.14 | 0
2025-02-07 14:00 | 43.09 | 78.03 | 43.09 | 0 | 0 | 0 | 0 | 34.94 | 0
2025-02-07 15:00 | 43.17 | 55.39 | 43.17 | 0 | 0 | 0 | 0 | 12.22 | 0
2025-02-07 16:00 | 43.06 | 0.15 | 0.15 | 42.91 | 0 | 0 | 0 | 0 | 0
2025-02-07 17:00 | 43.28 | 0 | 0 | 43.28 | 0 | 0 | 0 | 0 | 0
2025-02-07 18:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 0 | 0 | 0
2025-02-07 19:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 0 | 0 | 0
2025-02-07 20:00 | 41.07 | 0 | 0 | 41.07 | 0 | 0 | 0 | 0 | 0
2025-02-07 21:00 | 39.82 | 0 | 0 | 39.82 | 0 | 0 | 0 | 0 | 0
2025-02-07 22:00 | 39.36 | 0 | 0 | 39.36 | 0 | 0 | 0 | 0 | 0
2025-02-07 23:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-02-08 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 0 | 0 | 0
2025-02-08 01:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0 | 0 | 0
2025-02-08 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-02-08 03:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0 | 0 | 0
2025-02-08 04:00 | 35.97 | 0 | 0 | 35.97 | 0 | 0 | 0 | 0 | 0
2025-02-08 05:00 | 36.39 | 0 | 0 | 36.39 | 0 | 0 | 0 | 0 | 0
2025-02-08 06:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0 | 0 | 0
2025-02-08 07:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 0 | 0 | 0
2025-02-08 08:00 | 39.53 | 26.24 | 26.24 | 13.28 | 0 | 0 | 0 | 0 | 0
2025-02-08 09:00 | 39.53 | 62.76 | 39.53 | 0 | 0 | 0 | 0 | 23.23 | 0
2025-02-08 10:00 | 40.94 | 69.38 | 40.94 | 0 | 0 | 0 | 0 | 28.44 | 0
2025-02-08 11:00 | 42.63 | 64.2 | 42.63 | 0 | 0 | 0 | 0 | 21.57 | 0
2025-02-08 12:00 | 42.6 | 58.78 | 42.6 | 0 | 0 | 0 | 0 | 16.18 | 0
2025-02-08 13:00 | 42.68 | 68.03 | 42.68 | 0 | 0 | 0 | 0 | 25.35 | 0
2025-02-08 14:00 | 42.63 | 68.69 | 42.63 | 0 | 0 | 0 | 0 | 26.06 | 0
2025-02-08 15:00 | 42.74 | 76.88 | 42.74 | 0 | 0 | 0 | 0 | 34.14 | 0
2025-02-08 16:00 | 41.79 | 59.93 | 41.79 | 0 | 0 | 0 | 0 | 18.14 | 0
2025-02-08 17:00 | 42.73 | 0.95 | 0.95 | 41.77 | 0 | 0 | 0 | 0 | 0
2025-02-08 18:00 | 42.61 | 0 | 0 | 42.61 | 0 | 0 | 0 | 0 | 0
2025-02-08 19:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0 | 0 | 0
2025-02-08 20:00 | 40.62 | 0 | 0 | 40.62 | 0 | 0 | 0 | 0 | 0
2025-02-08 21:00 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 0 | 0 | 0
2025-02-08 22:00 | 38.92 | 0 | 0 | 38.92 | 0 | 0 | 0 | 0 | 0
2025-02-08 23:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 0 | 0 | 0
2025-02-09 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 0 | 0 | 0
2025-02-09 01:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 0 | 0 | 0
2025-02-09 02:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 0 | 0 | 0
2025-02-09 03:00 | 36.84 | 0 | 0 | 36.84 | 0 | 0 | 0 | 0 | 0
2025-02-09 04:00 | 35.85 | 0 | 0 | 35.85 | 0 | 0 | 0 | 0 | 0
2025-02-09 05:00 | 36.95 | 0 | 0 | 36.95 | 0 | 0 | 0 | 0 | 0
2025-02-09 06:00 | 38.64 | 0 | 0 | 38.64 | 0 | 0 | 0 | 0 | 0
2025-02-09 07:00 | 37.41 | 0 | 0 | 37.41 | 0 | 0 | 0 | 0 | 0
2025-02-09 08:00 | 39.54 | 5.15 | 5.15 | 34.38 | 0 | 0 | 0 | 0 | 0
2025-02-09 09:00 | 40.14 | 46.9 | 40.14 | 0 | 0 | 0 | 0 | 6.76 | 0
2025-02-09 10:00 | 42.17 | 63.94 | 42.17 | 0 | 0 | 0 | 0 | 21.77 | 0
2025-02-09 11:00 | 42.42 | 80.13 | 42.42 | 0 | 0 | 0 | 0 | 37.71 | 0
2025-02-09 12:00 | 43.84 | 68.89 | 43.84 | 0 | 0 | 0 | 0 | 25.05 | 0
2025-02-09 13:00 | 44.6 | 37.37 | 37.37 | 7.23 | 0 | 0 | 0 | 0 | 0
2025-02-09 14:00 | 45.67 | 11.68 | 11.68 | 33.99 | 0 | 0 | 0 | 0 | 0
2025-02-09 15:00 | 44.8 | 13.07 | 13.07 | 31.73 | 0 | 0 | 0 | 0 | 0
2025-02-09 16:00 | 44.94 | 0.1 | 0.1 | 44.83 | 0 | 0 | 0 | 0 | 0
2025-02-09 17:00 | 43.57 | 0.4 | 0.4 | 43.17 | 0 | 0 | 0 | 0 | 0
2025-02-09 18:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 0 | 0 | 0
2025-02-09 19:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 0 | 0 | 0
2025-02-09 20:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-02-09 21:00 | 40.71 | 0 | 0 | 40.71 | 0 | 0 | 0 | 0 | 0
2025-02-09 22:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0 | 0 | 0
2025-02-09 23:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 0 | 0 | 0
2025-02-10 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 0 | 0 | 0
2025-02-10 01:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0 | 0 | 0
2025-02-10 02:00 | 36.33 | 0 | 0 | 36.33 | 0 | 0 | 0 | 0 | 0
2025-02-10 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-02-10 04:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 0 | 0 | 0
2025-02-10 05:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 0 | 0 | 0
2025-02-10 06:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 0 | 0 | 0
2025-02-10 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0 | 0 | 0
2025-02-10 08:00 | 39.92 | 46.69 | 39.92 | 0 | 0 | 0 | 0 | 6.77 | 0
2025-02-10 09:00 | 41.03 | 87.4 | 41.03 | 0 | 0 | 0 | 0 | 46.38 | 0
2025-02-10 10:00 | 42.82 | 83.84 | 42.82 | 0 | 0 | 0 | 0 | 41.02 | 0
2025-02-10 11:00 | 43.14 | 73.06 | 43.14 | 0 | 0 | 0 | 0 | 29.91 | 0
2025-02-10 12:00 | 44.14 | 67.79 | 44.14 | 0 | 0 | 0 | 0 | 23.65 | 0
2025-02-10 13:00 | 45.87 | 71.3 | 45.87 | 0 | 0 | 0 | 0 | 25.43 | 0
2025-02-10 14:00 | 44.86 | 79.67 | 44.86 | 0 | 0 | 0 | 0 | 34.82 | 0
2025-02-10 15:00 | 44.72 | 84.97 | 44.72 | 0 | 0 | 0 | 0 | 40.25 | 0
2025-02-10 16:00 | 45.18 | 63.83 | 45.18 | 0 | 0 | 0 | 0 | 18.65 | 0
2025-02-10 17:00 | 44.73 | 1.37 | 1.37 | 43.36 | 0 | 0 | 0 | 0 | 0
2025-02-10 18:00 | 43.54 | 0 | 0 | 43.54 | 0 | 0 | 0 | 0 | 0
2025-02-10 19:00 | 42.39 | 0 | 0 | 42.39 | 0 | 0 | 0 | 0 | 0
2025-02-10 20:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 0 | 0 | 0
2025-02-10 21:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 0 | 0 | 0
2025-02-10 22:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0 | 0 | 0
2025-02-10 23:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 0 | 0 | 0
2025-02-11 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 0 | 0 | 0
2025-02-11 01:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 0 | 0 | 0
2025-02-11 02:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0 | 0 | 0
2025-02-11 03:00 | 36.4 | 0 | 0 | 36.4 | 0 | 0 | 0 | 0 | 0
2025-02-11 04:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 0 | 0 | 0
2025-02-11 05:00 | 38.49 | 0 | 0 | 38.49 | 0 | 0 | 0 | 0 | 0
2025-02-11 06:00 | 38.35 | 0 | 0 | 38.35 | 0 | 0 | 0 | 0 | 0
2025-02-11 07:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 0 | 0 | 0
2025-02-11 08:00 | 39.56 | 27.92 | 27.92 | 11.64 | 0 | 0 | 0 | 0 | 0
2025-02-11 09:00 | 40.62 | 20.51 | 20.51 | 20.11 | 0 | 0 | 0 | 0 | 0
2025-02-11 10:00 | 41.74 | 38.6 | 38.6 | 3.14 | 0 | 0 | 0 | 0 | 0
2025-02-11 11:00 | 42.66 | 44.1 | 42.66 | 0 | 0 | 0 | 0 | 1.44 | 0
2025-02-11 12:00 | 44.17 | 33.39 | 33.39 | 10.78 | 0 | 0 | 0 | 0 | 0
2025-02-11 13:00 | 43.52 | 54.17 | 43.52 | 0 | 0 | 0 | 0 | 10.65 | 0
2025-02-11 14:00 | 45.24 | 73.51 | 45.24 | 0 | 0 | 0 | 0 | 28.27 | 0
2025-02-11 15:00 | 44.77 | 96.26 | 44.77 | 0 | 0 | 0 | 0 | 51.49 | 0
2025-02-11 16:00 | 45 | 71.46 | 45 | 0 | 0 | 0 | 0 | 26.46 | 0
2025-02-11 17:00 | 43.82 | 4.65 | 4.65 | 39.17 | 0 | 0 | 0 | 0 | 0
2025-02-11 18:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 0 | 0 | 0
2025-02-11 19:00 | 43.47 | 0 | 0 | 43.47 | 0 | 0 | 0 | 0 | 0
2025-02-11 20:00 | 42.34 | 0 | 0 | 42.34 | 0 | 0 | 0 | 0 | 0
2025-02-11 21:00 | 40.07 | 0 | 0 | 40.07 | 0 | 0 | 0 | 0 | 0
2025-02-11 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 0 | 0 | 0
2025-02-11 23:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 0 | 0 | 0
2025-02-12 | 37.33 | 0 | 0 | 37.33 | 0 | 0 | 0 | 0 | 0
2025-02-12 01:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 0 | 0 | 0
2025-02-12 02:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 0 | 0 | 0
2025-02-12 03:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 0 | 0 | 0
2025-02-12 04:00 | 37.3 | 0 | 0 | 37.3 | 0 | 0 | 0 | 0 | 0
2025-02-12 05:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 0 | 0 | 0
2025-02-12 06:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 0 | 0 | 0
2025-02-12 07:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 0 | 0 | 0
2025-02-12 08:00 | 38.23 | 20.27 | 20.27 | 17.96 | 0 | 0 | 0 | 0 | 0
2025-02-12 09:00 | 40.34 | 44.77 | 40.34 | 0 | 0 | 0 | 0 | 4.43 | 0
2025-02-12 10:00 | 41.23 | 20.02 | 20.02 | 21.21 | 0 | 0 | 0 | 0 | 0
2025-02-12 11:00 | 41.17 | 29.6 | 29.6 | 11.58 | 0 | 0 | 0 | 0 | 0
2025-02-12 12:00 | 42.7 | 16.46 | 16.46 | 26.24 | 0 | 0 | 0 | 0 | 0
2025-02-12 13:00 | 43.74 | 49.2 | 43.74 | 0 | 0 | 0 | 0 | 5.47 | 0
2025-02-12 14:00 | 42.85 | 92.14 | 42.85 | 0 | 0 | 0 | 0 | 49.29 | 0
2025-02-12 15:00 | 43.65 | 100.86 | 43.65 | 0 | 0 | 0 | 0 | 57.21 | 0
2025-02-12 16:00 | 42.93 | 83.76 | 42.93 | 0 | 0 | 0 | 0 | 40.83 | 0
2025-02-12 17:00 | 42.78 | 5.42 | 5.42 | 37.36 | 0 | 0 | 0 | 0 | 0
2025-02-12 18:00 | 43.4 | 0 | 0 | 43.4 | 0 | 0 | 0 | 0 | 0
2025-02-12 19:00 | 41.78 | 0 | 0 | 41.78 | 0 | 0 | 0 | 0 | 0
2025-02-12 20:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 0 | 0 | 0
2025-02-12 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0 | 0 | 0
2025-02-12 22:00 | 40.59 | 0 | 0 | 40.59 | 0 | 0 | 0 | 0 | 0
2025-02-12 23:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0 | 0 | 0
2025-02-13 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-02-13 01:00 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 0 | 0 | 0
2025-02-13 02:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 0 | 0 | 0
2025-02-13 03:00 | 37.72 | 0 | 0 | 37.72 | 0 | 0 | 0 | 0 | 0
2025-02-13 04:00 | 37.09 | 0 | 0 | 37.09 | 0 | 0 | 0 | 0 | 0
2025-02-13 05:00 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 0 | 0 | 0
2025-02-13 06:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 0 | 0 | 0
2025-02-13 07:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 0 | 0 | 0
2025-02-13 08:00 | 40.24 | 8.21 | 8.21 | 32.02 | 0 | 0 | 0 | 0 | 0
2025-02-13 09:00 | 41 | 16.36 | 16.36 | 24.64 | 0 | 0 | 0 | 0 | 0
2025-02-13 10:00 | 42.19 | 6.13 | 6.13 | 36.06 | 0 | 0 | 0 | 0 | 0
2025-02-13 11:00 | 42.8 | 51.45 | 42.8 | 0 | 0 | 0 | 0 | 8.65 | 0
2025-02-13 12:00 | 43.87 | 68.26 | 43.87 | 0 | 0 | 0 | 0 | 24.39 | 0
2025-02-13 13:00 | 44.03 | 64.78 | 44.03 | 0 | 0 | 0 | 0 | 20.75 | 0
2025-02-13 14:00 | 45.75 | 59.18 | 45.75 | 0 | 0 | 0 | 0 | 13.43 | 0
2025-02-13 15:00 | 43.99 | 25.63 | 25.63 | 18.36 | 0 | 0 | 0 | 0 | 0
2025-02-13 16:00 | 45.26 | 54.09 | 45.26 | 0 | 0 | 0 | 0 | 8.82 | 0
2025-02-13 17:00 | 44.92 | 1.17 | 1.17 | 43.76 | 0 | 0 | 0 | 0 | 0
2025-02-13 18:00 | 43.19 | 0 | 0 | 43.19 | 0 | 0 | 0 | 0 | 0
2025-02-13 19:00 | 43.92 | 0 | 0 | 43.92 | 0 | 0 | 0 | 0 | 0
2025-02-13 20:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 0 | 0 | 0
2025-02-13 21:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 0 | 0 | 0
2025-02-13 22:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 0 | 0 | 0
2025-02-13 23:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 0 | 0 | 0
2025-02-14 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 0 | 0 | 0
2025-02-14 01:00 | 37.87 | 0 | 0 | 37.87 | 0 | 0 | 0 | 0 | 0
2025-02-14 02:00 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0
2025-02-14 03:00 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 0 | 0 | 0
2025-02-14 04:00 | 36.84 | 0 | 0 | 36.84 | 0 | 0 | 0 | 0 | 0
2025-02-14 05:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0 | 0 | 0
2025-02-14 06:00 | 38.72 | 0 | 0 | 38.72 | 0 | 0 | 0 | 0 | 0
2025-02-14 07:00 | 39.36 | 0 | 0 | 39.36 | 0 | 0 | 0 | 0 | 0
2025-02-14 08:00 | 40.31 | 13.51 | 13.51 | 26.8 | 0 | 0 | 0 | 0 | 0
2025-02-14 09:00 | 40.78 | 1.76 | 1.76 | 39.02 | 0 | 0 | 0 | 0 | 0
2025-02-14 10:00 | 41.43 | 45.83 | 41.43 | 0 | 0 | 0 | 0 | 4.41 | 0
2025-02-14 11:00 | 42.38 | 31.82 | 31.82 | 10.56 | 0 | 0 | 0 | 0 | 0
2025-02-14 12:00 | 42.79 | 34.43 | 34.43 | 8.36 | 0 | 0 | 0 | 0 | 0
2025-02-14 13:00 | 44.33 | 34.05 | 34.05 | 10.28 | 0 | 0 | 0 | 0 | 0
2025-02-14 14:00 | 44.56 | 22.54 | 22.54 | 22.02 | 0 | 0 | 0 | 0 | 0
2025-02-14 15:00 | 44.51 | 53.08 | 44.51 | 0 | 0 | 0 | 0 | 8.57 | 0
2025-02-14 16:00 | 43.12 | 59.61 | 43.12 | 0 | 0 | 0 | 0 | 16.49 | 0
2025-02-14 17:00 | 43.59 | 0.97 | 0.97 | 42.62 | 0 | 0 | 0 | 0 | 0
2025-02-14 18:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 0 | 0 | 0
2025-02-14 19:00 | 42.48 | 0 | 0 | 42.48 | 0 | 0 | 0 | 0 | 0
2025-02-14 20:00 | 42.07 | 0 | 0 | 42.07 | 0 | 0 | 0 | 0 | 0
2025-02-14 21:00 | 40.22 | 0 | 0 | 40.22 | 0 | 0 | 0 | 0 | 0
2025-02-14 22:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 0 | 0 | 0
2025-02-14 23:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0 | 0 | 0
2025-02-15 | 38.47 | 0 | 0 | 38.47 | 0 | 0 | 0 | 0 | 0
2025-02-15 01:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 0 | 0 | 0
2025-02-15 02:00 | 38.11 | 0 | 0 | 38.11 | 0 | 0 | 0 | 0 | 0
2025-02-15 03:00 | 37.07 | 0 | 0 | 37.07 | 0 | 0 | 0 | 0 | 0
2025-02-15 04:00 | 37.05 | 0 | 0 | 37.05 | 0 | 0 | 0 | 0 | 0
2025-02-15 05:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 0 | 0 | 0
2025-02-15 06:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 0 | 0 | 0
2025-02-15 07:00 | 39.06 | 0.02 | 0.02 | 39.03 | 0 | 0 | 0 | 0 | 0
2025-02-15 08:00 | 39.83 | 23.32 | 23.32 | 16.51 | 0 | 0 | 0 | 0 | 0
2025-02-15 09:00 | 41.76 | 68.23 | 41.76 | 0 | 0 | 0 | 0 | 26.46 | 0
2025-02-15 10:00 | 41.98 | 71.9 | 41.98 | 0 | 0 | 0 | 0 | 29.91 | 0
2025-02-15 11:00 | 44.14 | 53.27 | 44.14 | 0 | 0 | 0 | 0 | 9.13 | 0
2025-02-15 12:00 | 43.86 | 54.72 | 43.86 | 0 | 0 | 0 | 0 | 10.86 | 0
2025-02-15 13:00 | 45.34 | 31.92 | 31.92 | 13.42 | 0 | 0 | 0 | 0 | 0
2025-02-15 14:00 | 45.03 | 49 | 45.03 | 0 | 0 | 0 | 0 | 3.97 | 0
2025-02-15 15:00 | 45.47 | 73.4 | 45.47 | 0 | 0 | 0 | 0 | 27.94 | 0
2025-02-15 16:00 | 44.49 | 61.85 | 44.49 | 0 | 0 | 0 | 0 | 17.36 | 0
2025-02-15 17:00 | 44.02 | 0.75 | 0.75 | 43.27 | 0 | 0 | 0 | 0 | 0
2025-02-15 18:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 0 | 0 | 0
2025-02-15 19:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0 | 0 | 0
2025-02-15 20:00 | 42.06 | 0 | 0 | 42.06 | 0 | 0 | 0 | 0 | 0
2025-02-15 21:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 0 | 0 | 0
2025-02-15 22:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 0 | 0 | 0
2025-02-15 23:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 0 | 0 | 0
2025-02-16 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 0 | 0 | 0
2025-02-16 01:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 0 | 0 | 0
2025-02-16 02:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 0 | 0 | 0
2025-02-16 03:00 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 0 | 0 | 0
2025-02-16 04:00 | 36.27 | 0 | 0 | 36.27 | 0 | 0 | 0 | 0 | 0
2025-02-16 05:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0 | 0 | 0
2025-02-16 06:00 | 38.32 | 0 | 0 | 38.32 | 0 | 0 | 0 | 0 | 0
2025-02-16 07:00 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 0 | 0 | 0
2025-02-16 08:00 | 39.5 | 1.21 | 1.21 | 38.3 | 0 | 0 | 0 | 0 | 0
2025-02-16 09:00 | 41.14 | 2.78 | 2.78 | 38.37 | 0 | 0 | 0 | 0 | 0
2025-02-16 10:00 | 43.34 | 6.08 | 6.08 | 37.26 | 0 | 0 | 0 | 0 | 0
2025-02-16 11:00 | 43.82 | 5.75 | 5.75 | 38.07 | 0 | 0 | 0 | 0 | 0
2025-02-16 12:00 | 44.85 | 9.5 | 9.5 | 35.35 | 0 | 0 | 0 | 0 | 0
2025-02-16 13:00 | 45.4 | 51.23 | 45.4 | 0 | 0 | 0 | 0 | 5.83 | 0
2025-02-16 14:00 | 45.99 | 45.33 | 45.33 | 0.66 | 0 | 0 | 0 | 0 | 0
2025-02-16 15:00 | 46.38 | 36.31 | 36.31 | 10.08 | 0 | 0 | 0 | 0 | 0
2025-02-16 16:00 | 45.42 | 29.12 | 29.12 | 16.3 | 0 | 0 | 0 | 0 | 0
2025-02-16 17:00 | 45.78 | 2.11 | 2.11 | 43.66 | 0 | 0 | 0 | 0 | 0
2025-02-16 18:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 0 | 0 | 0
2025-02-16 19:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 0 | 0 | 0
2025-02-16 20:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 0 | 0 | 0
2025-02-16 21:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 0 | 0 | 0
2025-02-16 22:00 | 40.22 | 0 | 0 | 40.22 | 0 | 0 | 0 | 0 | 0
2025-02-16 23:00 | 38.92 | 0 | 0 | 38.92 | 0 | 0 | 0 | 0 | 0
2025-02-17 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 0 | 0 | 0
2025-02-17 01:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0 | 0 | 0
2025-02-17 02:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 0 | 0 | 0
2025-02-17 03:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 0 | 0 | 0
2025-02-17 04:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 0 | 0 | 0
2025-02-17 05:00 | 38.19 | 0 | 0 | 38.19 | 0 | 0 | 0 | 0 | 0
2025-02-17 06:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0 | 0 | 0
2025-02-17 07:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0 | 0 | 0
2025-02-17 08:00 | 39.88 | 0.09 | 0.09 | 39.79 | 0 | 0 | 0 | 0 | 0
2025-02-17 09:00 | 41.87 | 1.72 | 1.72 | 40.15 | 0 | 0 | 0 | 0 | 0
2025-02-17 10:00 | 42.4 | 3.04 | 3.04 | 39.36 | 0 | 0 | 0 | 0 | 0
2025-02-17 11:00 | 43.1 | 4.06 | 4.06 | 39.04 | 0 | 0 | 0 | 0 | 0
2025-02-17 12:00 | 44.3 | 4.48 | 4.48 | 39.82 | 0 | 0 | 0 | 0 | 0
2025-02-17 13:00 | 43.64 | 47.2 | 43.64 | 0 | 0 | 0 | 0 | 3.56 | 0
2025-02-17 14:00 | 45.08 | 46.46 | 45.08 | 0 | 0 | 0 | 0 | 1.37 | 0
2025-02-17 15:00 | 46.24 | 35.17 | 35.17 | 11.08 | 0 | 0 | 0 | 0 | 0
2025-02-17 16:00 | 45.17 | 34.89 | 34.89 | 10.28 | 0 | 0 | 0 | 0 | 0
2025-02-17 17:00 | 44.73 | 1.98 | 1.98 | 42.75 | 0 | 0 | 0 | 0 | 0
2025-02-17 18:00 | 44.32 | 0 | 0 | 44.32 | 0 | 0 | 0 | 0 | 0
2025-02-17 19:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0 | 0 | 0
2025-02-17 20:00 | 41.24 | 0 | 0 | 41.24 | 0 | 0 | 0 | 0 | 0
2025-02-17 21:00 | 40.37 | 0 | 0 | 40.37 | 0 | 0 | 0 | 0 | 0
2025-02-17 22:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 0 | 0 | 0
2025-02-17 23:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 0 | 0 | 0
2025-02-18 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 0 | 0 | 0
2025-02-18 01:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 0 | 0 | 0
2025-02-18 02:00 | 36.54 | 0 | 0 | 36.54 | 0 | 0 | 0 | 0 | 0
2025-02-18 03:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 0 | 0 | 0
2025-02-18 04:00 | 36.13 | 0 | 0 | 36.13 | 0 | 0 | 0 | 0 | 0
2025-02-18 05:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0 | 0 | 0
2025-02-18 06:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0 | 0 | 0
2025-02-18 07:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0 | 0 | 0
2025-02-18 08:00 | 40.9 | 5.26 | 5.26 | 35.64 | 0 | 0 | 0 | 0 | 0
2025-02-18 09:00 | 42.06 | 7.33 | 7.33 | 34.73 | 0 | 0 | 0 | 0 | 0
2025-02-18 10:00 | 42.51 | 17.9 | 17.9 | 24.61 | 0 | 0 | 0 | 0 | 0
2025-02-18 11:00 | 42.61 | 28.85 | 28.85 | 13.75 | 0 | 0 | 0 | 0 | 0
2025-02-18 12:00 | 44.94 | 23.36 | 23.36 | 21.58 | 0 | 0 | 0 | 0 | 0
2025-02-18 13:00 | 45.65 | 18.86 | 18.86 | 26.8 | 0 | 0 | 0 | 0 | 0
2025-02-18 14:00 | 46 | 14.62 | 14.62 | 31.38 | 0 | 0 | 0 | 0 | 0
2025-02-18 15:00 | 46.5 | 9.8 | 9.8 | 36.7 | 0 | 0 | 0 | 0 | 0
2025-02-18 16:00 | 45.27 | 2.02 | 2.02 | 43.25 | 0 | 0 | 0 | 0 | 0
2025-02-18 17:00 | 46.38 | 0.05 | 0.05 | 46.33 | 0 | 0 | 0 | 0 | 0
2025-02-18 18:00 | 44.15 | 0 | 0 | 44.15 | 0 | 0 | 0 | 0 | 0
2025-02-18 19:00 | 44.05 | 0 | 0 | 44.05 | 0 | 0 | 0 | 0 | 0
2025-02-18 20:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 0 | 0 | 0
2025-02-18 21:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 0 | 0 | 0
2025-02-18 22:00 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 0 | 0 | 0
2025-02-18 23:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0
2025-02-19 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0 | 0 | 0
2025-02-19 01:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 0 | 0 | 0
2025-02-19 02:00 | 37.51 | 0 | 0 | 37.51 | 0 | 0 | 0 | 0 | 0
2025-02-19 03:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-02-19 04:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0 | 0 | 0
2025-02-19 05:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 0 | 0 | 0
2025-02-19 06:00 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 0 | 0 | 0
2025-02-19 07:00 | 39.66 | 0.6 | 0.6 | 39.06 | 0 | 0 | 0 | 0 | 0
2025-02-19 08:00 | 40.53 | 25.45 | 25.45 | 15.08 | 0 | 0 | 0 | 0 | 0
2025-02-19 09:00 | 40.56 | 65.5 | 40.56 | 0 | 0 | 0 | 0 | 24.94 | 0
2025-02-19 10:00 | 42 | 71 | 42 | 0 | 0 | 0 | 0 | 28.99 | 0
2025-02-19 11:00 | 43.03 | 73.02 | 43.03 | 0 | 0 | 0 | 0 | 29.99 | 0
2025-02-19 12:00 | 43.96 | 68.64 | 43.96 | 0 | 0 | 0 | 0 | 24.68 | 0
2025-02-19 13:00 | 44.08 | 71.86 | 44.08 | 0 | 0 | 0 | 0 | 27.78 | 0
2025-02-19 14:00 | 44.85 | 68.45 | 44.85 | 0 | 0 | 0 | 0 | 23.6 | 0
2025-02-19 15:00 | 44.94 | 65.61 | 44.94 | 0 | 0 | 0 | 0 | 20.67 | 0
2025-02-19 16:00 | 45.55 | 32.82 | 32.82 | 12.74 | 0 | 0 | 0 | 0 | 0
2025-02-19 17:00 | 45.17 | 4.9 | 4.9 | 40.28 | 0 | 0 | 0 | 0 | 0
2025-02-19 18:00 | 44.07 | 0 | 0 | 44.07 | 0 | 0 | 0 | 0 | 0
2025-02-19 19:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0 | 0 | 0
2025-02-19 20:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 0 | 0 | 0
2025-02-19 21:00 | 40.94 | 0 | 0 | 40.94 | 0 | 0 | 0 | 0 | 0
2025-02-19 22:00 | 39.75 | 0 | 0 | 39.75 | 0 | 0 | 0 | 0 | 0
2025-02-19 23:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 0 | 0 | 0
2025-02-20 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0 | 0 | 0
2025-02-20 01:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 0 | 0 | 0
2025-02-20 02:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 0 | 0 | 0
2025-02-20 03:00 | 37.86 | 0 | 0 | 37.86 | 0 | 0 | 0 | 0 | 0
2025-02-20 04:00 | 36.83 | 0 | 0 | 36.83 | 0 | 0 | 0 | 0 | 0
2025-02-20 05:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 0 | 0 | 0
2025-02-20 06:00 | 38.54 | 0 | 0 | 38.54 | 0 | 0 | 0 | 0 | 0
2025-02-20 07:00 | 39.65 | 1.23 | 1.23 | 38.43 | 0 | 0 | 0 | 0 | 0
2025-02-20 08:00 | 40.45 | 58.24 | 40.45 | 0 | 0 | 0 | 0 | 17.79 | 0
2025-02-20 09:00 | 40.8 | 77.64 | 40.8 | 0 | 0 | 0 | 0 | 36.84 | 0
2025-02-20 10:00 | 41.97 | 80 | 41.97 | 0 | 0 | 0 | 0 | 38.03 | 0
2025-02-20 11:00 | 43.63 | 70.88 | 43.63 | 0 | 0 | 0 | 0 | 27.25 | 0
2025-02-20 12:00 | 45.01 | 66.4 | 45.01 | 0 | 0 | 0 | 0 | 21.39 | 0
2025-02-20 13:00 | 44.07 | 70.19 | 44.07 | 0 | 0 | 0 | 0 | 26.12 | 0
2025-02-20 14:00 | 45.78 | 79.21 | 45.78 | 0 | 0 | 0 | 0 | 33.42 | 0
2025-02-20 15:00 | 46.35 | 70.73 | 46.35 | 0 | 0 | 0 | 0 | 24.38 | 0
2025-02-20 16:00 | 45.53 | 57.18 | 45.53 | 0 | 0 | 0 | 0 | 11.65 | 0
2025-02-20 17:00 | 45.45 | 7.96 | 7.96 | 37.49 | 0 | 0 | 0 | 0 | 0
2025-02-20 18:00 | 44.14 | 0 | 0 | 44.14 | 0 | 0 | 0 | 0 | 0
2025-02-20 19:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0 | 0 | 0
2025-02-20 20:00 | 41.79 | 0 | 0 | 41.79 | 0 | 0 | 0 | 0 | 0
2025-02-20 21:00 | 40.35 | 0 | 0 | 40.35 | 0 | 0 | 0 | 0 | 0
2025-02-20 22:00 | 40.93 | 0 | 0 | 40.93 | 0 | 0 | 0 | 0 | 0
2025-02-20 23:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0 | 0 | 0
2025-02-21 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 0 | 0 | 0
2025-02-21 01:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 0 | 0 | 0
2025-02-21 02:00 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 0 | 0 | 0
2025-02-21 03:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 0 | 0 | 0
2025-02-21 04:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0 | 0 | 0
2025-02-21 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-02-21 06:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0 | 0 | 0
2025-02-21 07:00 | 39.75 | 0.33 | 0.33 | 39.43 | 0 | 0 | 0 | 0 | 0
2025-02-21 08:00 | 40.74 | 19.2 | 19.2 | 21.53 | 0 | 0 | 0 | 0 | 0
2025-02-21 09:00 | 42.54 | 49.15 | 42.54 | 0 | 0 | 0 | 0 | 6.61 | 0
2025-02-21 10:00 | 42.38 | 72.83 | 42.38 | 0 | 0 | 0 | 0 | 30.45 | 0
2025-02-21 11:00 | 43.99 | 83.86 | 43.99 | 0 | 0 | 0 | 0 | 39.87 | 0
2025-02-21 12:00 | 45.56 | 40.3 | 40.3 | 5.26 | 0 | 0 | 0 | 0 | 0
2025-02-21 13:00 | 46.38 | 23.61 | 23.61 | 22.77 | 0 | 0 | 0 | 0 | 0
2025-02-21 14:00 | 45.52 | 6.16 | 6.16 | 39.36 | 0 | 0 | 0 | 0 | 0
2025-02-21 15:00 | 46.24 | 4.11 | 4.11 | 42.13 | 0 | 0 | 0 | 0 | 0
2025-02-21 16:00 | 46.91 | 1.23 | 1.23 | 45.68 | 0 | 0 | 0 | 0 | 0
2025-02-21 17:00 | 46 | 0.54 | 0.54 | 45.46 | 0 | 0 | 0 | 0 | 0
2025-02-21 18:00 | 45.09 | 0 | 0 | 45.09 | 0 | 0 | 0 | 0 | 0
2025-02-21 19:00 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 0 | 0 | 0
2025-02-21 20:00 | 42.72 | 0 | 0 | 42.72 | 0 | 0 | 0 | 0 | 0
2025-02-21 21:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 0 | 0 | 0
2025-02-21 22:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0 | 0 | 0
2025-02-21 23:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0 | 0 | 0
2025-02-22 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0 | 0 | 0
2025-02-22 01:00 | 37.8 | 0 | 0 | 37.8 | 0 | 0 | 0 | 0 | 0
2025-02-22 02:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0 | 0 | 0
2025-02-22 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0 | 0 | 0
2025-02-22 04:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 0 | 0 | 0
2025-02-22 05:00 | 38.3 | 0 | 0 | 38.3 | 0 | 0 | 0 | 0 | 0
2025-02-22 06:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 0 | 0 | 0
2025-02-22 07:00 | 39.78 | 1.94 | 1.94 | 37.84 | 0 | 0 | 0 | 0 | 0
2025-02-22 08:00 | 40.32 | 62.8 | 40.32 | 0 | 0 | 0 | 0 | 22.48 | 0
2025-02-22 09:00 | 41.48 | 81.93 | 41.48 | 0 | 0 | 0 | 0 | 40.45 | 0
2025-02-22 10:00 | 42.42 | 64.32 | 42.42 | 0 | 0 | 0 | 0 | 21.9 | 0
2025-02-22 11:00 | 42.55 | 75.36 | 42.55 | 0 | 0 | 0 | 0 | 32.81 | 0
2025-02-22 12:00 | 43.5 | 78.18 | 43.5 | 0 | 0 | 0 | 0 | 34.68 | 0
2025-02-22 13:00 | 42.1 | 54.19 | 42.1 | 0 | 0 | 0 | 0 | 12.09 | 0
2025-02-22 14:00 | 44.27 | 41.51 | 41.51 | 2.76 | 0 | 0 | 0 | 0 | 0
2025-02-22 15:00 | 43.73 | 26.19 | 26.19 | 17.54 | 0 | 0 | 0 | 0 | 0
2025-02-22 16:00 | 44.01 | 5.74 | 5.74 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-02-22 17:00 | 42.66 | 0.95 | 0.95 | 41.72 | 0 | 0 | 0 | 0 | 0
2025-02-22 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0 | 0 | 0
2025-02-22 19:00 | 42.53 | 0 | 0 | 42.53 | 0 | 0 | 0 | 0 | 0
2025-02-22 20:00 | 41.83 | 0 | 0 | 41.83 | 0 | 0 | 0 | 0 | 0
2025-02-22 21:00 | 41.24 | 0 | 0 | 41.24 | 0 | 0 | 0 | 0 | 0
2025-02-22 22:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0 | 0 | 0
2025-02-22 23:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0 | 0 | 0
2025-02-23 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0 | 0 | 0
2025-02-23 01:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 0 | 0 | 0
2025-02-23 02:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 0 | 0 | 0
2025-02-23 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0 | 0 | 0
2025-02-23 04:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 0 | 0 | 0
2025-02-23 05:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 0 | 0 | 0
2025-02-23 06:00 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 0 | 0 | 0
2025-02-23 07:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0 | 0 | 0
2025-02-23 08:00 | 40.65 | 9 | 9 | 31.65 | 0 | 0 | 0 | 0 | 0
2025-02-23 09:00 | 41.56 | 9.29 | 9.29 | 32.28 | 0 | 0 | 0 | 0 | 0
2025-02-23 10:00 | 43.19 | 3.13 | 3.13 | 40.07 | 0 | 0 | 0 | 0 | 0
2025-02-23 11:00 | 43.42 | 85.53 | 43.42 | 0 | 0 | 0 | 0 | 42.11 | 0
2025-02-23 12:00 | 43.92 | 65.48 | 43.92 | 0 | 0 | 0 | 0 | 21.55 | 0
2025-02-23 13:00 | 44.6 | 44.84 | 44.6 | 0 | 0 | 0 | 0 | 0.24 | 0
2025-02-23 14:00 | 45.85 | 42.71 | 42.71 | 3.14 | 0 | 0 | 0 | 0 | 0
2025-02-23 15:00 | 45.6 | 89.97 | 45.6 | 0 | 0 | 0 | 0 | 44.37 | 0
2025-02-23 16:00 | 45.02 | 81.84 | 45.02 | 0 | 0 | 0 | 0 | 36.82 | 0
2025-02-23 17:00 | 44.73 | 16.11 | 16.11 | 28.62 | 0 | 0 | 0 | 0 | 0
2025-02-23 18:00 | 43.49 | 0 | 0 | 43.49 | 0 | 0 | 0 | 0 | 0
2025-02-23 19:00 | 43.7 | 0 | 0 | 43.7 | 0 | 0 | 0 | 0 | 0
2025-02-23 20:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 0 | 0 | 0
2025-02-23 21:00 | 42 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0
2025-02-23 22:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 0 | 0 | 0
2025-02-23 23:00 | 40.87 | 0 | 0 | 40.87 | 0 | 0 | 0 | 0 | 0
2025-02-24 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 0 | 0 | 0
2025-02-24 01:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0 | 0 | 0
2025-02-24 02:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0 | 0 | 0
2025-02-24 03:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0 | 0 | 0
2025-02-24 04:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0 | 0 | 0
2025-02-24 05:00 | 38.4 | 0 | 0 | 38.4 | 0 | 0 | 0 | 0 | 0
2025-02-24 06:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0 | 0 | 0
2025-02-24 07:00 | 39.9 | 6.12 | 6.12 | 33.78 | 0 | 0 | 0 | 0 | 0
2025-02-24 08:00 | 40.34 | 77.32 | 40.34 | 0 | 0 | 0 | 0 | 36.98 | 0
2025-02-24 09:00 | 41.63 | 75.75 | 41.63 | 0 | 0 | 0 | 0 | 34.12 | 0
2025-02-24 10:00 | 41.84 | 85.13 | 41.84 | 0 | 0 | 0 | 0 | 43.29 | 0
2025-02-24 11:00 | 43.58 | 91.48 | 43.58 | 0 | 0 | 0 | 0 | 47.89 | 0
2025-02-24 12:00 | 44.48 | 85.72 | 44.48 | 0 | 0 | 0 | 0 | 41.24 | 0
2025-02-24 13:00 | 44.69 | 61.01 | 44.69 | 0 | 0 | 0 | 0 | 16.32 | 0
2025-02-24 14:00 | 44.34 | 59.19 | 44.34 | 0 | 0 | 0 | 0 | 14.85 | 0
2025-02-24 15:00 | 45.76 | 9.79 | 9.79 | 35.97 | 0 | 0 | 0 | 0 | 0
2025-02-24 16:00 | 45.33 | 1.1 | 1.1 | 44.23 | 0 | 0 | 0 | 0 | 0
2025-02-24 17:00 | 44.44 | 0 | 0 | 44.44 | 0 | 0 | 0 | 0 | 0
2025-02-24 18:00 | 44.11 | 0 | 0 | 44.11 | 0 | 0 | 0 | 0 | 0
2025-02-24 19:00 | 42.77 | 0 | 0 | 42.77 | 0 | 0 | 0 | 0 | 0
2025-02-24 20:00 | 42.13 | 0 | 0 | 42.13 | 0 | 0 | 0 | 0 | 0
2025-02-24 21:00 | 41.41 | 0 | 0 | 41.41 | 0 | 0 | 0 | 0 | 0
2025-02-24 22:00 | 41.31 | 0 | 0 | 41.31 | 0 | 0 | 0 | 0 | 0
2025-02-24 23:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 0 | 0 | 0
2025-02-25 | 39.33 | 0 | 0 | 39.33 | 0 | 0 | 0 | 0 | 0
2025-02-25 01:00 | 38.09 | 0 | 0 | 38.09 | 0 | 0 | 0 | 0 | 0
2025-02-25 02:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0 | 0 | 0
2025-02-25 03:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 0 | 0 | 0
2025-02-25 04:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 0 | 0 | 0
2025-02-25 05:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 0 | 0 | 0
2025-02-25 06:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 0 | 0 | 0
2025-02-25 07:00 | 39.14 | 2.1 | 2.1 | 37.04 | 0 | 0 | 0 | 0 | 0
2025-02-25 08:00 | 40.5 | 58.95 | 40.5 | 0 | 0 | 0 | 0 | 18.45 | 0
2025-02-25 09:00 | 41.11 | 79 | 41.11 | 0 | 0 | 0 | 0 | 37.89 | 0
2025-02-25 10:00 | 42.87 | 82.37 | 42.87 | 0 | 0 | 0 | 0 | 39.5 | 0
2025-02-25 11:00 | 43.28 | 72.09 | 43.28 | 0 | 0 | 0 | 0 | 28.82 | 0
2025-02-25 12:00 | 45.4 | 71.06 | 45.4 | 0 | 0 | 0 | 0 | 25.66 | 0
2025-02-25 13:00 | 43.87 | 77.21 | 43.87 | 0 | 0 | 0 | 0 | 33.34 | 0
2025-02-25 14:00 | 45.16 | 76.33 | 45.16 | 0 | 0 | 0 | 0 | 31.16 | 0
2025-02-25 15:00 | 44.61 | 64.23 | 44.61 | 0 | 0 | 0 | 0 | 19.62 | 0
2025-02-25 16:00 | 44.82 | 65.45 | 44.82 | 0 | 0 | 0 | 0 | 20.64 | 0
2025-02-25 17:00 | 44.81 | 11.01 | 11.01 | 33.8 | 0 | 0 | 0 | 0 | 0
2025-02-25 18:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 0 | 0 | 0
2025-02-25 19:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 0 | 0 | 0
2025-02-25 20:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 0 | 0 | 0
2025-02-25 21:00 | 41.5 | 0 | 0 | 41.5 | 0 | 0 | 0 | 0 | 0
2025-02-25 22:00 | 40.89 | 0 | 0 | 40.89 | 0 | 0 | 0 | 0 | 0
2025-02-25 23:00 | 40.34 | 0 | 0 | 40.34 | 0 | 0 | 0 | 0 | 0
2025-02-26 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0
2025-02-26 01:00 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0 | 0 | 0
2025-02-26 02:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 0 | 0 | 0
2025-02-26 03:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0 | 0 | 0
2025-02-26 04:00 | 37.97 | 0 | 0 | 37.97 | 0 | 0 | 0 | 0 | 0
2025-02-26 05:00 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 0 | 0 | 0
2025-02-26 06:00 | 39.17 | 0 | 0 | 39.17 | 0 | 0 | 0 | 0 | 0
2025-02-26 07:00 | 39.67 | 2.84 | 2.84 | 36.82 | 0 | 0 | 0 | 0 | 0
2025-02-26 08:00 | 40.68 | 24.75 | 24.75 | 15.92 | 0 | 0 | 0 | 0 | 0
2025-02-26 09:00 | 42.29 | 78.92 | 42.29 | 0 | 0 | 0 | 0 | 36.64 | 0
2025-02-26 10:00 | 42.34 | 87.6 | 42.34 | 0 | 0 | 0 | 0 | 45.26 | 0
2025-02-26 11:00 | 44.48 | 78.02 | 44.48 | 0 | 0 | 0 | 0 | 33.54 | 0
2025-02-26 12:00 | 44.06 | 78.32 | 44.06 | 0 | 0 | 0 | 0 | 34.25 | 0
2025-02-26 13:00 | 45.04 | 63.27 | 45.04 | 0 | 0 | 0 | 0 | 18.23 | 0
2025-02-26 14:00 | 46.71 | 39.39 | 39.39 | 7.32 | 0 | 0 | 0 | 0 | 0
2025-02-26 15:00 | 46.44 | 19.29 | 19.29 | 27.15 | 0 | 0 | 0 | 0 | 0
2025-02-26 16:00 | 45.8 | 4.99 | 4.99 | 40.81 | 0 | 0 | 0 | 0 | 0
2025-02-26 17:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0 | 0 | 0
2025-02-26 18:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 0 | 0 | 0
2025-02-26 19:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0
2025-02-26 20:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0 | 0 | 0
2025-02-26 21:00 | 41.94 | 0 | 0 | 41.94 | 0 | 0 | 0 | 0 | 0
2025-02-26 22:00 | 40.93 | 0 | 0 | 40.93 | 0 | 0 | 0 | 0 | 0
2025-02-26 23:00 | 39.85 | 0 | 0 | 39.85 | 0 | 0 | 0 | 0 | 0
2025-02-27 | 38.53 | 0 | 0 | 38.53 | 0 | 0 | 0 | 0 | 0
2025-02-27 01:00 | 38.27 | 0 | 0 | 38.27 | 0 | 0 | 0 | 0 | 0
2025-02-27 02:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 0 | 0 | 0
2025-02-27 03:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 0 | 0 | 0
2025-02-27 04:00 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0
2025-02-27 05:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-02-27 06:00 | 39.3 | 0 | 0 | 39.3 | 0 | 0 | 0 | 0 | 0
2025-02-27 07:00 | 40.03 | 4.97 | 4.97 | 35.06 | 0 | 0 | 0 | 0 | 0
2025-02-27 08:00 | 42.16 | 77.21 | 42.16 | 0 | 0 | 0 | 0 | 35.05 | 0
2025-02-27 09:00 | 43.04 | 91.12 | 43.04 | 0 | 0 | 0 | 0 | 48.09 | 0
2025-02-27 10:00 | 43.57 | 89.2 | 43.57 | 0 | 0 | 0 | 0 | 45.63 | 0
2025-02-27 11:00 | 45.97 | 83.43 | 45.97 | 0 | 0 | 0 | 0 | 37.46 | 0
2025-02-27 12:00 | 46.51 | 76.75 | 46.51 | 0 | 0 | 0 | 0 | 30.24 | 0
2025-02-27 13:00 | 47.61 | 80.25 | 47.61 | 0 | 0 | 0 | 0 | 32.64 | 0
2025-02-27 14:00 | 48.7 | 87.23 | 48.7 | 0 | 0 | 0 | 0 | 38.53 | 0
2025-02-27 15:00 | 48.52 | 94.02 | 48.52 | 0 | 0 | 0 | 0 | 45.5 | 0
2025-02-27 16:00 | 48.99 | 85.24 | 48.99 | 0 | 0 | 0 | 0 | 36.25 | 0
2025-02-27 17:00 | 47.51 | 20.07 | 20.07 | 27.44 | 0 | 0 | 0 | 0 | 0
2025-02-27 18:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0 | 0 | 0
2025-02-27 19:00 | 45.3 | 0 | 0 | 45.3 | 0 | 0 | 0 | 0 | 0
2025-02-27 20:00 | 43.94 | 0 | 0 | 43.94 | 0 | 0 | 0 | 0 | 0
2025-02-27 21:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 0 | 0 | 0
2025-02-27 22:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0 | 0 | 0
2025-02-27 23:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 0 | 0 | 0
2025-02-28 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 0 | 0 | 0
2025-02-28 01:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0 | 0 | 0
2025-02-28 02:00 | 38.21 | 0 | 0 | 38.21 | 0 | 0 | 0 | 0 | 0
2025-02-28 03:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 0 | 0 | 0
2025-02-28 04:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0 | 0 | 0
2025-02-28 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-02-28 06:00 | 38.73 | 0 | 0 | 38.73 | 0 | 0 | 0 | 0 | 0
2025-02-28 07:00 | 39.57 | 5.75 | 5.75 | 33.83 | 0 | 0 | 0 | 0 | 0
2025-02-28 08:00 | 40.96 | 86.96 | 40.96 | 0 | 0 | 0 | 0 | 46 | 0
2025-02-28 09:00 | 41.39 | 98.33 | 41.39 | 0 | 0 | 0 | 0 | 56.94 | 0
2025-02-28 10:00 | 43.34 | 94.42 | 43.34 | 0 | 0 | 0 | 0 | 51.08 | 0
2025-02-28 11:00 | 43.28 | 86.89 | 43.28 | 0 | 0 | 0 | 0 | 43.62 | 0
2025-02-28 12:00 | 45.81 | 81.98 | 45.81 | 0 | 0 | 0 | 0 | 36.17 | 0
2025-02-28 13:00 | 44.68 | 84.82 | 44.68 | 0 | 0 | 0 | 0 | 40.15 | 0
2025-02-28 14:00 | 45.24 | 91.46 | 45.24 | 0 | 0 | 0 | 0 | 46.22 | 0
2025-02-28 15:00 | 44.66 | 97.1 | 44.66 | 0 | 0 | 0 | 0 | 52.44 | 0
2025-02-28 16:00 | 46.06 | 91.6 | 46.06 | 0 | 0 | 0 | 0 | 45.55 | 0
2025-02-28 17:00 | 45.46 | 25.19 | 25.19 | 20.28 | 0 | 0 | 0 | 0 | 0
2025-02-28 18:00 | 44.56 | 0 | 0 | 44.56 | 0 | 0 | 0 | 0 | 0
2025-02-28 19:00 | 43.06 | 0 | 0 | 43.06 | 0 | 0 | 0 | 0 | 0
2025-02-28 20:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0 | 0 | 0
2025-02-28 21:00 | 41.44 | 0 | 0 | 41.44 | 0 | 0 | 0 | 0 | 0
2025-02-28 22:00 | 41.77 | 0 | 0 | 41.77 | 0 | 0 | 0 | 0 | 0
2025-02-28 23:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 0 | 0 | 0
2025-03-01 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 0 | 0 | 0
2025-03-01 01:00 | 37.47 | 0 | 0 | 37.47 | 0 | 0 | 0 | 0 | 0
2025-03-01 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0 | 0 | 0
2025-03-01 03:00 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 0 | 0 | 0
2025-03-01 04:00 | 38.86 | 0 | 0 | 38.86 | 0 | 0 | 0 | 0 | 0
2025-03-01 05:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0 | 0 | 0
2025-03-01 06:00 | 38.62 | 0 | 0 | 38.62 | 0 | 0 | 0 | 0 | 0
2025-03-01 07:00 | 40.53 | 4.6 | 4.6 | 35.93 | 0 | 0 | 0 | 0 | 0
2025-03-01 08:00 | 42.05 | 60.17 | 42.05 | 0 | 0 | 0 | 0 | 18.12 | 0
2025-03-01 09:00 | 42.02 | 45.65 | 42.02 | 0 | 0 | 0 | 0 | 3.63 | 0
2025-03-01 10:00 | 44.2 | 70.62 | 44.2 | 0 | 0 | 0 | 0 | 26.42 | 0
2025-03-01 11:00 | 45.64 | 60.91 | 45.64 | 0 | 0 | 0 | 0 | 15.27 | 0
2025-03-01 12:00 | 46.51 | 69.53 | 46.51 | 0 | 0 | 0 | 0 | 23.02 | 0
2025-03-01 13:00 | 46.65 | 68.62 | 46.65 | 0 | 0 | 0 | 0 | 21.97 | 0
2025-03-01 14:00 | 47.99 | 71.77 | 47.99 | 0 | 0 | 0 | 0 | 23.78 | 0
2025-03-01 15:00 | 48.19 | 74.43 | 48.19 | 0 | 0 | 0 | 0 | 26.24 | 0
2025-03-01 16:00 | 48.08 | 78.28 | 48.08 | 0 | 0 | 0 | 0 | 30.19 | 0
2025-03-01 17:00 | 47.29 | 21.25 | 21.25 | 26.04 | 0 | 0 | 0 | 0 | 0
2025-03-01 18:00 | 46.44 | 0 | 0 | 46.44 | 0 | 0 | 0 | 0 | 0
2025-03-01 19:00 | 45.49 | 0 | 0 | 45.49 | 0 | 0 | 0 | 0 | 0
2025-03-01 20:00 | 44.42 | 0 | 0 | 44.42 | 0 | 0 | 0 | 0 | 0
2025-03-01 21:00 | 42.7 | 0 | 0 | 42.7 | 0 | 0 | 0 | 0 | 0
2025-03-01 22:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 0 | 0 | 0
2025-03-01 23:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0 | 0 | 0
2025-03-02 | 38.45 | 0 | 0 | 38.45 | 0 | 0 | 0 | 0 | 0
2025-03-02 01:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0 | 0 | 0
2025-03-02 02:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0 | 0 | 0
2025-03-02 03:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0 | 0 | 0
2025-03-02 04:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0 | 0 | 0
2025-03-02 05:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0 | 0 | 0
2025-03-02 06:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0 | 0 | 0
2025-03-02 07:00 | 40.36 | 8.56 | 8.56 | 31.8 | 0 | 0 | 0 | 0 | 0
2025-03-02 08:00 | 41.08 | 81.17 | 41.08 | 0 | 0 | 0 | 0 | 40.08 | 0
2025-03-02 09:00 | 42.01 | 96.6 | 42.01 | 0 | 0 | 0 | 0 | 54.59 | 0
2025-03-02 10:00 | 42.45 | 93.91 | 42.45 | 0 | 0 | 0 | 0 | 51.46 | 0
2025-03-02 11:00 | 43.64 | 86.93 | 43.64 | 0 | 0 | 0 | 0 | 43.3 | 0
2025-03-02 12:00 | 44.24 | 82.38 | 44.24 | 0 | 0 | 0 | 0 | 38.14 | 0
2025-03-02 13:00 | 44.34 | 86.12 | 44.34 | 0 | 0 | 0 | 0 | 41.78 | 0
2025-03-02 14:00 | 44.15 | 92.51 | 44.15 | 0 | 0 | 0 | 0 | 48.35 | 0
2025-03-02 15:00 | 43.29 | 95.99 | 43.29 | 0 | 0 | 0 | 0 | 52.7 | 0
2025-03-02 16:00 | 44.67 | 85.82 | 44.67 | 0 | 0 | 0 | 0 | 41.16 | 0
2025-03-02 17:00 | 44.71 | 25.89 | 25.89 | 18.82 | 0 | 0 | 0 | 0 | 0
2025-03-02 18:00 | 44.1 | 0 | 0 | 44.1 | 0 | 0 | 0 | 0 | 0
2025-03-02 19:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 0 | 0 | 0
2025-03-02 20:00 | 43.02 | 0 | 0 | 43.02 | 0 | 0 | 0 | 0 | 0
2025-03-02 21:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 0 | 0 | 0
2025-03-02 22:00 | 41.87 | 0 | 0 | 41.87 | 0 | 0 | 0 | 0 | 0
2025-03-02 23:00 | 39.78 | 0 | 0 | 39.78 | 0 | 0 | 0 | 0 | 0
2025-03-03 | 39.44 | 0 | 0 | 39.44 | 0 | 0 | 0 | 0 | 0
2025-03-03 01:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0
2025-03-03 02:00 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 0 | 0 | 0
2025-03-03 03:00 | 37.7 | 0 | 0 | 37.7 | 0 | 0 | 0 | 0 | 0
2025-03-03 04:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0 | 0 | 0
2025-03-03 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0 | 0 | 0
2025-03-03 06:00 | 39.6 | 0 | 0 | 39.6 | 0 | 0 | 0 | 0 | 0
2025-03-03 07:00 | 40.57 | 0.13 | 0.13 | 40.44 | 0 | 0 | 0 | 0 | 0
2025-03-03 08:00 | 41.37 | 19.83 | 19.83 | 21.55 | 0 | 0 | 0 | 0 | 0
2025-03-03 09:00 | 43.34 | 2.59 | 2.59 | 40.74 | 0 | 0 | 0 | 0 | 0
2025-03-03 10:00 | 43.23 | 33.59 | 33.59 | 9.64 | 0 | 0 | 0 | 0 | 0
2025-03-03 11:00 | 44.38 | 62.55 | 44.38 | 0 | 0 | 0 | 0 | 18.17 | 0
2025-03-03 12:00 | 45.51 | 44.69 | 44.69 | 0.83 | 0 | 0 | 0 | 0 | 0
2025-03-03 13:00 | 46.58 | 25.12 | 25.12 | 21.47 | 0 | 0 | 0 | 0 | 0
2025-03-03 14:00 | 45.79 | 37.92 | 37.92 | 7.87 | 0 | 0 | 0 | 0 | 0
2025-03-03 15:00 | 46.02 | 24.56 | 24.56 | 21.45 | 0 | 0 | 0 | 0 | 0
2025-03-03 16:00 | 45.52 | 54.9 | 45.52 | 0 | 0 | 0 | 0 | 9.38 | 0
2025-03-03 17:00 | 46.16 | 15.77 | 15.77 | 30.39 | 0 | 0 | 0 | 0 | 0
2025-03-03 18:00 | 44.95 | 0 | 0 | 44.95 | 0 | 0 | 0 | 0 | 0
2025-03-03 19:00 | 44.48 | 0 | 0 | 44.48 | 0 | 0 | 0 | 0 | 0
2025-03-03 20:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 0 | 0 | 0
2025-03-03 21:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0 | 0 | 0
2025-03-03 22:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 0 | 0 | 0
2025-03-03 23:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 0 | 0 | 0
2025-03-04 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 0 | 0 | 0
2025-03-04 01:00 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 0 | 0 | 0
2025-03-04 02:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 0 | 0 | 0
2025-03-04 03:00 | 38.25 | 0 | 0 | 38.25 | 0 | 0 | 0 | 0 | 0
2025-03-04 04:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 0 | 0 | 0
2025-03-04 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0 | 0 | 0
2025-03-04 06:00 | 38.97 | 0 | 0 | 38.97 | 0 | 0 | 0 | 0 | 0
2025-03-04 07:00 | 40.95 | 7.99 | 7.99 | 32.96 | 0 | 0 | 0 | 0 | 0
2025-03-04 08:00 | 41.19 | 39.13 | 39.13 | 2.07 | 0 | 0 | 0 | 0 | 0
2025-03-04 09:00 | 43.65 | 85.24 | 43.65 | 0 | 0 | 0 | 0 | 41.59 | 0
2025-03-04 10:00 | 44.66 | 40.85 | 40.85 | 3.82 | 0 | 0 | 0 | 0 | 0
2025-03-04 11:00 | 45.44 | 50.67 | 45.44 | 0 | 0 | 0 | 0 | 5.24 | 0
2025-03-04 12:00 | 46.35 | 53.82 | 46.35 | 0 | 0 | 0 | 0 | 7.46 | 0
2025-03-04 13:00 | 46.93 | 61.45 | 46.93 | 0 | 0 | 0 | 0 | 14.52 | 0
2025-03-04 14:00 | 47.85 | 97.16 | 47.85 | 0 | 0 | 0 | 0 | 49.3 | 0
2025-03-04 15:00 | 47.49 | 76.36 | 47.49 | 0 | 0 | 0 | 0 | 28.87 | 0
2025-03-04 16:00 | 47.63 | 47.32 | 47.32 | 0.31 | 0 | 0 | 0 | 0 | 0
2025-03-04 17:00 | 47.47 | 10.34 | 10.34 | 37.13 | 0 | 0 | 0 | 0 | 0
2025-03-04 18:00 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 0 | 0 | 0
2025-03-04 19:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0 | 0 | 0
2025-03-04 20:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0 | 0 | 0
2025-03-04 21:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 0 | 0 | 0
2025-03-04 22:00 | 40.82 | 0 | 0 | 40.82 | 0 | 0 | 0 | 0 | 0
2025-03-04 23:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 0 | 0 | 0
2025-03-05 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 0 | 0 | 0
2025-03-05 01:00 | 39.75 | 0 | 0 | 39.75 | 0 | 0 | 0 | 0 | 0
2025-03-05 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0 | 0 | 0
2025-03-05 03:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0 | 0 | 0
2025-03-05 04:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0 | 0 | 0
2025-03-05 05:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0 | 0 | 0
2025-03-05 06:00 | 39.84 | 0 | 0 | 39.84 | 0 | 0 | 0 | 0 | 0
2025-03-05 07:00 | 39.77 | 9.62 | 9.62 | 30.16 | 0 | 0 | 0 | 0 | 0
2025-03-05 08:00 | 42.09 | 97.11 | 42.09 | 0 | 0 | 0 | 0 | 55.02 | 0
2025-03-05 09:00 | 42.72 | 100.21 | 42.72 | 0 | 0 | 0 | 0 | 57.48 | 0
2025-03-05 10:00 | 44.69 | 87.68 | 44.69 | 0 | 0 | 0 | 0 | 42.99 | 0
2025-03-05 11:00 | 45.08 | 71.89 | 45.08 | 0 | 0 | 0 | 0 | 26.81 | 0
2025-03-05 12:00 | 47.24 | 54.23 | 47.24 | 0 | 0 | 0 | 0 | 6.99 | 0
2025-03-05 13:00 | 48.35 | 45.76 | 45.76 | 2.59 | 0 | 0 | 0 | 0 | 0
2025-03-05 14:00 | 48 | 42.47 | 42.47 | 5.53 | 0 | 0 | 0 | 0 | 0
2025-03-05 15:00 | 48.01 | 38.32 | 38.32 | 9.69 | 0 | 0 | 0 | 0 | 0
2025-03-05 16:00 | 47.31 | 25.29 | 25.29 | 22.03 | 0 | 0 | 0 | 0 | 0
2025-03-05 17:00 | 47.71 | 3.62 | 3.62 | 44.09 | 0 | 0 | 0 | 0 | 0
2025-03-05 18:00 | 46.68 | 0 | 0 | 46.68 | 0 | 0 | 0 | 0 | 0
2025-03-05 19:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 0 | 0 | 0
2025-03-05 20:00 | 44.82 | 0 | 0 | 44.82 | 0 | 0 | 0 | 0 | 0
2025-03-05 21:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0 | 0 | 0
2025-03-05 22:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0 | 0 | 0
2025-03-05 23:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 0 | 0 | 0
2025-03-06 | 40.43 | 0 | 0 | 40.43 | 0 | 0 | 0 | 0 | 0
2025-03-06 01:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 0 | 0 | 0
2025-03-06 02:00 | 38.59 | 0 | 0 | 38.59 | 0 | 0 | 0 | 0 | 0
2025-03-06 03:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0 | 0 | 0
2025-03-06 04:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0 | 0 | 0
2025-03-06 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0 | 0 | 0
2025-03-06 06:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 0 | 0 | 0
2025-03-06 07:00 | 40.67 | 12.98 | 12.98 | 27.69 | 0 | 0 | 0 | 0 | 0
2025-03-06 08:00 | 42.33 | 74.38 | 42.33 | 0 | 0 | 0 | 0 | 32.04 | 0
2025-03-06 09:00 | 43.07 | 88.67 | 43.07 | 0 | 0 | 0 | 0 | 45.61 | 0
2025-03-06 10:00 | 45.09 | 86.36 | 45.09 | 0 | 0 | 0 | 0 | 41.27 | 0
2025-03-06 11:00 | 46.43 | 84.74 | 46.43 | 0 | 0 | 0 | 0 | 38.3 | 0
2025-03-06 12:00 | 45.86 | 81.76 | 45.86 | 0 | 0 | 0 | 0 | 35.9 | 0
2025-03-06 13:00 | 48.82 | 86.9 | 48.82 | 0 | 0 | 0 | 0 | 38.08 | 0
2025-03-06 14:00 | 47.29 | 95.31 | 47.29 | 0 | 0 | 0 | 0 | 48.02 | 0
2025-03-06 15:00 | 48.7 | 94.48 | 48.7 | 0 | 0 | 0 | 0 | 45.78 | 0
2025-03-06 16:00 | 49.32 | 83.23 | 49.32 | 0 | 0 | 0 | 0 | 33.91 | 0
2025-03-06 17:00 | 48.07 | 31.2 | 31.2 | 16.87 | 0 | 0 | 0 | 0 | 0
2025-03-06 18:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0 | 0 | 0
2025-03-06 19:00 | 45.61 | 0 | 0 | 45.61 | 0 | 0 | 0 | 0 | 0
2025-03-06 20:00 | 45.35 | 0 | 0 | 45.35 | 0 | 0 | 0 | 0 | 0
2025-03-06 21:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 0 | 0 | 0
2025-03-06 22:00 | 42.68 | 0 | 0 | 42.68 | 0 | 0 | 0 | 0 | 0
2025-03-06 23:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 0 | 0 | 0
2025-03-07 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 0 | 0 | 0
2025-03-07 01:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0 | 0 | 0
2025-03-07 02:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0 | 0 | 0
2025-03-07 03:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0
2025-03-07 04:00 | 39.11 | 0 | 0 | 39.11 | 0 | 0 | 0 | 0 | 0
2025-03-07 05:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 0 | 0 | 0
2025-03-07 06:00 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 0 | 0 | 0
2025-03-07 07:00 | 40.6 | 19.12 | 19.12 | 21.48 | 0 | 0 | 0 | 0 | 0
2025-03-07 08:00 | 42.92 | 85.22 | 42.92 | 0 | 0 | 0 | 0 | 42.31 | 0
2025-03-07 09:00 | 42.97 | 92.76 | 42.97 | 0 | 0 | 0 | 0 | 49.79 | 0
2025-03-07 10:00 | 45.86 | 92.32 | 45.86 | 0 | 0 | 0 | 0 | 46.46 | 0
2025-03-07 11:00 | 46.41 | 85.91 | 46.41 | 0 | 0 | 0 | 0 | 39.51 | 0
2025-03-07 12:00 | 47.04 | 77.75 | 47.04 | 0 | 0 | 0 | 0 | 30.71 | 0
2025-03-07 13:00 | 48.23 | 79.15 | 48.23 | 0 | 0 | 0 | 0 | 30.92 | 0
2025-03-07 14:00 | 48.77 | 80 | 48.77 | 0 | 0 | 0 | 0 | 31.23 | 0
2025-03-07 15:00 | 48.74 | 80.55 | 48.74 | 0 | 0 | 0 | 0 | 31.82 | 0
2025-03-07 16:00 | 49.21 | 82.72 | 49.21 | 0 | 0 | 0 | 0 | 33.51 | 0
2025-03-07 17:00 | 47.95 | 32.93 | 32.93 | 15.02 | 0 | 0 | 0 | 0 | 0
2025-03-07 18:00 | 46.53 | 0 | 0 | 46.53 | 0 | 0 | 0 | 0 | 0
2025-03-07 19:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 0 | 0 | 0
2025-03-07 20:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 0 | 0 | 0
2025-03-07 21:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 0 | 0 | 0
2025-03-07 22:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 0 | 0 | 0
2025-03-07 23:00 | 40.59 | 0 | 0 | 40.59 | 0 | 0 | 0 | 0 | 0
2025-03-08 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 0 | 0 | 0
2025-03-08 01:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0 | 0 | 0
2025-03-08 02:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0 | 0 | 0
2025-03-08 03:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0 | 0 | 0
2025-03-08 04:00 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 0 | 0 | 0
2025-03-08 05:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0 | 0 | 0
2025-03-08 06:00 | 39.55 | 0 | 0 | 39.55 | 0 | 0 | 0 | 0 | 0
2025-03-08 07:00 | 41.48 | 20.12 | 20.12 | 21.36 | 0 | 0 | 0 | 0 | 0
2025-03-08 08:00 | 41.53 | 75.45 | 41.53 | 0 | 0 | 0 | 0 | 33.92 | 0
2025-03-08 09:00 | 43.16 | 89.27 | 43.16 | 0 | 0 | 0 | 0 | 46.11 | 0
2025-03-08 10:00 | 44.16 | 87.98 | 44.16 | 0 | 0 | 0 | 0 | 43.82 | 0
2025-03-08 11:00 | 45.59 | 83.92 | 45.59 | 0 | 0 | 0 | 0 | 38.33 | 0
2025-03-08 12:00 | 46.08 | 82.02 | 46.08 | 0 | 0 | 0 | 0 | 35.94 | 0
2025-03-08 13:00 | 46.94 | 83.58 | 46.94 | 0 | 0 | 0 | 0 | 36.64 | 0
2025-03-08 14:00 | 47.38 | 84.11 | 47.38 | 0 | 0 | 0 | 0 | 36.74 | 0
2025-03-08 15:00 | 47.27 | 89.17 | 47.27 | 0 | 0 | 0 | 0 | 41.9 | 0
2025-03-08 16:00 | 47.74 | 86.84 | 47.74 | 0 | 0 | 0 | 0 | 39.1 | 0
2025-03-08 17:00 | 47.19 | 34.87 | 34.87 | 12.33 | 0 | 0 | 0 | 0 | 0
2025-03-08 18:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 0 | 0 | 0
2025-03-08 19:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 0 | 0 | 0
2025-03-08 20:00 | 44.85 | 0 | 0 | 44.85 | 0 | 0 | 0 | 0 | 0
2025-03-08 21:00 | 43.19 | 0 | 0 | 43.19 | 0 | 0 | 0 | 0 | 0
2025-03-08 22:00 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 0 | 0 | 0
2025-03-08 23:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 0 | 0 | 0
2025-03-09 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0 | 0 | 0
2025-03-09 01:00 | 38.74 | 0 | 0 | 38.74 | 0 | 0 | 0 | 0 | 0
2025-03-09 02:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 0 | 0 | 0
2025-03-09 03:00 | 37.82 | 0 | 0 | 37.82 | 0 | 0 | 0 | 0 | 0
2025-03-09 04:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 0 | 0 | 0
2025-03-09 05:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 0 | 0 | 0
2025-03-09 06:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0 | 0 | 0
2025-03-09 07:00 | 41.22 | 22.18 | 22.18 | 19.03 | 0 | 0 | 0 | 0 | 0
2025-03-09 08:00 | 41.96 | 80.47 | 41.96 | 0 | 0 | 0 | 0 | 38.51 | 0
2025-03-09 09:00 | 43.42 | 94.87 | 43.42 | 0 | 0 | 0 | 0 | 51.45 | 0
2025-03-09 10:00 | 44.42 | 91.81 | 44.42 | 0 | 0 | 0 | 0 | 47.39 | 0
2025-03-09 11:00 | 45.18 | 86.48 | 45.18 | 0 | 0 | 0 | 0 | 41.29 | 0
2025-03-09 12:00 | 46.3 | 83.19 | 46.3 | 0 | 0 | 0 | 0 | 36.89 | 0
2025-03-09 13:00 | 47.2 | 84.31 | 47.2 | 0 | 0 | 0 | 0 | 37.1 | 0
2025-03-09 14:00 | 47.13 | 85.11 | 47.13 | 0 | 0 | 0 | 0 | 37.98 | 0
2025-03-09 15:00 | 47.24 | 86.96 | 47.24 | 0 | 0 | 0 | 0 | 39.72 | 0
2025-03-09 16:00 | 46.83 | 72.75 | 46.83 | 0 | 0 | 0 | 0 | 25.92 | 0
2025-03-09 17:00 | 47.3 | 34.04 | 34.04 | 13.25 | 0 | 0 | 0 | 0 | 0
2025-03-09 18:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 0 | 0 | 0
2025-03-09 19:00 | 45.69 | 0 | 0 | 45.69 | 0 | 0 | 0 | 0 | 0
2025-03-09 20:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 0 | 0 | 0
2025-03-09 21:00 | 43.45 | 0 | 0 | 43.45 | 0 | 0 | 0 | 0 | 0
2025-03-09 22:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0 | 0 | 0
2025-03-09 23:00 | 41.29 | 0 | 0 | 41.29 | 0 | 0 | 0 | 0 | 0
2025-03-10 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 0 | 0 | 0
2025-03-10 01:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0 | 0 | 0
2025-03-10 02:00 | 40.13 | 0 | 0 | 40.13 | 0 | 0 | 0 | 0 | 0
2025-03-10 03:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 0 | 0 | 0
2025-03-10 04:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 0 | 0 | 0
2025-03-10 05:00 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 0 | 0 | 0
2025-03-10 06:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 0 | 0 | 0
2025-03-10 07:00 | 40.7 | 23.9 | 23.9 | 16.8 | 0 | 0 | 0 | 0 | 0
2025-03-10 08:00 | 43.26 | 75.89 | 43.26 | 0 | 0 | 0 | 0 | 32.63 | 0
2025-03-10 09:00 | 44.1 | 81.14 | 44.1 | 0 | 0 | 0 | 0 | 37.05 | 0
2025-03-10 10:00 | 45.08 | 96.37 | 45.08 | 0 | 0 | 0 | 0 | 51.29 | 0
2025-03-10 11:00 | 47.67 | 86.26 | 47.67 | 0 | 0 | 0 | 0 | 38.59 | 0
2025-03-10 12:00 | 48.66 | 76.34 | 48.66 | 0 | 0 | 0 | 0 | 27.68 | 0
2025-03-10 13:00 | 48.71 | 79.31 | 48.71 | 0 | 0 | 0 | 0 | 30.61 | 0
2025-03-10 14:00 | 50.86 | 77.72 | 50.86 | 0 | 0 | 0 | 0 | 26.85 | 0
2025-03-10 15:00 | 50.52 | 63.51 | 50.52 | 0 | 0 | 0 | 0 | 12.99 | 0
2025-03-10 16:00 | 49.97 | 33.47 | 33.47 | 16.5 | 0 | 0 | 0 | 0 | 0
2025-03-10 17:00 | 50.13 | 5.56 | 5.56 | 44.58 | 0 | 0 | 0 | 0 | 0
2025-03-10 18:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0 | 0 | 0
2025-03-10 19:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 0 | 0 | 0
2025-03-10 20:00 | 45.31 | 0 | 0 | 45.31 | 0 | 0 | 0 | 0 | 0
2025-03-10 21:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0 | 0 | 0
2025-03-10 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0 | 0 | 0
2025-03-10 23:00 | 41.41 | 0 | 0 | 41.41 | 0 | 0 | 0 | 0 | 0
2025-03-11 | 40 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0
2025-03-11 01:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0 | 0 | 0
2025-03-11 02:00 | 39.08 | 0 | 0 | 39.08 | 0 | 0 | 0 | 0 | 0
2025-03-11 03:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-03-11 04:00 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 0 | 0 | 0
2025-03-11 05:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0 | 0 | 0
2025-03-11 06:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 0 | 0 | 0
2025-03-11 07:00 | 41.51 | 8.45 | 8.45 | 33.07 | 0 | 0 | 0 | 0 | 0
2025-03-11 08:00 | 42.35 | 16.52 | 16.52 | 25.83 | 0 | 0 | 0 | 0 | 0
2025-03-11 09:00 | 44.49 | 46.23 | 44.49 | 0 | 0 | 0 | 0 | 1.74 | 0
2025-03-11 10:00 | 44.83 | 70.45 | 44.83 | 0 | 0 | 0 | 0 | 25.62 | 0
2025-03-11 11:00 | 46.55 | 69.4 | 46.55 | 0 | 0 | 0 | 0 | 22.85 | 0
2025-03-11 12:00 | 46.99 | 79.68 | 46.99 | 0 | 0 | 0 | 0 | 32.69 | 0
2025-03-11 13:00 | 47.99 | 83.11 | 47.99 | 0 | 0 | 0 | 0 | 35.12 | 0
2025-03-11 14:00 | 48.77 | 87.94 | 48.77 | 0 | 0 | 0 | 0 | 39.18 | 0
2025-03-11 15:00 | 48.33 | 78.28 | 48.33 | 0 | 0 | 0 | 0 | 29.95 | 0
2025-03-11 16:00 | 48.9 | 63.85 | 48.9 | 0 | 0 | 0 | 0 | 14.95 | 0
2025-03-11 17:00 | 47.44 | 34.13 | 34.13 | 13.31 | 0 | 0 | 0 | 0 | 0
2025-03-11 18:00 | 47.34 | 0 | 0 | 47.34 | 0 | 0 | 0 | 0 | 0
2025-03-11 19:00 | 46.68 | 0 | 0 | 46.68 | 0 | 0 | 0 | 0 | 0
2025-03-11 20:00 | 45.4 | 0 | 0 | 45.4 | 0 | 0 | 0 | 0 | 0
2025-03-11 21:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 0 | 0 | 0
2025-03-11 22:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 0 | 0 | 0
2025-03-11 23:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 0 | 0 | 0
2025-03-12 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 0 | 0 | 0
2025-03-12 01:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 0 | 0 | 0
2025-03-12 02:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 0 | 0 | 0
2025-03-12 03:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 0 | 0 | 0
2025-03-12 04:00 | 38.65 | 0 | 0 | 38.65 | 0 | 0 | 0 | 0 | 0
2025-03-12 05:00 | 40.09 | 0 | 0 | 40.09 | 0 | 0 | 0 | 0 | 0
2025-03-12 06:00 | 39.85 | 0 | 0 | 39.85 | 0 | 0 | 0 | 0 | 0
2025-03-12 07:00 | 42 | 18.83 | 18.83 | 23.16 | 0 | 0 | 0 | 0 | 0
2025-03-12 08:00 | 43.89 | 65.3 | 43.89 | 0 | 0 | 0 | 0 | 21.41 | 0
2025-03-12 09:00 | 43.69 | 85.82 | 43.69 | 0 | 0 | 0 | 0 | 42.14 | 0
2025-03-12 10:00 | 44.76 | 59.03 | 44.76 | 0 | 0 | 0 | 0 | 14.26 | 0
2025-03-12 11:00 | 45.06 | 70 | 45.06 | 0 | 0 | 0 | 0 | 24.94 | 0
2025-03-12 12:00 | 45.06 | 60.39 | 45.06 | 0 | 0 | 0 | 0 | 15.33 | 0
2025-03-12 13:00 | 46.13 | 74.88 | 46.13 | 0 | 0 | 0 | 0 | 28.75 | 0
2025-03-12 14:00 | 46.17 | 68.25 | 46.17 | 0 | 0 | 0 | 0 | 22.08 | 0
2025-03-12 15:00 | 46.09 | 61.31 | 46.09 | 0 | 0 | 0 | 0 | 15.23 | 0
2025-03-12 16:00 | 47.58 | 66.9 | 47.58 | 0 | 0 | 0 | 0 | 19.32 | 0
2025-03-12 17:00 | 46.57 | 36.2 | 36.2 | 10.38 | 0 | 0 | 0 | 0 | 0
2025-03-12 18:00 | 46.15 | 0 | 0 | 46.15 | 0 | 0 | 0 | 0 | 0
2025-03-12 19:00 | 45.15 | 0 | 0 | 45.15 | 0 | 0 | 0 | 0 | 0
2025-03-12 20:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 0 | 0 | 0
2025-03-12 21:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 0 | 0 | 0
2025-03-12 22:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0 | 0 | 0
2025-03-12 23:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 0 | 0 | 0
2025-03-13 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0 | 0 | 0
2025-03-13 01:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 0 | 0 | 0
2025-03-13 02:00 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 0 | 0 | 0
2025-03-13 03:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 0 | 0 | 0
2025-03-13 04:00 | 39.17 | 0 | 0 | 39.17 | 0 | 0 | 0 | 0 | 0
2025-03-13 05:00 | 39.84 | 0 | 0 | 39.84 | 0 | 0 | 0 | 0 | 0
2025-03-13 06:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 0 | 0 | 0
2025-03-13 07:00 | 41.54 | 1.76 | 1.76 | 39.78 | 0 | 0 | 0 | 0 | 0
2025-03-13 08:00 | 42.66 | 11.73 | 11.73 | 30.94 | 0 | 0 | 0 | 0 | 0
2025-03-13 09:00 | 42.65 | 17.85 | 17.85 | 24.8 | 0 | 0 | 0 | 0 | 0
2025-03-13 10:00 | 44.29 | 33.1 | 33.1 | 11.19 | 0 | 0 | 0 | 0 | 0
2025-03-13 11:00 | 45.83 | 46.65 | 45.83 | 0 | 0 | 0 | 0 | 0.82 | 0
2025-03-13 12:00 | 46.54 | 62.44 | 46.54 | 0 | 0 | 0 | 0 | 15.91 | 0
2025-03-13 13:00 | 46.28 | 70.32 | 46.28 | 0 | 0 | 0 | 0 | 24.04 | 0
2025-03-13 14:00 | 47.25 | 69.23 | 47.25 | 0 | 0 | 0 | 0 | 21.98 | 0
2025-03-13 15:00 | 47.78 | 86.84 | 47.78 | 0 | 0 | 0 | 0 | 39.06 | 0
2025-03-13 16:00 | 47.56 | 103.26 | 47.56 | 0 | 0 | 0 | 0 | 55.7 | 0
2025-03-13 17:00 | 46.81 | 38.09 | 38.09 | 8.72 | 0 | 0 | 0 | 0 | 0
2025-03-13 18:00 | 46.11 | 0 | 0 | 46.11 | 0 | 0 | 0 | 0 | 0
2025-03-13 19:00 | 45.32 | 0 | 0 | 45.32 | 0 | 0 | 0 | 0 | 0
2025-03-13 20:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0 | 0 | 0
2025-03-13 21:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 0 | 0 | 0
2025-03-13 22:00 | 42.95 | 0 | 0 | 42.95 | 0 | 0 | 0 | 0 | 0
2025-03-13 23:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 0 | 0 | 0
2025-03-14 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 0 | 0 | 0
2025-03-14 01:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 0 | 0 | 0
2025-03-14 02:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 0 | 0 | 0
2025-03-14 03:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 0 | 0 | 0
2025-03-14 04:00 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
2025-03-14 05:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 0 | 0 | 0
2025-03-14 06:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 0 | 0 | 0
2025-03-14 07:00 | 41.84 | 44.95 | 41.84 | 0 | 0 | 0 | 0 | 3.1 | 0
2025-03-14 08:00 | 41.98 | 103.66 | 41.98 | 0 | 0 | 0 | 0 | 61.68 | 0
2025-03-14 09:00 | 43.63 | 75.11 | 43.63 | 0 | 0 | 0 | 0 | 31.49 | 0
2025-03-14 10:00 | 45.46 | 59.69 | 45.46 | 0 | 0 | 0 | 0 | 14.23 | 0
2025-03-14 11:00 | 45.9 | 78.51 | 45.9 | 0 | 0 | 0 | 0 | 32.61 | 0
2025-03-14 12:00 | 46.57 | 102.98 | 46.57 | 0 | 0 | 0 | 0 | 56.4 | 0
2025-03-14 13:00 | 48.11 | 92.12 | 48.11 | 0 | 0 | 0 | 0 | 44.01 | 0
2025-03-14 14:00 | 47.24 | 48.56 | 47.24 | 0 | 0 | 0 | 0 | 1.32 | 0
2025-03-14 15:00 | 47.48 | 3.65 | 3.65 | 43.83 | 0 | 0 | 0 | 0 | 0
2025-03-14 16:00 | 47.87 | 20.84 | 20.84 | 27.03 | 0 | 0 | 0 | 0 | 0
2025-03-14 17:00 | 47.6 | 2.91 | 2.91 | 44.69 | 0 | 0 | 0 | 0 | 0
2025-03-14 18:00 | 47.08 | 0 | 0 | 47.08 | 0 | 0 | 0 | 0 | 0
2025-03-14 19:00 | 46.5 | 0 | 0 | 46.5 | 0 | 0 | 0 | 0 | 0
2025-03-14 20:00 | 45.17 | 0 | 0 | 45.17 | 0 | 0 | 0 | 0 | 0
2025-03-14 21:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 0 | 0 | 0
2025-03-14 22:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0 | 0 | 0
2025-03-14 23:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0 | 0 | 0
2025-03-15 | 40.94 | 0 | 0 | 40.94 | 0 | 0 | 0 | 0 | 0
2025-03-15 01:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 0 | 0 | 0
2025-03-15 02:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0 | 0 | 0
2025-03-15 03:00 | 39.6 | 0 | 0 | 39.6 | 0 | 0 | 0 | 0 | 0
2025-03-15 04:00 | 39.53 | 0 | 0 | 39.53 | 0 | 0 | 0 | 0 | 0
2025-03-15 05:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0 | 0 | 0
2025-03-15 06:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0 | 0 | 0
2025-03-15 07:00 | 42 | 3.34 | 3.34 | 38.65 | 0 | 0 | 0 | 0 | 0
2025-03-15 08:00 | 43.45 | 8.38 | 8.38 | 35.06 | 0 | 0 | 0 | 0 | 0
2025-03-15 09:00 | 45.92 | 12.94 | 12.94 | 32.98 | 0 | 0 | 0 | 0 | 0
2025-03-15 10:00 | 46.05 | 12.96 | 12.96 | 33.1 | 0 | 0 | 0 | 0 | 0
2025-03-15 11:00 | 47.95 | 6.48 | 6.48 | 41.47 | 0 | 0 | 0 | 0 | 0
2025-03-15 12:00 | 49.52 | 24.1 | 24.1 | 25.42 | 0 | 0 | 0 | 0 | 0
2025-03-15 13:00 | 50 | 32.89 | 32.89 | 17.11 | 0 | 0 | 0 | 0 | 0
2025-03-15 14:00 | 51.73 | 42.88 | 42.88 | 8.86 | 0 | 0 | 0 | 0 | 0
2025-03-15 15:00 | 50.59 | 38.92 | 38.92 | 11.66 | 0 | 0 | 0 | 0 | 0
2025-03-15 16:00 | 50.73 | 56.03 | 50.73 | 0 | 0 | 0 | 0 | 5.31 | 0
2025-03-15 17:00 | 49.55 | 35.18 | 35.18 | 14.38 | 0 | 0 | 0 | 0 | 0
2025-03-15 18:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 0 | 0 | 0
2025-03-15 19:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 0 | 0 | 0
2025-03-15 20:00 | 46.74 | 0 | 0 | 46.74 | 0 | 0 | 0 | 0 | 0
2025-03-15 21:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0 | 0 | 0
2025-03-15 22:00 | 43.98 | 0 | 0 | 43.98 | 0 | 0 | 0 | 0 | 0
2025-03-15 23:00 | 41.96 | 0 | 0 | 41.96 | 0 | 0 | 0 | 0 | 0
2025-03-16 | 40.83 | 0 | 0 | 40.83 | 0 | 0 | 0 | 0 | 0
2025-03-16 01:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-03-16 02:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 0 | 0 | 0
2025-03-16 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0 | 0 | 0
2025-03-16 04:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 0 | 0 | 0
2025-03-16 05:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0 | 0 | 0
2025-03-16 06:00 | 41.46 | 0 | 0 | 41.46 | 0 | 0 | 0 | 0 | 0
2025-03-16 07:00 | 41.92 | 14.95 | 14.95 | 26.97 | 0 | 0 | 0 | 0 | 0
2025-03-16 08:00 | 43.48 | 21.45 | 21.45 | 22.03 | 0 | 0 | 0 | 0 | 0
2025-03-16 09:00 | 44.79 | 32.26 | 32.26 | 12.53 | 0 | 0 | 0 | 0 | 0
2025-03-16 10:00 | 46.6 | 31.93 | 31.93 | 14.67 | 0 | 0 | 0 | 0 | 0
2025-03-16 11:00 | 47.14 | 38.63 | 38.63 | 8.52 | 0 | 0 | 0 | 0 | 0
2025-03-16 12:00 | 48.18 | 31.11 | 31.11 | 17.07 | 0 | 0 | 0 | 0 | 0
2025-03-16 13:00 | 49.71 | 19.71 | 19.71 | 30.01 | 0 | 0 | 0 | 0 | 0
2025-03-16 14:00 | 50.46 | 13.27 | 13.27 | 37.19 | 0 | 0 | 0 | 0 | 0
2025-03-16 15:00 | 50.52 | 15.26 | 15.26 | 35.26 | 0 | 0 | 0 | 0 | 0
2025-03-16 16:00 | 49.76 | 10.85 | 10.85 | 38.9 | 0 | 0 | 0 | 0 | 0
2025-03-16 17:00 | 49.94 | 4.07 | 4.07 | 45.87 | 0 | 0 | 0 | 0 | 0
2025-03-16 18:00 | 48.35 | 0 | 0 | 48.35 | 0 | 0 | 0 | 0 | 0
2025-03-16 19:00 | 47.31 | 0 | 0 | 47.31 | 0 | 0 | 0 | 0 | 0
2025-03-16 20:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 0 | 0 | 0
2025-03-16 21:00 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 0 | 0 | 0
2025-03-16 22:00 | 43.73 | 0 | 0 | 43.73 | 0 | 0 | 0 | 0 | 0
2025-03-16 23:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 0 | 0 | 0
2025-03-17 | 41.76 | 0 | 0 | 41.76 | 0 | 0 | 0 | 0 | 0
2025-03-17 01:00 | 41.66 | 0 | 0 | 41.66 | 0 | 0 | 0 | 0 | 0
2025-03-17 02:00 | 38.86 | 0 | 0 | 38.86 | 0 | 0 | 0 | 0 | 0
2025-03-17 03:00 | 39.16 | 0 | 0 | 39.16 | 0 | 0 | 0 | 0 | 0
2025-03-17 04:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 0 | 0 | 0
2025-03-17 05:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0 | 0 | 0
2025-03-17 06:00 | 40.6 | 0 | 0 | 40.6 | 0 | 0 | 0 | 0 | 0
2025-03-17 07:00 | 42.16 | 0 | 0 | 42.16 | 0 | 0 | 0 | 0 | 0
2025-03-17 08:00 | 43.1 | 2.45 | 2.45 | 40.65 | 0 | 0 | 0 | 0 | 0
2025-03-17 09:00 | 45.43 | 4.31 | 4.31 | 41.12 | 0 | 0 | 0 | 0 | 0
2025-03-17 10:00 | 46.88 | 5.16 | 5.16 | 41.72 | 0 | 0 | 0 | 0 | 0
2025-03-17 11:00 | 48.62 | 7.18 | 7.18 | 41.44 | 0 | 0 | 0 | 0 | 0
2025-03-17 12:00 | 49.97 | 7.39 | 7.39 | 42.59 | 0 | 0 | 0 | 0 | 0
2025-03-17 13:00 | 51.07 | 62.54 | 51.07 | 0 | 0 | 0 | 0 | 11.47 | 0
2025-03-17 14:00 | 51.25 | 57.12 | 51.25 | 0 | 0 | 0 | 0 | 5.87 | 0
2025-03-17 15:00 | 52.73 | 51.99 | 51.99 | 0.74 | 0 | 0 | 0 | 0 | 0
2025-03-17 16:00 | 51.55 | 40.06 | 40.06 | 11.49 | 0 | 0 | 0 | 0 | 0
2025-03-17 17:00 | 49.84 | 19.98 | 19.98 | 29.86 | 0 | 0 | 0 | 0 | 0
2025-03-17 18:00 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 0 | 0 | 0
2025-03-17 19:00 | 47.51 | 0 | 0 | 47.51 | 0 | 0 | 0 | 0 | 0
2025-03-17 20:00 | 46.86 | 0 | 0 | 46.86 | 0 | 0 | 0 | 0 | 0
2025-03-17 21:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 0 | 0 | 0
2025-03-17 22:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0 | 0 | 0
2025-03-17 23:00 | 43.32 | 0 | 0 | 43.32 | 0 | 0 | 0 | 0 | 0
2025-03-18 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-03-18 01:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 0 | 0 | 0
2025-03-18 02:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 0 | 0 | 0
2025-03-18 03:00 | 39.13 | 0 | 0 | 39.13 | 0 | 0 | 0 | 0 | 0
2025-03-18 04:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0 | 0 | 0
2025-03-18 05:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 0 | 0 | 0
2025-03-18 06:00 | 40.29 | 0.04 | 0.04 | 40.24 | 0 | 0 | 0 | 0 | 0
2025-03-18 07:00 | 42.22 | 0.01 | 0.01 | 42.22 | 0 | 0 | 0 | 0 | 0
2025-03-18 08:00 | 43.58 | 41.14 | 41.14 | 2.44 | 0 | 0 | 0 | 0 | 0
2025-03-18 09:00 | 44.78 | 104.28 | 44.78 | 0 | 0 | 0 | 0 | 59.5 | 0
2025-03-18 10:00 | 45.78 | 109.1 | 45.78 | 0 | 0 | 0 | 0 | 63.33 | 0
2025-03-18 11:00 | 47.09 | 99.65 | 47.09 | 0 | 0 | 0 | 0 | 52.56 | 0
2025-03-18 12:00 | 48.27 | 100.48 | 48.27 | 0 | 0 | 0 | 0 | 52.21 | 0
2025-03-18 13:00 | 49.15 | 61.6 | 49.15 | 0 | 0 | 0 | 0 | 12.44 | 0
2025-03-18 14:00 | 49.88 | 25.46 | 25.46 | 24.41 | 0 | 0 | 0 | 0 | 0
2025-03-18 15:00 | 50.27 | 3.68 | 3.68 | 46.59 | 0 | 0 | 0 | 0 | 0
2025-03-18 16:00 | 49.43 | 1.98 | 1.98 | 47.45 | 0 | 0 | 0 | 0 | 0
2025-03-18 17:00 | 48.88 | 25.22 | 25.22 | 23.66 | 0 | 0 | 0 | 0 | 0
2025-03-18 18:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0 | 0 | 0
2025-03-18 19:00 | 47.67 | 0 | 0 | 47.67 | 0 | 0 | 0 | 0 | 0
2025-03-18 20:00 | 45.97 | 0 | 0 | 45.97 | 0 | 0 | 0 | 0 | 0
2025-03-18 21:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 0 | 0 | 0
2025-03-18 22:00 | 44.06 | 0 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0
2025-03-18 23:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 0 | 0 | 0
2025-03-19 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 0 | 0 | 0
2025-03-19 01:00 | 40.04 | 0 | 0 | 40.04 | 0 | 0 | 0 | 0 | 0
2025-03-19 02:00 | 39.93 | 0 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0
2025-03-19 03:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 0 | 0 | 0
2025-03-19 04:00 | 39.87 | 0 | 0 | 39.87 | 0 | 0 | 0 | 0 | 0
2025-03-19 05:00 | 40.15 | 0 | 0 | 40.15 | 0 | 0 | 0 | 0 | 0
2025-03-19 06:00 | 40.62 | 0 | 0 | 40.62 | 0 | 0 | 0 | 0 | 0
2025-03-19 07:00 | 42.57 | 15.79 | 15.79 | 26.78 | 0 | 0 | 0 | 0 | 0
2025-03-19 08:00 | 43.5 | 40 | 40 | 3.5 | 0 | 0 | 0 | 0 | 0
2025-03-19 09:00 | 45.4 | 48.8 | 45.4 | 0 | 0 | 0 | 0 | 3.39 | 0
2025-03-19 10:00 | 46.44 | 80.53 | 46.44 | 0 | 0 | 0 | 0 | 34.08 | 0
2025-03-19 11:00 | 47.68 | 71.06 | 47.68 | 0 | 0 | 0 | 0 | 23.38 | 0
2025-03-19 12:00 | 49.55 | 66.07 | 49.55 | 0 | 0 | 0 | 0 | 16.52 | 0
2025-03-19 13:00 | 50.43 | 90.94 | 50.43 | 0 | 0 | 0 | 0 | 40.5 | 0
2025-03-19 14:00 | 51.23 | 94.6 | 51.23 | 0 | 0 | 0 | 0 | 43.36 | 0
2025-03-19 15:00 | 52.24 | 70.83 | 52.24 | 0 | 0 | 0 | 0 | 18.6 | 0
2025-03-19 16:00 | 51.08 | 65.82 | 51.08 | 0 | 0 | 0 | 0 | 14.74 | 0
2025-03-19 17:00 | 50.6 | 27.73 | 27.73 | 22.88 | 0 | 0 | 0 | 0 | 0
2025-03-19 18:00 | 48.89 | 0.33 | 0.33 | 48.57 | 0 | 0 | 0 | 0 | 0
2025-03-19 19:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0 | 0 | 0
2025-03-19 20:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0 | 0 | 0
2025-03-19 21:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0 | 0 | 0
2025-03-19 22:00 | 43.36 | 0 | 0 | 43.36 | 0 | 0 | 0 | 0 | 0
2025-03-19 23:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 0 | 0 | 0
2025-03-20 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 0 | 0 | 0
2025-03-20 01:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 0 | 0 | 0
2025-03-20 02:00 | 39.88 | 0 | 0 | 39.88 | 0 | 0 | 0 | 0 | 0
2025-03-20 03:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 0 | 0 | 0
2025-03-20 04:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0 | 0 | 0
2025-03-20 05:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 0 | 0 | 0
2025-03-20 06:00 | 41.98 | 0.01 | 0.01 | 41.97 | 0 | 0 | 0 | 0 | 0
2025-03-20 07:00 | 42.97 | 21.23 | 21.23 | 21.75 | 0 | 0 | 0 | 0 | 0
2025-03-20 08:00 | 43.87 | 44.86 | 43.87 | 0 | 0 | 0 | 0 | 0.99 | 0
2025-03-20 09:00 | 44.99 | 70.98 | 44.99 | 0 | 0 | 0 | 0 | 26 | 0
2025-03-20 10:00 | 47.04 | 67.15 | 47.04 | 0 | 0 | 0 | 0 | 20.11 | 0
2025-03-20 11:00 | 48.96 | 70.78 | 48.96 | 0 | 0 | 0 | 0 | 21.82 | 0
2025-03-20 12:00 | 50.94 | 79.82 | 50.94 | 0 | 0 | 0 | 0 | 28.88 | 0
2025-03-20 13:00 | 50.91 | 84.15 | 50.91 | 0 | 0 | 0 | 0 | 33.24 | 0
2025-03-20 14:00 | 52.07 | 85.22 | 52.07 | 0 | 0 | 0 | 0 | 33.15 | 0
2025-03-20 15:00 | 52.69 | 79.71 | 52.69 | 0 | 0 | 0 | 0 | 27.02 | 0
2025-03-20 16:00 | 50.92 | 97.17 | 50.92 | 0 | 0 | 0 | 0 | 46.25 | 0
2025-03-20 17:00 | 51.95 | 71.64 | 51.95 | 0 | 0 | 0 | 0 | 19.69 | 0
2025-03-20 18:00 | 49.77 | 1.24 | 1.24 | 48.53 | 0 | 0 | 0 | 0 | 0
2025-03-20 19:00 | 49.15 | 0 | 0 | 49.15 | 0 | 0 | 0 | 0 | 0
2025-03-20 20:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0 | 0 | 0
2025-03-20 21:00 | 46.32 | 0 | 0 | 46.32 | 0 | 0 | 0 | 0 | 0
2025-03-20 22:00 | 44.45 | 0 | 0 | 44.45 | 0 | 0 | 0 | 0 | 0
2025-03-20 23:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 0 | 0 | 0
2025-03-21 | 41.21 | 0 | 0 | 41.21 | 0 | 0 | 0 | 0 | 0
2025-03-21 01:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 0 | 0 | 0
2025-03-21 02:00 | 40.04 | 0 | 0 | 40.04 | 0 | 0 | 0 | 0 | 0
2025-03-21 03:00 | 40.18 | 0 | 0 | 40.18 | 0 | 0 | 0 | 0 | 0
2025-03-21 04:00 | 40.53 | 0 | 0 | 40.53 | 0 | 0 | 0 | 0 | 0
2025-03-21 05:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0 | 0 | 0
2025-03-21 06:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-03-21 07:00 | 41.83 | 6.39 | 6.39 | 35.44 | 0 | 0 | 0 | 0 | 0
2025-03-21 08:00 | 43.85 | 17.78 | 17.78 | 26.07 | 0 | 0 | 0 | 0 | 0
2025-03-21 09:00 | 45.69 | 39.53 | 39.53 | 6.17 | 0 | 0 | 0 | 0 | 0
2025-03-21 10:00 | 46.32 | 39.7 | 39.7 | 6.62 | 0 | 0 | 0 | 0 | 0
2025-03-21 11:00 | 48.45 | 50.93 | 48.45 | 0 | 0 | 0 | 0 | 2.48 | 0
2025-03-21 12:00 | 49.66 | 49.98 | 49.66 | 0 | 0 | 0 | 0 | 0.32 | 0
2025-03-21 13:00 | 50.09 | 34.83 | 34.83 | 15.25 | 0 | 0 | 0 | 0 | 0
2025-03-21 14:00 | 49 | 23.98 | 23.98 | 25.02 | 0 | 0 | 0 | 0 | 0
2025-03-21 15:00 | 50.07 | 12.79 | 12.79 | 37.28 | 0 | 0 | 0 | 0 | 0
2025-03-21 16:00 | 51.48 | 9.36 | 9.36 | 42.12 | 0 | 0 | 0 | 0 | 0
2025-03-21 17:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0 | 0 | 0
2025-03-21 18:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 0 | 0 | 0
2025-03-21 19:00 | 48.75 | 0 | 0 | 48.75 | 0 | 0 | 0 | 0 | 0
2025-03-21 20:00 | 46.87 | 0 | 0 | 46.87 | 0 | 0 | 0 | 0 | 0
2025-03-21 21:00 | 46.04 | 0 | 0 | 46.04 | 0 | 0 | 0 | 0 | 0
2025-03-21 22:00 | 44.22 | 0 | 0 | 44.22 | 0 | 0 | 0 | 0 | 0
2025-03-21 23:00 | 42.98 | 0 | 0 | 42.98 | 0 | 0 | 0 | 0 | 0
2025-03-22 | 41.94 | 0 | 0 | 41.94 | 0 | 0 | 0 | 0 | 0
2025-03-22 01:00 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 0 | 0 | 0
2025-03-22 02:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 0 | 0 | 0
2025-03-22 03:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 0 | 0 | 0
2025-03-22 04:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 0 | 0 | 0
2025-03-22 05:00 | 41.05 | 0 | 0 | 41.05 | 0 | 0 | 0 | 0 | 0
2025-03-22 06:00 | 42.33 | 0.13 | 0.13 | 42.2 | 0 | 0 | 0 | 0 | 0
2025-03-22 07:00 | 43.6 | 4.36 | 4.36 | 39.24 | 0 | 0 | 0 | 0 | 0
2025-03-22 08:00 | 44.25 | 41.83 | 41.83 | 2.41 | 0 | 0 | 0 | 0 | 0
2025-03-22 09:00 | 46.65 | 61.56 | 46.65 | 0 | 0 | 0 | 0 | 14.91 | 0
2025-03-22 10:00 | 48.16 | 56.68 | 48.16 | 0 | 0 | 0 | 0 | 8.52 | 0
2025-03-22 11:00 | 50.54 | 55.04 | 50.54 | 0 | 0 | 0 | 0 | 4.5 | 0
2025-03-22 12:00 | 50.23 | 70.72 | 50.23 | 0 | 0 | 0 | 0 | 20.49 | 0
2025-03-22 13:00 | 51.4 | 52.75 | 51.4 | 0 | 0 | 0 | 0 | 1.34 | 0
2025-03-22 14:00 | 52.17 | 69.78 | 52.17 | 0 | 0 | 0 | 0 | 17.61 | 0
2025-03-22 15:00 | 52.31 | 110.66 | 52.31 | 0 | 0 | 0 | 0 | 58.35 | 0
2025-03-22 16:00 | 51.88 | 75.8 | 51.88 | 0 | 0 | 0 | 0 | 23.92 | 0
2025-03-22 17:00 | 50.28 | 53.58 | 50.28 | 0 | 0 | 0 | 0 | 3.3 | 0
2025-03-22 18:00 | 50.39 | 0.52 | 0.52 | 49.87 | 0 | 0 | 0 | 0 | 0
2025-03-22 19:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 0 | 0 | 0
2025-03-22 20:00 | 47.45 | 0 | 0 | 47.45 | 0 | 0 | 0 | 0 | 0
2025-03-22 21:00 | 47.03 | 0 | 0 | 47.03 | 0 | 0 | 0 | 0 | 0
2025-03-22 22:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 0 | 0 | 0
2025-03-22 23:00 | 43.64 | 0 | 0 | 43.64 | 0 | 0 | 0 | 0 | 0
2025-03-23 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 0 | 0 | 0
2025-03-23 01:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 0 | 0 | 0
2025-03-23 02:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 0 | 0 | 0
2025-03-23 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0 | 0 | 0
2025-03-23 04:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 0 | 0 | 0
2025-03-23 05:00 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 0 | 0 | 0
2025-03-23 06:00 | 42.03 | 0.62 | 0.62 | 41.4 | 0 | 0 | 0 | 0 | 0
2025-03-23 07:00 | 42.86 | 47.26 | 42.86 | 0 | 0 | 0 | 0 | 4.4 | 0
2025-03-23 08:00 | 44.51 | 88.35 | 44.51 | 0 | 0 | 0 | 0 | 43.84 | 0
2025-03-23 09:00 | 46.78 | 101.35 | 46.78 | 0 | 0 | 0 | 0 | 54.56 | 0
2025-03-23 10:00 | 46.84 | 96.08 | 46.84 | 0 | 0 | 0 | 0 | 49.24 | 0
2025-03-23 11:00 | 48.37 | 91.41 | 48.37 | 0 | 0 | 0 | 0 | 43.04 | 0
2025-03-23 12:00 | 49.77 | 90.52 | 49.77 | 0 | 0 | 0 | 0 | 40.76 | 0
2025-03-23 13:00 | 50.44 | 91.85 | 50.44 | 0 | 0 | 0 | 0 | 41.41 | 0
2025-03-23 14:00 | 50.33 | 97.14 | 50.33 | 0 | 0 | 0 | 0 | 46.81 | 0
2025-03-23 15:00 | 49.28 | 96.71 | 49.28 | 0 | 0 | 0 | 0 | 47.43 | 0
2025-03-23 16:00 | 50.58 | 79.24 | 50.58 | 0 | 0 | 0 | 0 | 28.66 | 0
2025-03-23 17:00 | 48.76 | 44.7 | 44.7 | 4.06 | 0 | 0 | 0 | 0 | 0
2025-03-23 18:00 | 49.87 | 0.91 | 0.91 | 48.96 | 0 | 0 | 0 | 0 | 0
2025-03-23 19:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 0 | 0 | 0
2025-03-23 20:00 | 47.48 | 0 | 0 | 47.48 | 0 | 0 | 0 | 0 | 0
2025-03-23 21:00 | 45.21 | 0 | 0 | 45.21 | 0 | 0 | 0 | 0 | 0
2025-03-23 22:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0 | 0 | 0
2025-03-23 23:00 | 43.13 | 0 | 0 | 43.13 | 0 | 0 | 0 | 0 | 0
2025-03-24 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 0 | 0 | 0
2025-03-24 01:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 0 | 0 | 0
2025-03-24 02:00 | 40.51 | 0 | 0 | 40.51 | 0 | 0 | 0 | 0 | 0
2025-03-24 03:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 0 | 0 | 0
2025-03-24 04:00 | 40.89 | 0 | 0 | 40.89 | 0 | 0 | 0 | 0 | 0
2025-03-24 05:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 0 | 0 | 0
2025-03-24 06:00 | 42.41 | 0.89 | 0.89 | 41.52 | 0 | 0 | 0 | 0 | 0
2025-03-24 07:00 | 43.93 | 70.1 | 43.93 | 0 | 0 | 0 | 0 | 26.17 | 0
2025-03-24 08:00 | 44.47 | 96.17 | 44.47 | 0 | 0 | 0 | 0 | 51.71 | 0
2025-03-24 09:00 | 44.98 | 6.15 | 6.15 | 38.83 | 0 | 0 | 0 | 0 | 0
2025-03-24 10:00 | 47.34 | 29.44 | 29.44 | 17.9 | 0 | 0 | 0 | 0 | 0
2025-03-24 11:00 | 49.14 | 22.52 | 22.52 | 26.62 | 0 | 0 | 0 | 0 | 0
2025-03-24 12:00 | 49.35 | 53.96 | 49.35 | 0 | 0 | 0 | 0 | 4.61 | 0
2025-03-24 13:00 | 50.58 | 107.36 | 50.58 | 0 | 0 | 0 | 0 | 56.78 | 0
2025-03-24 14:00 | 50.84 | 112.43 | 50.84 | 0 | 0 | 0 | 0 | 61.59 | 0
2025-03-24 15:00 | 52.11 | 116.21 | 52.11 | 0 | 0 | 0 | 0 | 64.1 | 0
2025-03-24 16:00 | 51.56 | 112.42 | 51.56 | 0 | 0 | 0 | 0 | 60.86 | 0
2025-03-24 17:00 | 50.99 | 75.48 | 50.99 | 0 | 0 | 0 | 0 | 24.49 | 0
2025-03-24 18:00 | 50.15 | 2.42 | 2.42 | 47.72 | 0 | 0 | 0 | 0 | 0
2025-03-24 19:00 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 0 | 0 | 0
2025-03-24 20:00 | 47.53 | 0 | 0 | 47.53 | 0 | 0 | 0 | 0 | 0
2025-03-24 21:00 | 45.42 | 0 | 0 | 45.42 | 0 | 0 | 0 | 0 | 0
2025-03-24 22:00 | 43.47 | 0 | 0 | 43.47 | 0 | 0 | 0 | 0 | 0
2025-03-24 23:00 | 43.26 | 0 | 0 | 43.26 | 0 | 0 | 0 | 0 | 0
2025-03-25 | 42.29 | 0 | 0 | 42.29 | 0 | 0 | 0 | 0 | 0
2025-03-25 01:00 | 41.79 | 0 | 0 | 41.79 | 0 | 0 | 0 | 0 | 0
2025-03-25 02:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 0 | 0 | 0
2025-03-25 03:00 | 41.16 | 0 | 0 | 41.16 | 0 | 0 | 0 | 0 | 0
2025-03-25 04:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 0 | 0 | 0
2025-03-25 05:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0 | 0 | 0
2025-03-25 06:00 | 42.36 | 0.89 | 0.89 | 41.47 | 0 | 0 | 0 | 0 | 0
2025-03-25 07:00 | 44.6 | 56.07 | 44.6 | 0 | 0 | 0 | 0 | 11.47 | 0
2025-03-25 08:00 | 45.46 | 81.64 | 45.46 | 0 | 0 | 0 | 0 | 36.17 | 0
2025-03-25 09:00 | 46.75 | 100.18 | 46.75 | 0 | 0 | 0 | 0 | 53.43 | 0
2025-03-25 10:00 | 47.43 | 95.28 | 47.43 | 0 | 0 | 0 | 0 | 47.85 | 0
2025-03-25 11:00 | 48.5 | 91.9 | 48.5 | 0 | 0 | 0 | 0 | 43.41 | 0
2025-03-25 12:00 | 50.44 | 93.31 | 50.44 | 0 | 0 | 0 | 0 | 42.87 | 0
2025-03-25 13:00 | 50.33 | 70.1 | 50.33 | 0 | 0 | 0 | 0 | 19.77 | 0
2025-03-25 14:00 | 51.29 | 75.5 | 51.29 | 0 | 0 | 0 | 0 | 24.22 | 0
2025-03-25 15:00 | 51.52 | 68.59 | 51.52 | 0 | 0 | 0 | 0 | 17.06 | 0
2025-03-25 16:00 | 52.2 | 49.36 | 49.36 | 2.84 | 0 | 0 | 0 | 0 | 0
2025-03-25 17:00 | 50.71 | 23.19 | 23.19 | 27.51 | 0 | 0 | 0 | 0 | 0
2025-03-25 18:00 | 48.83 | 1.04 | 1.04 | 47.78 | 0 | 0 | 0 | 0 | 0
2025-03-25 19:00 | 49.19 | 0 | 0 | 49.19 | 0 | 0 | 0 | 0 | 0
2025-03-25 20:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 0 | 0 | 0
2025-03-25 21:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 0 | 0 | 0
2025-03-25 22:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0 | 0 | 0
2025-03-25 23:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 0 | 0 | 0
2025-03-26 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 0 | 0 | 0
2025-03-26 01:00 | 40.53 | 0 | 0 | 40.53 | 0 | 0 | 0 | 0 | 0
2025-03-26 02:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 0 | 0 | 0
2025-03-26 03:00 | 40.83 | 0 | 0 | 40.83 | 0 | 0 | 0 | 0 | 0
2025-03-26 04:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 0 | 0 | 0
2025-03-26 05:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0 | 0 | 0
2025-03-26 06:00 | 42.56 | 1.32 | 1.32 | 41.23 | 0 | 0 | 0 | 0 | 0
2025-03-26 07:00 | 43.94 | 56.25 | 43.94 | 0 | 0 | 0 | 0 | 12.32 | 0
2025-03-26 08:00 | 44.63 | 89.86 | 44.63 | 0 | 0 | 0 | 0 | 45.23 | 0
2025-03-26 09:00 | 44.95 | 100.72 | 44.95 | 0 | 0 | 0 | 0 | 55.77 | 0
2025-03-26 10:00 | 47.48 | 99.55 | 47.48 | 0 | 0 | 0 | 0 | 52.07 | 0
2025-03-26 11:00 | 47.33 | 95.17 | 47.33 | 0 | 0 | 0 | 0 | 47.84 | 0
2025-03-26 12:00 | 49.14 | 91.87 | 49.14 | 0 | 0 | 0 | 0 | 42.73 | 0
2025-03-26 13:00 | 49.14 | 95.36 | 49.14 | 0 | 0 | 0 | 0 | 46.22 | 0
2025-03-26 14:00 | 49.36 | 97.22 | 49.36 | 0 | 0 | 0 | 0 | 47.86 | 0
2025-03-26 15:00 | 49.84 | 100.8 | 49.84 | 0 | 0 | 0 | 0 | 50.96 | 0
2025-03-26 16:00 | 49.85 | 90.11 | 49.85 | 0 | 0 | 0 | 0 | 40.26 | 0
2025-03-26 17:00 | 49.26 | 59.1 | 49.26 | 0 | 0 | 0 | 0 | 9.84 | 0
2025-03-26 18:00 | 49.28 | 1.43 | 1.43 | 47.85 | 0 | 0 | 0 | 0 | 0
2025-03-26 19:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0 | 0 | 0
2025-03-26 20:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 0 | 0 | 0
2025-03-26 21:00 | 46.07 | 0 | 0 | 46.07 | 0 | 0 | 0 | 0 | 0
2025-03-26 22:00 | 44.3 | 0 | 0 | 44.3 | 0 | 0 | 0 | 0 | 0
2025-03-26 23:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0 | 0 | 0
2025-03-27 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 0 | 0 | 0
2025-03-27 01:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 0 | 0 | 0
2025-03-27 02:00 | 40.64 | 0 | 0 | 40.64 | 0 | 0 | 0 | 0 | 0
2025-03-27 03:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0 | 0 | 0
2025-03-27 04:00 | 40.55 | 0 | 0 | 40.55 | 0 | 0 | 0 | 0 | 0
2025-03-27 05:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 0 | 0 | 0
2025-03-27 06:00 | 43.22 | 1.32 | 1.32 | 41.91 | 0 | 0 | 0 | 0 | 0
2025-03-27 07:00 | 42.91 | 55.68 | 42.91 | 0 | 0 | 0 | 0 | 12.77 | 0
2025-03-27 08:00 | 44.61 | 93.66 | 44.61 | 0 | 0 | 0 | 0 | 49.05 | 0
2025-03-27 09:00 | 47.61 | 106.18 | 47.61 | 0 | 0 | 0 | 0 | 58.58 | 0
2025-03-27 10:00 | 49.49 | 107.81 | 49.49 | 0 | 0 | 0 | 0 | 58.32 | 0
2025-03-27 11:00 | 50.11 | 87.49 | 50.11 | 0 | 0 | 0 | 0 | 37.38 | 0
2025-03-27 12:00 | 51.62 | 76.58 | 51.62 | 0 | 0 | 0 | 0 | 24.96 | 0
2025-03-27 13:00 | 53.38 | 80.81 | 53.38 | 0 | 0 | 0 | 0 | 27.42 | 0
2025-03-27 14:00 | 52.63 | 93.62 | 52.63 | 0 | 0 | 0 | 0 | 40.98 | 0
2025-03-27 15:00 | 53.11 | 75.08 | 53.11 | 0 | 0 | 0 | 0 | 21.97 | 0
2025-03-27 16:00 | 53.65 | 37.82 | 37.82 | 15.84 | 0 | 0 | 0 | 0 | 0
2025-03-27 17:00 | 53.85 | 25.65 | 25.65 | 28.2 | 0 | 0 | 0 | 0 | 0
2025-03-27 18:00 | 51.72 | 1.4 | 1.4 | 50.32 | 0 | 0 | 0 | 0 | 0
2025-03-27 19:00 | 50.53 | 0 | 0 | 50.53 | 0 | 0 | 0 | 0 | 0
2025-03-27 20:00 | 49.38 | 0 | 0 | 49.38 | 0 | 0 | 0 | 0 | 0
2025-03-27 21:00 | 48.11 | 0 | 0 | 48.11 | 0 | 0 | 0 | 0 | 0
2025-03-27 22:00 | 45.04 | 0 | 0 | 45.04 | 0 | 0 | 0 | 0 | 0
2025-03-27 23:00 | 43.75 | 0 | 0 | 43.75 | 0 | 0 | 0 | 0 | 0
2025-03-28 | 43.44 | 0 | 0 | 43.44 | 0 | 0 | 0 | 0 | 0
2025-03-28 01:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0 | 0 | 0
2025-03-28 02:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 0 | 0 | 0
2025-03-28 03:00 | 40.21 | 0 | 0 | 40.21 | 0 | 0 | 0 | 0 | 0
2025-03-28 04:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 0 | 0 | 0
2025-03-28 05:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 0 | 0 | 0
2025-03-28 06:00 | 42.05 | 2.6 | 2.6 | 39.45 | 0 | 0 | 0 | 0 | 0
2025-03-28 07:00 | 43.29 | 79.14 | 43.29 | 0 | 0 | 0 | 0 | 35.85 | 0
2025-03-28 08:00 | 45.35 | 111.12 | 45.35 | 0 | 0 | 0 | 0 | 65.77 | 0
2025-03-28 09:00 | 47.21 | 114.7 | 47.21 | 0 | 0 | 0 | 0 | 67.49 | 0
2025-03-28 10:00 | 48.12 | 111.79 | 48.12 | 0 | 0 | 0 | 0 | 63.67 | 0
2025-03-28 11:00 | 49.55 | 106.32 | 49.55 | 0 | 0 | 0 | 0 | 56.77 | 0
2025-03-28 12:00 | 50.92 | 102.67 | 50.92 | 0 | 0 | 0 | 0 | 51.75 | 0
2025-03-28 13:00 | 50.99 | 105.08 | 50.99 | 0 | 0 | 0 | 0 | 54.08 | 0
2025-03-28 14:00 | 52.37 | 109.65 | 52.37 | 0 | 0 | 0 | 0 | 57.28 | 0
2025-03-28 15:00 | 52.59 | 111.58 | 52.59 | 0 | 0 | 0 | 0 | 58.99 | 0
2025-03-28 16:00 | 53.3 | 106.52 | 53.3 | 0 | 0 | 0 | 0 | 53.22 | 0
2025-03-28 17:00 | 51.29 | 73.15 | 51.29 | 0 | 0 | 0 | 0 | 21.86 | 0
2025-03-28 18:00 | 50.4 | 2.01 | 2.01 | 48.39 | 0 | 0 | 0 | 0 | 0
2025-03-28 19:00 | 49.9 | 0 | 0 | 49.9 | 0 | 0 | 0 | 0 | 0
2025-03-28 20:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 0 | 0 | 0
2025-03-28 21:00 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 0 | 0 | 0
2025-03-28 22:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 0 | 0 | 0
2025-03-28 23:00 | 44.05 | 0 | 0 | 44.05 | 0 | 0 | 0 | 0 | 0
2025-03-29 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0 | 0 | 0
2025-03-29 01:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 0 | 0 | 0
2025-03-29 02:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 0 | 0 | 0
2025-03-29 03:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0 | 0 | 0
2025-03-29 04:00 | 40.75 | 0 | 0 | 40.75 | 0 | 0 | 0 | 0 | 0
2025-03-29 05:00 | 40.76 | 0 | 0 | 40.76 | 0 | 0 | 0 | 0 | 0
2025-03-29 06:00 | 41.73 | 3.26 | 3.26 | 38.47 | 0 | 0 | 0 | 0 | 0
2025-03-29 07:00 | 43.38 | 85.91 | 43.38 | 0 | 0 | 0 | 0 | 42.53 | 0
2025-03-29 08:00 | 44.88 | 114.49 | 44.88 | 0 | 0 | 0 | 0 | 69.61 | 0
2025-03-29 09:00 | 47.11 | 117.2 | 47.11 | 0 | 0 | 0 | 0 | 70.09 | 0
2025-03-29 10:00 | 48.24 | 112.6 | 48.24 | 0 | 0 | 0 | 0 | 64.37 | 0
2025-03-29 11:00 | 50.01 | 106.35 | 50.01 | 0 | 0 | 0 | 0 | 56.34 | 0
2025-03-29 12:00 | 51.3 | 103.21 | 51.3 | 0 | 0 | 0 | 0 | 51.91 | 0
2025-03-29 13:00 | 52.47 | 105.29 | 52.47 | 0 | 0 | 0 | 0 | 52.82 | 0
2025-03-29 14:00 | 53.99 | 109.28 | 53.99 | 0 | 0 | 0 | 0 | 55.29 | 0
2025-03-29 15:00 | 53.88 | 111.62 | 53.88 | 0 | 0 | 0 | 0 | 57.74 | 0
2025-03-29 16:00 | 53.34 | 108.92 | 53.34 | 0 | 0 | 0 | 0 | 55.58 | 0
2025-03-29 17:00 | 52.46 | 80.28 | 52.46 | 0 | 0 | 0 | 0 | 27.82 | 0
2025-03-29 18:00 | 51.47 | 2.78 | 2.78 | 48.68 | 0 | 0 | 0 | 0 | 0
2025-03-29 19:00 | 50.53 | 0 | 0 | 50.53 | 0 | 0 | 0 | 0 | 0
2025-03-29 20:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 0 | 0 | 0
2025-03-29 21:00 | 46.73 | 0 | 0 | 46.73 | 0 | 0 | 0 | 0 | 0
2025-03-29 22:00 | 45.56 | 0 | 0 | 45.56 | 0 | 0 | 0 | 0 | 0
2025-03-29 23:00 | 42.99 | 0 | 0 | 42.99 | 0 | 0 | 0 | 0 | 0
2025-03-30 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 0 | 0 | 0
2025-03-30 01:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 0 | 0 | 0
2025-03-30 02:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 0 | 0 | 0
2025-03-30 03:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 0 | 0 | 0
2025-03-30 04:00 | 40.73 | 0 | 0 | 40.73 | 0 | 0 | 0 | 0 | 0
2025-03-30 05:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 0 | 0 | 0
2025-03-30 06:00 | 42.84 | 4.6 | 4.6 | 38.23 | 0 | 0 | 0 | 0 | 0
2025-03-30 07:00 | 44.18 | 85.45 | 44.18 | 0 | 0 | 0 | 0 | 41.27 | 0
2025-03-30 08:00 | 45.81 | 112.38 | 45.81 | 0 | 0 | 0 | 0 | 66.57 | 0
2025-03-30 09:00 | 47.71 | 114.91 | 47.71 | 0 | 0 | 0 | 0 | 67.2 | 0
2025-03-30 10:00 | 49.91 | 111.14 | 49.91 | 0 | 0 | 0 | 0 | 61.24 | 0
2025-03-30 11:00 | 51.9 | 105.13 | 51.9 | 0 | 0 | 0 | 0 | 53.22 | 0
2025-03-30 12:00 | 52.73 | 102.74 | 52.73 | 0 | 0 | 0 | 0 | 50.01 | 0
2025-03-30 13:00 | 54.32 | 103.79 | 54.32 | 0 | 0 | 0 | 0 | 49.47 | 0
2025-03-30 14:00 | 54.31 | 107.48 | 54.31 | 0 | 0 | 0 | 0 | 53.17 | 0
2025-03-30 15:00 | 55.3 | 110.5 | 55.3 | 0 | 0 | 0 | 0 | 55.2 | 0
2025-03-30 16:00 | 54.28 | 104.55 | 54.28 | 0 | 0 | 0 | 0 | 50.27 | 0
2025-03-30 17:00 | 54.46 | 75.48 | 54.46 | 0 | 0 | 0 | 0 | 21.02 | 0
2025-03-30 18:00 | 53.84 | 3.03 | 3.03 | 50.81 | 0 | 0 | 0 | 0 | 0
2025-03-30 19:00 | 51.16 | 0 | 0 | 51.16 | 0 | 0 | 0 | 0 | 0
2025-03-30 20:00 | 48.38 | 0 | 0 | 48.38 | 0 | 0 | 0 | 0 | 0
2025-03-30 21:00 | 47.38 | 0 | 0 | 47.38 | 0 | 0 | 0 | 0 | 0
2025-03-30 22:00 | 46.48 | 0 | 0 | 46.48 | 0 | 0 | 0 | 0 | 0
2025-03-30 23:00 | 44.51 | 0 | 0 | 44.51 | 0 | 0 | 0 | 0 | 0
2025-03-31 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0 | 0 | 0
2025-03-31 01:00 | 42.45 | 0 | 0 | 42.45 | 0 | 0 | 0 | 0 | 0
2025-03-31 02:00 | 41.53 | 0 | 0 | 41.53 | 0 | 0 | 0 | 0 | 0
2025-03-31 03:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 0 | 0 | 0
2025-03-31 04:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 0 | 0 | 0
2025-03-31 05:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0 | 0 | 0
2025-03-31 06:00 | 43.18 | 4.54 | 4.54 | 38.63 | 0 | 0 | 0 | 0 | 0
2025-03-31 07:00 | 44.84 | 88.76 | 44.84 | 0 | 0 | 0 | 0 | 43.92 | 0
2025-03-31 08:00 | 45.88 | 113.26 | 45.88 | 0 | 0 | 0 | 0 | 67.38 | 0
2025-03-31 09:00 | 47.54 | 115.56 | 47.54 | 0 | 0 | 0 | 0 | 68.02 | 0
2025-03-31 10:00 | 50.53 | 112.89 | 50.53 | 0 | 0 | 0 | 0 | 62.36 | 0
2025-03-31 11:00 | 51.53 | 107.98 | 51.53 | 0 | 0 | 0 | 0 | 56.45 | 0
2025-03-31 12:00 | 53.35 | 104.82 | 53.35 | 0 | 0 | 0 | 0 | 51.47 | 0
2025-03-31 13:00 | 54.19 | 106.99 | 54.19 | 0 | 0 | 0 | 0 | 52.8 | 0
2025-03-31 14:00 | 54.59 | 111.66 | 54.59 | 0 | 0 | 0 | 0 | 57.07 | 0
2025-03-31 15:00 | 55.14 | 114.66 | 55.14 | 0 | 0 | 0 | 0 | 59.52 | 0
2025-03-31 16:00 | 55.6 | 112.13 | 55.6 | 0 | 0 | 0 | 0 | 56.54 | 0
2025-03-31 17:00 | 54.41 | 85.18 | 54.41 | 0 | 0 | 0 | 0 | 30.77 | 0
2025-03-31 18:00 | 52.09 | 4.07 | 4.07 | 48.02 | 0 | 0 | 0 | 0 | 0
2025-03-31 19:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 0 | 0 | 0
2025-03-31 20:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 0 | 0 | 0
2025-03-31 21:00 | 47.73 | 0 | 0 | 47.73 | 0 | 0 | 0 | 0 | 0
2025-03-31 22:00 | 45.14 | 0 | 0 | 45.14 | 0 | 0 | 0 | 0 | 0
2025-03-31 23:00 | 45.34 | 0 | 0 | 45.34 | 0 | 0 | 0 | 0 | 0
2025-04-01 | 43.49 | 0 | 0 | 43.49 | 0 | 0 | 0 | 0 | 0
2025-04-01 01:00 | 42.04 | 0 | 0 | 42.04 | 0 | 0 | 0 | 0 | 0
2025-04-01 02:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 0 | 0 | 0
2025-04-01 03:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 0 | 0 | 0
2025-04-01 04:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0 | 0 | 0
2025-04-01 05:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 0 | 0 | 0
2025-04-01 06:00 | 43.42 | 3.11 | 3.11 | 40.31 | 0 | 0 | 0 | 0 | 0
2025-04-01 07:00 | 44.7 | 12.61 | 12.61 | 32.09 | 0 | 0 | 0 | 0 | 0
2025-04-01 08:00 | 46.36 | 49.59 | 46.36 | 0 | 0 | 0 | 0 | 3.23 | 0
2025-04-01 09:00 | 48.09 | 55.41 | 48.09 | 0 | 0 | 0 | 0 | 7.32 | 0
2025-04-01 10:00 | 50.64 | 52.99 | 50.64 | 0 | 0 | 0 | 0 | 2.35 | 0
2025-04-01 11:00 | 51.54 | 70.33 | 51.54 | 0 | 0 | 0 | 0 | 18.79 | 0
2025-04-01 12:00 | 52.79 | 34.85 | 34.85 | 17.94 | 0 | 0 | 0 | 0 | 0
2025-04-01 13:00 | 55.18 | 68.41 | 55.18 | 0 | 0 | 0 | 0 | 13.23 | 0
2025-04-01 14:00 | 56 | 34.98 | 34.98 | 21.01 | 0 | 0 | 0 | 0 | 0
2025-04-01 15:00 | 56.2 | 49.87 | 49.87 | 6.33 | 0 | 0 | 0 | 0 | 0
2025-04-01 16:00 | 55.88 | 19.1 | 19.1 | 36.78 | 0 | 0 | 0 | 0 | 0
2025-04-01 17:00 | 54.71 | 4.46 | 4.46 | 50.25 | 0 | 0 | 0 | 0 | 0
2025-04-01 18:00 | 53.99 | 0 | 0 | 53.99 | 0 | 0 | 0 | 0 | 0
2025-04-01 19:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0 | 0 | 0
2025-04-01 20:00 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 0 | 0 | 0
2025-04-01 21:00 | 48.02 | 0 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0
2025-04-01 22:00 | 47.3 | 0 | 0 | 47.3 | 0 | 0 | 0 | 0 | 0
2025-04-01 23:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 0 | 0 | 0
2025-04-02 | 43.51 | 0 | 0 | 43.51 | 0 | 0 | 0 | 0 | 0
2025-04-02 01:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 0 | 0 | 0
2025-04-02 02:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 0 | 0 | 0
2025-04-02 03:00 | 41.09 | 0 | 0 | 41.09 | 0 | 0 | 0 | 0 | 0
2025-04-02 04:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0 | 0 | 0
2025-04-02 05:00 | 42.39 | 0 | 0 | 42.39 | 0 | 0 | 0 | 0 | 0
2025-04-02 06:00 | 43.07 | 0.52 | 0.52 | 42.55 | 0 | 0 | 0 | 0 | 0
2025-04-02 07:00 | 43.58 | 4.07 | 4.07 | 39.51 | 0 | 0 | 0 | 0 | 0
2025-04-02 08:00 | 46.64 | 9.3 | 9.3 | 37.34 | 0 | 0 | 0 | 0 | 0
2025-04-02 09:00 | 48.64 | 14.88 | 14.88 | 33.76 | 0 | 0 | 0 | 0 | 0
2025-04-02 10:00 | 50.37 | 23.3 | 23.3 | 27.06 | 0 | 0 | 0 | 0 | 0
2025-04-02 11:00 | 51.37 | 26.41 | 26.41 | 24.96 | 0 | 0 | 0 | 0 | 0
2025-04-02 12:00 | 52.56 | 25.56 | 25.56 | 27 | 0 | 0 | 0 | 0 | 0
2025-04-02 13:00 | 54.23 | 21.26 | 21.26 | 32.97 | 0 | 0 | 0 | 0 | 0
2025-04-02 14:00 | 55.05 | 19.85 | 19.85 | 35.2 | 0 | 0 | 0 | 0 | 0
2025-04-02 15:00 | 55 | 17.83 | 17.83 | 37.17 | 0 | 0 | 0 | 0 | 0
2025-04-02 16:00 | 53.74 | 11.22 | 11.22 | 42.53 | 0 | 0 | 0 | 0 | 0
2025-04-02 17:00 | 53.67 | 5.12 | 5.12 | 48.55 | 0 | 0 | 0 | 0 | 0
2025-04-02 18:00 | 52.76 | 0.27 | 0.27 | 52.49 | 0 | 0 | 0 | 0 | 0
2025-04-02 19:00 | 50.29 | 0 | 0 | 50.29 | 0 | 0 | 0 | 0 | 0
2025-04-02 20:00 | 49.86 | 0 | 0 | 49.86 | 0 | 0 | 0 | 0 | 0
2025-04-02 21:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0 | 0 | 0
2025-04-02 22:00 | 46.54 | 0 | 0 | 46.54 | 0 | 0 | 0 | 0 | 0
2025-04-02 23:00 | 45.37 | 0 | 0 | 45.37 | 0 | 0 | 0 | 0 | 0
2025-04-03 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0 | 0 | 0
2025-04-03 01:00 | 42.29 | 0 | 0 | 42.29 | 0 | 0 | 0 | 0 | 0
2025-04-03 02:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 0 | 0 | 0
2025-04-03 03:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 0 | 0 | 0
2025-04-03 04:00 | 41.17 | 0 | 0 | 41.17 | 0 | 0 | 0 | 0 | 0
2025-04-03 05:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 0 | 0 | 0
2025-04-03 06:00 | 44.07 | 1.17 | 1.17 | 42.9 | 0 | 0 | 0 | 0 | 0
2025-04-03 07:00 | 44.25 | 6.13 | 6.13 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-04-03 08:00 | 46.78 | 16.34 | 16.34 | 30.44 | 0 | 0 | 0 | 0 | 0
2025-04-03 09:00 | 47.89 | 19.67 | 19.67 | 28.22 | 0 | 0 | 0 | 0 | 0
2025-04-03 10:00 | 49.71 | 26.73 | 26.73 | 22.97 | 0 | 0 | 0 | 0 | 0
2025-04-03 11:00 | 51.23 | 21.46 | 21.46 | 29.77 | 0 | 0 | 0 | 0 | 0
2025-04-03 12:00 | 52.72 | 28.87 | 28.87 | 23.85 | 0 | 0 | 0 | 0 | 0
2025-04-03 13:00 | 53.2 | 32.61 | 32.61 | 20.59 | 0 | 0 | 0 | 0 | 0
2025-04-03 14:00 | 54.44 | 28.94 | 28.94 | 25.5 | 0 | 0 | 0 | 0 | 0
2025-04-03 15:00 | 54.09 | 25.94 | 25.94 | 28.14 | 0 | 0 | 0 | 0 | 0
2025-04-03 16:00 | 54.05 | 14.72 | 14.72 | 39.33 | 0 | 0 | 0 | 0 | 0
2025-04-03 17:00 | 52.74 | 4.65 | 4.65 | 48.09 | 0 | 0 | 0 | 0 | 0
2025-04-03 18:00 | 53.31 | 0.27 | 0.27 | 53.04 | 0 | 0 | 0 | 0 | 0
2025-04-03 19:00 | 51.23 | 0 | 0 | 51.23 | 0 | 0 | 0 | 0 | 0
2025-04-03 20:00 | 49.89 | 0 | 0 | 49.89 | 0 | 0 | 0 | 0 | 0
2025-04-03 21:00 | 47.13 | 0 | 0 | 47.13 | 0 | 0 | 0 | 0 | 0
2025-04-03 22:00 | 45.89 | 0 | 0 | 45.89 | 0 | 0 | 0 | 0 | 0
2025-04-03 23:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 0 | 0 | 0
2025-04-04 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0 | 0 | 0
2025-04-04 01:00 | 41.5 | 0 | 0 | 41.5 | 0 | 0 | 0 | 0 | 0
2025-04-04 02:00 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 0 | 0 | 0
2025-04-04 03:00 | 41.27 | 0 | 0 | 41.27 | 0 | 0 | 0 | 0 | 0
2025-04-04 04:00 | 42.48 | 0 | 0 | 42.48 | 0 | 0 | 0 | 0 | 0
2025-04-04 05:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 0 | 0 | 0
2025-04-04 06:00 | 43.65 | 9.78 | 9.78 | 33.87 | 0 | 0 | 0 | 0 | 0
2025-04-04 07:00 | 45.55 | 102.33 | 45.55 | 0 | 0 | 0 | 0 | 56.78 | 0
2025-04-04 08:00 | 46.15 | 124.05 | 46.15 | 0 | 0 | 0 | 0 | 77.9 | 0
2025-04-04 09:00 | 47.86 | 121.2 | 47.86 | 0 | 0 | 0 | 0 | 73.34 | 0
2025-04-04 10:00 | 50 | 123.82 | 50 | 0 | 0 | 0 | 0 | 73.83 | 0
2025-04-04 11:00 | 52.13 | 88.13 | 52.13 | 0 | 0 | 0 | 0 | 36 | 0
2025-04-04 12:00 | 52.44 | 52.44 | 52.44 | 0 | 0 | 0 | 0 | 0 | 0
2025-04-04 13:00 | 53.33 | 22.17 | 22.17 | 31.16 | 0 | 0 | 0 | 0 | 0
2025-04-04 14:00 | 55.24 | 36.57 | 36.57 | 18.68 | 0 | 0 | 0 | 0 | 0
2025-04-04 15:00 | 54.76 | 28.49 | 28.49 | 26.27 | 0 | 0 | 0 | 0 | 0
2025-04-04 16:00 | 54.64 | 30.1 | 30.1 | 24.54 | 0 | 0 | 0 | 0 | 0
2025-04-04 17:00 | 53.24 | 12.32 | 12.32 | 40.92 | 0 | 0 | 0 | 0 | 0
2025-04-04 18:00 | 52.77 | 5.39 | 5.39 | 47.38 | 0 | 0 | 0 | 0 | 0
2025-04-04 19:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0 | 0 | 0
2025-04-04 20:00 | 50.56 | 0 | 0 | 50.56 | 0 | 0 | 0 | 0 | 0
2025-04-04 21:00 | 47.97 | 0 | 0 | 47.97 | 0 | 0 | 0 | 0 | 0
2025-04-04 22:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0 | 0 | 0
2025-04-04 23:00 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 0 | 0 | 0
2025-04-05 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 0 | 0 | 0
2025-04-05 01:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 0 | 0 | 0
2025-04-05 02:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 0 | 0 | 0
2025-04-05 03:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 0 | 0 | 0
2025-04-05 04:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 0 | 0 | 0
2025-04-05 05:00 | 43.25 | 0 | 0 | 43.25 | 0 | 0 | 0 | 0 | 0
2025-04-05 06:00 | 44.34 | 3.66 | 3.66 | 40.68 | 0 | 0 | 0 | 0 | 0
2025-04-05 07:00 | 44.47 | 69.96 | 44.47 | 0 | 0 | 0 | 0 | 25.5 | 0
2025-04-05 08:00 | 46.21 | 93.95 | 46.21 | 0 | 0 | 0 | 0 | 47.74 | 0
2025-04-05 09:00 | 47.6 | 49.3 | 47.6 | 0 | 0 | 0 | 0 | 1.7 | 0
2025-04-05 10:00 | 48.24 | 73.96 | 48.24 | 0 | 0 | 0 | 0 | 25.72 | 0
2025-04-05 11:00 | 49.68 | 87.07 | 49.68 | 0 | 0 | 0 | 0 | 37.39 | 0
2025-04-05 12:00 | 50.45 | 56.86 | 50.45 | 0 | 0 | 0 | 0 | 6.41 | 0
2025-04-05 13:00 | 51.52 | 49.81 | 49.81 | 1.71 | 0 | 0 | 0 | 0 | 0
2025-04-05 14:00 | 51.84 | 18.98 | 18.98 | 32.86 | 0 | 0 | 0 | 0 | 0
2025-04-05 15:00 | 51.17 | 53.64 | 51.17 | 0 | 0 | 0 | 0 | 2.47 | 0
2025-04-05 16:00 | 51.13 | 82.27 | 51.13 | 0 | 0 | 0 | 0 | 31.13 | 0
2025-04-05 17:00 | 51.28 | 61.51 | 51.28 | 0 | 0 | 0 | 0 | 10.22 | 0
2025-04-05 18:00 | 50.15 | 4.54 | 4.54 | 45.62 | 0 | 0 | 0 | 0 | 0
2025-04-05 19:00 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0
2025-04-05 20:00 | 48.69 | 0 | 0 | 48.69 | 0 | 0 | 0 | 0 | 0
2025-04-05 21:00 | 47.07 | 0 | 0 | 47.07 | 0 | 0 | 0 | 0 | 0
2025-04-05 22:00 | 45.75 | 0 | 0 | 45.75 | 0 | 0 | 0 | 0 | 0
2025-04-05 23:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 0 | 0 | 0
2025-04-06 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0 | 0 | 0
2025-04-06 01:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0 | 0 | 0
2025-04-06 02:00 | 41.77 | 0 | 0 | 41.77 | 0 | 0 | 0 | 0 | 0
2025-04-06 03:00 | 41.93 | 0 | 0 | 41.93 | 0 | 0 | 0 | 0 | 0
2025-04-06 04:00 | 43.22 | 0 | 0 | 43.22 | 0 | 0 | 0 | 0 | 0
2025-04-06 05:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 0 | 0 | 0
2025-04-06 06:00 | 42.82 | 4.61 | 4.61 | 38.21 | 0 | 0 | 0 | 0 | 0
2025-04-06 07:00 | 45.72 | 20.71 | 20.71 | 25.01 | 0 | 0 | 0 | 0 | 0
2025-04-06 08:00 | 46.08 | 50.81 | 46.08 | 0 | 0 | 0 | 0 | 4.73 | 0
2025-04-06 09:00 | 47.89 | 57.76 | 47.89 | 0 | 0 | 0 | 0 | 9.87 | 0
2025-04-06 10:00 | 48.9 | 64.28 | 48.9 | 0 | 0 | 0 | 0 | 15.38 | 0
2025-04-06 11:00 | 50.41 | 67.98 | 50.41 | 0 | 0 | 0 | 0 | 17.57 | 0
2025-04-06 12:00 | 50.65 | 49.64 | 49.64 | 1.01 | 0 | 0 | 0 | 0 | 0
2025-04-06 13:00 | 51.63 | 48.22 | 48.22 | 3.42 | 0 | 0 | 0 | 0 | 0
2025-04-06 14:00 | 52.3 | 47.36 | 47.36 | 4.94 | 0 | 0 | 0 | 0 | 0
2025-04-06 15:00 | 51.68 | 100.98 | 51.68 | 0 | 0 | 0 | 0 | 49.3 | 0
2025-04-06 16:00 | 51.72 | 78.76 | 51.72 | 0 | 0 | 0 | 0 | 27.04 | 0
2025-04-06 17:00 | 51.55 | 79.15 | 51.55 | 0 | 0 | 0 | 0 | 27.6 | 0
2025-04-06 18:00 | 50.41 | 11.1 | 11.1 | 39.31 | 0 | 0 | 0 | 0 | 0
2025-04-06 19:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 0 | 0 | 0
2025-04-06 20:00 | 49.25 | 0 | 0 | 49.25 | 0 | 0 | 0 | 0 | 0
2025-04-06 21:00 | 47.7 | 0 | 0 | 47.7 | 0 | 0 | 0 | 0 | 0
2025-04-06 22:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 0 | 0 | 0
2025-04-06 23:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 0 | 0 | 0
2025-04-07 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0 | 0 | 0
2025-04-07 01:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 0 | 0 | 0
2025-04-07 02:00 | 42.87 | 0 | 0 | 42.87 | 0 | 0 | 0 | 0 | 0
2025-04-07 03:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 0 | 0 | 0
2025-04-07 04:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 0 | 0 | 0
2025-04-07 05:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 0 | 0 | 0
2025-04-07 06:00 | 44.11 | 3.28 | 3.28 | 40.82 | 0 | 0 | 0 | 0 | 0
2025-04-07 07:00 | 46.04 | 17.34 | 17.34 | 28.7 | 0 | 0 | 0 | 0 | 0
2025-04-07 08:00 | 46.98 | 39.72 | 39.72 | 7.26 | 0 | 0 | 0 | 0 | 0
2025-04-07 09:00 | 47.3 | 13.38 | 13.38 | 33.91 | 0 | 0 | 0 | 0 | 0
2025-04-07 10:00 | 49.76 | 14.62 | 14.62 | 35.14 | 0 | 0 | 0 | 0 | 0
2025-04-07 11:00 | 51.3 | 44.81 | 44.81 | 6.49 | 0 | 0 | 0 | 0 | 0
2025-04-07 12:00 | 51.48 | 56.77 | 51.48 | 0 | 0 | 0 | 0 | 5.28 | 0
2025-04-07 13:00 | 52.74 | 99.85 | 52.74 | 0 | 0 | 0 | 0 | 47.1 | 0
2025-04-07 14:00 | 52.29 | 114.26 | 52.29 | 0 | 0 | 0 | 0 | 61.97 | 0
2025-04-07 15:00 | 52.02 | 52.45 | 52.02 | 0 | 0 | 0 | 0 | 0.44 | 0
2025-04-07 16:00 | 52.7 | 103.3 | 52.7 | 0 | 0 | 0 | 0 | 50.6 | 0
2025-04-07 17:00 | 51.37 | 76.92 | 51.37 | 0 | 0 | 0 | 0 | 25.55 | 0
2025-04-07 18:00 | 51.48 | 6.85 | 6.85 | 44.62 | 0 | 0 | 0 | 0 | 0
2025-04-07 19:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 0 | 0 | 0
2025-04-07 20:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0 | 0 | 0
2025-04-07 21:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0 | 0 | 0
2025-04-07 22:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 0 | 0 | 0
2025-04-07 23:00 | 45.23 | 0 | 0 | 45.23 | 0 | 0 | 0 | 0 | 0
2025-04-08 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 0 | 0 | 0
2025-04-08 01:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0 | 0 | 0
2025-04-08 02:00 | 42.76 | 0 | 0 | 42.76 | 0 | 0 | 0 | 0 | 0
2025-04-08 03:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0 | 0 | 0
2025-04-08 04:00 | 42.35 | 0 | 0 | 42.35 | 0 | 0 | 0 | 0 | 0
2025-04-08 05:00 | 43.18 | 0 | 0 | 43.18 | 0 | 0 | 0 | 0 | 0
2025-04-08 06:00 | 43.66 | 14.91 | 14.91 | 28.74 | 0 | 0 | 0 | 0 | 0
2025-04-08 07:00 | 45.91 | 74.11 | 45.91 | 0 | 0 | 0 | 0 | 28.2 | 0
2025-04-08 08:00 | 46.47 | 96.98 | 46.47 | 0 | 0 | 0 | 0 | 50.51 | 0
2025-04-08 09:00 | 49.01 | 105.24 | 49.01 | 0 | 0 | 0 | 0 | 56.23 | 0
2025-04-08 10:00 | 50.68 | 101.39 | 50.68 | 0 | 0 | 0 | 0 | 50.72 | 0
2025-04-08 11:00 | 51.5 | 102.42 | 51.5 | 0 | 0 | 0 | 0 | 50.92 | 0
2025-04-08 12:00 | 52.37 | 102.53 | 52.37 | 0 | 0 | 0 | 0 | 50.16 | 0
2025-04-08 13:00 | 53.43 | 98.12 | 53.43 | 0 | 0 | 0 | 0 | 44.68 | 0
2025-04-08 14:00 | 52.28 | 96.16 | 52.28 | 0 | 0 | 0 | 0 | 43.88 | 0
2025-04-08 15:00 | 54.02 | 101.12 | 54.02 | 0 | 0 | 0 | 0 | 47.11 | 0
2025-04-08 16:00 | 53.65 | 92.8 | 53.65 | 0 | 0 | 0 | 0 | 39.15 | 0
2025-04-08 17:00 | 53.21 | 64.85 | 53.21 | 0 | 0 | 0 | 0 | 11.64 | 0
2025-04-08 18:00 | 52.81 | 10.05 | 10.05 | 42.76 | 0 | 0 | 0 | 0 | 0
2025-04-08 19:00 | 51.36 | 0 | 0 | 51.36 | 0 | 0 | 0 | 0 | 0
2025-04-08 20:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0 | 0 | 0
2025-04-08 21:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 0 | 0 | 0
2025-04-08 22:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 0 | 0 | 0
2025-04-08 23:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 0 | 0 | 0
2025-04-09 | 44.4 | 0 | 0 | 44.4 | 0 | 0 | 0 | 0 | 0
2025-04-09 01:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0 | 0 | 0
2025-04-09 02:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 0 | 0 | 0
2025-04-09 03:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 0 | 0 | 0
2025-04-09 04:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 0 | 0 | 0
2025-04-09 05:00 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 0 | 0 | 0
2025-04-09 06:00 | 44.41 | 18.68 | 18.68 | 25.73 | 0 | 0 | 0 | 0 | 0
2025-04-09 07:00 | 45.58 | 81.76 | 45.58 | 0 | 0 | 0 | 0 | 36.18 | 0
2025-04-09 08:00 | 47.53 | 92.74 | 47.53 | 0 | 0 | 0 | 0 | 45.22 | 0
2025-04-09 09:00 | 49.27 | 100.13 | 49.27 | 0 | 0 | 0 | 0 | 50.86 | 0
2025-04-09 10:00 | 51.68 | 98.85 | 51.68 | 0 | 0 | 0 | 0 | 47.17 | 0
2025-04-09 11:00 | 54.62 | 97.36 | 54.62 | 0 | 0 | 0 | 0 | 42.75 | 0
2025-04-09 12:00 | 54.75 | 98.62 | 54.75 | 0 | 0 | 0 | 0 | 43.87 | 0
2025-04-09 13:00 | 56.11 | 98.85 | 56.11 | 0 | 0 | 0 | 0 | 42.74 | 0
2025-04-09 14:00 | 56.87 | 103.87 | 56.87 | 0 | 0 | 0 | 0 | 47 | 0
2025-04-09 15:00 | 58.67 | 103.3 | 58.67 | 0 | 0 | 0 | 0 | 44.63 | 0
2025-04-09 16:00 | 57.29 | 95.73 | 57.29 | 0 | 0 | 0 | 0 | 38.44 | 0
2025-04-09 17:00 | 56.68 | 78.52 | 56.68 | 0 | 0 | 0 | 0 | 21.84 | 0
2025-04-09 18:00 | 55.18 | 11.82 | 11.82 | 43.36 | 0 | 0 | 0 | 0 | 0
2025-04-09 19:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0 | 0 | 0
2025-04-09 20:00 | 51.64 | 0 | 0 | 51.64 | 0 | 0 | 0 | 0 | 0
2025-04-09 21:00 | 50.95 | 0 | 0 | 50.95 | 0 | 0 | 0 | 0 | 0
2025-04-09 22:00 | 48.41 | 0 | 0 | 48.41 | 0 | 0 | 0 | 0 | 0
2025-04-09 23:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0 | 0 | 0
2025-04-10 | 44.72 | 0 | 0 | 44.72 | 0 | 0 | 0 | 0 | 0
2025-04-10 01:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 0 | 0 | 0
2025-04-10 02:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 0 | 0 | 0
2025-04-10 03:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 0 | 0 | 0
2025-04-10 04:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 0 | 0 | 0
2025-04-10 05:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0 | 0 | 0
2025-04-10 06:00 | 44.16 | 4.4 | 4.4 | 39.76 | 0 | 0 | 0 | 0 | 0
2025-04-10 07:00 | 45.74 | 1.1 | 1.1 | 44.64 | 0 | 0 | 0 | 0 | 0
2025-04-10 08:00 | 47.8 | 3.89 | 3.89 | 43.92 | 0 | 0 | 0 | 0 | 0
2025-04-10 09:00 | 49.27 | 25.95 | 25.95 | 23.31 | 0 | 0 | 0 | 0 | 0
2025-04-10 10:00 | 50.43 | 110.24 | 50.43 | 0 | 0 | 0 | 0 | 59.81 | 0
2025-04-10 11:00 | 51.2 | 115.78 | 51.2 | 0 | 0 | 0 | 0 | 64.58 | 0
2025-04-10 12:00 | 53.2 | 112.86 | 53.2 | 0 | 0 | 0 | 0 | 59.66 | 0
2025-04-10 13:00 | 54.51 | 72.39 | 54.51 | 0 | 0 | 0 | 0 | 17.88 | 0
2025-04-10 14:00 | 53.88 | 56.82 | 53.88 | 0 | 0 | 0 | 0 | 2.94 | 0
2025-04-10 15:00 | 54.97 | 117.8 | 54.97 | 0 | 0 | 0 | 0 | 62.82 | 0
2025-04-10 16:00 | 54.65 | 84.24 | 54.65 | 0 | 0 | 0 | 0 | 29.59 | 0
2025-04-10 17:00 | 54.35 | 88.71 | 54.35 | 0 | 0 | 0 | 0 | 34.36 | 0
2025-04-10 18:00 | 53.58 | 16.08 | 16.08 | 37.5 | 0 | 0 | 0 | 0 | 0
2025-04-10 19:00 | 51.66 | 0 | 0 | 51.66 | 0 | 0 | 0 | 0 | 0
2025-04-10 20:00 | 49.82 | 0 | 0 | 49.82 | 0 | 0 | 0 | 0 | 0
2025-04-10 21:00 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 0 | 0 | 0
2025-04-10 22:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0 | 0 | 0
2025-04-10 23:00 | 45.56 | 0 | 0 | 45.56 | 0 | 0 | 0 | 0 | 0
2025-04-11 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 0 | 0 | 0
2025-04-11 01:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 0 | 0 | 0
2025-04-11 02:00 | 43.54 | 0 | 0 | 43.54 | 0 | 0 | 0 | 0 | 0
2025-04-11 03:00 | 42.82 | 0 | 0 | 42.82 | 0 | 0 | 0 | 0 | 0
2025-04-11 04:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 0 | 0 | 0
2025-04-11 05:00 | 43.89 | 0 | 0 | 43.89 | 0 | 0 | 0 | 0 | 0
2025-04-11 06:00 | 44.86 | 24.54 | 24.54 | 20.33 | 0 | 0 | 0 | 0 | 0
2025-04-11 07:00 | 45.96 | 79.42 | 45.96 | 0 | 0 | 0 | 0 | 33.46 | 0
2025-04-11 08:00 | 47.73 | 105.97 | 47.73 | 0 | 0 | 0 | 0 | 58.24 | 0
2025-04-11 09:00 | 49.42 | 115.39 | 49.42 | 0 | 0 | 0 | 0 | 65.97 | 0
2025-04-11 10:00 | 52.74 | 101.85 | 52.74 | 0 | 0 | 0 | 0 | 49.11 | 0
2025-04-11 11:00 | 53.33 | 77.36 | 53.33 | 0 | 0 | 0 | 0 | 24.03 | 0
2025-04-11 12:00 | 54.2 | 82.59 | 54.2 | 0 | 0 | 0 | 0 | 28.39 | 0
2025-04-11 13:00 | 55.71 | 97.07 | 55.71 | 0 | 0 | 0 | 0 | 41.36 | 0
2025-04-11 14:00 | 55.62 | 80.71 | 55.62 | 0 | 0 | 0 | 0 | 25.08 | 0
2025-04-11 15:00 | 57.1 | 75.14 | 57.1 | 0 | 0 | 0 | 0 | 18.04 | 0
2025-04-11 16:00 | 55.8 | 56.58 | 55.8 | 0 | 0 | 0 | 0 | 0.79 | 0
2025-04-11 17:00 | 55.73 | 59.13 | 55.73 | 0 | 0 | 0 | 0 | 3.4 | 0
2025-04-11 18:00 | 54.97 | 11.73 | 11.73 | 43.24 | 0 | 0 | 0 | 0 | 0
2025-04-11 19:00 | 53.25 | 0 | 0 | 53.25 | 0 | 0 | 0 | 0 | 0
2025-04-11 20:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0 | 0 | 0
2025-04-11 21:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 0 | 0 | 0
2025-04-11 22:00 | 47.78 | 0 | 0 | 47.78 | 0 | 0 | 0 | 0 | 0
2025-04-11 23:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 0 | 0 | 0
2025-04-12 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 0 | 0 | 0
2025-04-12 01:00 | 44.3 | 0 | 0 | 44.3 | 0 | 0 | 0 | 0 | 0
2025-04-12 02:00 | 42.74 | 0 | 0 | 42.74 | 0 | 0 | 0 | 0 | 0
2025-04-12 03:00 | 42.14 | 0 | 0 | 42.14 | 0 | 0 | 0 | 0 | 0
2025-04-12 04:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 0 | 0 | 0
2025-04-12 05:00 | 44.11 | 0 | 0 | 44.11 | 0 | 0 | 0 | 0 | 0
2025-04-12 06:00 | 45.16 | 20.01 | 20.01 | 25.16 | 0 | 0 | 0 | 0 | 0
2025-04-12 07:00 | 46.82 | 75.02 | 46.82 | 0 | 0 | 0 | 0 | 28.2 | 0
2025-04-12 08:00 | 48.5 | 119.78 | 48.5 | 0 | 0 | 0 | 0 | 71.27 | 0
2025-04-12 09:00 | 51.28 | 124.64 | 51.28 | 0 | 0 | 0 | 0 | 73.36 | 0
2025-04-12 10:00 | 53.14 | 122.32 | 53.14 | 0 | 0 | 0 | 0 | 69.17 | 0
2025-04-12 11:00 | 55.75 | 118.16 | 55.75 | 0 | 0 | 0 | 0 | 62.4 | 0
2025-04-12 12:00 | 58.52 | 115.65 | 58.52 | 0 | 0 | 0 | 0 | 57.13 | 0
2025-04-12 13:00 | 60.18 | 7.21 | 7.21 | 52.97 | 0 | 0 | 0 | 0 | 0
2025-04-12 14:00 | 60.35 | 53.97 | 53.97 | 6.37 | 0 | 0 | 0 | 0 | 0
2025-04-12 15:00 | 60.79 | 98.2 | 60.79 | 0 | 0 | 0 | 0 | 37.41 | 0
2025-04-12 16:00 | 60.89 | 118.28 | 60.89 | 0 | 0 | 0 | 0 | 57.38 | 0
2025-04-12 17:00 | 60.61 | 99.43 | 60.61 | 0 | 0 | 0 | 0 | 38.83 | 0
2025-04-12 18:00 | 57.08 | 20.2 | 20.2 | 36.88 | 0 | 0 | 0 | 0 | 0
2025-04-12 19:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 0 | 0 | 0
2025-04-12 20:00 | 52.78 | 0 | 0 | 52.78 | 0 | 0 | 0 | 0 | 0
2025-04-12 21:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 0 | 0 | 0
2025-04-12 22:00 | 48.45 | 0 | 0 | 48.45 | 0 | 0 | 0 | 0 | 0
2025-04-12 23:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 0 | 0 | 0
2025-04-13 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 0 | 0 | 0
2025-04-13 01:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0 | 0 | 0
2025-04-13 02:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 0 | 0 | 0
2025-04-13 03:00 | 41.93 | 0 | 0 | 41.93 | 0 | 0 | 0 | 0 | 0
2025-04-13 04:00 | 43.31 | 0 | 0 | 43.31 | 0 | 0 | 0 | 0 | 0
2025-04-13 05:00 | 44.06 | 0 | 0 | 44.06 | 0 | 0 | 0 | 0 | 0
2025-04-13 06:00 | 45.3 | 30.47 | 30.47 | 14.84 | 0 | 0 | 0 | 0 | 0
2025-04-13 07:00 | 45.66 | 91.46 | 45.66 | 0 | 0 | 0 | 0 | 45.8 | 0
2025-04-13 08:00 | 48.35 | 108.65 | 48.35 | 0 | 0 | 0 | 0 | 60.3 | 0
2025-04-13 09:00 | 50.41 | 111.39 | 50.41 | 0 | 0 | 0 | 0 | 60.98 | 0
2025-04-13 10:00 | 51.4 | 108.26 | 51.4 | 0 | 0 | 0 | 0 | 56.86 | 0
2025-04-13 11:00 | 53.6 | 104.16 | 53.6 | 0 | 0 | 0 | 0 | 50.56 | 0
2025-04-13 12:00 | 54.97 | 104.1 | 54.97 | 0 | 0 | 0 | 0 | 49.13 | 0
2025-04-13 13:00 | 57.02 | 109 | 57.02 | 0 | 0 | 0 | 0 | 51.98 | 0
2025-04-13 14:00 | 57.73 | 112.54 | 57.73 | 0 | 0 | 0 | 0 | 54.8 | 0
2025-04-13 15:00 | 56.17 | 112.52 | 56.17 | 0 | 0 | 0 | 0 | 56.35 | 0
2025-04-13 16:00 | 58.02 | 109.05 | 58.02 | 0 | 0 | 0 | 0 | 51.03 | 0
2025-04-13 17:00 | 55.64 | 91.81 | 55.64 | 0 | 0 | 0 | 0 | 36.16 | 0
2025-04-13 18:00 | 55.51 | 18.04 | 18.04 | 37.47 | 0 | 0 | 0 | 0 | 0
2025-04-13 19:00 | 54.09 | 0 | 0 | 54.09 | 0 | 0 | 0 | 0 | 0
2025-04-13 20:00 | 51.42 | 0 | 0 | 51.42 | 0 | 0 | 0 | 0 | 0
2025-04-13 21:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 0 | 0 | 0
2025-04-13 22:00 | 48.15 | 0 | 0 | 48.15 | 0 | 0 | 0 | 0 | 0
2025-04-13 23:00 | 46.71 | 0 | 0 | 46.71 | 0 | 0 | 0 | 0 | 0
2025-04-14 | 45.22 | 0 | 0 | 45.22 | 0 | 0 | 0 | 0 | 0
2025-04-14 01:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0 | 0 | 0
2025-04-14 02:00 | 43.09 | 0 | 0 | 43.09 | 0 | 0 | 0 | 0 | 0
2025-04-14 03:00 | 42.7 | 0 | 0 | 42.7 | 0 | 0 | 0 | 0 | 0
2025-04-14 04:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0 | 0 | 0
2025-04-14 05:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 0 | 0 | 0
2025-04-14 06:00 | 45.47 | 16.71 | 16.71 | 28.75 | 0 | 0 | 0 | 0 | 0
2025-04-14 07:00 | 46.46 | 66.96 | 46.46 | 0 | 0 | 0 | 0 | 20.5 | 0
2025-04-14 08:00 | 48.29 | 82.55 | 48.29 | 0 | 0 | 0 | 0 | 34.26 | 0
2025-04-14 09:00 | 50.77 | 98.27 | 50.77 | 0 | 0 | 0 | 0 | 47.5 | 0
2025-04-14 10:00 | 53.05 | 105.36 | 53.05 | 0 | 0 | 0 | 0 | 52.31 | 0
2025-04-14 11:00 | 55.97 | 99.99 | 55.97 | 0 | 0 | 0 | 0 | 44.02 | 0
2025-04-14 12:00 | 58.01 | 96.77 | 58.01 | 0 | 0 | 0 | 0 | 38.76 | 0
2025-04-14 13:00 | 58.97 | 96.48 | 58.97 | 0 | 0 | 0 | 0 | 37.51 | 0
2025-04-14 14:00 | 60.73 | 80.36 | 60.73 | 0 | 0 | 0 | 0 | 19.63 | 0
2025-04-14 15:00 | 61.04 | 88.06 | 61.04 | 0 | 0 | 0 | 0 | 27.02 | 0
2025-04-14 16:00 | 60.14 | 63.55 | 60.14 | 0 | 0 | 0 | 0 | 3.41 | 0
2025-04-14 17:00 | 58.64 | 74.27 | 58.64 | 0 | 0 | 0 | 0 | 15.64 | 0
2025-04-14 18:00 | 58.31 | 17.53 | 17.53 | 40.78 | 0 | 0 | 0 | 0 | 0
2025-04-14 19:00 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 0 | 0 | 0
2025-04-14 20:00 | 53.42 | 0 | 0 | 53.42 | 0 | 0 | 0 | 0 | 0
2025-04-14 21:00 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 0 | 0 | 0
2025-04-14 22:00 | 48.37 | 0 | 0 | 48.37 | 0 | 0 | 0 | 0 | 0
2025-04-14 23:00 | 46.06 | 0 | 0 | 46.06 | 0 | 0 | 0 | 0 | 0
2025-04-15 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 0 | 0 | 0
2025-04-15 01:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0 | 0 | 0
2025-04-15 02:00 | 44.71 | 0 | 0 | 44.71 | 0 | 0 | 0 | 0 | 0
2025-04-15 03:00 | 42.37 | 0 | 0 | 42.37 | 0 | 0 | 0 | 0 | 0
2025-04-15 04:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 0 | 0 | 0
2025-04-15 05:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 0 | 0 | 0
2025-04-15 06:00 | 45.92 | 32.3 | 32.3 | 13.62 | 0 | 0 | 0 | 0 | 0
2025-04-15 07:00 | 46.7 | 82.6 | 46.7 | 0 | 0 | 0 | 0 | 35.89 | 0
2025-04-15 08:00 | 48.65 | 97.7 | 48.65 | 0 | 0 | 0 | 0 | 49.05 | 0
2025-04-15 09:00 | 49.18 | 104.08 | 49.18 | 0 | 0 | 0 | 0 | 54.9 | 0
2025-04-15 10:00 | 51.41 | 101.77 | 51.41 | 0 | 0 | 0 | 0 | 50.36 | 0
2025-04-15 11:00 | 52.66 | 99.76 | 52.66 | 0 | 0 | 0 | 0 | 47.1 | 0
2025-04-15 12:00 | 53.44 | 100.93 | 53.44 | 0 | 0 | 0 | 0 | 47.49 | 0
2025-04-15 13:00 | 55.32 | 104.05 | 55.32 | 0 | 0 | 0 | 0 | 48.73 | 0
2025-04-15 14:00 | 54.67 | 106.25 | 54.67 | 0 | 0 | 0 | 0 | 51.59 | 0
2025-04-15 15:00 | 55.31 | 104.12 | 55.31 | 0 | 0 | 0 | 0 | 48.81 | 0
2025-04-15 16:00 | 55.52 | 100.34 | 55.52 | 0 | 0 | 0 | 0 | 44.81 | 0
2025-04-15 17:00 | 54.84 | 85.95 | 54.84 | 0 | 0 | 0 | 0 | 31.11 | 0
2025-04-15 18:00 | 54.58 | 19.53 | 19.53 | 35.05 | 0 | 0 | 0 | 0 | 0
2025-04-15 19:00 | 53.35 | 0 | 0 | 53.35 | 0 | 0 | 0 | 0 | 0
2025-04-15 20:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0 | 0 | 0
2025-04-15 21:00 | 50.48 | 0 | 0 | 50.48 | 0 | 0 | 0 | 0 | 0
2025-04-15 22:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0 | 0 | 0
2025-04-15 23:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 0 | 0 | 0
2025-04-16 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 0 | 0 | 0
2025-04-16 01:00 | 44.36 | 0 | 0 | 44.36 | 0 | 0 | 0 | 0 | 0
2025-04-16 02:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 0 | 0 | 0
2025-04-16 03:00 | 42.84 | 0 | 0 | 42.84 | 0 | 0 | 0 | 0 | 0
2025-04-16 04:00 | 43.14 | 0 | 0 | 43.14 | 0 | 0 | 0 | 0 | 0
2025-04-16 05:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0 | 0 | 0
2025-04-16 06:00 | 45.56 | 9.12 | 9.12 | 36.44 | 0 | 0 | 0 | 0 | 0
2025-04-16 07:00 | 46.93 | 19.7 | 19.7 | 27.22 | 0 | 0 | 0 | 0 | 0
2025-04-16 08:00 | 48.51 | 30.65 | 30.65 | 17.86 | 0 | 0 | 0 | 0 | 0
2025-04-16 09:00 | 50.5 | 53.51 | 50.5 | 0 | 0 | 0 | 0 | 3.01 | 0
2025-04-16 10:00 | 52.2 | 58.5 | 52.2 | 0 | 0 | 0 | 0 | 6.3 | 0
2025-04-16 11:00 | 55.11 | 54.2 | 54.2 | 0.91 | 0 | 0 | 0 | 0 | 0
2025-04-16 12:00 | 56.2 | 42.96 | 42.96 | 13.24 | 0 | 0 | 0 | 0 | 0
2025-04-16 13:00 | 56.91 | 48.5 | 48.5 | 8.41 | 0 | 0 | 0 | 0 | 0
2025-04-16 14:00 | 58.48 | 46.21 | 46.21 | 12.27 | 0 | 0 | 0 | 0 | 0
2025-04-16 15:00 | 58.05 | 32.68 | 32.68 | 25.37 | 0 | 0 | 0 | 0 | 0
2025-04-16 16:00 | 57.38 | 17.82 | 17.82 | 39.55 | 0 | 0 | 0 | 0 | 0
2025-04-16 17:00 | 57.85 | 7.45 | 7.45 | 50.4 | 0 | 0 | 0 | 0 | 0
2025-04-16 18:00 | 55.9 | 0 | 0 | 55.9 | 0 | 0 | 0 | 0 | 0
2025-04-16 19:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 0 | 0 | 0
2025-04-16 20:00 | 52.82 | 0 | 0 | 52.82 | 0 | 0 | 0 | 0 | 0
2025-04-16 21:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-04-16 22:00 | 48.85 | 0 | 0 | 48.85 | 0 | 0 | 0 | 0 | 0
2025-04-16 23:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 0 | 0 | 0
2025-04-17 | 45.73 | 0 | 0 | 45.73 | 0 | 0 | 0 | 0 | 0
2025-04-17 01:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 0 | 0 | 0
2025-04-17 02:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 0 | 0 | 0
2025-04-17 03:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0 | 0 | 0
2025-04-17 04:00 | 42.32 | 0 | 0 | 42.32 | 0 | 0 | 0 | 0 | 0
2025-04-17 05:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 0 | 0 | 0
2025-04-17 06:00 | 46.43 | 45.29 | 45.29 | 1.15 | 0 | 0 | 0 | 0 | 0
2025-04-17 07:00 | 47.8 | 109.23 | 47.8 | 0 | 0 | 0 | 0 | 61.43 | 0
2025-04-17 08:00 | 49.66 | 121.48 | 49.66 | 0 | 0 | 0 | 0 | 71.83 | 0
2025-04-17 09:00 | 50 | 122.78 | 50 | 0 | 0 | 0 | 0 | 72.77 | 0
2025-04-17 10:00 | 52.64 | 120.02 | 52.64 | 0 | 0 | 0 | 0 | 67.37 | 0
2025-04-17 11:00 | 53.31 | 115.97 | 53.31 | 0 | 0 | 0 | 0 | 62.66 | 0
2025-04-17 12:00 | 54.99 | 113.86 | 54.99 | 0 | 0 | 0 | 0 | 58.87 | 0
2025-04-17 13:00 | 55.12 | 116.57 | 55.12 | 0 | 0 | 0 | 0 | 61.45 | 0
2025-04-17 14:00 | 55.98 | 119.92 | 55.98 | 0 | 0 | 0 | 0 | 63.94 | 0
2025-04-17 15:00 | 56.14 | 122.41 | 56.14 | 0 | 0 | 0 | 0 | 66.26 | 0
2025-04-17 16:00 | 56.75 | 119.24 | 56.75 | 0 | 0 | 0 | 0 | 62.49 | 0
2025-04-17 17:00 | 56.16 | 104.54 | 56.16 | 0 | 0 | 0 | 0 | 48.38 | 0
2025-04-17 18:00 | 55.01 | 28.57 | 28.57 | 26.44 | 0 | 0 | 0 | 0 | 0
2025-04-17 19:00 | 52.99 | 0 | 0 | 52.99 | 0 | 0 | 0 | 0 | 0
2025-04-17 20:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 0 | 0 | 0
2025-04-17 21:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0 | 0 | 0
2025-04-17 22:00 | 49.18 | 0 | 0 | 49.18 | 0 | 0 | 0 | 0 | 0
2025-04-17 23:00 | 47.6 | 0 | 0 | 47.6 | 0 | 0 | 0 | 0 | 0
2025-04-18 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 0 | 0 | 0
2025-04-18 01:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0
2025-04-18 02:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 0 | 0 | 0
2025-04-18 03:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 0 | 0 | 0
2025-04-18 04:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 0 | 0 | 0
2025-04-18 05:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0 | 0 | 0
2025-04-18 06:00 | 45.28 | 43.09 | 43.09 | 2.19 | 0 | 0 | 0 | 0 | 0
2025-04-18 07:00 | 48.12 | 100.64 | 48.12 | 0 | 0 | 0 | 0 | 52.52 | 0
2025-04-18 08:00 | 49.81 | 114.46 | 49.81 | 0 | 0 | 0 | 0 | 64.65 | 0
2025-04-18 09:00 | 51.18 | 116.71 | 51.18 | 0 | 0 | 0 | 0 | 65.52 | 0
2025-04-18 10:00 | 52.98 | 114.77 | 52.98 | 0 | 0 | 0 | 0 | 61.79 | 0
2025-04-18 11:00 | 54.86 | 111.24 | 54.86 | 0 | 0 | 0 | 0 | 56.38 | 0
2025-04-18 12:00 | 56.55 | 107.8 | 56.55 | 0 | 0 | 0 | 0 | 51.24 | 0
2025-04-18 13:00 | 58.39 | 109.37 | 58.39 | 0 | 0 | 0 | 0 | 50.98 | 0
2025-04-18 14:00 | 58.52 | 112.67 | 58.52 | 0 | 0 | 0 | 0 | 54.16 | 0
2025-04-18 15:00 | 58.91 | 114.32 | 58.91 | 0 | 0 | 0 | 0 | 55.4 | 0
2025-04-18 16:00 | 58.89 | 107.97 | 58.89 | 0 | 0 | 0 | 0 | 49.08 | 0
2025-04-18 17:00 | 57 | 90.16 | 57 | 0 | 0 | 0 | 0 | 33.15 | 0
2025-04-18 18:00 | 56.82 | 25.3 | 25.3 | 31.52 | 0 | 0 | 0 | 0 | 0
2025-04-18 19:00 | 54.78 | 0 | 0 | 54.78 | 0 | 0 | 0 | 0 | 0
2025-04-18 20:00 | 51.87 | 0 | 0 | 51.87 | 0 | 0 | 0 | 0 | 0
2025-04-18 21:00 | 50.11 | 0 | 0 | 50.11 | 0 | 0 | 0 | 0 | 0
2025-04-18 22:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 0 | 0 | 0
2025-04-18 23:00 | 47.56 | 0 | 0 | 47.56 | 0 | 0 | 0 | 0 | 0
2025-04-19 | 45.94 | 0 | 0 | 45.94 | 0 | 0 | 0 | 0 | 0
2025-04-19 01:00 | 44.63 | 0 | 0 | 44.63 | 0 | 0 | 0 | 0 | 0
2025-04-19 02:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0 | 0 | 0
2025-04-19 03:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 0 | 0 | 0
2025-04-19 04:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0 | 0 | 0
2025-04-19 05:00 | 44.69 | 0 | 0 | 44.69 | 0 | 0 | 0 | 0 | 0
2025-04-19 06:00 | 45.52 | 16.34 | 16.34 | 29.17 | 0 | 0 | 0 | 0 | 0
2025-04-19 07:00 | 47.7 | 37.04 | 37.04 | 10.66 | 0 | 0 | 0 | 0 | 0
2025-04-19 08:00 | 49.06 | 49.3 | 49.06 | 0 | 0 | 0 | 0 | 0.24 | 0
2025-04-19 09:00 | 52.97 | 56.09 | 52.97 | 0 | 0 | 0 | 0 | 3.12 | 0
2025-04-19 10:00 | 54.41 | 86.83 | 54.41 | 0 | 0 | 0 | 0 | 32.42 | 0
2025-04-19 11:00 | 58.16 | 78.73 | 58.16 | 0 | 0 | 0 | 0 | 20.57 | 0
2025-04-19 12:00 | 59.24 | 88.4 | 59.24 | 0 | 0 | 0 | 0 | 29.16 | 0
2025-04-19 13:00 | 61.43 | 104.92 | 61.43 | 0 | 0 | 0 | 0 | 43.49 | 0
2025-04-19 14:00 | 61.95 | 108.09 | 61.95 | 0 | 0 | 0 | 0 | 46.14 | 0
2025-04-19 15:00 | 62.33 | 108.74 | 62.33 | 0 | 0 | 0 | 0 | 46.42 | 0
2025-04-19 16:00 | 61.68 | 125.09 | 61.68 | 0 | 0 | 0 | 0 | 63.41 | 0
2025-04-19 17:00 | 60.98 | 114.33 | 60.98 | 0 | 0 | 0 | 0 | 53.35 | 0
2025-04-19 18:00 | 59.42 | 37.37 | 37.37 | 22.05 | 0 | 0 | 0 | 0 | 0
2025-04-19 19:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 0 | 0 | 0
2025-04-19 20:00 | 54.69 | 0 | 0 | 54.69 | 0 | 0 | 0 | 0 | 0
2025-04-19 21:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 0 | 0 | 0
2025-04-19 22:00 | 51 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0
2025-04-19 23:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 0 | 0 | 0
2025-04-20 | 46.65 | 0 | 0 | 46.65 | 0 | 0 | 0 | 0 | 0
2025-04-20 01:00 | 44.55 | 0 | 0 | 44.55 | 0 | 0 | 0 | 0 | 0
2025-04-20 02:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 0 | 0 | 0
2025-04-20 03:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 0 | 0 | 0
2025-04-20 04:00 | 43.61 | 0 | 0 | 43.61 | 0 | 0 | 0 | 0 | 0
2025-04-20 05:00 | 44.75 | 0.3 | 0.3 | 44.45 | 0 | 0 | 0 | 0 | 0
2025-04-20 06:00 | 46.67 | 4.54 | 4.54 | 42.12 | 0 | 0 | 0 | 0 | 0
2025-04-20 07:00 | 47.5 | 74.82 | 47.5 | 0 | 0 | 0 | 0 | 27.33 | 0
2025-04-20 08:00 | 49.69 | 123.97 | 49.69 | 0 | 0 | 0 | 0 | 74.27 | 0
2025-04-20 09:00 | 50.89 | 108.04 | 50.89 | 0 | 0 | 0 | 0 | 57.15 | 0
2025-04-20 10:00 | 52.78 | 104.14 | 52.78 | 0 | 0 | 0 | 0 | 51.37 | 0
2025-04-20 11:00 | 53.08 | 38.85 | 38.85 | 14.23 | 0 | 0 | 0 | 0 | 0
2025-04-20 12:00 | 55.17 | 74.9 | 55.17 | 0 | 0 | 0 | 0 | 19.74 | 0
2025-04-20 13:00 | 54.32 | 130.93 | 54.32 | 0 | 0 | 0 | 0 | 76.61 | 0
2025-04-20 14:00 | 54.51 | 45.84 | 45.84 | 8.67 | 0 | 0 | 0 | 0 | 0
2025-04-20 15:00 | 54.4 | 5.91 | 5.91 | 48.49 | 0 | 0 | 0 | 0 | 0
2025-04-20 16:00 | 56.06 | 3.85 | 3.85 | 52.21 | 0 | 0 | 0 | 0 | 0
2025-04-20 17:00 | 54.97 | 1.73 | 1.73 | 53.24 | 0 | 0 | 0 | 0 | 0
2025-04-20 18:00 | 53.8 | 0 | 0 | 53.8 | 0 | 0 | 0 | 0 | 0
2025-04-20 19:00 | 53.73 | 0 | 0 | 53.73 | 0 | 0 | 0 | 0 | 0
2025-04-20 20:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0 | 0 | 0
2025-04-20 21:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0 | 0 | 0
2025-04-20 22:00 | 48.23 | 0 | 0 | 48.23 | 0 | 0 | 0 | 0 | 0
2025-04-20 23:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 0 | 0 | 0
2025-04-21 | 45.94 | 0 | 0 | 45.94 | 0 | 0 | 0 | 0 | 0
2025-04-21 01:00 | 43.83 | 0 | 0 | 43.83 | 0 | 0 | 0 | 0 | 0
2025-04-21 02:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 0 | 0 | 0
2025-04-21 03:00 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 0 | 0 | 0
2025-04-21 04:00 | 44.34 | 0 | 0 | 44.34 | 0 | 0 | 0 | 0 | 0
2025-04-21 05:00 | 45.99 | 0.12 | 0.12 | 45.88 | 0 | 0 | 0 | 0 | 0
2025-04-21 06:00 | 46 | 47.49 | 46 | 0 | 0 | 0 | 0 | 1.49 | 0
2025-04-21 07:00 | 47.76 | 100.95 | 47.76 | 0 | 0 | 0 | 0 | 53.2 | 0
2025-04-21 08:00 | 50.15 | 113.68 | 50.15 | 0 | 0 | 0 | 0 | 63.54 | 0
2025-04-21 09:00 | 52.91 | 118.91 | 52.91 | 0 | 0 | 0 | 0 | 66 | 0
2025-04-21 10:00 | 54.5 | 114.88 | 54.5 | 0 | 0 | 0 | 0 | 60.38 | 0
2025-04-21 11:00 | 56.71 | 111.38 | 56.71 | 0 | 0 | 0 | 0 | 54.67 | 0
2025-04-21 12:00 | 59.51 | 109.34 | 59.51 | 0 | 0 | 0 | 0 | 49.83 | 0
2025-04-21 13:00 | 60.69 | 110.78 | 60.69 | 0 | 0 | 0 | 0 | 50.09 | 0
2025-04-21 14:00 | 60.45 | 113.69 | 60.45 | 0 | 0 | 0 | 0 | 53.25 | 0
2025-04-21 15:00 | 61.18 | 116.1 | 61.18 | 0 | 0 | 0 | 0 | 54.92 | 0
2025-04-21 16:00 | 62.22 | 110.88 | 62.22 | 0 | 0 | 0 | 0 | 48.66 | 0
2025-04-21 17:00 | 60.7 | 95.24 | 60.7 | 0 | 0 | 0 | 0 | 34.54 | 0
2025-04-21 18:00 | 58.6 | 31.33 | 31.33 | 27.27 | 0 | 0 | 0 | 0 | 0
2025-04-21 19:00 | 56.94 | 0 | 0 | 56.94 | 0 | 0 | 0 | 0 | 0
2025-04-21 20:00 | 54.78 | 0 | 0 | 54.78 | 0 | 0 | 0 | 0 | 0
2025-04-21 21:00 | 52.78 | 0 | 0 | 52.78 | 0 | 0 | 0 | 0 | 0
2025-04-21 22:00 | 49.41 | 0 | 0 | 49.41 | 0 | 0 | 0 | 0 | 0
2025-04-21 23:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0 | 0 | 0
2025-04-22 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 0 | 0 | 0
2025-04-22 01:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0 | 0 | 0
2025-04-22 02:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 0 | 0 | 0
2025-04-22 03:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 0 | 0 | 0
2025-04-22 04:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 0 | 0 | 0
2025-04-22 05:00 | 45.5 | 0.22 | 0.22 | 45.28 | 0 | 0 | 0 | 0 | 0
2025-04-22 06:00 | 46.56 | 45.42 | 45.42 | 1.14 | 0 | 0 | 0 | 0 | 0
2025-04-22 07:00 | 48.17 | 91.78 | 48.17 | 0 | 0 | 0 | 0 | 43.6 | 0
2025-04-22 08:00 | 50.16 | 106.11 | 50.16 | 0 | 0 | 0 | 0 | 55.95 | 0
2025-04-22 09:00 | 52.07 | 112.73 | 52.07 | 0 | 0 | 0 | 0 | 60.66 | 0
2025-04-22 10:00 | 54.76 | 111.17 | 54.76 | 0 | 0 | 0 | 0 | 56.42 | 0
2025-04-22 11:00 | 57.59 | 102.94 | 57.59 | 0 | 0 | 0 | 0 | 45.35 | 0
2025-04-22 12:00 | 58.78 | 101.28 | 58.78 | 0 | 0 | 0 | 0 | 42.5 | 0
2025-04-22 13:00 | 59.85 | 97.88 | 59.85 | 0 | 0 | 0 | 0 | 38.03 | 0
2025-04-22 14:00 | 60.97 | 100.24 | 60.97 | 0 | 0 | 0 | 0 | 39.28 | 0
2025-04-22 15:00 | 61.63 | 96.38 | 61.63 | 0 | 0 | 0 | 0 | 34.76 | 0
2025-04-22 16:00 | 61.03 | 87.69 | 61.03 | 0 | 0 | 0 | 0 | 26.66 | 0
2025-04-22 17:00 | 60.54 | 70.73 | 60.54 | 0 | 0 | 0 | 0 | 10.19 | 0
2025-04-22 18:00 | 59.1 | 26.9 | 26.9 | 32.2 | 0 | 0 | 0 | 0 | 0
2025-04-22 19:00 | 57.41 | 0 | 0 | 57.41 | 0 | 0 | 0 | 0 | 0
2025-04-22 20:00 | 55.5 | 0 | 0 | 55.5 | 0 | 0 | 0 | 0 | 0
2025-04-22 21:00 | 52.99 | 0 | 0 | 52.99 | 0 | 0 | 0 | 0 | 0
2025-04-22 22:00 | 49.74 | 0 | 0 | 49.74 | 0 | 0 | 0 | 0 | 0
2025-04-22 23:00 | 47.65 | 0 | 0 | 47.65 | 0 | 0 | 0 | 0 | 0
2025-04-23 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 0 | 0 | 0
2025-04-23 01:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 0 | 0 | 0
2025-04-23 02:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0 | 0 | 0
2025-04-23 03:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 0 | 0 | 0
2025-04-23 04:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0
2025-04-23 05:00 | 44.75 | 0.55 | 0.55 | 44.2 | 0 | 0 | 0 | 0 | 0
2025-04-23 06:00 | 46.26 | 49.69 | 46.26 | 0 | 0 | 0 | 0 | 3.43 | 0
2025-04-23 07:00 | 48.71 | 79.56 | 48.71 | 0 | 0 | 0 | 0 | 30.85 | 0
2025-04-23 08:00 | 50.15 | 92.56 | 50.15 | 0 | 0 | 0 | 0 | 42.4 | 0
2025-04-23 09:00 | 53.3 | 75.06 | 53.3 | 0 | 0 | 0 | 0 | 21.76 | 0
2025-04-23 10:00 | 54.11 | 85.03 | 54.11 | 0 | 0 | 0 | 0 | 30.92 | 0
2025-04-23 11:00 | 55.64 | 98.81 | 55.64 | 0 | 0 | 0 | 0 | 43.17 | 0
2025-04-23 12:00 | 57.26 | 96.7 | 57.26 | 0 | 0 | 0 | 0 | 39.43 | 0
2025-04-23 13:00 | 58.49 | 99.07 | 58.49 | 0 | 0 | 0 | 0 | 40.57 | 0
2025-04-23 14:00 | 59.26 | 108.41 | 59.26 | 0 | 0 | 0 | 0 | 49.15 | 0
2025-04-23 15:00 | 60.32 | 110.96 | 60.32 | 0 | 0 | 0 | 0 | 50.64 | 0
2025-04-23 16:00 | 58.62 | 111.21 | 58.62 | 0 | 0 | 0 | 0 | 52.58 | 0
2025-04-23 17:00 | 58.79 | 81.47 | 58.79 | 0 | 0 | 0 | 0 | 22.68 | 0
2025-04-23 18:00 | 57.36 | 21.24 | 21.24 | 36.13 | 0 | 0 | 0 | 0 | 0
2025-04-23 19:00 | 55 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0
2025-04-23 20:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 0 | 0 | 0
2025-04-23 21:00 | 52.7 | 0 | 0 | 52.7 | 0 | 0 | 0 | 0 | 0
2025-04-23 22:00 | 49.62 | 0 | 0 | 49.62 | 0 | 0 | 0 | 0 | 0
2025-04-23 23:00 | 48.12 | 0 | 0 | 48.12 | 0 | 0 | 0 | 0 | 0
2025-04-24 | 45.65 | 0 | 0 | 45.65 | 0 | 0 | 0 | 0 | 0
2025-04-24 01:00 | 44.58 | 0 | 0 | 44.58 | 0 | 0 | 0 | 0 | 0
2025-04-24 02:00 | 44.89 | 0 | 0 | 44.89 | 0 | 0 | 0 | 0 | 0
2025-04-24 03:00 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 0 | 0 | 0
2025-04-24 04:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 0 | 0 | 0
2025-04-24 05:00 | 45.33 | 0 | 0 | 45.33 | 0 | 0 | 0 | 0 | 0
2025-04-24 06:00 | 46.25 | 13.97 | 13.97 | 32.29 | 0 | 0 | 0 | 0 | 0
2025-04-24 07:00 | 47.89 | 74.62 | 47.89 | 0 | 0 | 0 | 0 | 26.72 | 0
2025-04-24 08:00 | 50.25 | 77.86 | 50.25 | 0 | 0 | 0 | 0 | 27.6 | 0
2025-04-24 09:00 | 51.04 | 48.69 | 48.69 | 2.34 | 0 | 0 | 0 | 0 | 0
2025-04-24 10:00 | 52.75 | 53.23 | 52.75 | 0 | 0 | 0 | 0 | 0.48 | 0
2025-04-24 11:00 | 54.62 | 34.9 | 34.9 | 19.72 | 0 | 0 | 0 | 0 | 0
2025-04-24 12:00 | 56.08 | 33.08 | 33.08 | 23 | 0 | 0 | 0 | 0 | 0
2025-04-24 13:00 | 56.95 | 21.18 | 21.18 | 35.77 | 0 | 0 | 0 | 0 | 0
2025-04-24 14:00 | 56.44 | 43.72 | 43.72 | 12.71 | 0 | 0 | 0 | 0 | 0
2025-04-24 15:00 | 57.38 | 36.54 | 36.54 | 20.84 | 0 | 0 | 0 | 0 | 0
2025-04-24 16:00 | 56.38 | 27.1 | 27.1 | 29.27 | 0 | 0 | 0 | 0 | 0
2025-04-24 17:00 | 57.25 | 5.02 | 5.02 | 52.23 | 0 | 0 | 0 | 0 | 0
2025-04-24 18:00 | 55.03 | 0 | 0 | 55.03 | 0 | 0 | 0 | 0 | 0
2025-04-24 19:00 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 0 | 0 | 0
2025-04-24 20:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 0 | 0 | 0
2025-04-24 21:00 | 52.63 | 0 | 0 | 52.63 | 0 | 0 | 0 | 0 | 0
2025-04-24 22:00 | 50.18 | 0 | 0 | 50.18 | 0 | 0 | 0 | 0 | 0
2025-04-24 23:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0 | 0 | 0
2025-04-25 | 46.51 | 0 | 0 | 46.51 | 0 | 0 | 0 | 0 | 0
2025-04-25 01:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 0 | 0 | 0
2025-04-25 02:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 0 | 0 | 0
2025-04-25 03:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 0 | 0 | 0
2025-04-25 04:00 | 44.52 | 0 | 0 | 44.52 | 0 | 0 | 0 | 0 | 0
2025-04-25 05:00 | 45.75 | 0.08 | 0.08 | 45.67 | 0 | 0 | 0 | 0 | 0
2025-04-25 06:00 | 46.84 | 8.5 | 8.5 | 38.34 | 0 | 0 | 0 | 0 | 0
2025-04-25 07:00 | 47.95 | 52.54 | 47.95 | 0 | 0 | 0 | 0 | 4.58 | 0
2025-04-25 08:00 | 50.33 | 51.1 | 50.33 | 0 | 0 | 0 | 0 | 0.77 | 0
2025-04-25 09:00 | 53.15 | 29.38 | 29.38 | 23.77 | 0 | 0 | 0 | 0 | 0
2025-04-25 10:00 | 55.94 | 40.62 | 40.62 | 15.32 | 0 | 0 | 0 | 0 | 0
2025-04-25 11:00 | 58.29 | 91.98 | 58.29 | 0 | 0 | 0 | 0 | 33.69 | 0
2025-04-25 12:00 | 59.73 | 95.89 | 59.73 | 0 | 0 | 0 | 0 | 36.16 | 0
2025-04-25 13:00 | 60.91 | 122.74 | 60.91 | 0 | 0 | 0 | 0 | 61.83 | 0
2025-04-25 14:00 | 62.04 | 125.1 | 62.04 | 0 | 0 | 0 | 0 | 63.06 | 0
2025-04-25 15:00 | 61.64 | 125.04 | 61.64 | 0 | 0 | 0 | 0 | 63.4 | 0
2025-04-25 16:00 | 61.59 | 99.31 | 61.59 | 0 | 0 | 0 | 0 | 37.72 | 0
2025-04-25 17:00 | 60.36 | 101.78 | 60.36 | 0 | 0 | 0 | 0 | 41.42 | 0
2025-04-25 18:00 | 58.72 | 37.49 | 37.49 | 21.23 | 0 | 0 | 0 | 0 | 0
2025-04-25 19:00 | 57.65 | 0 | 0 | 57.65 | 0 | 0 | 0 | 0 | 0
2025-04-25 20:00 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 0 | 0 | 0
2025-04-25 21:00 | 53.37 | 0 | 0 | 53.37 | 0 | 0 | 0 | 0 | 0
2025-04-25 22:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 0 | 0 | 0
2025-04-25 23:00 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 0 | 0 | 0
2025-04-26 | 47.17 | 0 | 0 | 47.17 | 0 | 0 | 0 | 0 | 0
2025-04-26 01:00 | 45.49 | 0 | 0 | 45.49 | 0 | 0 | 0 | 0 | 0
2025-04-26 02:00 | 44.84 | 0 | 0 | 44.84 | 0 | 0 | 0 | 0 | 0
2025-04-26 03:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 0 | 0 | 0
2025-04-26 04:00 | 44.81 | 0 | 0 | 44.81 | 0 | 0 | 0 | 0 | 0
2025-04-26 05:00 | 45.84 | 0.78 | 0.78 | 45.06 | 0 | 0 | 0 | 0 | 0
2025-04-26 06:00 | 46.55 | 8.81 | 8.81 | 37.74 | 0 | 0 | 0 | 0 | 0
2025-04-26 07:00 | 48.68 | 11.62 | 11.62 | 37.06 | 0 | 0 | 0 | 0 | 0
2025-04-26 08:00 | 50.36 | 38.69 | 38.69 | 11.67 | 0 | 0 | 0 | 0 | 0
2025-04-26 09:00 | 52.51 | 47.36 | 47.36 | 5.15 | 0 | 0 | 0 | 0 | 0
2025-04-26 10:00 | 54.26 | 68.33 | 54.26 | 0 | 0 | 0 | 0 | 14.07 | 0
2025-04-26 11:00 | 57.31 | 101.8 | 57.31 | 0 | 0 | 0 | 0 | 44.5 | 0
2025-04-26 12:00 | 58.77 | 101 | 58.77 | 0 | 0 | 0 | 0 | 42.23 | 0
2025-04-26 13:00 | 59.67 | 84.31 | 59.67 | 0 | 0 | 0 | 0 | 24.64 | 0
2025-04-26 14:00 | 61.11 | 94.76 | 61.11 | 0 | 0 | 0 | 0 | 33.64 | 0
2025-04-26 15:00 | 60.28 | 86.27 | 60.28 | 0 | 0 | 0 | 0 | 25.99 | 0
2025-04-26 16:00 | 61.64 | 57.22 | 57.22 | 4.43 | 0 | 0 | 0 | 0 | 0
2025-04-26 17:00 | 59.29 | 20.34 | 20.34 | 38.95 | 0 | 0 | 0 | 0 | 0
2025-04-26 18:00 | 58.36 | 4.79 | 4.79 | 53.57 | 0 | 0 | 0 | 0 | 0
2025-04-26 19:00 | 56.48 | 0 | 0 | 56.48 | 0 | 0 | 0 | 0 | 0
2025-04-26 20:00 | 55.01 | 0 | 0 | 55.01 | 0 | 0 | 0 | 0 | 0
2025-04-26 21:00 | 53.19 | 0 | 0 | 53.19 | 0 | 0 | 0 | 0 | 0
2025-04-26 22:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 0 | 0 | 0
2025-04-26 23:00 | 49.54 | 0 | 0 | 49.54 | 0 | 0 | 0 | 0 | 0
2025-04-27 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 0 | 0 | 0
2025-04-27 01:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 0 | 0 | 0
2025-04-27 02:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 0 | 0 | 0
2025-04-27 03:00 | 44.67 | 0 | 0 | 44.67 | 0 | 0 | 0 | 0 | 0
2025-04-27 04:00 | 44.7 | 0 | 0 | 44.7 | 0 | 0 | 0 | 0 | 0
2025-04-27 05:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 0 | 0 | 0
2025-04-27 06:00 | 46.71 | 0.14 | 0.14 | 46.57 | 0 | 0 | 0 | 0 | 0
2025-04-27 07:00 | 50.32 | 25.36 | 25.36 | 24.96 | 0 | 0 | 0 | 0 | 0
2025-04-27 08:00 | 51.07 | 44.59 | 44.59 | 6.48 | 0 | 0 | 0 | 0 | 0
2025-04-27 09:00 | 52.88 | 98.32 | 52.88 | 0 | 0 | 0 | 0 | 45.45 | 0
2025-04-27 10:00 | 55.68 | 65.37 | 55.68 | 0 | 0 | 0 | 0 | 9.69 | 0
2025-04-27 11:00 | 58.29 | 82.57 | 58.29 | 0 | 0 | 0 | 0 | 24.27 | 0
2025-04-27 12:00 | 60.57 | 59.87 | 59.87 | 0.7 | 0 | 0 | 0 | 0 | 0
2025-04-27 13:00 | 62.11 | 52.63 | 52.63 | 9.48 | 0 | 0 | 0 | 0 | 0
2025-04-27 14:00 | 63.14 | 38.83 | 38.83 | 24.3 | 0 | 0 | 0 | 0 | 0
2025-04-27 15:00 | 62.8 | 55.97 | 55.97 | 6.83 | 0 | 0 | 0 | 0 | 0
2025-04-27 16:00 | 62.97 | 57.33 | 57.33 | 5.63 | 0 | 0 | 0 | 0 | 0
2025-04-27 17:00 | 61.39 | 86.82 | 61.39 | 0 | 0 | 0 | 0 | 25.43 | 0
2025-04-27 18:00 | 59.99 | 34.56 | 34.56 | 25.43 | 0 | 0 | 0 | 0 | 0
2025-04-27 19:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 0 | 0 | 0
2025-04-27 20:00 | 55.44 | 0 | 0 | 55.44 | 0 | 0 | 0 | 0 | 0
2025-04-27 21:00 | 54.14 | 0 | 0 | 54.14 | 0 | 0 | 0 | 0 | 0
2025-04-27 22:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 0 | 0 | 0
2025-04-27 23:00 | 49.47 | 0 | 0 | 49.47 | 0 | 0 | 0 | 0 | 0
2025-04-28 | 47.26 | 0 | 0 | 47.26 | 0 | 0 | 0 | 0 | 0
2025-04-28 01:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 0 | 0 | 0
2025-04-28 02:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 0 | 0 | 0
2025-04-28 03:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 0 | 0 | 0
2025-04-28 04:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0 | 0 | 0
2025-04-28 05:00 | 46.11 | 0.67 | 0.67 | 45.44 | 0 | 0 | 0 | 0 | 0
2025-04-28 06:00 | 47.43 | 17.9 | 17.9 | 29.53 | 0 | 0 | 0 | 0 | 0
2025-04-28 07:00 | 48.62 | 37.07 | 37.07 | 11.55 | 0 | 0 | 0 | 0 | 0
2025-04-28 08:00 | 50.56 | 59.88 | 50.56 | 0 | 0 | 0 | 0 | 9.32 | 0
2025-04-28 09:00 | 53.3 | 100.35 | 53.3 | 0 | 0 | 0 | 0 | 47.05 | 0
2025-04-28 10:00 | 56.29 | 115.48 | 56.29 | 0 | 0 | 0 | 0 | 59.19 | 0
2025-04-28 11:00 | 58.55 | 98.48 | 58.55 | 0 | 0 | 0 | 0 | 39.93 | 0
2025-04-28 12:00 | 59.41 | 64.34 | 59.41 | 0 | 0 | 0 | 0 | 4.93 | 0
2025-04-28 13:00 | 61.05 | 60.28 | 60.28 | 0.77 | 0 | 0 | 0 | 0 | 0
2025-04-28 14:00 | 62.09 | 61.82 | 61.82 | 0.27 | 0 | 0 | 0 | 0 | 0
2025-04-28 15:00 | 62.58 | 33.16 | 33.16 | 29.43 | 0 | 0 | 0 | 0 | 0
2025-04-28 16:00 | 61.77 | 21.09 | 21.09 | 40.68 | 0 | 0 | 0 | 0 | 0
2025-04-28 17:00 | 60.83 | 1.11 | 1.11 | 59.72 | 0 | 0 | 0 | 0 | 0
2025-04-28 18:00 | 59.68 | 0 | 0 | 59.68 | 0 | 0 | 0 | 0 | 0
2025-04-28 19:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 0 | 0 | 0
2025-04-28 20:00 | 55.42 | 0 | 0 | 55.42 | 0 | 0 | 0 | 0 | 0
2025-04-28 21:00 | 53.6 | 0 | 0 | 53.6 | 0 | 0 | 0 | 0 | 0
2025-04-28 22:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 0 | 0 | 0
2025-04-28 23:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 0 | 0 | 0
2025-04-29 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 0 | 0 | 0
2025-04-29 01:00 | 46.48 | 0 | 0 | 46.48 | 0 | 0 | 0 | 0 | 0
2025-04-29 02:00 | 44.82 | 0 | 0 | 44.82 | 0 | 0 | 0 | 0 | 0
2025-04-29 03:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0 | 0 | 0
2025-04-29 04:00 | 45.61 | 0 | 0 | 45.61 | 0 | 0 | 0 | 0 | 0
2025-04-29 05:00 | 45.81 | 1.33 | 1.33 | 44.48 | 0 | 0 | 0 | 0 | 0
2025-04-29 06:00 | 48.06 | 28.37 | 28.37 | 19.69 | 0 | 0 | 0 | 0 | 0
2025-04-29 07:00 | 49.83 | 84.62 | 49.83 | 0 | 0 | 0 | 0 | 34.79 | 0
2025-04-29 08:00 | 52.05 | 46.47 | 46.47 | 5.58 | 0 | 0 | 0 | 0 | 0
2025-04-29 09:00 | 55.42 | 65.39 | 55.42 | 0 | 0 | 0 | 0 | 9.98 | 0
2025-04-29 10:00 | 58.48 | 107.99 | 58.48 | 0 | 0 | 0 | 0 | 49.52 | 0
2025-04-29 11:00 | 61.91 | 71.76 | 61.91 | 0 | 0 | 0 | 0 | 9.85 | 0
2025-04-29 12:00 | 63.9 | 96.4 | 63.9 | 0 | 0 | 0 | 0 | 32.51 | 0
2025-04-29 13:00 | 66.39 | 107.24 | 66.39 | 0 | 0 | 0 | 0 | 40.84 | 0
2025-04-29 14:00 | 67.76 | 122.04 | 67.76 | 0 | 0 | 0 | 0 | 54.28 | 0
2025-04-29 15:00 | 68.63 | 121.78 | 68.63 | 0 | 0 | 0 | 0 | 53.15 | 0
2025-04-29 16:00 | 67.28 | 118.85 | 67.28 | 0 | 0 | 0 | 0 | 51.57 | 0
2025-04-29 17:00 | 66.88 | 100.12 | 66.88 | 0 | 0 | 0 | 0 | 33.24 | 0
2025-04-29 18:00 | 64.4 | 40.38 | 40.38 | 24.02 | 0 | 0 | 0 | 0 | 0
2025-04-29 19:00 | 60.74 | 0 | 0 | 60.74 | 0 | 0 | 0 | 0 | 0
2025-04-29 20:00 | 58.92 | 0 | 0 | 58.92 | 0 | 0 | 0 | 0 | 0
2025-04-29 21:00 | 56.3 | 0 | 0 | 56.3 | 0 | 0 | 0 | 0 | 0
2025-04-29 22:00 | 52.72 | 0 | 0 | 52.72 | 0 | 0 | 0 | 0 | 0
2025-04-29 23:00 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 0 | 0 | 0
2025-04-30 | 47.58 | 0 | 0 | 47.58 | 0 | 0 | 0 | 0 | 0
2025-04-30 01:00 | 45.25 | 0 | 0 | 45.25 | 0 | 0 | 0 | 0 | 0
2025-04-30 02:00 | 44.24 | 0 | 0 | 44.24 | 0 | 0 | 0 | 0 | 0
2025-04-30 03:00 | 44.97 | 0 | 0 | 44.97 | 0 | 0 | 0 | 0 | 0
2025-04-30 04:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 0 | 0 | 0
2025-04-30 05:00 | 45.62 | 1.38 | 1.38 | 44.24 | 0 | 0 | 0 | 0 | 0
2025-04-30 06:00 | 47.5 | 30.1 | 30.1 | 17.4 | 0 | 0 | 0 | 0 | 0
2025-04-30 07:00 | 49.72 | 59.36 | 49.72 | 0 | 0 | 0 | 0 | 9.64 | 0
2025-04-30 08:00 | 50.86 | 94.24 | 50.86 | 0 | 0 | 0 | 0 | 43.38 | 0
2025-04-30 09:00 | 53.66 | 96.66 | 53.66 | 0 | 0 | 0 | 0 | 43 | 0
2025-04-30 10:00 | 56.91 | 98.46 | 56.91 | 0 | 0 | 0 | 0 | 41.55 | 0
2025-04-30 11:00 | 57.72 | 99.82 | 57.72 | 0 | 0 | 0 | 0 | 42.1 | 0
2025-04-30 12:00 | 60.47 | 101.89 | 60.47 | 0 | 0 | 0 | 0 | 41.42 | 0
2025-04-30 13:00 | 61.15 | 104.15 | 61.15 | 0 | 0 | 0 | 0 | 43 | 0
2025-04-30 14:00 | 62.51 | 97.84 | 62.51 | 0 | 0 | 0 | 0 | 35.34 | 0
2025-04-30 15:00 | 63.07 | 91.86 | 63.07 | 0 | 0 | 0 | 0 | 28.79 | 0
2025-04-30 16:00 | 62.61 | 62.54 | 62.54 | 0.07 | 0 | 0 | 0 | 0 | 0
2025-04-30 17:00 | 61.84 | 64.11 | 61.84 | 0 | 0 | 0 | 0 | 2.26 | 0
2025-04-30 18:00 | 59.46 | 35.69 | 35.69 | 23.77 | 0 | 0 | 0 | 0 | 0
2025-04-30 19:00 | 58.81 | 0 | 0 | 58.81 | 0 | 0 | 0 | 0 | 0
2025-04-30 20:00 | 55.73 | 0 | 0 | 55.73 | 0 | 0 | 0 | 0 | 0
2025-04-30 21:00 | 54.01 | 0 | 0 | 54.01 | 0 | 0 | 0 | 0 | 0
2025-04-30 22:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0 | 0 | 0
2025-04-30 23:00 | 49.66 | 0 | 0 | 49.66 | 0 | 0 | 0 | 0 | 0
2025-05-01 | 47.8 | 0 | 0 | 47.8 | 0 | 0 | 0 | 0 | 0
2025-05-01 01:00 | 45.78 | 0 | 0 | 45.78 | 0 | 0 | 0 | 0 | 0
2025-05-01 02:00 | 44.61 | 0 | 0 | 44.61 | 0 | 0 | 0 | 0 | 0
2025-05-01 03:00 | 45.41 | 0 | 0 | 45.41 | 0 | 0 | 0 | 0 | 0
2025-05-01 04:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 0 | 0 | 0
2025-05-01 05:00 | 46.78 | 0 | 0 | 46.78 | 0 | 0 | 0 | 0 | 0
2025-05-01 06:00 | 47.61 | 4.29 | 4.29 | 43.32 | 0 | 0 | 0 | 0 | 0
2025-05-01 07:00 | 48.72 | 5.86 | 5.86 | 42.86 | 0 | 0 | 0 | 0 | 0
2025-05-01 08:00 | 51.9 | 7.5 | 7.5 | 44.4 | 0 | 0 | 0 | 0 | 0
2025-05-01 09:00 | 53.26 | 16.01 | 16.01 | 37.25 | 0 | 0 | 0 | 0 | 0
2025-05-01 10:00 | 55.53 | 17.46 | 17.46 | 38.07 | 0 | 0 | 0 | 0 | 0
2025-05-01 11:00 | 56.71 | 22.8 | 22.8 | 33.91 | 0 | 0 | 0 | 0 | 0
2025-05-01 12:00 | 59.22 | 30.33 | 30.33 | 28.89 | 0 | 0 | 0 | 0 | 0
2025-05-01 13:00 | 58.95 | 39.8 | 39.8 | 19.16 | 0 | 0 | 0 | 0 | 0
2025-05-01 14:00 | 59.83 | 43.18 | 43.18 | 16.65 | 0 | 0 | 0 | 0 | 0
2025-05-01 15:00 | 60.25 | 59.31 | 59.31 | 0.95 | 0 | 0 | 0 | 0 | 0
2025-05-01 16:00 | 59.45 | 32.24 | 32.24 | 27.21 | 0 | 0 | 0 | 0 | 0
2025-05-01 17:00 | 59.56 | 33.98 | 33.98 | 25.58 | 0 | 0 | 0 | 0 | 0
2025-05-01 18:00 | 59.2 | 35.76 | 35.76 | 23.45 | 0 | 0 | 0 | 0 | 0
2025-05-01 19:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 0 | 0 | 0
2025-05-01 20:00 | 55.55 | 0 | 0 | 55.55 | 0 | 0 | 0 | 0 | 0
2025-05-01 21:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 0 | 0 | 0
2025-05-01 22:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-05-01 23:00 | 49.27 | 0 | 0 | 49.27 | 0 | 0 | 0 | 0 | 0
2025-05-02 | 47.46 | 0 | 0 | 47.46 | 0 | 0 | 0 | 0 | 0
2025-05-02 01:00 | 46.91 | 0 | 0 | 46.91 | 0 | 0 | 0 | 0 | 0
2025-05-02 02:00 | 45.26 | 0 | 0 | 45.26 | 0 | 0 | 0 | 0 | 0
2025-05-02 03:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 0 | 0 | 0
2025-05-02 04:00 | 45.23 | 0 | 0 | 45.23 | 0 | 0 | 0 | 0 | 0
2025-05-02 05:00 | 45.41 | 0.56 | 0.56 | 44.84 | 0 | 0 | 0 | 0 | 0
2025-05-02 06:00 | 47.31 | 14.56 | 14.56 | 32.75 | 0 | 0 | 0 | 0 | 0
2025-05-02 07:00 | 50.33 | 14.81 | 14.81 | 35.52 | 0 | 0 | 0 | 0 | 0
2025-05-02 08:00 | 51.11 | 18.51 | 18.51 | 32.61 | 0 | 0 | 0 | 0 | 0
2025-05-02 09:00 | 54.29 | 6.41 | 6.41 | 47.89 | 0 | 0 | 0 | 0 | 0
2025-05-02 10:00 | 57 | 26.03 | 26.03 | 30.98 | 0 | 0 | 0 | 0 | 0
2025-05-02 11:00 | 60.45 | 57 | 57 | 3.45 | 0 | 0 | 0 | 0 | 0
2025-05-02 12:00 | 62.02 | 69.07 | 62.02 | 0 | 0 | 0 | 0 | 7.06 | 0
2025-05-02 13:00 | 62.94 | 73.25 | 62.94 | 0 | 0 | 0 | 0 | 10.32 | 0
2025-05-02 14:00 | 64.87 | 52.82 | 52.82 | 12.05 | 0 | 0 | 0 | 0 | 0
2025-05-02 15:00 | 64.19 | 69.83 | 64.19 | 0 | 0 | 0 | 0 | 5.64 | 0
2025-05-02 16:00 | 64.72 | 43.46 | 43.46 | 21.26 | 0 | 0 | 0 | 0 | 0
2025-05-02 17:00 | 62.54 | 21.72 | 21.72 | 40.81 | 0 | 0 | 0 | 0 | 0
2025-05-02 18:00 | 62.17 | 2.69 | 2.69 | 59.47 | 0 | 0 | 0 | 0 | 0
2025-05-02 19:00 | 59.38 | 0 | 0 | 59.38 | 0 | 0 | 0 | 0 | 0
2025-05-02 20:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 0 | 0 | 0
2025-05-02 21:00 | 54.57 | 0 | 0 | 54.57 | 0 | 0 | 0 | 0 | 0
2025-05-02 22:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0 | 0 | 0
2025-05-02 23:00 | 49.6 | 0 | 0 | 49.6 | 0 | 0 | 0 | 0 | 0
2025-05-03 | 48.31 | 0 | 0 | 48.31 | 0 | 0 | 0 | 0 | 0
2025-05-03 01:00 | 46.22 | 0 | 0 | 46.22 | 0 | 0 | 0 | 0 | 0
2025-05-03 02:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 0 | 0 | 0
2025-05-03 03:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0 | 0 | 0
2025-05-03 04:00 | 45.52 | 0 | 0 | 45.52 | 0 | 0 | 0 | 0 | 0
2025-05-03 05:00 | 46.29 | 2.88 | 2.88 | 43.41 | 0 | 0 | 0 | 0 | 0
2025-05-03 06:00 | 48.11 | 59.25 | 48.11 | 0 | 0 | 0 | 0 | 11.14 | 0
2025-05-03 07:00 | 50.31 | 113.74 | 50.31 | 0 | 0 | 0 | 0 | 63.44 | 0
2025-05-03 08:00 | 53.42 | 119.36 | 53.42 | 0 | 0 | 0 | 0 | 65.94 | 0
2025-05-03 09:00 | 55.4 | 121.35 | 55.4 | 0 | 0 | 0 | 0 | 65.95 | 0
2025-05-03 10:00 | 57.99 | 121.72 | 57.99 | 0 | 0 | 0 | 0 | 63.72 | 0
2025-05-03 11:00 | 61.47 | 51.45 | 51.45 | 10.02 | 0 | 0 | 0 | 0 | 0
2025-05-03 12:00 | 62.28 | 46.45 | 46.45 | 15.83 | 0 | 0 | 0 | 0 | 0
2025-05-03 13:00 | 63.89 | 49.85 | 49.85 | 14.04 | 0 | 0 | 0 | 0 | 0
2025-05-03 14:00 | 65.02 | 52.21 | 52.21 | 12.8 | 0 | 0 | 0 | 0 | 0
2025-05-03 15:00 | 64.51 | 59.55 | 59.55 | 4.96 | 0 | 0 | 0 | 0 | 0
2025-05-03 16:00 | 64.44 | 50.54 | 50.54 | 13.91 | 0 | 0 | 0 | 0 | 0
2025-05-03 17:00 | 63.39 | 27.13 | 27.13 | 36.26 | 0 | 0 | 0 | 0 | 0
2025-05-03 18:00 | 62.35 | 10.43 | 10.43 | 51.92 | 0 | 0 | 0 | 0 | 0
2025-05-03 19:00 | 59.84 | 0 | 0 | 59.84 | 0 | 0 | 0 | 0 | 0
2025-05-03 20:00 | 57.58 | 0 | 0 | 57.58 | 0 | 0 | 0 | 0 | 0
2025-05-03 21:00 | 55.48 | 0 | 0 | 55.48 | 0 | 0 | 0 | 0 | 0
2025-05-03 22:00 | 52.82 | 0 | 0 | 52.82 | 0 | 0 | 0 | 0 | 0
2025-05-03 23:00 | 49.95 | 0 | 0 | 49.95 | 0 | 0 | 0 | 0 | 0
2025-05-04 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0 | 0 | 0
2025-05-04 01:00 | 47.23 | 0 | 0 | 47.23 | 0 | 0 | 0 | 0 | 0
2025-05-04 02:00 | 46.07 | 0 | 0 | 46.07 | 0 | 0 | 0 | 0 | 0
2025-05-04 03:00 | 44.55 | 0 | 0 | 44.55 | 0 | 0 | 0 | 0 | 0
2025-05-04 04:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 0 | 0 | 0
2025-05-04 05:00 | 46.75 | 3.76 | 3.76 | 42.99 | 0 | 0 | 0 | 0 | 0
2025-05-04 06:00 | 48.66 | 65.58 | 48.66 | 0 | 0 | 0 | 0 | 16.92 | 0
2025-05-04 07:00 | 50.91 | 83.25 | 50.91 | 0 | 0 | 0 | 0 | 32.34 | 0
2025-05-04 08:00 | 53.27 | 88.89 | 53.27 | 0 | 0 | 0 | 0 | 35.62 | 0
2025-05-04 09:00 | 56.43 | 99.04 | 56.43 | 0 | 0 | 0 | 0 | 42.61 | 0
2025-05-04 10:00 | 59.35 | 108.22 | 59.35 | 0 | 0 | 0 | 0 | 48.87 | 0
2025-05-04 11:00 | 62.08 | 106.64 | 62.08 | 0 | 0 | 0 | 0 | 44.57 | 0
2025-05-04 12:00 | 65.05 | 103.03 | 65.05 | 0 | 0 | 0 | 0 | 37.97 | 0
2025-05-04 13:00 | 67.39 | 103.76 | 67.39 | 0 | 0 | 0 | 0 | 36.37 | 0
2025-05-04 14:00 | 68.77 | 103.5 | 68.77 | 0 | 0 | 0 | 0 | 34.73 | 0
2025-05-04 15:00 | 68.33 | 105.2 | 68.33 | 0 | 0 | 0 | 0 | 36.87 | 0
2025-05-04 16:00 | 68.59 | 104.09 | 68.59 | 0 | 0 | 0 | 0 | 35.5 | 0
2025-05-04 17:00 | 67.41 | 67.57 | 67.41 | 0 | 0 | 0 | 0 | 0.17 | 0
2025-05-04 18:00 | 65.04 | 27.76 | 27.76 | 37.28 | 0 | 0 | 0 | 0 | 0
2025-05-04 19:00 | 62.29 | 0.08 | 0.08 | 62.21 | 0 | 0 | 0 | 0 | 0
2025-05-04 20:00 | 59.56 | 0 | 0 | 59.56 | 0 | 0 | 0 | 0 | 0
2025-05-04 21:00 | 55.6 | 0 | 0 | 55.6 | 0 | 0 | 0 | 0 | 0
2025-05-04 22:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0 | 0 | 0
2025-05-04 23:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0 | 0 | 0
2025-05-05 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 0 | 0 | 0
2025-05-05 01:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 0 | 0 | 0
2025-05-05 02:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 0 | 0 | 0
2025-05-05 03:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 0 | 0 | 0
2025-05-05 04:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 0 | 0 | 0
2025-05-05 05:00 | 46.92 | 8.83 | 8.83 | 38.09 | 0 | 0 | 0 | 0 | 0
2025-05-05 06:00 | 48.48 | 86.85 | 48.48 | 0 | 0 | 0 | 0 | 38.37 | 0
2025-05-05 07:00 | 50.79 | 124.72 | 50.79 | 0 | 0 | 0 | 0 | 73.93 | 0
2025-05-05 08:00 | 52.62 | 134.3 | 52.62 | 0 | 0 | 0 | 0 | 81.69 | 0
2025-05-05 09:00 | 55.95 | 135.94 | 55.95 | 0 | 0 | 0 | 0 | 80 | 0
2025-05-05 10:00 | 59.06 | 132.78 | 59.06 | 0 | 0 | 0 | 0 | 73.72 | 0
2025-05-05 11:00 | 62.09 | 77.95 | 62.09 | 0 | 0 | 0 | 0 | 15.86 | 0
2025-05-05 12:00 | 63.77 | 68.64 | 63.77 | 0 | 0 | 0 | 0 | 4.87 | 0
2025-05-05 13:00 | 65.95 | 46.54 | 46.54 | 19.41 | 0 | 0 | 0 | 0 | 0
2025-05-05 14:00 | 66.02 | 42.22 | 42.22 | 23.8 | 0 | 0 | 0 | 0 | 0
2025-05-05 15:00 | 67.49 | 46.39 | 46.39 | 21.1 | 0 | 0 | 0 | 0 | 0
2025-05-05 16:00 | 67.11 | 36.35 | 36.35 | 30.76 | 0 | 0 | 0 | 0 | 0
2025-05-05 17:00 | 65.61 | 21.21 | 21.21 | 44.4 | 0 | 0 | 0 | 0 | 0
2025-05-05 18:00 | 64.25 | 0.11 | 0.11 | 64.14 | 0 | 0 | 0 | 0 | 0
2025-05-05 19:00 | 61.65 | 0 | 0 | 61.65 | 0 | 0 | 0 | 0 | 0
2025-05-05 20:00 | 57.72 | 0 | 0 | 57.72 | 0 | 0 | 0 | 0 | 0
2025-05-05 21:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 0 | 0 | 0
2025-05-05 22:00 | 52.61 | 0 | 0 | 52.61 | 0 | 0 | 0 | 0 | 0
2025-05-05 23:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 0 | 0 | 0
2025-05-06 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 0 | 0 | 0
2025-05-06 01:00 | 46.94 | 0 | 0 | 46.94 | 0 | 0 | 0 | 0 | 0
2025-05-06 02:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 0 | 0 | 0
2025-05-06 03:00 | 45.76 | 0 | 0 | 45.76 | 0 | 0 | 0 | 0 | 0
2025-05-06 04:00 | 46.01 | 0 | 0 | 46.01 | 0 | 0 | 0 | 0 | 0
2025-05-06 05:00 | 46.8 | 4.93 | 4.93 | 41.87 | 0 | 0 | 0 | 0 | 0
2025-05-06 06:00 | 47.74 | 65.33 | 47.74 | 0 | 0 | 0 | 0 | 17.59 | 0
2025-05-06 07:00 | 49.85 | 99.88 | 49.85 | 0 | 0 | 0 | 0 | 50.03 | 0
2025-05-06 08:00 | 52.75 | 112.09 | 52.75 | 0 | 0 | 0 | 0 | 59.34 | 0
2025-05-06 09:00 | 55.71 | 113.12 | 55.71 | 0 | 0 | 0 | 0 | 57.41 | 0
2025-05-06 10:00 | 58.13 | 112.01 | 58.13 | 0 | 0 | 0 | 0 | 53.87 | 0
2025-05-06 11:00 | 61.32 | 109.31 | 61.32 | 0 | 0 | 0 | 0 | 47.99 | 0
2025-05-06 12:00 | 63.1 | 108.34 | 63.1 | 0 | 0 | 0 | 0 | 45.24 | 0
2025-05-06 13:00 | 64.5 | 107.74 | 64.5 | 0 | 0 | 0 | 0 | 43.24 | 0
2025-05-06 14:00 | 65.94 | 108.46 | 65.94 | 0 | 0 | 0 | 0 | 42.52 | 0
2025-05-06 15:00 | 66.57 | 103.78 | 66.57 | 0 | 0 | 0 | 0 | 37.22 | 0
2025-05-06 16:00 | 66.24 | 93.92 | 66.24 | 0 | 0 | 0 | 0 | 27.68 | 0
2025-05-06 17:00 | 65.92 | 76.57 | 65.92 | 0 | 0 | 0 | 0 | 10.66 | 0
2025-05-06 18:00 | 62.91 | 35.38 | 35.38 | 27.53 | 0 | 0 | 0 | 0 | 0
2025-05-06 19:00 | 60.97 | 0.3 | 0.3 | 60.67 | 0 | 0 | 0 | 0 | 0
2025-05-06 20:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 0 | 0 | 0
2025-05-06 21:00 | 55.71 | 0 | 0 | 55.71 | 0 | 0 | 0 | 0 | 0
2025-05-06 22:00 | 52.79 | 0 | 0 | 52.79 | 0 | 0 | 0 | 0 | 0
2025-05-06 23:00 | 49.81 | 0 | 0 | 49.81 | 0 | 0 | 0 | 0 | 0
2025-05-07 | 48.49 | 0 | 0 | 48.49 | 0 | 0 | 0 | 0 | 0
2025-05-07 01:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 0 | 0 | 0
2025-05-07 02:00 | 45.21 | 0 | 0 | 45.21 | 0 | 0 | 0 | 0 | 0
2025-05-07 03:00 | 45.34 | 0 | 0 | 45.34 | 0 | 0 | 0 | 0 | 0
2025-05-07 04:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 0 | 0 | 0
2025-05-07 05:00 | 47.38 | 0.49 | 0.49 | 46.89 | 0 | 0 | 0 | 0 | 0
2025-05-07 06:00 | 49.04 | 12.37 | 12.37 | 36.67 | 0 | 0 | 0 | 0 | 0
2025-05-07 07:00 | 50.55 | 31.61 | 31.61 | 18.94 | 0 | 0 | 0 | 0 | 0
2025-05-07 08:00 | 53.65 | 50.42 | 50.42 | 3.22 | 0 | 0 | 0 | 0 | 0
2025-05-07 09:00 | 55.99 | 54.23 | 54.23 | 1.76 | 0 | 0 | 0 | 0 | 0
2025-05-07 10:00 | 59.99 | 44.31 | 44.31 | 15.68 | 0 | 0 | 0 | 0 | 0
2025-05-07 11:00 | 63.69 | 29.25 | 29.25 | 34.44 | 0 | 0 | 0 | 0 | 0
2025-05-07 12:00 | 66.82 | 33.43 | 33.43 | 33.38 | 0 | 0 | 0 | 0 | 0
2025-05-07 13:00 | 68.36 | 28.17 | 28.17 | 40.19 | 0 | 0 | 0 | 0 | 0
2025-05-07 14:00 | 70.72 | 12.91 | 12.91 | 57.82 | 0 | 0 | 0 | 0 | 0
2025-05-07 15:00 | 69.95 | 11.82 | 11.82 | 58.14 | 0 | 0 | 0 | 0 | 0
2025-05-07 16:00 | 69.57 | 16.55 | 16.55 | 53.03 | 0 | 0 | 0 | 0 | 0
2025-05-07 17:00 | 69.07 | 8.19 | 8.19 | 60.88 | 0 | 0 | 0 | 0 | 0
2025-05-07 18:00 | 67.24 | 2.2 | 2.2 | 65.04 | 0 | 0 | 0 | 0 | 0
2025-05-07 19:00 | 63.74 | 0 | 0 | 63.74 | 0 | 0 | 0 | 0 | 0
2025-05-07 20:00 | 60.22 | 0 | 0 | 60.22 | 0 | 0 | 0 | 0 | 0
2025-05-07 21:00 | 55.82 | 0 | 0 | 55.82 | 0 | 0 | 0 | 0 | 0
2025-05-07 22:00 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 0 | 0 | 0
2025-05-07 23:00 | 51.07 | 0 | 0 | 51.07 | 0 | 0 | 0 | 0 | 0
2025-05-08 | 48.51 | 0 | 0 | 48.51 | 0 | 0 | 0 | 0 | 0
2025-05-08 01:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 0 | 0 | 0
2025-05-08 02:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 0 | 0 | 0
2025-05-08 03:00 | 45.92 | 0 | 0 | 45.92 | 0 | 0 | 0 | 0 | 0
2025-05-08 04:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 0 | 0 | 0
2025-05-08 05:00 | 47.25 | 0.17 | 0.17 | 47.08 | 0 | 0 | 0 | 0 | 0
2025-05-08 06:00 | 49.31 | 3.97 | 3.97 | 45.34 | 0 | 0 | 0 | 0 | 0
2025-05-08 07:00 | 50.59 | 11.5 | 11.5 | 39.09 | 0 | 0 | 0 | 0 | 0
2025-05-08 08:00 | 52.61 | 17.42 | 17.42 | 35.19 | 0 | 0 | 0 | 0 | 0
2025-05-08 09:00 | 55.3 | 18.51 | 18.51 | 36.79 | 0 | 0 | 0 | 0 | 0
2025-05-08 10:00 | 56.24 | 36.22 | 36.22 | 20.02 | 0 | 0 | 0 | 0 | 0
2025-05-08 11:00 | 59.83 | 26.55 | 26.55 | 33.28 | 0 | 0 | 0 | 0 | 0
2025-05-08 12:00 | 59.97 | 29.16 | 29.16 | 30.81 | 0 | 0 | 0 | 0 | 0
2025-05-08 13:00 | 60.95 | 23.11 | 23.11 | 37.84 | 0 | 0 | 0 | 0 | 0
2025-05-08 14:00 | 61.61 | 43.06 | 43.06 | 18.55 | 0 | 0 | 0 | 0 | 0
2025-05-08 15:00 | 62.48 | 43.45 | 43.45 | 19.04 | 0 | 0 | 0 | 0 | 0
2025-05-08 16:00 | 61.74 | 42.22 | 42.22 | 19.53 | 0 | 0 | 0 | 0 | 0
2025-05-08 17:00 | 59.96 | 24.57 | 24.57 | 35.39 | 0 | 0 | 0 | 0 | 0
2025-05-08 18:00 | 60.48 | 5.43 | 5.43 | 55.05 | 0 | 0 | 0 | 0 | 0
2025-05-08 19:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 0 | 0 | 0
2025-05-08 20:00 | 56.78 | 0 | 0 | 56.78 | 0 | 0 | 0 | 0 | 0
2025-05-08 21:00 | 54.13 | 0 | 0 | 54.13 | 0 | 0 | 0 | 0 | 0
2025-05-08 22:00 | 52.93 | 0 | 0 | 52.93 | 0 | 0 | 0 | 0 | 0
2025-05-08 23:00 | 50.26 | 0 | 0 | 50.26 | 0 | 0 | 0 | 0 | 0
2025-05-09 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0 | 0 | 0
2025-05-09 01:00 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 0 | 0 | 0
2025-05-09 02:00 | 47.29 | 0 | 0 | 47.29 | 0 | 0 | 0 | 0 | 0
2025-05-09 03:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 0 | 0 | 0
2025-05-09 04:00 | 46.35 | 0 | 0 | 46.35 | 0 | 0 | 0 | 0 | 0
2025-05-09 05:00 | 47.36 | 0.46 | 0.46 | 46.9 | 0 | 0 | 0 | 0 | 0
2025-05-09 06:00 | 48.7 | 1.71 | 1.71 | 46.99 | 0 | 0 | 0 | 0 | 0
2025-05-09 07:00 | 51.43 | 7.43 | 7.43 | 44 | 0 | 0 | 0 | 0 | 0
2025-05-09 08:00 | 52.97 | 31.22 | 31.22 | 21.74 | 0 | 0 | 0 | 0 | 0
2025-05-09 09:00 | 55.26 | 44.82 | 44.82 | 10.44 | 0 | 0 | 0 | 0 | 0
2025-05-09 10:00 | 58.23 | 52.75 | 52.75 | 5.48 | 0 | 0 | 0 | 0 | 0
2025-05-09 11:00 | 59.51 | 62.79 | 59.51 | 0 | 0 | 0 | 0 | 3.27 | 0
2025-05-09 12:00 | 61.46 | 47.49 | 47.49 | 13.97 | 0 | 0 | 0 | 0 | 0
2025-05-09 13:00 | 61.96 | 41.94 | 41.94 | 20.03 | 0 | 0 | 0 | 0 | 0
2025-05-09 14:00 | 63.89 | 30.57 | 30.57 | 33.32 | 0 | 0 | 0 | 0 | 0
2025-05-09 15:00 | 64.77 | 21.13 | 21.13 | 43.64 | 0 | 0 | 0 | 0 | 0
2025-05-09 16:00 | 63.9 | 3.18 | 3.18 | 60.72 | 0 | 0 | 0 | 0 | 0
2025-05-09 17:00 | 63.48 | 4.8 | 4.8 | 58.69 | 0 | 0 | 0 | 0 | 0
2025-05-09 18:00 | 61.06 | 2.81 | 2.81 | 58.25 | 0 | 0 | 0 | 0 | 0
2025-05-09 19:00 | 59.9 | 0 | 0 | 59.9 | 0 | 0 | 0 | 0 | 0
2025-05-09 20:00 | 57.27 | 0 | 0 | 57.27 | 0 | 0 | 0 | 0 | 0
2025-05-09 21:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 0 | 0 | 0
2025-05-09 22:00 | 53.52 | 0 | 0 | 53.52 | 0 | 0 | 0 | 0 | 0
2025-05-09 23:00 | 50.93 | 0 | 0 | 50.93 | 0 | 0 | 0 | 0 | 0
2025-05-10 | 48.31 | 0 | 0 | 48.31 | 0 | 0 | 0 | 0 | 0
2025-05-10 01:00 | 46.8 | 0 | 0 | 46.8 | 0 | 0 | 0 | 0 | 0
2025-05-10 02:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 0 | 0 | 0
2025-05-10 03:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 0 | 0 | 0
2025-05-10 04:00 | 47.49 | 0 | 0 | 47.49 | 0 | 0 | 0 | 0 | 0
2025-05-10 05:00 | 48.14 | 2.42 | 2.42 | 45.72 | 0 | 0 | 0 | 0 | 0
2025-05-10 06:00 | 48.07 | 68.65 | 48.07 | 0 | 0 | 0 | 0 | 20.59 | 0
2025-05-10 07:00 | 51.69 | 101.92 | 51.69 | 0 | 0 | 0 | 0 | 50.23 | 0
2025-05-10 08:00 | 53.64 | 104.06 | 53.64 | 0 | 0 | 0 | 0 | 50.41 | 0
2025-05-10 09:00 | 54.65 | 112.35 | 54.65 | 0 | 0 | 0 | 0 | 57.7 | 0
2025-05-10 10:00 | 57.4 | 121.88 | 57.4 | 0 | 0 | 0 | 0 | 64.47 | 0
2025-05-10 11:00 | 59.99 | 90.73 | 59.99 | 0 | 0 | 0 | 0 | 30.74 | 0
2025-05-10 12:00 | 61.26 | 91.74 | 61.26 | 0 | 0 | 0 | 0 | 30.48 | 0
2025-05-10 13:00 | 61.46 | 45.75 | 45.75 | 15.71 | 0 | 0 | 0 | 0 | 0
2025-05-10 14:00 | 63.11 | 28.27 | 28.27 | 34.84 | 0 | 0 | 0 | 0 | 0
2025-05-10 15:00 | 61.97 | 5.1 | 5.1 | 56.87 | 0 | 0 | 0 | 0 | 0
2025-05-10 16:00 | 62.69 | 21.06 | 21.06 | 41.63 | 0 | 0 | 0 | 0 | 0
2025-05-10 17:00 | 62.68 | 12.62 | 12.62 | 50.06 | 0 | 0 | 0 | 0 | 0
2025-05-10 18:00 | 60.99 | 6.42 | 6.42 | 54.57 | 0 | 0 | 0 | 0 | 0
2025-05-10 19:00 | 59.19 | 0 | 0 | 59.19 | 0 | 0 | 0 | 0 | 0
2025-05-10 20:00 | 58 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0
2025-05-10 21:00 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 0 | 0 | 0
2025-05-10 22:00 | 53.83 | 0 | 0 | 53.83 | 0 | 0 | 0 | 0 | 0
2025-05-10 23:00 | 51.42 | 0 | 0 | 51.42 | 0 | 0 | 0 | 0 | 0
2025-05-11 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0 | 0 | 0
2025-05-11 01:00 | 47.97 | 0 | 0 | 47.97 | 0 | 0 | 0 | 0 | 0
2025-05-11 02:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 0 | 0 | 0
2025-05-11 03:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 0 | 0 | 0
2025-05-11 04:00 | 46.47 | 0 | 0 | 46.47 | 0 | 0 | 0 | 0 | 0
2025-05-11 05:00 | 47 | 4.27 | 4.27 | 42.73 | 0 | 0 | 0 | 0 | 0
2025-05-11 06:00 | 48.73 | 50.51 | 48.73 | 0 | 0 | 0 | 0 | 1.78 | 0
2025-05-11 07:00 | 51.13 | 49.13 | 49.13 | 2 | 0 | 0 | 0 | 0 | 0
2025-05-11 08:00 | 53.75 | 63.3 | 53.75 | 0 | 0 | 0 | 0 | 9.54 | 0
2025-05-11 09:00 | 56.84 | 96.07 | 56.84 | 0 | 0 | 0 | 0 | 39.23 | 0
2025-05-11 10:00 | 58.54 | 91.37 | 58.54 | 0 | 0 | 0 | 0 | 32.83 | 0
2025-05-11 11:00 | 61.3 | 95.43 | 61.3 | 0 | 0 | 0 | 0 | 34.13 | 0
2025-05-11 12:00 | 63.22 | 86.43 | 63.22 | 0 | 0 | 0 | 0 | 23.21 | 0
2025-05-11 13:00 | 63.99 | 73.42 | 63.99 | 0 | 0 | 0 | 0 | 9.43 | 0
2025-05-11 14:00 | 65.29 | 99.07 | 65.29 | 0 | 0 | 0 | 0 | 33.78 | 0
2025-05-11 15:00 | 65.17 | 110.83 | 65.17 | 0 | 0 | 0 | 0 | 45.66 | 0
2025-05-11 16:00 | 65.65 | 105.94 | 65.65 | 0 | 0 | 0 | 0 | 40.29 | 0
2025-05-11 17:00 | 64.42 | 100.78 | 64.42 | 0 | 0 | 0 | 0 | 36.36 | 0
2025-05-11 18:00 | 62.08 | 58.68 | 58.68 | 3.4 | 0 | 0 | 0 | 0 | 0
2025-05-11 19:00 | 60.88 | 1.62 | 1.62 | 59.26 | 0 | 0 | 0 | 0 | 0
2025-05-11 20:00 | 59.39 | 0 | 0 | 59.39 | 0 | 0 | 0 | 0 | 0
2025-05-11 21:00 | 56.03 | 0 | 0 | 56.03 | 0 | 0 | 0 | 0 | 0
2025-05-11 22:00 | 53.86 | 0 | 0 | 53.86 | 0 | 0 | 0 | 0 | 0
2025-05-11 23:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 0 | 0 | 0
2025-05-12 | 48.76 | 0 | 0 | 48.76 | 0 | 0 | 0 | 0 | 0
2025-05-12 01:00 | 47.98 | 0 | 0 | 47.98 | 0 | 0 | 0 | 0 | 0
2025-05-12 02:00 | 46.02 | 0 | 0 | 46.02 | 0 | 0 | 0 | 0 | 0
2025-05-12 03:00 | 46.05 | 0 | 0 | 46.05 | 0 | 0 | 0 | 0 | 0
2025-05-12 04:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 0 | 0 | 0
2025-05-12 05:00 | 47.9 | 10.28 | 10.28 | 37.62 | 0 | 0 | 0 | 0 | 0
2025-05-12 06:00 | 49.13 | 78.62 | 49.13 | 0 | 0 | 0 | 0 | 29.5 | 0
2025-05-12 07:00 | 51.43 | 102.71 | 51.43 | 0 | 0 | 0 | 0 | 51.28 | 0
2025-05-12 08:00 | 53.29 | 116.09 | 53.29 | 0 | 0 | 0 | 0 | 62.8 | 0
2025-05-12 09:00 | 55.42 | 120.08 | 55.42 | 0 | 0 | 0 | 0 | 64.65 | 0
2025-05-12 10:00 | 57.67 | 117.34 | 57.67 | 0 | 0 | 0 | 0 | 59.67 | 0
2025-05-12 11:00 | 58.62 | 115.37 | 58.62 | 0 | 0 | 0 | 0 | 56.75 | 0
2025-05-12 12:00 | 60.29 | 113.03 | 60.29 | 0 | 0 | 0 | 0 | 52.74 | 0
2025-05-12 13:00 | 61.03 | 114.58 | 61.03 | 0 | 0 | 0 | 0 | 53.55 | 0
2025-05-12 14:00 | 60.94 | 115.3 | 60.94 | 0 | 0 | 0 | 0 | 54.36 | 0
2025-05-12 15:00 | 61.45 | 111.32 | 61.45 | 0 | 0 | 0 | 0 | 49.87 | 0
2025-05-12 16:00 | 62.51 | 105.9 | 62.51 | 0 | 0 | 0 | 0 | 43.39 | 0
2025-05-12 17:00 | 61.38 | 91.54 | 61.38 | 0 | 0 | 0 | 0 | 30.16 | 0
2025-05-12 18:00 | 59.61 | 48.47 | 48.47 | 11.14 | 0 | 0 | 0 | 0 | 0
2025-05-12 19:00 | 58.21 | 1.11 | 1.11 | 57.1 | 0 | 0 | 0 | 0 | 0
2025-05-12 20:00 | 57.29 | 0 | 0 | 57.29 | 0 | 0 | 0 | 0 | 0
2025-05-12 21:00 | 56.2 | 0 | 0 | 56.2 | 0 | 0 | 0 | 0 | 0
2025-05-12 22:00 | 53.22 | 0 | 0 | 53.22 | 0 | 0 | 0 | 0 | 0
2025-05-12 23:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 0 | 0 | 0
2025-05-13 | 49.76 | 0 | 0 | 49.76 | 0 | 0 | 0 | 0 | 0
2025-05-13 01:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 0 | 0 | 0
2025-05-13 02:00 | 46.17 | 0 | 0 | 46.17 | 0 | 0 | 0 | 0 | 0
2025-05-13 03:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 0 | 0 | 0
2025-05-13 04:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 0 | 0 | 0
2025-05-13 05:00 | 48.32 | 10.33 | 10.33 | 38 | 0 | 0 | 0 | 0 | 0
2025-05-13 06:00 | 49.18 | 67.57 | 49.18 | 0 | 0 | 0 | 0 | 18.39 | 0
2025-05-13 07:00 | 51.93 | 94.3 | 51.93 | 0 | 0 | 0 | 0 | 42.36 | 0
2025-05-13 08:00 | 54.71 | 109.3 | 54.71 | 0 | 0 | 0 | 0 | 54.58 | 0
2025-05-13 09:00 | 57.43 | 114.62 | 57.43 | 0 | 0 | 0 | 0 | 57.19 | 0
2025-05-13 10:00 | 60.75 | 113.63 | 60.75 | 0 | 0 | 0 | 0 | 52.88 | 0
2025-05-13 11:00 | 63.33 | 110.24 | 63.33 | 0 | 0 | 0 | 0 | 46.91 | 0
2025-05-13 12:00 | 65.69 | 108.44 | 65.69 | 0 | 0 | 0 | 0 | 42.74 | 0
2025-05-13 13:00 | 68.81 | 108.74 | 68.81 | 0 | 0 | 0 | 0 | 39.92 | 0
2025-05-13 14:00 | 69.8 | 110.24 | 69.8 | 0 | 0 | 0 | 0 | 40.43 | 0
2025-05-13 15:00 | 69.34 | 107.89 | 69.34 | 0 | 0 | 0 | 0 | 38.55 | 0
2025-05-13 16:00 | 69.56 | 93.92 | 69.56 | 0 | 0 | 0 | 0 | 24.35 | 0
2025-05-13 17:00 | 67.64 | 76.83 | 67.64 | 0 | 0 | 0 | 0 | 9.19 | 0
2025-05-13 18:00 | 65.42 | 43.16 | 43.16 | 22.26 | 0 | 0 | 0 | 0 | 0
2025-05-13 19:00 | 63.98 | 1.18 | 1.18 | 62.8 | 0 | 0 | 0 | 0 | 0
2025-05-13 20:00 | 59.7 | 0 | 0 | 59.7 | 0 | 0 | 0 | 0 | 0
2025-05-13 21:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 0 | 0 | 0
2025-05-13 22:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 0 | 0 | 0
2025-05-13 23:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 0 | 0 | 0
2025-05-14 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 0 | 0 | 0
2025-05-14 01:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 0 | 0 | 0
2025-05-14 02:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 0 | 0 | 0
2025-05-14 03:00 | 46.97 | 0 | 0 | 46.97 | 0 | 0 | 0 | 0 | 0
2025-05-14 04:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 0 | 0 | 0
2025-05-14 05:00 | 47.38 | 12.95 | 12.95 | 34.43 | 0 | 0 | 0 | 0 | 0
2025-05-14 06:00 | 49.58 | 78.6 | 49.58 | 0 | 0 | 0 | 0 | 29.02 | 0
2025-05-14 07:00 | 52.5 | 99.04 | 52.5 | 0 | 0 | 0 | 0 | 46.54 | 0
2025-05-14 08:00 | 55.12 | 9.92 | 9.92 | 45.2 | 0 | 0 | 0 | 0 | 0
2025-05-14 09:00 | 57.27 | 29.56 | 29.56 | 27.71 | 0 | 0 | 0 | 0 | 0
2025-05-14 10:00 | 58.91 | 91.47 | 58.91 | 0 | 0 | 0 | 0 | 32.56 | 0
2025-05-14 11:00 | 62.15 | 117.51 | 62.15 | 0 | 0 | 0 | 0 | 55.36 | 0
2025-05-14 12:00 | 64.36 | 122.97 | 64.36 | 0 | 0 | 0 | 0 | 58.6 | 0
2025-05-14 13:00 | 65.85 | 100.71 | 65.85 | 0 | 0 | 0 | 0 | 34.86 | 0
2025-05-14 14:00 | 66.85 | 84.33 | 66.85 | 0 | 0 | 0 | 0 | 17.48 | 0
2025-05-14 15:00 | 66.97 | 96.84 | 66.97 | 0 | 0 | 0 | 0 | 29.87 | 0
2025-05-14 16:00 | 66.42 | 40.14 | 40.14 | 26.28 | 0 | 0 | 0 | 0 | 0
2025-05-14 17:00 | 65.19 | 11.13 | 11.13 | 54.06 | 0 | 0 | 0 | 0 | 0
2025-05-14 18:00 | 62.99 | 0 | 0 | 62.99 | 0 | 0 | 0 | 0 | 0
2025-05-14 19:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 0 | 0 | 0
2025-05-14 20:00 | 59.6 | 0 | 0 | 59.6 | 0 | 0 | 0 | 0 | 0
2025-05-14 21:00 | 57.19 | 0 | 0 | 57.19 | 0 | 0 | 0 | 0 | 0
2025-05-14 22:00 | 53.61 | 0 | 0 | 53.61 | 0 | 0 | 0 | 0 | 0
2025-05-14 23:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 0 | 0 | 0
2025-05-15 | 50.74 | 0 | 0 | 50.74 | 0 | 0 | 0 | 0 | 0
2025-05-15 01:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0 | 0 | 0
2025-05-15 02:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 0 | 0 | 0
2025-05-15 03:00 | 46.88 | 0 | 0 | 46.88 | 0 | 0 | 0 | 0 | 0
2025-05-15 04:00 | 48.1 | 0 | 0 | 48.1 | 0 | 0 | 0 | 0 | 0
2025-05-15 05:00 | 47.61 | 11.78 | 11.78 | 35.83 | 0 | 0 | 0 | 0 | 0
2025-05-15 06:00 | 49.81 | 67.46 | 49.81 | 0 | 0 | 0 | 0 | 17.65 | 0
2025-05-15 07:00 | 51.28 | 93.85 | 51.28 | 0 | 0 | 0 | 0 | 42.57 | 0
2025-05-15 08:00 | 53.54 | 109.56 | 53.54 | 0 | 0 | 0 | 0 | 56.02 | 0
2025-05-15 09:00 | 55.9 | 113.37 | 55.9 | 0 | 0 | 0 | 0 | 57.47 | 0
2025-05-15 10:00 | 58.52 | 114.44 | 58.52 | 0 | 0 | 0 | 0 | 55.91 | 0
2025-05-15 11:00 | 60.37 | 113.44 | 60.37 | 0 | 0 | 0 | 0 | 53.07 | 0
2025-05-15 12:00 | 60.96 | 112.81 | 60.96 | 0 | 0 | 0 | 0 | 51.85 | 0
2025-05-15 13:00 | 61.43 | 112.11 | 61.43 | 0 | 0 | 0 | 0 | 50.68 | 0
2025-05-15 14:00 | 63.39 | 109.64 | 63.39 | 0 | 0 | 0 | 0 | 46.24 | 0
2025-05-15 15:00 | 62.1 | 105.09 | 62.1 | 0 | 0 | 0 | 0 | 42.99 | 0
2025-05-15 16:00 | 61.86 | 92.54 | 61.86 | 0 | 0 | 0 | 0 | 30.68 | 0
2025-05-15 17:00 | 60.74 | 80.82 | 60.74 | 0 | 0 | 0 | 0 | 20.08 | 0
2025-05-15 18:00 | 61.43 | 44.28 | 44.28 | 17.16 | 0 | 0 | 0 | 0 | 0
2025-05-15 19:00 | 59.96 | 1.72 | 1.72 | 58.23 | 0 | 0 | 0 | 0 | 0
2025-05-15 20:00 | 59.06 | 0 | 0 | 59.06 | 0 | 0 | 0 | 0 | 0
2025-05-15 21:00 | 55.23 | 0 | 0 | 55.23 | 0 | 0 | 0 | 0 | 0
2025-05-15 22:00 | 54.54 | 0 | 0 | 54.54 | 0 | 0 | 0 | 0 | 0
2025-05-15 23:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0 | 0 | 0
2025-05-16 | 50.3 | 0 | 0 | 50.3 | 0 | 0 | 0 | 0 | 0
2025-05-16 01:00 | 47.44 | 0 | 0 | 47.44 | 0 | 0 | 0 | 0 | 0
2025-05-16 02:00 | 47.95 | 0 | 0 | 47.95 | 0 | 0 | 0 | 0 | 0
2025-05-16 03:00 | 47.24 | 0 | 0 | 47.24 | 0 | 0 | 0 | 0 | 0
2025-05-16 04:00 | 47.19 | 0 | 0 | 47.19 | 0 | 0 | 0 | 0 | 0
2025-05-16 05:00 | 48.59 | 13.94 | 13.94 | 34.65 | 0 | 0 | 0 | 0 | 0
2025-05-16 06:00 | 49.51 | 73.42 | 49.51 | 0 | 0 | 0 | 0 | 23.91 | 0
2025-05-16 07:00 | 51.66 | 101.1 | 51.66 | 0 | 0 | 0 | 0 | 49.44 | 0
2025-05-16 08:00 | 54 | 98.29 | 54 | 0 | 0 | 0 | 0 | 44.28 | 0
2025-05-16 09:00 | 55.63 | 113.55 | 55.63 | 0 | 0 | 0 | 0 | 57.92 | 0
2025-05-16 10:00 | 59.19 | 109.66 | 59.19 | 0 | 0 | 0 | 0 | 50.47 | 0
2025-05-16 11:00 | 61.28 | 107.52 | 61.28 | 0 | 0 | 0 | 0 | 46.24 | 0
2025-05-16 12:00 | 61.9 | 106.83 | 61.9 | 0 | 0 | 0 | 0 | 44.93 | 0
2025-05-16 13:00 | 63.57 | 106.46 | 63.57 | 0 | 0 | 0 | 0 | 42.89 | 0
2025-05-16 14:00 | 63.95 | 105.6 | 63.95 | 0 | 0 | 0 | 0 | 41.65 | 0
2025-05-16 15:00 | 64.48 | 96.4 | 64.48 | 0 | 0 | 0 | 0 | 31.92 | 0
2025-05-16 16:00 | 63.77 | 80.12 | 63.77 | 0 | 0 | 0 | 0 | 16.34 | 0
2025-05-16 17:00 | 62.95 | 49.74 | 49.74 | 13.21 | 0 | 0 | 0 | 0 | 0
2025-05-16 18:00 | 62.77 | 28.88 | 28.88 | 33.9 | 0 | 0 | 0 | 0 | 0
2025-05-16 19:00 | 60.65 | 1.47 | 1.47 | 59.19 | 0 | 0 | 0 | 0 | 0
2025-05-16 20:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 0 | 0 | 0
2025-05-16 21:00 | 56.58 | 0 | 0 | 56.58 | 0 | 0 | 0 | 0 | 0
2025-05-16 22:00 | 53.77 | 0 | 0 | 53.77 | 0 | 0 | 0 | 0 | 0
2025-05-16 23:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 0 | 0 | 0
2025-05-17 | 50.47 | 0 | 0 | 50.47 | 0 | 0 | 0 | 0 | 0
2025-05-17 01:00 | 48.78 | 0 | 0 | 48.78 | 0 | 0 | 0 | 0 | 0
2025-05-17 02:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 0 | 0 | 0
2025-05-17 03:00 | 46.64 | 0 | 0 | 46.64 | 0 | 0 | 0 | 0 | 0
2025-05-17 04:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 0 | 0 | 0
2025-05-17 05:00 | 48.33 | 12.21 | 12.21 | 36.12 | 0 | 0 | 0 | 0 | 0
2025-05-17 06:00 | 49.51 | 52.04 | 49.51 | 0 | 0 | 0 | 0 | 2.53 | 0
2025-05-17 07:00 | 52.3 | 77.34 | 52.3 | 0 | 0 | 0 | 0 | 25.04 | 0
2025-05-17 08:00 | 55.79 | 89.68 | 55.79 | 0 | 0 | 0 | 0 | 33.89 | 0
2025-05-17 09:00 | 58.17 | 87.16 | 58.17 | 0 | 0 | 0 | 0 | 28.99 | 0
2025-05-17 10:00 | 60.34 | 89.8 | 60.34 | 0 | 0 | 0 | 0 | 29.46 | 0
2025-05-17 11:00 | 63.04 | 95 | 63.04 | 0 | 0 | 0 | 0 | 31.96 | 0
2025-05-17 12:00 | 67.08 | 103.07 | 67.08 | 0 | 0 | 0 | 0 | 35.98 | 0
2025-05-17 13:00 | 68.09 | 112.3 | 68.09 | 0 | 0 | 0 | 0 | 44.21 | 0
2025-05-17 14:00 | 69 | 113.89 | 69 | 0 | 0 | 0 | 0 | 44.89 | 0
2025-05-17 15:00 | 69.6 | 120.85 | 69.6 | 0 | 0 | 0 | 0 | 51.25 | 0
2025-05-17 16:00 | 68.59 | 112.29 | 68.59 | 0 | 0 | 0 | 0 | 43.7 | 0
2025-05-17 17:00 | 68.84 | 99.52 | 68.84 | 0 | 0 | 0 | 0 | 30.67 | 0
2025-05-17 18:00 | 66.05 | 61.6 | 61.6 | 4.45 | 0 | 0 | 0 | 0 | 0
2025-05-17 19:00 | 64.5 | 2.74 | 2.74 | 61.76 | 0 | 0 | 0 | 0 | 0
2025-05-17 20:00 | 61.04 | 0 | 0 | 61.04 | 0 | 0 | 0 | 0 | 0
2025-05-17 21:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 0 | 0 | 0
2025-05-17 22:00 | 55.25 | 0 | 0 | 55.25 | 0 | 0 | 0 | 0 | 0
2025-05-17 23:00 | 52.86 | 0 | 0 | 52.86 | 0 | 0 | 0 | 0 | 0
2025-05-18 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0 | 0 | 0
2025-05-18 01:00 | 48.87 | 0 | 0 | 48.87 | 0 | 0 | 0 | 0 | 0
2025-05-18 02:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0 | 0 | 0
2025-05-18 03:00 | 46.97 | 0 | 0 | 46.97 | 0 | 0 | 0 | 0 | 0
2025-05-18 04:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0 | 0 | 0
2025-05-18 05:00 | 48.1 | 17.08 | 17.08 | 31.02 | 0 | 0 | 0 | 0 | 0
2025-05-18 06:00 | 50.34 | 88.99 | 50.34 | 0 | 0 | 0 | 0 | 38.65 | 0
2025-05-18 07:00 | 52.73 | 115.02 | 52.73 | 0 | 0 | 0 | 0 | 62.29 | 0
2025-05-18 08:00 | 55.79 | 123.53 | 55.79 | 0 | 0 | 0 | 0 | 67.74 | 0
2025-05-18 09:00 | 58.55 | 125.64 | 58.55 | 0 | 0 | 0 | 0 | 67.09 | 0
2025-05-18 10:00 | 62.22 | 124.88 | 62.22 | 0 | 0 | 0 | 0 | 62.66 | 0
2025-05-18 11:00 | 65.14 | 123.2 | 65.14 | 0 | 0 | 0 | 0 | 58.06 | 0
2025-05-18 12:00 | 67.22 | 121.93 | 67.22 | 0 | 0 | 0 | 0 | 54.71 | 0
2025-05-18 13:00 | 70.21 | 123.68 | 70.21 | 0 | 0 | 0 | 0 | 53.47 | 0
2025-05-18 14:00 | 71.06 | 125.51 | 71.06 | 0 | 0 | 0 | 0 | 54.46 | 0
2025-05-18 15:00 | 71.22 | 124.72 | 71.22 | 0 | 0 | 0 | 0 | 53.5 | 0
2025-05-18 16:00 | 71.67 | 120.58 | 71.67 | 0 | 0 | 0 | 0 | 48.91 | 0
2025-05-18 17:00 | 70.45 | 106.53 | 70.45 | 0 | 0 | 0 | 0 | 36.08 | 0
2025-05-18 18:00 | 68.28 | 68.43 | 68.28 | 0 | 0 | 0 | 0 | 0.15 | 0
2025-05-18 19:00 | 65.51 | 2.63 | 2.63 | 62.87 | 0 | 0 | 0 | 0 | 0
2025-05-18 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 0 | 0 | 0
2025-05-18 21:00 | 58.09 | 0 | 0 | 58.09 | 0 | 0 | 0 | 0 | 0
2025-05-18 22:00 | 56.58 | 0 | 0 | 56.58 | 0 | 0 | 0 | 0 | 0
2025-05-18 23:00 | 52.2 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0
2025-05-19 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 0 | 0 | 0
2025-05-19 01:00 | 48.37 | 0 | 0 | 48.37 | 0 | 0 | 0 | 0 | 0
2025-05-19 02:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0 | 0 | 0
2025-05-19 03:00 | 46.89 | 0 | 0 | 46.89 | 0 | 0 | 0 | 0 | 0
2025-05-19 04:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 0 | 0 | 0
2025-05-19 05:00 | 48.78 | 16.09 | 16.09 | 32.69 | 0 | 0 | 0 | 0 | 0
2025-05-19 06:00 | 50.36 | 71.2 | 50.36 | 0 | 0 | 0 | 0 | 20.85 | 0
2025-05-19 07:00 | 52.65 | 91.5 | 52.65 | 0 | 0 | 0 | 0 | 38.85 | 0
2025-05-19 08:00 | 56.54 | 102.38 | 56.54 | 0 | 0 | 0 | 0 | 45.84 | 0
2025-05-19 09:00 | 59.51 | 111.27 | 59.51 | 0 | 0 | 0 | 0 | 51.76 | 0
2025-05-19 10:00 | 64.32 | 113.55 | 64.32 | 0 | 0 | 0 | 0 | 49.23 | 0
2025-05-19 11:00 | 69.37 | 110.24 | 69.37 | 0 | 0 | 0 | 0 | 40.87 | 0
2025-05-19 12:00 | 72.3 | 101.37 | 72.3 | 0 | 0 | 0 | 0 | 29.07 | 0
2025-05-19 13:00 | 74.84 | 101.02 | 74.84 | 0 | 0 | 0 | 0 | 26.18 | 0
2025-05-19 14:00 | 76.29 | 101.36 | 76.29 | 0 | 0 | 0 | 0 | 25.08 | 0
2025-05-19 15:00 | 76 | 98.12 | 76 | 0 | 0 | 0 | 0 | 22.12 | 0
2025-05-19 16:00 | 75.67 | 77.74 | 75.67 | 0 | 0 | 0 | 0 | 2.08 | 0
2025-05-19 17:00 | 75.12 | 63.85 | 63.85 | 11.28 | 0 | 0 | 0 | 0 | 0
2025-05-19 18:00 | 71.23 | 23.14 | 23.14 | 48.09 | 0 | 0 | 0 | 0 | 0
2025-05-19 19:00 | 67.7 | 1.84 | 1.84 | 65.86 | 0 | 0 | 0 | 0 | 0
2025-05-19 20:00 | 64.02 | 0 | 0 | 64.02 | 0 | 0 | 0 | 0 | 0
2025-05-19 21:00 | 59.59 | 0 | 0 | 59.59 | 0 | 0 | 0 | 0 | 0
2025-05-19 22:00 | 55.79 | 0 | 0 | 55.79 | 0 | 0 | 0 | 0 | 0
2025-05-19 23:00 | 53.15 | 0 | 0 | 53.15 | 0 | 0 | 0 | 0 | 0
2025-05-20 | 50.36 | 0 | 0 | 50.36 | 0 | 0 | 0 | 0 | 0
2025-05-20 01:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 0 | 0 | 0
2025-05-20 02:00 | 47.31 | 0 | 0 | 47.31 | 0 | 0 | 0 | 0 | 0
2025-05-20 03:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0 | 0 | 0
2025-05-20 04:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0 | 0 | 0
2025-05-20 05:00 | 48.77 | 20.83 | 20.83 | 27.93 | 0 | 0 | 0 | 0 | 0
2025-05-20 06:00 | 51.1 | 68.71 | 51.1 | 0 | 0 | 0 | 0 | 17.6 | 0
2025-05-20 07:00 | 53.49 | 103.75 | 53.49 | 0 | 0 | 0 | 0 | 50.26 | 0
2025-05-20 08:00 | 56.95 | 133.3 | 56.95 | 0 | 0 | 0 | 0 | 76.35 | 0
2025-05-20 09:00 | 61.48 | 92.86 | 61.48 | 0 | 0 | 0 | 0 | 31.37 | 0
2025-05-20 10:00 | 66.13 | 8.78 | 8.78 | 57.35 | 0 | 0 | 0 | 0 | 0
2025-05-20 11:00 | 70.31 | 20.68 | 20.68 | 49.62 | 0 | 0 | 0 | 0 | 0
2025-05-20 12:00 | 74.63 | 9.5 | 9.5 | 65.12 | 0 | 0 | 0 | 0 | 0
2025-05-20 13:00 | 77.59 | 22.58 | 22.58 | 55.01 | 0 | 0 | 0 | 0 | 0
2025-05-20 14:00 | 79.76 | 8.1 | 8.1 | 71.66 | 0 | 0 | 0 | 0 | 0
2025-05-20 15:00 | 81.34 | 87.11 | 81.34 | 0 | 0 | 0 | 0 | 5.77 | 0
2025-05-20 16:00 | 80.41 | 115.03 | 80.41 | 0 | 0 | 0 | 0 | 34.61 | 0
2025-05-20 17:00 | 78.21 | 29.54 | 29.54 | 48.67 | 0 | 0 | 0 | 0 | 0
2025-05-20 18:00 | 74.73 | 39.15 | 39.15 | 35.57 | 0 | 0 | 0 | 0 | 0
2025-05-20 19:00 | 70.4 | 0.71 | 0.71 | 69.69 | 0 | 0 | 0 | 0 | 0
2025-05-20 20:00 | 66.14 | 0 | 0 | 66.14 | 0 | 0 | 0 | 0 | 0
2025-05-20 21:00 | 61.72 | 0 | 0 | 61.72 | 0 | 0 | 0 | 0 | 0
2025-05-20 22:00 | 57.55 | 0 | 0 | 57.55 | 0 | 0 | 0 | 0 | 0
2025-05-20 23:00 | 53.51 | 0 | 0 | 53.51 | 0 | 0 | 0 | 0 | 0
2025-05-21 | 51.43 | 0 | 0 | 51.43 | 0 | 0 | 0 | 0 | 0
2025-05-21 01:00 | 49.05 | 0 | 0 | 49.05 | 0 | 0 | 0 | 0 | 0
2025-05-21 02:00 | 48.14 | 0 | 0 | 48.14 | 0 | 0 | 0 | 0 | 0
2025-05-21 03:00 | 47.58 | 0 | 0 | 47.58 | 0 | 0 | 0 | 0 | 0
2025-05-21 04:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0 | 0 | 0
2025-05-21 05:00 | 48.57 | 7.9 | 7.9 | 40.67 | 0 | 0 | 0 | 0 | 0
2025-05-21 06:00 | 51.08 | 43.37 | 43.37 | 7.72 | 0 | 0 | 0 | 0 | 0
2025-05-21 07:00 | 54.53 | 106.15 | 54.53 | 0 | 0 | 0 | 0 | 51.62 | 0
2025-05-21 08:00 | 55.72 | 100.1 | 55.72 | 0 | 0 | 0 | 0 | 44.37 | 0
2025-05-21 09:00 | 59.01 | 117.61 | 59.01 | 0 | 0 | 0 | 0 | 58.6 | 0
2025-05-21 10:00 | 61.87 | 104.91 | 61.87 | 0 | 0 | 0 | 0 | 43.04 | 0
2025-05-21 11:00 | 64.8 | 92.48 | 64.8 | 0 | 0 | 0 | 0 | 27.68 | 0
2025-05-21 12:00 | 68.4 | 76.43 | 68.4 | 0 | 0 | 0 | 0 | 8.04 | 0
2025-05-21 13:00 | 69.29 | 69.8 | 69.29 | 0 | 0 | 0 | 0 | 0.51 | 0
2025-05-21 14:00 | 70.66 | 64.83 | 64.83 | 5.82 | 0 | 0 | 0 | 0 | 0
2025-05-21 15:00 | 70.54 | 92.07 | 70.54 | 0 | 0 | 0 | 0 | 21.53 | 0
2025-05-21 16:00 | 70.52 | 100.47 | 70.52 | 0 | 0 | 0 | 0 | 29.95 | 0
2025-05-21 17:00 | 68.77 | 109.57 | 68.77 | 0 | 0 | 0 | 0 | 40.8 | 0
2025-05-21 18:00 | 67.94 | 70.44 | 67.94 | 0 | 0 | 0 | 0 | 2.5 | 0
2025-05-21 19:00 | 66.45 | 2.83 | 2.83 | 63.62 | 0 | 0 | 0 | 0 | 0
2025-05-21 20:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 0 | 0 | 0
2025-05-21 21:00 | 58.14 | 0 | 0 | 58.14 | 0 | 0 | 0 | 0 | 0
2025-05-21 22:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 0 | 0 | 0
2025-05-21 23:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 0 | 0 | 0
2025-05-22 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-05-22 01:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 0 | 0 | 0
2025-05-22 02:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0 | 0 | 0
2025-05-22 03:00 | 47.47 | 0 | 0 | 47.47 | 0 | 0 | 0 | 0 | 0
2025-05-22 04:00 | 48.32 | 0 | 0 | 48.32 | 0 | 0 | 0 | 0 | 0
2025-05-22 05:00 | 48.93 | 9.76 | 9.76 | 39.17 | 0 | 0 | 0 | 0 | 0
2025-05-22 06:00 | 50.5 | 56.87 | 50.5 | 0 | 0 | 0 | 0 | 6.36 | 0
2025-05-22 07:00 | 52.81 | 19.86 | 19.86 | 32.95 | 0 | 0 | 0 | 0 | 0
2025-05-22 08:00 | 54.67 | 54.59 | 54.59 | 0.08 | 0 | 0 | 0 | 0 | 0
2025-05-22 09:00 | 57.96 | 51.47 | 51.47 | 6.49 | 0 | 0 | 0 | 0 | 0
2025-05-22 10:00 | 59.18 | 105.04 | 59.18 | 0 | 0 | 0 | 0 | 45.86 | 0
2025-05-22 11:00 | 61.89 | 77.21 | 61.89 | 0 | 0 | 0 | 0 | 15.32 | 0
2025-05-22 12:00 | 64.15 | 67.51 | 64.15 | 0 | 0 | 0 | 0 | 3.36 | 0
2025-05-22 13:00 | 65.13 | 85.86 | 65.13 | 0 | 0 | 0 | 0 | 20.73 | 0
2025-05-22 14:00 | 66.01 | 91.88 | 66.01 | 0 | 0 | 0 | 0 | 25.87 | 0
2025-05-22 15:00 | 65.93 | 106.27 | 65.93 | 0 | 0 | 0 | 0 | 40.33 | 0
2025-05-22 16:00 | 66.3 | 124.45 | 66.3 | 0 | 0 | 0 | 0 | 58.14 | 0
2025-05-22 17:00 | 65.44 | 115.69 | 65.44 | 0 | 0 | 0 | 0 | 50.24 | 0
2025-05-22 18:00 | 63.99 | 82.69 | 63.99 | 0 | 0 | 0 | 0 | 18.7 | 0
2025-05-22 19:00 | 62.58 | 7.67 | 7.67 | 54.91 | 0 | 0 | 0 | 0 | 0
2025-05-22 20:00 | 60.45 | 0 | 0 | 60.45 | 0 | 0 | 0 | 0 | 0
2025-05-22 21:00 | 57.54 | 0 | 0 | 57.54 | 0 | 0 | 0 | 0 | 0
2025-05-22 22:00 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 0 | 0 | 0
2025-05-22 23:00 | 53.12 | 0 | 0 | 53.12 | 0 | 0 | 0 | 0 | 0
2025-05-23 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 0 | 0 | 0
2025-05-23 01:00 | 49.69 | 0 | 0 | 49.69 | 0 | 0 | 0 | 0 | 0
2025-05-23 02:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0 | 0 | 0
2025-05-23 03:00 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 0 | 0 | 0
2025-05-23 04:00 | 48.28 | 0 | 0 | 48.28 | 0 | 0 | 0 | 0 | 0
2025-05-23 05:00 | 49.11 | 17.61 | 17.61 | 31.49 | 0 | 0 | 0 | 0 | 0
2025-05-23 06:00 | 49.85 | 72.37 | 49.85 | 0 | 0 | 0 | 0 | 22.53 | 0
2025-05-23 07:00 | 52.96 | 101.99 | 52.96 | 0 | 0 | 0 | 0 | 49.03 | 0
2025-05-23 08:00 | 53.92 | 110.66 | 53.92 | 0 | 0 | 0 | 0 | 56.74 | 0
2025-05-23 09:00 | 56.32 | 114.9 | 56.32 | 0 | 0 | 0 | 0 | 58.58 | 0
2025-05-23 10:00 | 59.12 | 111.7 | 59.12 | 0 | 0 | 0 | 0 | 52.58 | 0
2025-05-23 11:00 | 60.64 | 109.87 | 60.64 | 0 | 0 | 0 | 0 | 49.23 | 0
2025-05-23 12:00 | 60.01 | 110.26 | 60.01 | 0 | 0 | 0 | 0 | 50.25 | 0
2025-05-23 13:00 | 61.02 | 110.96 | 61.02 | 0 | 0 | 0 | 0 | 49.93 | 0
2025-05-23 14:00 | 61.5 | 110.74 | 61.5 | 0 | 0 | 0 | 0 | 49.23 | 0
2025-05-23 15:00 | 62.47 | 105.77 | 62.47 | 0 | 0 | 0 | 0 | 43.31 | 0
2025-05-23 16:00 | 61.24 | 100.43 | 61.24 | 0 | 0 | 0 | 0 | 39.19 | 0
2025-05-23 17:00 | 60.95 | 80.51 | 60.95 | 0 | 0 | 0 | 0 | 19.56 | 0
2025-05-23 18:00 | 61.4 | 53.14 | 53.14 | 8.26 | 0 | 0 | 0 | 0 | 0
2025-05-23 19:00 | 59.54 | 4.35 | 4.35 | 55.19 | 0 | 0 | 0 | 0 | 0
2025-05-23 20:00 | 58.8 | 0 | 0 | 58.8 | 0 | 0 | 0 | 0 | 0
2025-05-23 21:00 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 0 | 0 | 0
2025-05-23 22:00 | 54.76 | 0 | 0 | 54.76 | 0 | 0 | 0 | 0 | 0
2025-05-23 23:00 | 51.94 | 0 | 0 | 51.94 | 0 | 0 | 0 | 0 | 0
2025-05-24 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 0 | 0 | 0
2025-05-24 01:00 | 49.73 | 0 | 0 | 49.73 | 0 | 0 | 0 | 0 | 0
2025-05-24 02:00 | 48.15 | 0 | 0 | 48.15 | 0 | 0 | 0 | 0 | 0
2025-05-24 03:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0 | 0 | 0
2025-05-24 04:00 | 47.8 | 0 | 0 | 47.8 | 0 | 0 | 0 | 0 | 0
2025-05-24 05:00 | 49.2 | 15.06 | 15.06 | 34.14 | 0 | 0 | 0 | 0 | 0
2025-05-24 06:00 | 51.29 | 39.98 | 39.98 | 11.31 | 0 | 0 | 0 | 0 | 0
2025-05-24 07:00 | 54.03 | 72.18 | 54.03 | 0 | 0 | 0 | 0 | 18.16 | 0
2025-05-24 08:00 | 55.05 | 93.46 | 55.05 | 0 | 0 | 0 | 0 | 38.42 | 0
2025-05-24 09:00 | 59.01 | 98.08 | 59.01 | 0 | 0 | 0 | 0 | 39.07 | 0
2025-05-24 10:00 | 62.6 | 110.62 | 62.6 | 0 | 0 | 0 | 0 | 48.02 | 0
2025-05-24 11:00 | 65.4 | 102.63 | 65.4 | 0 | 0 | 0 | 0 | 37.23 | 0
2025-05-24 12:00 | 68.18 | 106.46 | 68.18 | 0 | 0 | 0 | 0 | 38.28 | 0
2025-05-24 13:00 | 70.08 | 106.29 | 70.08 | 0 | 0 | 0 | 0 | 36.21 | 0
2025-05-24 14:00 | 71.03 | 111.18 | 71.03 | 0 | 0 | 0 | 0 | 40.15 | 0
2025-05-24 15:00 | 71.34 | 110.24 | 71.34 | 0 | 0 | 0 | 0 | 38.9 | 0
2025-05-24 16:00 | 71.06 | 94.32 | 71.06 | 0 | 0 | 0 | 0 | 23.26 | 0
2025-05-24 17:00 | 70.52 | 79.48 | 70.52 | 0 | 0 | 0 | 0 | 8.96 | 0
2025-05-24 18:00 | 67.62 | 48.39 | 48.39 | 19.22 | 0 | 0 | 0 | 0 | 0
2025-05-24 19:00 | 65.42 | 4.42 | 4.42 | 61 | 0 | 0 | 0 | 0 | 0
2025-05-24 20:00 | 62.62 | 0 | 0 | 62.62 | 0 | 0 | 0 | 0 | 0
2025-05-24 21:00 | 60.2 | 0 | 0 | 60.2 | 0 | 0 | 0 | 0 | 0
2025-05-24 22:00 | 56.21 | 0 | 0 | 56.21 | 0 | 0 | 0 | 0 | 0
2025-05-24 23:00 | 54.02 | 0 | 0 | 54.02 | 0 | 0 | 0 | 0 | 0
2025-05-25 | 51.79 | 0 | 0 | 51.79 | 0 | 0 | 0 | 0 | 0
2025-05-25 01:00 | 49.38 | 0 | 0 | 49.38 | 0 | 0 | 0 | 0 | 0
2025-05-25 02:00 | 48.18 | 0 | 0 | 48.18 | 0 | 0 | 0 | 0 | 0
2025-05-25 03:00 | 47.73 | 0 | 0 | 47.73 | 0 | 0 | 0 | 0 | 0
2025-05-25 04:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0 | 0 | 0
2025-05-25 05:00 | 49.84 | 1.55 | 1.55 | 48.29 | 0 | 0 | 0 | 0 | 0
2025-05-25 06:00 | 51.29 | 9.06 | 9.06 | 42.23 | 0 | 0 | 0 | 0 | 0
2025-05-25 07:00 | 53.53 | 19.33 | 19.33 | 34.2 | 0 | 0 | 0 | 0 | 0
2025-05-25 08:00 | 55.36 | 34 | 34 | 21.36 | 0 | 0 | 0 | 0 | 0
2025-05-25 09:00 | 58.02 | 42.1 | 42.1 | 15.93 | 0 | 0 | 0 | 0 | 0
2025-05-25 10:00 | 62.05 | 52.29 | 52.29 | 9.76 | 0 | 0 | 0 | 0 | 0
2025-05-25 11:00 | 63.09 | 56.05 | 56.05 | 7.04 | 0 | 0 | 0 | 0 | 0
2025-05-25 12:00 | 64.61 | 49.25 | 49.25 | 15.36 | 0 | 0 | 0 | 0 | 0
2025-05-25 13:00 | 67.05 | 55.92 | 55.92 | 11.13 | 0 | 0 | 0 | 0 | 0
2025-05-25 14:00 | 67.3 | 49.55 | 49.55 | 17.75 | 0 | 0 | 0 | 0 | 0
2025-05-25 15:00 | 67.73 | 27.4 | 27.4 | 40.32 | 0 | 0 | 0 | 0 | 0
2025-05-25 16:00 | 67.09 | 17.77 | 17.77 | 49.33 | 0 | 0 | 0 | 0 | 0
2025-05-25 17:00 | 66.18 | 9.87 | 9.87 | 56.31 | 0 | 0 | 0 | 0 | 0
2025-05-25 18:00 | 64.91 | 0 | 0 | 64.91 | 0 | 0 | 0 | 0 | 0
2025-05-25 19:00 | 62.49 | 0 | 0 | 62.49 | 0 | 0 | 0 | 0 | 0
2025-05-25 20:00 | 60.93 | 0 | 0 | 60.93 | 0 | 0 | 0 | 0 | 0
2025-05-25 21:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 0 | 0 | 0
2025-05-25 22:00 | 56.85 | 0 | 0 | 56.85 | 0 | 0 | 0 | 0 | 0
2025-05-25 23:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 0 | 0 | 0
2025-05-26 | 50.18 | 0 | 0 | 50.18 | 0 | 0 | 0 | 0 | 0
2025-05-26 01:00 | 49.5 | 0 | 0 | 49.5 | 0 | 0 | 0 | 0 | 0
2025-05-26 02:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 0 | 0 | 0
2025-05-26 03:00 | 48.44 | 0 | 0 | 48.44 | 0 | 0 | 0 | 0 | 0
2025-05-26 04:00 | 48 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0
2025-05-26 05:00 | 49.84 | 20.12 | 20.12 | 29.72 | 0 | 0 | 0 | 0 | 0
2025-05-26 06:00 | 50.98 | 55.47 | 50.98 | 0 | 0 | 0 | 0 | 4.49 | 0
2025-05-26 07:00 | 52.99 | 109.28 | 52.99 | 0 | 0 | 0 | 0 | 56.29 | 0
2025-05-26 08:00 | 56.14 | 123.77 | 56.14 | 0 | 0 | 0 | 0 | 67.63 | 0
2025-05-26 09:00 | 59.15 | 121.63 | 59.15 | 0 | 0 | 0 | 0 | 62.48 | 0
2025-05-26 10:00 | 60.9 | 56.11 | 56.11 | 4.79 | 0 | 0 | 0 | 0 | 0
2025-05-26 11:00 | 63.75 | 76.42 | 63.75 | 0 | 0 | 0 | 0 | 12.67 | 0
2025-05-26 12:00 | 66.43 | 101.34 | 66.43 | 0 | 0 | 0 | 0 | 34.91 | 0
2025-05-26 13:00 | 67.81 | 125.96 | 67.81 | 0 | 0 | 0 | 0 | 58.14 | 0
2025-05-26 14:00 | 69.2 | 102.72 | 69.2 | 0 | 0 | 0 | 0 | 33.52 | 0
2025-05-26 15:00 | 68.73 | 125.3 | 68.73 | 0 | 0 | 0 | 0 | 56.57 | 0
2025-05-26 16:00 | 69.36 | 119.71 | 69.36 | 0 | 0 | 0 | 0 | 50.35 | 0
2025-05-26 17:00 | 67.42 | 104.21 | 67.42 | 0 | 0 | 0 | 0 | 36.79 | 0
2025-05-26 18:00 | 67.25 | 70.25 | 67.25 | 0 | 0 | 0 | 0 | 3 | 0
2025-05-26 19:00 | 63.47 | 7.79 | 7.79 | 55.68 | 0 | 0 | 0 | 0 | 0
2025-05-26 20:00 | 61.29 | 0 | 0 | 61.29 | 0 | 0 | 0 | 0 | 0
2025-05-26 21:00 | 59.31 | 0 | 0 | 59.31 | 0 | 0 | 0 | 0 | 0
2025-05-26 22:00 | 57.15 | 0 | 0 | 57.15 | 0 | 0 | 0 | 0 | 0
2025-05-26 23:00 | 53.82 | 0 | 0 | 53.82 | 0 | 0 | 0 | 0 | 0
2025-05-27 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 0 | 0 | 0
2025-05-27 01:00 | 49.67 | 0 | 0 | 49.67 | 0 | 0 | 0 | 0 | 0
2025-05-27 02:00 | 48 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0
2025-05-27 03:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 0 | 0 | 0
2025-05-27 04:00 | 47.91 | 0 | 0 | 47.91 | 0 | 0 | 0 | 0 | 0
2025-05-27 05:00 | 49.02 | 22.89 | 22.89 | 26.13 | 0 | 0 | 0 | 0 | 0
2025-05-27 06:00 | 51.66 | 87.41 | 51.66 | 0 | 0 | 0 | 0 | 35.75 | 0
2025-05-27 07:00 | 53.2 | 104.75 | 53.2 | 0 | 0 | 0 | 0 | 51.55 | 0
2025-05-27 08:00 | 56.53 | 116.91 | 56.53 | 0 | 0 | 0 | 0 | 60.38 | 0
2025-05-27 09:00 | 58.43 | 110.39 | 58.43 | 0 | 0 | 0 | 0 | 51.96 | 0
2025-05-27 10:00 | 61.86 | 108.58 | 61.86 | 0 | 0 | 0 | 0 | 46.71 | 0
2025-05-27 11:00 | 63.84 | 97.62 | 63.84 | 0 | 0 | 0 | 0 | 33.78 | 0
2025-05-27 12:00 | 66.77 | 79.32 | 66.77 | 0 | 0 | 0 | 0 | 12.55 | 0
2025-05-27 13:00 | 67.71 | 103.04 | 67.71 | 0 | 0 | 0 | 0 | 35.33 | 0
2025-05-27 14:00 | 69.08 | 89.07 | 69.08 | 0 | 0 | 0 | 0 | 19.99 | 0
2025-05-27 15:00 | 68.4 | 60.62 | 60.62 | 7.77 | 0 | 0 | 0 | 0 | 0
2025-05-27 16:00 | 68.49 | 56.28 | 56.28 | 12.21 | 0 | 0 | 0 | 0 | 0
2025-05-27 17:00 | 67.06 | 32.8 | 32.8 | 34.25 | 0 | 0 | 0 | 0 | 0
2025-05-27 18:00 | 65.86 | 19.16 | 19.16 | 46.7 | 0 | 0 | 0 | 0 | 0
2025-05-27 19:00 | 63.96 | 1.93 | 1.93 | 62.03 | 0 | 0 | 0 | 0 | 0
2025-05-27 20:00 | 61.35 | 0 | 0 | 61.35 | 0 | 0 | 0 | 0 | 0
2025-05-27 21:00 | 58.48 | 0 | 0 | 58.48 | 0 | 0 | 0 | 0 | 0
2025-05-27 22:00 | 55.66 | 0 | 0 | 55.66 | 0 | 0 | 0 | 0 | 0
2025-05-27 23:00 | 52.59 | 0 | 0 | 52.59 | 0 | 0 | 0 | 0 | 0
2025-05-28 | 51.11 | 0 | 0 | 51.11 | 0 | 0 | 0 | 0 | 0
2025-05-28 01:00 | 50.1 | 0 | 0 | 50.1 | 0 | 0 | 0 | 0 | 0
2025-05-28 02:00 | 47.83 | 0 | 0 | 47.83 | 0 | 0 | 0 | 0 | 0
2025-05-28 03:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0 | 0 | 0
2025-05-28 04:00 | 49.52 | 0 | 0 | 49.52 | 0 | 0 | 0 | 0 | 0
2025-05-28 05:00 | 49.47 | 0.66 | 0.66 | 48.82 | 0 | 0 | 0 | 0 | 0
2025-05-28 06:00 | 51.8 | 32.98 | 32.98 | 18.82 | 0 | 0 | 0 | 0 | 0
2025-05-28 07:00 | 54.36 | 28.37 | 28.37 | 25.99 | 0 | 0 | 0 | 0 | 0
2025-05-28 08:00 | 57.14 | 37.02 | 37.02 | 20.12 | 0 | 0 | 0 | 0 | 0
2025-05-28 09:00 | 59 | 83.94 | 59 | 0 | 0 | 0 | 0 | 24.94 | 0
2025-05-28 10:00 | 62.59 | 89.2 | 62.59 | 0 | 0 | 0 | 0 | 26.61 | 0
2025-05-28 11:00 | 64.61 | 106.7 | 64.61 | 0 | 0 | 0 | 0 | 42.09 | 0
2025-05-28 12:00 | 68.97 | 97.14 | 68.97 | 0 | 0 | 0 | 0 | 28.17 | 0
2025-05-28 13:00 | 68.72 | 116.42 | 68.72 | 0 | 0 | 0 | 0 | 47.7 | 0
2025-05-28 14:00 | 70.1 | 61.31 | 61.31 | 8.8 | 0 | 0 | 0 | 0 | 0
2025-05-28 15:00 | 70.48 | 64.78 | 64.78 | 5.71 | 0 | 0 | 0 | 0 | 0
2025-05-28 16:00 | 69.88 | 64.64 | 64.64 | 5.24 | 0 | 0 | 0 | 0 | 0
2025-05-28 17:00 | 70.19 | 63.42 | 63.42 | 6.77 | 0 | 0 | 0 | 0 | 0
2025-05-28 18:00 | 68.95 | 52.32 | 52.32 | 16.63 | 0 | 0 | 0 | 0 | 0
2025-05-28 19:00 | 65.18 | 2.46 | 2.46 | 62.73 | 0 | 0 | 0 | 0 | 0
2025-05-28 20:00 | 62.04 | 0 | 0 | 62.04 | 0 | 0 | 0 | 0 | 0
2025-05-28 21:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 0 | 0 | 0
2025-05-28 22:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 0 | 0 | 0
2025-05-28 23:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 0 | 0 | 0
2025-05-29 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0 | 0 | 0
2025-05-29 01:00 | 50.04 | 0 | 0 | 50.04 | 0 | 0 | 0 | 0 | 0
2025-05-29 02:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0 | 0 | 0
2025-05-29 03:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 0 | 0 | 0
2025-05-29 04:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0 | 0 | 0
2025-05-29 05:00 | 49.38 | 17.48 | 17.48 | 31.9 | 0 | 0 | 0 | 0 | 0
2025-05-29 06:00 | 52.21 | 69.15 | 52.21 | 0 | 0 | 0 | 0 | 16.94 | 0
2025-05-29 07:00 | 54.51 | 96.07 | 54.51 | 0 | 0 | 0 | 0 | 41.56 | 0
2025-05-29 08:00 | 58.12 | 108.84 | 58.12 | 0 | 0 | 0 | 0 | 50.72 | 0
2025-05-29 09:00 | 61.62 | 110.7 | 61.62 | 0 | 0 | 0 | 0 | 49.08 | 0
2025-05-29 10:00 | 64.22 | 112.65 | 64.22 | 0 | 0 | 0 | 0 | 48.43 | 0
2025-05-29 11:00 | 67.8 | 108.46 | 67.8 | 0 | 0 | 0 | 0 | 40.66 | 0
2025-05-29 12:00 | 71.33 | 102.98 | 71.33 | 0 | 0 | 0 | 0 | 31.65 | 0
2025-05-29 13:00 | 73.69 | 103.99 | 73.69 | 0 | 0 | 0 | 0 | 30.31 | 0
2025-05-29 14:00 | 76.2 | 98.78 | 76.2 | 0 | 0 | 0 | 0 | 22.58 | 0
2025-05-29 15:00 | 76.55 | 100.74 | 76.55 | 0 | 0 | 0 | 0 | 24.19 | 0
2025-05-29 16:00 | 76.37 | 72.29 | 72.29 | 4.08 | 0 | 0 | 0 | 0 | 0
2025-05-29 17:00 | 74.41 | 46.93 | 46.93 | 27.49 | 0 | 0 | 0 | 0 | 0
2025-05-29 18:00 | 71.81 | 24.65 | 24.65 | 47.15 | 0 | 0 | 0 | 0 | 0
2025-05-29 19:00 | 69.12 | 4.33 | 4.33 | 64.79 | 0 | 0 | 0 | 0 | 0
2025-05-29 20:00 | 65.17 | 0 | 0 | 65.17 | 0 | 0 | 0 | 0 | 0
2025-05-29 21:00 | 61.26 | 0 | 0 | 61.26 | 0 | 0 | 0 | 0 | 0
2025-05-29 22:00 | 58.41 | 0 | 0 | 58.41 | 0 | 0 | 0 | 0 | 0
2025-05-29 23:00 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 0 | 0 | 0
2025-05-30 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 0 | 0 | 0
2025-05-30 01:00 | 49.61 | 0 | 0 | 49.61 | 0 | 0 | 0 | 0 | 0
2025-05-30 02:00 | 49.2 | 0 | 0 | 49.2 | 0 | 0 | 0 | 0 | 0
2025-05-30 03:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0 | 0 | 0
2025-05-30 04:00 | 48.82 | 0 | 0 | 48.82 | 0 | 0 | 0 | 0 | 0
2025-05-30 05:00 | 50.69 | 22.44 | 22.44 | 28.25 | 0 | 0 | 0 | 0 | 0
2025-05-30 06:00 | 50.94 | 75.76 | 50.94 | 0 | 0 | 0 | 0 | 24.82 | 0
2025-05-30 07:00 | 54.38 | 98.35 | 54.38 | 0 | 0 | 0 | 0 | 43.97 | 0
2025-05-30 08:00 | 57.29 | 111.32 | 57.29 | 0 | 0 | 0 | 0 | 54.03 | 0
2025-05-30 09:00 | 60.09 | 110.94 | 60.09 | 0 | 0 | 0 | 0 | 50.85 | 0
2025-05-30 10:00 | 64.8 | 112.08 | 64.8 | 0 | 0 | 0 | 0 | 47.28 | 0
2025-05-30 11:00 | 66.54 | 110.41 | 66.54 | 0 | 0 | 0 | 0 | 43.86 | 0
2025-05-30 12:00 | 68.94 | 110.79 | 68.94 | 0 | 0 | 0 | 0 | 41.85 | 0
2025-05-30 13:00 | 71.13 | 109.49 | 71.13 | 0 | 0 | 0 | 0 | 38.36 | 0
2025-05-30 14:00 | 71.36 | 110.84 | 71.36 | 0 | 0 | 0 | 0 | 39.47 | 0
2025-05-30 15:00 | 72.41 | 107.76 | 72.41 | 0 | 0 | 0 | 0 | 35.35 | 0
2025-05-30 16:00 | 72.86 | 104.57 | 72.86 | 0 | 0 | 0 | 0 | 31.72 | 0
2025-05-30 17:00 | 70.8 | 93.81 | 70.8 | 0 | 0 | 0 | 0 | 23.01 | 0
2025-05-30 18:00 | 68.73 | 68.75 | 68.73 | 0 | 0 | 0 | 0 | 0.03 | 0
2025-05-30 19:00 | 67.23 | 8.97 | 8.97 | 58.27 | 0 | 0 | 0 | 0 | 0
2025-05-30 20:00 | 64.28 | 0 | 0 | 64.28 | 0 | 0 | 0 | 0 | 0
2025-05-30 21:00 | 60.71 | 0 | 0 | 60.71 | 0 | 0 | 0 | 0 | 0
2025-05-30 22:00 | 57.08 | 0 | 0 | 57.08 | 0 | 0 | 0 | 0 | 0
2025-05-30 23:00 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 0 | 0 | 0
2025-05-31 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 0 | 0 | 0
2025-05-31 01:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 0 | 0 | 0
2025-05-31 02:00 | 48.43 | 0 | 0 | 48.43 | 0 | 0 | 0 | 0 | 0
2025-05-31 03:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 0 | 0 | 0
2025-05-31 04:00 | 48.44 | 0 | 0 | 48.44 | 0 | 0 | 0 | 0 | 0
2025-05-31 05:00 | 49.36 | 29.23 | 29.23 | 20.13 | 0 | 0 | 0 | 0 | 0
2025-05-31 06:00 | 52.13 | 92.67 | 52.13 | 0 | 0 | 0 | 0 | 40.54 | 0
2025-05-31 07:00 | 54.58 | 113.34 | 54.58 | 0 | 0 | 0 | 0 | 58.76 | 0
2025-05-31 08:00 | 58.14 | 121.03 | 58.14 | 0 | 0 | 0 | 0 | 62.89 | 0
2025-05-31 09:00 | 59.96 | 122.72 | 59.96 | 0 | 0 | 0 | 0 | 62.76 | 0
2025-05-31 10:00 | 63.43 | 121.34 | 63.43 | 0 | 0 | 0 | 0 | 57.92 | 0
2025-05-31 11:00 | 66.19 | 119.25 | 66.19 | 0 | 0 | 0 | 0 | 53.06 | 0
2025-05-31 12:00 | 68.27 | 117.5 | 68.27 | 0 | 0 | 0 | 0 | 49.24 | 0
2025-05-31 13:00 | 70.56 | 119.28 | 70.56 | 0 | 0 | 0 | 0 | 48.72 | 0
2025-05-31 14:00 | 71.7 | 120.63 | 71.7 | 0 | 0 | 0 | 0 | 48.93 | 0
2025-05-31 15:00 | 71.86 | 119.35 | 71.86 | 0 | 0 | 0 | 0 | 47.49 | 0
2025-05-31 16:00 | 71.19 | 115.02 | 71.19 | 0 | 0 | 0 | 0 | 43.83 | 0
2025-05-31 17:00 | 70.01 | 100.58 | 70.01 | 0 | 0 | 0 | 0 | 30.56 | 0
2025-05-31 18:00 | 67.71 | 74.6 | 67.71 | 0 | 0 | 0 | 0 | 6.89 | 0
2025-05-31 19:00 | 65.64 | 8.12 | 8.12 | 57.51 | 0 | 0 | 0 | 0 | 0
2025-05-31 20:00 | 62.97 | 0 | 0 | 62.97 | 0 | 0 | 0 | 0 | 0
2025-05-31 21:00 | 59.73 | 0 | 0 | 59.73 | 0 | 0 | 0 | 0 | 0
2025-05-31 22:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 0 | 0 | 0
2025-05-31 23:00 | 55.06 | 0 | 0 | 55.06 | 0 | 0 | 0 | 0 | 0
2025-06-01 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 0 | 0 | 0
2025-06-01 01:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 0 | 0 | 0
2025-06-01 02:00 | 48.54 | 0 | 0 | 48.54 | 0 | 0 | 0 | 0 | 0
2025-06-01 03:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 0 | 0 | 0
2025-06-01 04:00 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 0 | 0 | 0
2025-06-01 05:00 | 50.54 | 30.5 | 30.5 | 20.05 | 0 | 0 | 0 | 0 | 0
2025-06-01 06:00 | 51.73 | 93.28 | 51.73 | 0 | 0 | 0 | 0 | 41.56 | 0
2025-06-01 07:00 | 54.87 | 113.48 | 54.87 | 0 | 0 | 0 | 0 | 58.6 | 0
2025-06-01 08:00 | 56.8 | 121.91 | 56.8 | 0 | 0 | 0 | 0 | 65.11 | 0
2025-06-01 09:00 | 59.2 | 124.1 | 59.2 | 0 | 0 | 0 | 0 | 64.9 | 0
2025-06-01 10:00 | 61.35 | 122.98 | 61.35 | 0 | 0 | 0 | 0 | 61.63 | 0
2025-06-01 11:00 | 64.25 | 121 | 64.25 | 0 | 0 | 0 | 0 | 56.75 | 0
2025-06-01 12:00 | 66.31 | 119.56 | 66.31 | 0 | 0 | 0 | 0 | 53.25 | 0
2025-06-01 13:00 | 67.27 | 120.29 | 67.27 | 0 | 0 | 0 | 0 | 53.02 | 0
2025-06-01 14:00 | 69.03 | 120.92 | 69.03 | 0 | 0 | 0 | 0 | 51.9 | 0
2025-06-01 15:00 | 68.88 | 120.48 | 68.88 | 0 | 0 | 0 | 0 | 51.6 | 0
2025-06-01 16:00 | 67.75 | 115.21 | 67.75 | 0 | 0 | 0 | 0 | 47.46 | 0
2025-06-01 17:00 | 66.98 | 104.89 | 66.98 | 0 | 0 | 0 | 0 | 37.91 | 0
2025-06-01 18:00 | 66.1 | 79.57 | 66.1 | 0 | 0 | 0 | 0 | 13.47 | 0
2025-06-01 19:00 | 63.7 | 8.44 | 8.44 | 55.26 | 0 | 0 | 0 | 0 | 0
2025-06-01 20:00 | 62.56 | 0 | 0 | 62.56 | 0 | 0 | 0 | 0 | 0
2025-06-01 21:00 | 59.71 | 0 | 0 | 59.71 | 0 | 0 | 0 | 0 | 0
2025-06-01 22:00 | 57.05 | 0 | 0 | 57.05 | 0 | 0 | 0 | 0 | 0
2025-06-01 23:00 | 54.71 | 0 | 0 | 54.71 | 0 | 0 | 0 | 0 | 0
2025-06-02 | 53 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0
2025-06-02 01:00 | 50.42 | 0 | 0 | 50.42 | 0 | 0 | 0 | 0 | 0
2025-06-02 02:00 | 49.11 | 0 | 0 | 49.11 | 0 | 0 | 0 | 0 | 0
2025-06-02 03:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0 | 0 | 0
2025-06-02 04:00 | 49.65 | 0 | 0 | 49.65 | 0 | 0 | 0 | 0 | 0
2025-06-02 05:00 | 50.18 | 28.22 | 28.22 | 21.96 | 0 | 0 | 0 | 0 | 0
2025-06-02 06:00 | 52.14 | 85.54 | 52.14 | 0 | 0 | 0 | 0 | 33.41 | 0
2025-06-02 07:00 | 54.43 | 105.29 | 54.43 | 0 | 0 | 0 | 0 | 50.86 | 0
2025-06-02 08:00 | 56.88 | 114.17 | 56.88 | 0 | 0 | 0 | 0 | 57.29 | 0
2025-06-02 09:00 | 58.32 | 116.57 | 58.32 | 0 | 0 | 0 | 0 | 58.25 | 0
2025-06-02 10:00 | 60.29 | 117.43 | 60.29 | 0 | 0 | 0 | 0 | 57.14 | 0
2025-06-02 11:00 | 62.32 | 115.6 | 62.32 | 0 | 0 | 0 | 0 | 53.29 | 0
2025-06-02 12:00 | 63.57 | 113.86 | 63.57 | 0 | 0 | 0 | 0 | 50.3 | 0
2025-06-02 13:00 | 64.61 | 113.78 | 64.61 | 0 | 0 | 0 | 0 | 49.16 | 0
2025-06-02 14:00 | 65.76 | 114.74 | 65.76 | 0 | 0 | 0 | 0 | 48.97 | 0
2025-06-02 15:00 | 65.53 | 112.94 | 65.53 | 0 | 0 | 0 | 0 | 47.41 | 0
2025-06-02 16:00 | 65.54 | 108.82 | 65.54 | 0 | 0 | 0 | 0 | 43.27 | 0
2025-06-02 17:00 | 64.32 | 97.42 | 64.32 | 0 | 0 | 0 | 0 | 33.09 | 0
2025-06-02 18:00 | 63.82 | 72.76 | 63.82 | 0 | 0 | 0 | 0 | 8.94 | 0
2025-06-02 19:00 | 63.05 | 8.52 | 8.52 | 54.53 | 0 | 0 | 0 | 0 | 0
2025-06-02 20:00 | 61.36 | 0 | 0 | 61.36 | 0 | 0 | 0 | 0 | 0
2025-06-02 21:00 | 58.64 | 0 | 0 | 58.64 | 0 | 0 | 0 | 0 | 0
2025-06-02 22:00 | 56.78 | 0 | 0 | 56.78 | 0 | 0 | 0 | 0 | 0
2025-06-02 23:00 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 0 | 0 | 0
2025-06-03 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 0 | 0 | 0
2025-06-03 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 0 | 0 | 0
2025-06-03 02:00 | 49.18 | 0 | 0 | 49.18 | 0 | 0 | 0 | 0 | 0
2025-06-03 03:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 0 | 0 | 0
2025-06-03 04:00 | 49.2 | 0 | 0 | 49.2 | 0 | 0 | 0 | 0 | 0
2025-06-03 05:00 | 50.46 | 26.46 | 26.46 | 24 | 0 | 0 | 0 | 0 | 0
2025-06-03 06:00 | 51.64 | 85.99 | 51.64 | 0 | 0 | 0 | 0 | 34.34 | 0
2025-06-03 07:00 | 54.31 | 109.48 | 54.31 | 0 | 0 | 0 | 0 | 55.17 | 0
2025-06-03 08:00 | 57.49 | 119.12 | 57.49 | 0 | 0 | 0 | 0 | 61.64 | 0
2025-06-03 09:00 | 60.38 | 121.73 | 60.38 | 0 | 0 | 0 | 0 | 61.35 | 0
2025-06-03 10:00 | 63.01 | 120.87 | 63.01 | 0 | 0 | 0 | 0 | 57.86 | 0
2025-06-03 11:00 | 65.78 | 118.83 | 65.78 | 0 | 0 | 0 | 0 | 53.05 | 0
2025-06-03 12:00 | 68.06 | 117.59 | 68.06 | 0 | 0 | 0 | 0 | 49.53 | 0
2025-06-03 13:00 | 70.1 | 118.27 | 70.1 | 0 | 0 | 0 | 0 | 48.17 | 0
2025-06-03 14:00 | 70.62 | 119.1 | 70.62 | 0 | 0 | 0 | 0 | 48.48 | 0
2025-06-03 15:00 | 71.21 | 117.31 | 71.21 | 0 | 0 | 0 | 0 | 46.1 | 0
2025-06-03 16:00 | 70.4 | 111.01 | 70.4 | 0 | 0 | 0 | 0 | 40.61 | 0
2025-06-03 17:00 | 69.94 | 97.52 | 69.94 | 0 | 0 | 0 | 0 | 27.57 | 0
2025-06-03 18:00 | 68.22 | 70.09 | 68.22 | 0 | 0 | 0 | 0 | 1.87 | 0
2025-06-03 19:00 | 66.3 | 9.96 | 9.96 | 56.35 | 0 | 0 | 0 | 0 | 0
2025-06-03 20:00 | 63.65 | 0 | 0 | 63.65 | 0 | 0 | 0 | 0 | 0
2025-06-03 21:00 | 60.76 | 0 | 0 | 60.76 | 0 | 0 | 0 | 0 | 0
2025-06-03 22:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 0 | 0 | 0
2025-06-03 23:00 | 54.92 | 0 | 0 | 54.92 | 0 | 0 | 0 | 0 | 0
2025-06-04 | 53.06 | 0 | 0 | 53.06 | 0 | 0 | 0 | 0 | 0
2025-06-04 01:00 | 50.27 | 0 | 0 | 50.27 | 0 | 0 | 0 | 0 | 0
2025-06-04 02:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0 | 0 | 0
2025-06-04 03:00 | 49.05 | 0 | 0 | 49.05 | 0 | 0 | 0 | 0 | 0
2025-06-04 04:00 | 49.58 | 0 | 0 | 49.58 | 0 | 0 | 0 | 0 | 0
2025-06-04 05:00 | 50.18 | 23.1 | 23.1 | 27.08 | 0 | 0 | 0 | 0 | 0
2025-06-04 06:00 | 52.49 | 77.45 | 52.49 | 0 | 0 | 0 | 0 | 24.96 | 0
2025-06-04 07:00 | 55 | 100.88 | 55 | 0 | 0 | 0 | 0 | 45.87 | 0
2025-06-04 08:00 | 56.87 | 111.86 | 56.87 | 0 | 0 | 0 | 0 | 54.99 | 0
2025-06-04 09:00 | 61 | 118.01 | 61 | 0 | 0 | 0 | 0 | 57.01 | 0
2025-06-04 10:00 | 64.16 | 117.83 | 64.16 | 0 | 0 | 0 | 0 | 53.68 | 0
2025-06-04 11:00 | 67.06 | 116.17 | 67.06 | 0 | 0 | 0 | 0 | 49.11 | 0
2025-06-04 12:00 | 70.34 | 115.41 | 70.34 | 0 | 0 | 0 | 0 | 45.07 | 0
2025-06-04 13:00 | 70.93 | 116.16 | 70.93 | 0 | 0 | 0 | 0 | 45.23 | 0
2025-06-04 14:00 | 72.32 | 116.11 | 72.32 | 0 | 0 | 0 | 0 | 43.79 | 0
2025-06-04 15:00 | 71.83 | 114.52 | 71.83 | 0 | 0 | 0 | 0 | 42.68 | 0
2025-06-04 16:00 | 72.49 | 107.36 | 72.49 | 0 | 0 | 0 | 0 | 34.86 | 0
2025-06-04 17:00 | 71.34 | 93.03 | 71.34 | 0 | 0 | 0 | 0 | 21.69 | 0
2025-06-04 18:00 | 69.37 | 64.81 | 64.81 | 4.56 | 0 | 0 | 0 | 0 | 0
2025-06-04 19:00 | 67.69 | 9.78 | 9.78 | 57.91 | 0 | 0 | 0 | 0 | 0
2025-06-04 20:00 | 64.66 | 0 | 0 | 64.66 | 0 | 0 | 0 | 0 | 0
2025-06-04 21:00 | 61.15 | 0 | 0 | 61.15 | 0 | 0 | 0 | 0 | 0
2025-06-04 22:00 | 57.79 | 0 | 0 | 57.79 | 0 | 0 | 0 | 0 | 0
2025-06-04 23:00 | 55.56 | 0 | 0 | 55.56 | 0 | 0 | 0 | 0 | 0
2025-06-05 | 52.81 | 0 | 0 | 52.81 | 0 | 0 | 0 | 0 | 0
2025-06-05 01:00 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 0 | 0 | 0
2025-06-05 02:00 | 48.62 | 0 | 0 | 48.62 | 0 | 0 | 0 | 0 | 0
2025-06-05 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0 | 0 | 0
2025-06-05 04:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0 | 0 | 0
2025-06-05 05:00 | 51.88 | 18.75 | 18.75 | 33.13 | 0 | 0 | 0 | 0 | 0
2025-06-05 06:00 | 52.85 | 64.49 | 52.85 | 0 | 0 | 0 | 0 | 11.64 | 0
2025-06-05 07:00 | 55.3 | 84.83 | 55.3 | 0 | 0 | 0 | 0 | 29.53 | 0
2025-06-05 08:00 | 58.64 | 106.6 | 58.64 | 0 | 0 | 0 | 0 | 47.96 | 0
2025-06-05 09:00 | 63.57 | 103.18 | 63.57 | 0 | 0 | 0 | 0 | 39.61 | 0
2025-06-05 10:00 | 66.73 | 102.33 | 66.73 | 0 | 0 | 0 | 0 | 35.6 | 0
2025-06-05 11:00 | 72.15 | 106.94 | 72.15 | 0 | 0 | 0 | 0 | 34.79 | 0
2025-06-05 12:00 | 76.12 | 103.54 | 76.12 | 0 | 0 | 0 | 0 | 27.42 | 0
2025-06-05 13:00 | 78.99 | 102.44 | 78.99 | 0 | 0 | 0 | 0 | 23.45 | 0
2025-06-05 14:00 | 80.64 | 106.76 | 80.64 | 0 | 0 | 0 | 0 | 26.12 | 0
2025-06-05 15:00 | 81.72 | 99.97 | 81.72 | 0 | 0 | 0 | 0 | 18.25 | 0
2025-06-05 16:00 | 80.84 | 89.19 | 80.84 | 0 | 0 | 0 | 0 | 8.35 | 0
2025-06-05 17:00 | 78.39 | 73.16 | 73.16 | 5.23 | 0 | 0 | 0 | 0 | 0
2025-06-05 18:00 | 76.64 | 52.25 | 52.25 | 24.4 | 0 | 0 | 0 | 0 | 0
2025-06-05 19:00 | 71.7 | 8.85 | 8.85 | 62.85 | 0 | 0 | 0 | 0 | 0
2025-06-05 20:00 | 68 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0
2025-06-05 21:00 | 62.08 | 0 | 0 | 62.08 | 0 | 0 | 0 | 0 | 0
2025-06-05 22:00 | 59.87 | 0 | 0 | 59.87 | 0 | 0 | 0 | 0 | 0
2025-06-05 23:00 | 56.42 | 0 | 0 | 56.42 | 0 | 0 | 0 | 0 | 0
2025-06-06 | 52.8 | 0 | 0 | 52.8 | 0 | 0 | 0 | 0 | 0
2025-06-06 01:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 0 | 0 | 0
2025-06-06 02:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0 | 0 | 0
2025-06-06 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0 | 0 | 0
2025-06-06 04:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0 | 0 | 0
2025-06-06 05:00 | 50.41 | 3.27 | 3.27 | 47.14 | 0 | 0 | 0 | 0 | 0
2025-06-06 06:00 | 52.48 | 6.99 | 6.99 | 45.49 | 0 | 0 | 0 | 0 | 0
2025-06-06 07:00 | 55.93 | 17.27 | 17.27 | 38.65 | 0 | 0 | 0 | 0 | 0
2025-06-06 08:00 | 58.87 | 33.84 | 33.84 | 25.03 | 0 | 0 | 0 | 0 | 0
2025-06-06 09:00 | 61.3 | 80.72 | 61.3 | 0 | 0 | 0 | 0 | 19.43 | 0
2025-06-06 10:00 | 64.56 | 129.79 | 64.56 | 0 | 0 | 0 | 0 | 65.23 | 0
2025-06-06 11:00 | 67.68 | 90.35 | 67.68 | 0 | 0 | 0 | 0 | 22.67 | 0
2025-06-06 12:00 | 71.03 | 32.46 | 32.46 | 38.57 | 0 | 0 | 0 | 0 | 0
2025-06-06 13:00 | 72.2 | 34.49 | 34.49 | 37.71 | 0 | 0 | 0 | 0 | 0
2025-06-06 14:00 | 74.17 | 29.18 | 29.18 | 44.99 | 0 | 0 | 0 | 0 | 0
2025-06-06 15:00 | 74.81 | 35.39 | 35.39 | 39.42 | 0 | 0 | 0 | 0 | 0
2025-06-06 16:00 | 73.95 | 3.85 | 3.85 | 70.1 | 0 | 0 | 0 | 0 | 0
2025-06-06 17:00 | 73.21 | 2.16 | 2.16 | 71.05 | 0 | 0 | 0 | 0 | 0
2025-06-06 18:00 | 70.51 | 0.63 | 0.63 | 69.87 | 0 | 0 | 0 | 0 | 0
2025-06-06 19:00 | 67.9 | 0 | 0 | 67.9 | 0 | 0 | 0 | 0 | 0
2025-06-06 20:00 | 64.44 | 0 | 0 | 64.44 | 0 | 0 | 0 | 0 | 0
2025-06-06 21:00 | 62.16 | 0 | 0 | 62.16 | 0 | 0 | 0 | 0 | 0
2025-06-06 22:00 | 58 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0
2025-06-06 23:00 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 0 | 0 | 0
2025-06-07 | 52.94 | 0 | 0 | 52.94 | 0 | 0 | 0 | 0 | 0
2025-06-07 01:00 | 50.41 | 0 | 0 | 50.41 | 0 | 0 | 0 | 0 | 0
2025-06-07 02:00 | 49.37 | 0 | 0 | 49.37 | 0 | 0 | 0 | 0 | 0
2025-06-07 03:00 | 49.94 | 0 | 0 | 49.94 | 0 | 0 | 0 | 0 | 0
2025-06-07 04:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 0 | 0 | 0
2025-06-07 05:00 | 50.43 | 19.15 | 19.15 | 31.28 | 0 | 0 | 0 | 0 | 0
2025-06-07 06:00 | 53.13 | 13.31 | 13.31 | 39.83 | 0 | 0 | 0 | 0 | 0
2025-06-07 07:00 | 55.66 | 43.2 | 43.2 | 12.46 | 0 | 0 | 0 | 0 | 0
2025-06-07 08:00 | 60.78 | 19.19 | 19.19 | 41.59 | 0 | 0 | 0 | 0 | 0
2025-06-07 09:00 | 62.91 | 39.6 | 39.6 | 23.31 | 0 | 0 | 0 | 0 | 0
2025-06-07 10:00 | 66.43 | 73.82 | 66.43 | 0 | 0 | 0 | 0 | 7.39 | 0
2025-06-07 11:00 | 71.06 | 87.76 | 71.06 | 0 | 0 | 0 | 0 | 16.7 | 0
2025-06-07 12:00 | 72.73 | 122.07 | 72.73 | 0 | 0 | 0 | 0 | 49.34 | 0
2025-06-07 13:00 | 76.3 | 99.16 | 76.3 | 0 | 0 | 0 | 0 | 22.87 | 0
2025-06-07 14:00 | 78.91 | 108.31 | 78.91 | 0 | 0 | 0 | 0 | 29.4 | 0
2025-06-07 15:00 | 78.43 | 101.03 | 78.43 | 0 | 0 | 0 | 0 | 22.61 | 0
2025-06-07 16:00 | 77.05 | 96.24 | 77.05 | 0 | 0 | 0 | 0 | 19.19 | 0
2025-06-07 17:00 | 76.05 | 32.92 | 32.92 | 43.13 | 0 | 0 | 0 | 0 | 0
2025-06-07 18:00 | 74.38 | 27.11 | 27.11 | 47.27 | 0 | 0 | 0 | 0 | 0
2025-06-07 19:00 | 70.54 | 4.56 | 4.56 | 65.98 | 0 | 0 | 0 | 0 | 0
2025-06-07 20:00 | 66.2 | 0 | 0 | 66.2 | 0 | 0 | 0 | 0 | 0
2025-06-07 21:00 | 62.42 | 0 | 0 | 62.42 | 0 | 0 | 0 | 0 | 0
2025-06-07 22:00 | 58.78 | 0 | 0 | 58.78 | 0 | 0 | 0 | 0 | 0
2025-06-07 23:00 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 0 | 0 | 0
2025-06-08 | 53.62 | 0 | 0 | 53.62 | 0 | 0 | 0 | 0 | 0
2025-06-08 01:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 0 | 0 | 0
2025-06-08 02:00 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0
2025-06-08 03:00 | 48.68 | 0 | 0 | 48.68 | 0 | 0 | 0 | 0 | 0
2025-06-08 04:00 | 49.1 | 0 | 0 | 49.1 | 0 | 0 | 0 | 0 | 0
2025-06-08 05:00 | 51.27 | 18.5 | 18.5 | 32.77 | 0 | 0 | 0 | 0 | 0
2025-06-08 06:00 | 52.28 | 18.04 | 18.04 | 34.24 | 0 | 0 | 0 | 0 | 0
2025-06-08 07:00 | 55.33 | 75.48 | 55.33 | 0 | 0 | 0 | 0 | 20.15 | 0
2025-06-08 08:00 | 58.44 | 94.84 | 58.44 | 0 | 0 | 0 | 0 | 36.39 | 0
2025-06-08 09:00 | 60.7 | 98.08 | 60.7 | 0 | 0 | 0 | 0 | 37.38 | 0
2025-06-08 10:00 | 63.66 | 91.39 | 63.66 | 0 | 0 | 0 | 0 | 27.72 | 0
2025-06-08 11:00 | 66.77 | 73.79 | 66.77 | 0 | 0 | 0 | 0 | 7.03 | 0
2025-06-08 12:00 | 69.28 | 36.52 | 36.52 | 32.75 | 0 | 0 | 0 | 0 | 0
2025-06-08 13:00 | 71.22 | 60.03 | 60.03 | 11.19 | 0 | 0 | 0 | 0 | 0
2025-06-08 14:00 | 72.03 | 95.12 | 72.03 | 0 | 0 | 0 | 0 | 23.09 | 0
2025-06-08 15:00 | 72.11 | 82.69 | 72.11 | 0 | 0 | 0 | 0 | 10.58 | 0
2025-06-08 16:00 | 71.35 | 62.59 | 62.59 | 8.76 | 0 | 0 | 0 | 0 | 0
2025-06-08 17:00 | 70.16 | 52.11 | 52.11 | 18.04 | 0 | 0 | 0 | 0 | 0
2025-06-08 18:00 | 68.77 | 64.21 | 64.21 | 4.56 | 0 | 0 | 0 | 0 | 0
2025-06-08 19:00 | 67.02 | 9.76 | 9.76 | 57.26 | 0 | 0 | 0 | 0 | 0
2025-06-08 20:00 | 64.34 | 0 | 0 | 64.34 | 0 | 0 | 0 | 0 | 0
2025-06-08 21:00 | 60.22 | 0 | 0 | 60.22 | 0 | 0 | 0 | 0 | 0
2025-06-08 22:00 | 57.9 | 0 | 0 | 57.9 | 0 | 0 | 0 | 0 | 0
2025-06-08 23:00 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 0 | 0 | 0
2025-06-09 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 0 | 0 | 0
2025-06-09 01:00 | 50.39 | 0 | 0 | 50.39 | 0 | 0 | 0 | 0 | 0
2025-06-09 02:00 | 51.04 | 0 | 0 | 51.04 | 0 | 0 | 0 | 0 | 0
2025-06-09 03:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0 | 0 | 0
2025-06-09 04:00 | 50.05 | 0 | 0 | 50.05 | 0 | 0 | 0 | 0 | 0
2025-06-09 05:00 | 51.29 | 24.58 | 24.58 | 26.72 | 0 | 0 | 0 | 0 | 0
2025-06-09 06:00 | 52.81 | 79.03 | 52.81 | 0 | 0 | 0 | 0 | 26.22 | 0
2025-06-09 07:00 | 55.02 | 103.01 | 55.02 | 0 | 0 | 0 | 0 | 48 | 0
2025-06-09 08:00 | 59.07 | 112.22 | 59.07 | 0 | 0 | 0 | 0 | 53.15 | 0
2025-06-09 09:00 | 61.15 | 116.22 | 61.15 | 0 | 0 | 0 | 0 | 55.07 | 0
2025-06-09 10:00 | 63.53 | 118.83 | 63.53 | 0 | 0 | 0 | 0 | 55.3 | 0
2025-06-09 11:00 | 65.54 | 116.54 | 65.54 | 0 | 0 | 0 | 0 | 51 | 0
2025-06-09 12:00 | 66.46 | 115.36 | 66.46 | 0 | 0 | 0 | 0 | 48.89 | 0
2025-06-09 13:00 | 68.84 | 115.39 | 68.84 | 0 | 0 | 0 | 0 | 46.55 | 0
2025-06-09 14:00 | 68.52 | 114.89 | 68.52 | 0 | 0 | 0 | 0 | 46.37 | 0
2025-06-09 15:00 | 69.33 | 113.16 | 69.33 | 0 | 0 | 0 | 0 | 43.83 | 0
2025-06-09 16:00 | 68.12 | 107.98 | 68.12 | 0 | 0 | 0 | 0 | 39.85 | 0
2025-06-09 17:00 | 67.18 | 95.84 | 67.18 | 0 | 0 | 0 | 0 | 28.66 | 0
2025-06-09 18:00 | 67.13 | 70.03 | 67.13 | 0 | 0 | 0 | 0 | 2.9 | 0
2025-06-09 19:00 | 64.85 | 12.74 | 12.74 | 52.11 | 0 | 0 | 0 | 0 | 0
2025-06-09 20:00 | 62.12 | 0 | 0 | 62.12 | 0 | 0 | 0 | 0 | 0
2025-06-09 21:00 | 60.92 | 0 | 0 | 60.92 | 0 | 0 | 0 | 0 | 0
2025-06-09 22:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 0 | 0 | 0
2025-06-09 23:00 | 56.07 | 0 | 0 | 56.07 | 0 | 0 | 0 | 0 | 0
2025-06-10 | 53 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0
2025-06-10 01:00 | 51.2 | 0 | 0 | 51.2 | 0 | 0 | 0 | 0 | 0
2025-06-10 02:00 | 50.4 | 0 | 0 | 50.4 | 0 | 0 | 0 | 0 | 0
2025-06-10 03:00 | 50.09 | 0 | 0 | 50.09 | 0 | 0 | 0 | 0 | 0
2025-06-10 04:00 | 49.78 | 0 | 0 | 49.78 | 0 | 0 | 0 | 0 | 0
2025-06-10 05:00 | 51.22 | 20.67 | 20.67 | 30.55 | 0 | 0 | 0 | 0 | 0
2025-06-10 06:00 | 53.28 | 65.83 | 53.28 | 0 | 0 | 0 | 0 | 12.55 | 0
2025-06-10 07:00 | 55.84 | 68.69 | 55.84 | 0 | 0 | 0 | 0 | 12.85 | 0
2025-06-10 08:00 | 58.21 | 91.61 | 58.21 | 0 | 0 | 0 | 0 | 33.4 | 0
2025-06-10 09:00 | 60.99 | 98.19 | 60.99 | 0 | 0 | 0 | 0 | 37.2 | 0
2025-06-10 10:00 | 64.37 | 104.41 | 64.37 | 0 | 0 | 0 | 0 | 40.04 | 0
2025-06-10 11:00 | 66.6 | 105.08 | 66.6 | 0 | 0 | 0 | 0 | 38.48 | 0
2025-06-10 12:00 | 68.12 | 106.76 | 68.12 | 0 | 0 | 0 | 0 | 38.64 | 0
2025-06-10 13:00 | 70.12 | 111.06 | 70.12 | 0 | 0 | 0 | 0 | 40.94 | 0
2025-06-10 14:00 | 69.91 | 111.34 | 69.91 | 0 | 0 | 0 | 0 | 41.43 | 0
2025-06-10 15:00 | 71.19 | 103.69 | 71.19 | 0 | 0 | 0 | 0 | 32.49 | 0
2025-06-10 16:00 | 70.37 | 106.29 | 70.37 | 0 | 0 | 0 | 0 | 35.92 | 0
2025-06-10 17:00 | 70.9 | 88.93 | 70.9 | 0 | 0 | 0 | 0 | 18.03 | 0
2025-06-10 18:00 | 67.28 | 58.76 | 58.76 | 8.53 | 0 | 0 | 0 | 0 | 0
2025-06-10 19:00 | 65.65 | 11.54 | 11.54 | 54.1 | 0 | 0 | 0 | 0 | 0
2025-06-10 20:00 | 63.89 | 0 | 0 | 63.89 | 0 | 0 | 0 | 0 | 0
2025-06-10 21:00 | 61.25 | 0 | 0 | 61.25 | 0 | 0 | 0 | 0 | 0
2025-06-10 22:00 | 59.25 | 0 | 0 | 59.25 | 0 | 0 | 0 | 0 | 0
2025-06-10 23:00 | 55.23 | 0 | 0 | 55.23 | 0 | 0 | 0 | 0 | 0
2025-06-11 | 53.71 | 0 | 0 | 53.71 | 0 | 0 | 0 | 0 | 0
2025-06-11 01:00 | 51.88 | 0 | 0 | 51.88 | 0 | 0 | 0 | 0 | 0
2025-06-11 02:00 | 50.4 | 0 | 0 | 50.4 | 0 | 0 | 0 | 0 | 0
2025-06-11 03:00 | 49.14 | 0 | 0 | 49.14 | 0 | 0 | 0 | 0 | 0
2025-06-11 04:00 | 50.75 | 0 | 0 | 50.75 | 0 | 0 | 0 | 0 | 0
2025-06-11 05:00 | 51.92 | 25.02 | 25.02 | 26.89 | 0 | 0 | 0 | 0 | 0
2025-06-11 06:00 | 53.56 | 67.06 | 53.56 | 0 | 0 | 0 | 0 | 13.5 | 0
2025-06-11 07:00 | 55.85 | 88.62 | 55.85 | 0 | 0 | 0 | 0 | 32.77 | 0
2025-06-11 08:00 | 58.68 | 119.08 | 58.68 | 0 | 0 | 0 | 0 | 60.41 | 0
2025-06-11 09:00 | 61.43 | 128.89 | 61.43 | 0 | 0 | 0 | 0 | 67.45 | 0
2025-06-11 10:00 | 64.59 | 129.16 | 64.59 | 0 | 0 | 0 | 0 | 64.57 | 0
2025-06-11 11:00 | 66.8 | 85.62 | 66.8 | 0 | 0 | 0 | 0 | 18.82 | 0
2025-06-11 12:00 | 68.44 | 65.97 | 65.97 | 2.46 | 0 | 0 | 0 | 0 | 0
2025-06-11 13:00 | 69.88 | 67.34 | 67.34 | 2.54 | 0 | 0 | 0 | 0 | 0
2025-06-11 14:00 | 70.98 | 47.51 | 47.51 | 23.47 | 0 | 0 | 0 | 0 | 0
2025-06-11 15:00 | 71.79 | 23.87 | 23.87 | 47.91 | 0 | 0 | 0 | 0 | 0
2025-06-11 16:00 | 71.34 | 17.39 | 17.39 | 53.95 | 0 | 0 | 0 | 0 | 0
2025-06-11 17:00 | 70.51 | 5.43 | 5.43 | 65.08 | 0 | 0 | 0 | 0 | 0
2025-06-11 18:00 | 69.11 | 0.76 | 0.76 | 68.35 | 0 | 0 | 0 | 0 | 0
2025-06-11 19:00 | 66.47 | 0 | 0 | 66.47 | 0 | 0 | 0 | 0 | 0
2025-06-11 20:00 | 65.01 | 0 | 0 | 65.01 | 0 | 0 | 0 | 0 | 0
2025-06-11 21:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 0 | 0 | 0
2025-06-11 22:00 | 58.35 | 0 | 0 | 58.35 | 0 | 0 | 0 | 0 | 0
2025-06-11 23:00 | 55.99 | 0 | 0 | 55.99 | 0 | 0 | 0 | 0 | 0
2025-06-12 | 52.73 | 0 | 0 | 52.73 | 0 | 0 | 0 | 0 | 0
2025-06-12 01:00 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 0 | 0 | 0
2025-06-12 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 0 | 0 | 0
2025-06-12 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0 | 0 | 0
2025-06-12 04:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0 | 0 | 0
2025-06-12 05:00 | 52.21 | 23.48 | 23.48 | 28.73 | 0 | 0 | 0 | 0 | 0
2025-06-12 06:00 | 53.46 | 71.72 | 53.46 | 0 | 0 | 0 | 0 | 18.25 | 0
2025-06-12 07:00 | 56.84 | 98.38 | 56.84 | 0 | 0 | 0 | 0 | 41.55 | 0
2025-06-12 08:00 | 61.06 | 106.83 | 61.06 | 0 | 0 | 0 | 0 | 45.78 | 0
2025-06-12 09:00 | 64.66 | 110.99 | 64.66 | 0 | 0 | 0 | 0 | 46.33 | 0
2025-06-12 10:00 | 70.06 | 115.39 | 70.06 | 0 | 0 | 0 | 0 | 45.33 | 0
2025-06-12 11:00 | 73.99 | 113.4 | 73.99 | 0 | 0 | 0 | 0 | 39.41 | 0
2025-06-12 12:00 | 78.35 | 113.32 | 78.35 | 0 | 0 | 0 | 0 | 34.97 | 0
2025-06-12 13:00 | 81.6 | 111.26 | 81.6 | 0 | 0 | 0 | 0 | 29.66 | 0
2025-06-12 14:00 | 84.38 | 111.27 | 84.38 | 0 | 0 | 0 | 0 | 26.89 | 0
2025-06-12 15:00 | 85.55 | 109.98 | 85.55 | 0 | 0 | 0 | 0 | 24.43 | 0
2025-06-12 16:00 | 84.12 | 108.16 | 84.12 | 0 | 0 | 0 | 0 | 24.05 | 0
2025-06-12 17:00 | 81.36 | 86.01 | 81.36 | 0 | 0 | 0 | 0 | 4.65 | 0
2025-06-12 18:00 | 78.04 | 60.74 | 60.74 | 17.3 | 0 | 0 | 0 | 0 | 0
2025-06-12 19:00 | 74.52 | 14.14 | 14.14 | 60.38 | 0 | 0 | 0 | 0 | 0
2025-06-12 20:00 | 70.54 | 0 | 0 | 70.54 | 0 | 0 | 0 | 0 | 0
2025-06-12 21:00 | 65.09 | 0 | 0 | 65.09 | 0 | 0 | 0 | 0 | 0
2025-06-12 22:00 | 60.3 | 0 | 0 | 60.3 | 0 | 0 | 0 | 0 | 0
2025-06-12 23:00 | 57.07 | 0 | 0 | 57.07 | 0 | 0 | 0 | 0 | 0
2025-06-13 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 0 | 0 | 0
2025-06-13 01:00 | 51.3 | 0 | 0 | 51.3 | 0 | 0 | 0 | 0 | 0
2025-06-13 02:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0 | 0 | 0
2025-06-13 03:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 0 | 0 | 0
2025-06-13 04:00 | 48.96 | 0 | 0 | 48.96 | 0 | 0 | 0 | 0 | 0
2025-06-13 05:00 | 51.89 | 22.46 | 22.46 | 29.43 | 0 | 0 | 0 | 0 | 0
2025-06-13 06:00 | 53.23 | 19.46 | 19.46 | 33.77 | 0 | 0 | 0 | 0 | 0
2025-06-13 07:00 | 55.75 | 53.32 | 53.32 | 2.44 | 0 | 0 | 0 | 0 | 0
2025-06-13 08:00 | 59.61 | 23.47 | 23.47 | 36.14 | 0 | 0 | 0 | 0 | 0
2025-06-13 09:00 | 61.3 | 63.45 | 61.3 | 0 | 0 | 0 | 0 | 2.15 | 0
2025-06-13 10:00 | 64.08 | 92.13 | 64.08 | 0 | 0 | 0 | 0 | 28.05 | 0
2025-06-13 11:00 | 66.81 | 86.6 | 66.81 | 0 | 0 | 0 | 0 | 19.79 | 0
2025-06-13 12:00 | 69.11 | 16.89 | 16.89 | 52.22 | 0 | 0 | 0 | 0 | 0
2025-06-13 13:00 | 70.18 | 76.48 | 70.18 | 0 | 0 | 0 | 0 | 6.31 | 0
2025-06-13 14:00 | 70.53 | 76.07 | 70.53 | 0 | 0 | 0 | 0 | 5.54 | 0
2025-06-13 15:00 | 71.19 | 41.92 | 41.92 | 29.28 | 0 | 0 | 0 | 0 | 0
2025-06-13 16:00 | 71.96 | 49.33 | 49.33 | 22.63 | 0 | 0 | 0 | 0 | 0
2025-06-13 17:00 | 70.44 | 5.93 | 5.93 | 64.5 | 0 | 0 | 0 | 0 | 0
2025-06-13 18:00 | 69.13 | 59.11 | 59.11 | 10.02 | 0 | 0 | 0 | 0 | 0
2025-06-13 19:00 | 66.75 | 1.14 | 1.14 | 65.6 | 0 | 0 | 0 | 0 | 0
2025-06-13 20:00 | 64.09 | 0 | 0 | 64.09 | 0 | 0 | 0 | 0 | 0
2025-06-13 21:00 | 62.49 | 0 | 0 | 62.49 | 0 | 0 | 0 | 0 | 0
2025-06-13 22:00 | 58.67 | 0 | 0 | 58.67 | 0 | 0 | 0 | 0 | 0
2025-06-13 23:00 | 55.74 | 0 | 0 | 55.74 | 0 | 0 | 0 | 0 | 0
2025-06-14 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 0 | 0 | 0
2025-06-14 01:00 | 51.26 | 0 | 0 | 51.26 | 0 | 0 | 0 | 0 | 0
2025-06-14 02:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 0 | 0 | 0
2025-06-14 03:00 | 49.88 | 0 | 0 | 49.88 | 0 | 0 | 0 | 0 | 0
2025-06-14 04:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 0 | 0 | 0
2025-06-14 05:00 | 51.75 | 27.39 | 27.39 | 24.35 | 0 | 0 | 0 | 0 | 0
2025-06-14 06:00 | 54.77 | 65.14 | 54.77 | 0 | 0 | 0 | 0 | 10.36 | 0
2025-06-14 07:00 | 56.72 | 96.14 | 56.72 | 0 | 0 | 0 | 0 | 39.42 | 0
2025-06-14 08:00 | 58.76 | 86.57 | 58.76 | 0 | 0 | 0 | 0 | 27.8 | 0
2025-06-14 09:00 | 63.88 | 60.74 | 60.74 | 3.15 | 0 | 0 | 0 | 0 | 0
2025-06-14 10:00 | 67.64 | 71.66 | 67.64 | 0 | 0 | 0 | 0 | 4.02 | 0
2025-06-14 11:00 | 71.39 | 123.15 | 71.39 | 0 | 0 | 0 | 0 | 51.76 | 0
2025-06-14 12:00 | 74.8 | 104.69 | 74.8 | 0 | 0 | 0 | 0 | 29.89 | 0
2025-06-14 13:00 | 77.26 | 60.72 | 60.72 | 16.55 | 0 | 0 | 0 | 0 | 0
2025-06-14 14:00 | 78.91 | 63.53 | 63.53 | 15.38 | 0 | 0 | 0 | 0 | 0
2025-06-14 15:00 | 79.81 | 104.97 | 79.81 | 0 | 0 | 0 | 0 | 25.16 | 0
2025-06-14 16:00 | 78.66 | 122.41 | 78.66 | 0 | 0 | 0 | 0 | 43.74 | 0
2025-06-14 17:00 | 76.8 | 111.53 | 76.8 | 0 | 0 | 0 | 0 | 34.73 | 0
2025-06-14 18:00 | 76.19 | 85.52 | 76.19 | 0 | 0 | 0 | 0 | 9.32 | 0
2025-06-14 19:00 | 71.01 | 18.72 | 18.72 | 52.29 | 0 | 0 | 0 | 0 | 0
2025-06-14 20:00 | 67.67 | 0 | 0 | 67.67 | 0 | 0 | 0 | 0 | 0
2025-06-14 21:00 | 62.97 | 0 | 0 | 62.97 | 0 | 0 | 0 | 0 | 0
2025-06-14 22:00 | 60.01 | 0 | 0 | 60.01 | 0 | 0 | 0 | 0 | 0
2025-06-14 23:00 | 56.09 | 0 | 0 | 56.09 | 0 | 0 | 0 | 0 | 0
2025-06-15 | 53.43 | 0 | 0 | 53.43 | 0 | 0 | 0 | 0 | 0
2025-06-15 01:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0 | 0 | 0
2025-06-15 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 0 | 0 | 0
2025-06-15 03:00 | 50.24 | 0 | 0 | 50.24 | 0 | 0 | 0 | 0 | 0
2025-06-15 04:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0 | 0 | 0
2025-06-15 05:00 | 52.59 | 24.19 | 24.19 | 28.4 | 0 | 0 | 0 | 0 | 0
2025-06-15 06:00 | 53.06 | 47.97 | 47.97 | 5.09 | 0 | 0 | 0 | 0 | 0
2025-06-15 07:00 | 56.93 | 94.91 | 56.93 | 0 | 0 | 0 | 0 | 37.99 | 0
2025-06-15 08:00 | 59.48 | 68.88 | 59.48 | 0 | 0 | 0 | 0 | 9.4 | 0
2025-06-15 09:00 | 62.13 | 105.04 | 62.13 | 0 | 0 | 0 | 0 | 42.91 | 0
2025-06-15 10:00 | 64.15 | 90.88 | 64.15 | 0 | 0 | 0 | 0 | 26.74 | 0
2025-06-15 11:00 | 67.07 | 103.41 | 67.07 | 0 | 0 | 0 | 0 | 36.34 | 0
2025-06-15 12:00 | 68.74 | 105.96 | 68.74 | 0 | 0 | 0 | 0 | 37.22 | 0
2025-06-15 13:00 | 70.45 | 112.26 | 70.45 | 0 | 0 | 0 | 0 | 41.81 | 0
2025-06-15 14:00 | 71.2 | 106.18 | 71.2 | 0 | 0 | 0 | 0 | 34.98 | 0
2025-06-15 15:00 | 70.6 | 81.22 | 70.6 | 0 | 0 | 0 | 0 | 10.62 | 0
2025-06-15 16:00 | 71.88 | 80.12 | 71.88 | 0 | 0 | 0 | 0 | 8.24 | 0
2025-06-15 17:00 | 70.39 | 67.17 | 67.17 | 3.22 | 0 | 0 | 0 | 0 | 0
2025-06-15 18:00 | 68.73 | 56.61 | 56.61 | 12.12 | 0 | 0 | 0 | 0 | 0
2025-06-15 19:00 | 66.71 | 20.37 | 20.37 | 46.34 | 0 | 0 | 0 | 0 | 0
2025-06-15 20:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 0 | 0 | 0
2025-06-15 21:00 | 61.39 | 0 | 0 | 61.39 | 0 | 0 | 0 | 0 | 0
2025-06-15 22:00 | 57.84 | 0 | 0 | 57.84 | 0 | 0 | 0 | 0 | 0
2025-06-15 23:00 | 56.37 | 0 | 0 | 56.37 | 0 | 0 | 0 | 0 | 0
2025-06-16 | 54.2 | 0 | 0 | 54.2 | 0 | 0 | 0 | 0 | 0
2025-06-16 01:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 0 | 0 | 0
2025-06-16 02:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 0 | 0 | 0
2025-06-16 03:00 | 50.08 | 0 | 0 | 50.08 | 0 | 0 | 0 | 0 | 0
2025-06-16 04:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0 | 0 | 0
2025-06-16 05:00 | 51.29 | 33.48 | 33.48 | 17.81 | 0 | 0 | 0 | 0 | 0
2025-06-16 06:00 | 53.56 | 108.26 | 53.56 | 0 | 0 | 0 | 0 | 54.69 | 0
2025-06-16 07:00 | 57.23 | 128.84 | 57.23 | 0 | 0 | 0 | 0 | 71.61 | 0
2025-06-16 08:00 | 60.08 | 137.15 | 60.08 | 0 | 0 | 0 | 0 | 77.06 | 0
2025-06-16 09:00 | 63.9 | 134.32 | 63.9 | 0 | 0 | 0 | 0 | 70.42 | 0
2025-06-16 10:00 | 69.1 | 121.64 | 69.1 | 0 | 0 | 0 | 0 | 52.54 | 0
2025-06-16 11:00 | 72.15 | 99.58 | 72.15 | 0 | 0 | 0 | 0 | 27.43 | 0
2025-06-16 12:00 | 75.56 | 86.85 | 75.56 | 0 | 0 | 0 | 0 | 11.29 | 0
2025-06-16 13:00 | 77.89 | 81.28 | 77.89 | 0 | 0 | 0 | 0 | 3.39 | 0
2025-06-16 14:00 | 79.49 | 67.11 | 67.11 | 12.38 | 0 | 0 | 0 | 0 | 0
2025-06-16 15:00 | 79.28 | 38.57 | 38.57 | 40.72 | 0 | 0 | 0 | 0 | 0
2025-06-16 16:00 | 80.27 | 29.7 | 29.7 | 50.57 | 0 | 0 | 0 | 0 | 0
2025-06-16 17:00 | 78.3 | 16.19 | 16.19 | 62.11 | 0 | 0 | 0 | 0 | 0
2025-06-16 18:00 | 75.3 | 7.39 | 7.39 | 67.91 | 0 | 0 | 0 | 0 | 0
2025-06-16 19:00 | 71.91 | 0 | 0 | 71.9 | 0 | 0 | 0 | 0 | 0
2025-06-16 20:00 | 68.49 | 0 | 0 | 68.49 | 0 | 0 | 0 | 0 | 0
2025-06-16 21:00 | 63.34 | 0 | 0 | 63.34 | 0 | 0 | 0 | 0 | 0
2025-06-16 22:00 | 59.97 | 0 | 0 | 59.97 | 0 | 0 | 0 | 0 | 0
2025-06-16 23:00 | 56.24 | 0 | 0 | 56.24 | 0 | 0 | 0 | 0 | 0
2025-06-17 | 54.86 | 0 | 0 | 54.86 | 0 | 0 | 0 | 0 | 0
2025-06-17 01:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0 | 0 | 0
2025-06-17 02:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 0 | 0 | 0
2025-06-17 03:00 | 49.36 | 0 | 0 | 49.36 | 0 | 0 | 0 | 0 | 0
2025-06-17 04:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 0 | 0 | 0
2025-06-17 05:00 | 51.64 | 2.53 | 2.53 | 49.11 | 0 | 0 | 0 | 0 | 0
2025-06-17 06:00 | 53.32 | 7.82 | 7.82 | 45.5 | 0 | 0 | 0 | 0 | 0
2025-06-17 07:00 | 57.73 | 54.5 | 54.5 | 3.23 | 0 | 0 | 0 | 0 | 0
2025-06-17 08:00 | 60.19 | 65.83 | 60.19 | 0 | 0 | 0 | 0 | 5.63 | 0
2025-06-17 09:00 | 63.86 | 91.73 | 63.86 | 0 | 0 | 0 | 0 | 27.88 | 0
2025-06-17 10:00 | 66.91 | 71.58 | 66.91 | 0 | 0 | 0 | 0 | 4.66 | 0
2025-06-17 11:00 | 71.07 | 61.89 | 61.89 | 9.18 | 0 | 0 | 0 | 0 | 0
2025-06-17 12:00 | 73.52 | 58.06 | 58.06 | 15.46 | 0 | 0 | 0 | 0 | 0
2025-06-17 13:00 | 75.9 | 36.21 | 36.21 | 39.69 | 0 | 0 | 0 | 0 | 0
2025-06-17 14:00 | 77.82 | 34.42 | 34.42 | 43.4 | 0 | 0 | 0 | 0 | 0
2025-06-17 15:00 | 77.21 | 50.88 | 50.88 | 26.33 | 0 | 0 | 0 | 0 | 0
2025-06-17 16:00 | 78.32 | 110.84 | 78.32 | 0 | 0 | 0 | 0 | 32.52 | 0
2025-06-17 17:00 | 76.13 | 58.92 | 58.92 | 17.21 | 0 | 0 | 0 | 0 | 0
2025-06-17 18:00 | 74.35 | 74.35 | 74.35 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 19:00 | 70.17 | 20.47 | 20.47 | 49.7 | 0 | 0 | 0 | 0 | 0
2025-06-17 20:00 | 66.8 | 0 | 0 | 66.8 | 0 | 0 | 0 | 0 | 0
2025-06-17 21:00 | 63.04 | 0 | 0 | 63.04 | 0 | 0 | 0 | 0 | 0
2025-06-17 22:00 | 60.16 | 0 | 0 | 60.16 | 0 | 0 | 0 | 0 | 0
2025-06-17 23:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 0 | 0 | 0
2025-06-18 | 53.79 | 0 | 0 | 53.79 | 0 | 0 | 0 | 0 | 0
2025-06-18 01:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 0 | 0 | 0
2025-06-18 02:00 | 50.01 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0
2025-06-18 03:00 | 50.17 | 0 | 0 | 50.17 | 0 | 0 | 0 | 0 | 0
2025-06-18 04:00 | 50.41 | 0 | 0 | 50.41 | 0 | 0 | 0 | 0 | 0
2025-06-18 05:00 | 51.61 | 24.19 | 24.19 | 27.42 | 0 | 0 | 0 | 0 | 0
2025-06-18 06:00 | 54.79 | 82.69 | 54.79 | 0 | 0 | 0 | 0 | 27.9 | 0
2025-06-18 07:00 | 56.66 | 89.71 | 56.66 | 0 | 0 | 0 | 0 | 33.05 | 0
2025-06-18 08:00 | 60.44 | 76.48 | 60.44 | 0 | 0 | 0 | 0 | 16.03 | 0
2025-06-18 09:00 | 62.85 | 126.23 | 62.85 | 0 | 0 | 0 | 0 | 63.38 | 0
2025-06-18 10:00 | 66.52 | 114.39 | 66.52 | 0 | 0 | 0 | 0 | 47.87 | 0
2025-06-18 11:00 | 69.41 | 113.42 | 69.41 | 0 | 0 | 0 | 0 | 44 | 0
2025-06-18 12:00 | 71.18 | 91.99 | 71.18 | 0 | 0 | 0 | 0 | 20.82 | 0
2025-06-18 13:00 | 74.72 | 97.81 | 74.72 | 0 | 0 | 0 | 0 | 23.09 | 0
2025-06-18 14:00 | 75.18 | 74.44 | 74.44 | 0.74 | 0 | 0 | 0 | 0 | 0
2025-06-18 15:00 | 76.04 | 49.89 | 49.89 | 26.15 | 0 | 0 | 0 | 0 | 0
2025-06-18 16:00 | 74.87 | 35.37 | 35.37 | 39.5 | 0 | 0 | 0 | 0 | 0
2025-06-18 17:00 | 73.92 | 26.15 | 26.15 | 47.77 | 0 | 0 | 0 | 0 | 0
2025-06-18 18:00 | 71.6 | 1.53 | 1.53 | 70.07 | 0 | 0 | 0 | 0 | 0
2025-06-18 19:00 | 70.06 | 0.26 | 0.26 | 69.8 | 0 | 0 | 0 | 0 | 0
2025-06-18 20:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 0 | 0 | 0
2025-06-18 21:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 0 | 0 | 0
2025-06-18 22:00 | 60.49 | 0 | 0 | 60.49 | 0 | 0 | 0 | 0 | 0
2025-06-18 23:00 | 57.28 | 0 | 0 | 57.28 | 0 | 0 | 0 | 0 | 0
2025-06-19 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 0 | 0 | 0
2025-06-19 01:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 0 | 0 | 0
2025-06-19 02:00 | 50.37 | 0 | 0 | 50.37 | 0 | 0 | 0 | 0 | 0
2025-06-19 03:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 0 | 0 | 0
2025-06-19 04:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0
2025-06-19 05:00 | 52.12 | 11.85 | 11.85 | 40.27 | 0 | 0 | 0 | 0 | 0
2025-06-19 06:00 | 53.43 | 55.3 | 53.43 | 0 | 0 | 0 | 0 | 1.87 | 0
2025-06-19 07:00 | 56.74 | 90.86 | 56.74 | 0 | 0 | 0 | 0 | 34.11 | 0
2025-06-19 08:00 | 59.25 | 112.68 | 59.25 | 0 | 0 | 0 | 0 | 53.43 | 0
2025-06-19 09:00 | 63.36 | 113.8 | 63.36 | 0 | 0 | 0 | 0 | 50.44 | 0
2025-06-19 10:00 | 65.93 | 109.24 | 65.93 | 0 | 0 | 0 | 0 | 43.3 | 0
2025-06-19 11:00 | 70.17 | 103.82 | 70.17 | 0 | 0 | 0 | 0 | 33.65 | 0
2025-06-19 12:00 | 72.78 | 101.62 | 72.78 | 0 | 0 | 0 | 0 | 28.84 | 0
2025-06-19 13:00 | 75.61 | 103.29 | 75.61 | 0 | 0 | 0 | 0 | 27.68 | 0
2025-06-19 14:00 | 76.38 | 98.56 | 76.38 | 0 | 0 | 0 | 0 | 22.18 | 0
2025-06-19 15:00 | 76.19 | 90.87 | 76.19 | 0 | 0 | 0 | 0 | 14.68 | 0
2025-06-19 16:00 | 76.37 | 78.14 | 76.37 | 0 | 0 | 0 | 0 | 1.77 | 0
2025-06-19 17:00 | 73.96 | 54.17 | 54.17 | 19.79 | 0 | 0 | 0 | 0 | 0
2025-06-19 18:00 | 72.11 | 33.87 | 33.87 | 38.25 | 0 | 0 | 0 | 0 | 0
2025-06-19 19:00 | 70.07 | 8.45 | 8.45 | 61.62 | 0 | 0 | 0 | 0 | 0
2025-06-19 20:00 | 65.68 | 0 | 0 | 65.68 | 0 | 0 | 0 | 0 | 0
2025-06-19 21:00 | 63.36 | 0 | 0 | 63.36 | 0 | 0 | 0 | 0 | 0
2025-06-19 22:00 | 59.49 | 0 | 0 | 59.49 | 0 | 0 | 0 | 0 | 0
2025-06-19 23:00 | 56.89 | 0 | 0 | 56.89 | 0 | 0 | 0 | 0 | 0
2025-06-20 | 53.61 | 0 | 0 | 53.61 | 0 | 0 | 0 | 0 | 0
2025-06-20 01:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0 | 0 | 0
2025-06-20 02:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 0 | 0 | 0
2025-06-20 03:00 | 51.05 | 0 | 0 | 51.05 | 0 | 0 | 0 | 0 | 0
2025-06-20 04:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 0 | 0 | 0
2025-06-20 05:00 | 51.72 | 25.01 | 25.01 | 26.71 | 0 | 0 | 0 | 0 | 0
2025-06-20 06:00 | 54.03 | 81.65 | 54.03 | 0 | 0 | 0 | 0 | 27.63 | 0
2025-06-20 07:00 | 56.09 | 108.1 | 56.09 | 0 | 0 | 0 | 0 | 52.02 | 0
2025-06-20 08:00 | 59.91 | 120.57 | 59.91 | 0 | 0 | 0 | 0 | 60.66 | 0
2025-06-20 09:00 | 63.08 | 124.42 | 63.08 | 0 | 0 | 0 | 0 | 61.34 | 0
2025-06-20 10:00 | 66.98 | 124.96 | 66.98 | 0 | 0 | 0 | 0 | 57.98 | 0
2025-06-20 11:00 | 68.1 | 123.57 | 68.1 | 0 | 0 | 0 | 0 | 55.47 | 0
2025-06-20 12:00 | 70.5 | 122.57 | 70.5 | 0 | 0 | 0 | 0 | 52.07 | 0
2025-06-20 13:00 | 72 | 109.1 | 72 | 0 | 0 | 0 | 0 | 37.1 | 0
2025-06-20 14:00 | 73.42 | 42.5 | 42.5 | 30.92 | 0 | 0 | 0 | 0 | 0
2025-06-20 15:00 | 73.85 | 47.09 | 47.09 | 26.76 | 0 | 0 | 0 | 0 | 0
2025-06-20 16:00 | 73.29 | 41.03 | 41.03 | 32.25 | 0 | 0 | 0 | 0 | 0
2025-06-20 17:00 | 72.83 | 98.21 | 72.83 | 0 | 0 | 0 | 0 | 25.38 | 0
2025-06-20 18:00 | 70.32 | 74.96 | 70.32 | 0 | 0 | 0 | 0 | 4.64 | 0
2025-06-20 19:00 | 68.91 | 17.57 | 17.57 | 51.34 | 0 | 0 | 0 | 0 | 0
2025-06-20 20:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 0 | 0 | 0
2025-06-20 21:00 | 62.77 | 0 | 0 | 62.77 | 0 | 0 | 0 | 0 | 0
2025-06-20 22:00 | 59.55 | 0 | 0 | 59.55 | 0 | 0 | 0 | 0 | 0
2025-06-20 23:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 0 | 0 | 0
2025-06-21 | 53.94 | 0 | 0 | 53.94 | 0 | 0 | 0 | 0 | 0
2025-06-21 01:00 | 52.35 | 0 | 0 | 52.35 | 0 | 0 | 0 | 0 | 0
2025-06-21 02:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 0 | 0 | 0
2025-06-21 03:00 | 51.31 | 0 | 0 | 51.31 | 0 | 0 | 0 | 0 | 0
2025-06-21 04:00 | 51.31 | 0 | 0 | 51.31 | 0 | 0 | 0 | 0 | 0
2025-06-21 05:00 | 51.87 | 13.05 | 13.05 | 38.82 | 0 | 0 | 0 | 0 | 0
2025-06-21 06:00 | 54.61 | 61.58 | 54.61 | 0 | 0 | 0 | 0 | 6.98 | 0
2025-06-21 07:00 | 57.31 | 96.5 | 57.31 | 0 | 0 | 0 | 0 | 39.18 | 0
2025-06-21 08:00 | 60.28 | 109.14 | 60.28 | 0 | 0 | 0 | 0 | 48.86 | 0
2025-06-21 09:00 | 64.59 | 119.79 | 64.59 | 0 | 0 | 0 | 0 | 55.2 | 0
2025-06-21 10:00 | 68.16 | 119.38 | 68.16 | 0 | 0 | 0 | 0 | 51.22 | 0
2025-06-21 11:00 | 71.62 | 109.79 | 71.62 | 0 | 0 | 0 | 0 | 38.17 | 0
2025-06-21 12:00 | 74.59 | 94.08 | 74.59 | 0 | 0 | 0 | 0 | 19.49 | 0
2025-06-21 13:00 | 77.24 | 106.55 | 77.24 | 0 | 0 | 0 | 0 | 29.31 | 0
2025-06-21 14:00 | 78.67 | 122.68 | 78.67 | 0 | 0 | 0 | 0 | 44.02 | 0
2025-06-21 15:00 | 79.11 | 126.38 | 79.11 | 0 | 0 | 0 | 0 | 47.27 | 0
2025-06-21 16:00 | 78.23 | 121.83 | 78.23 | 0 | 0 | 0 | 0 | 43.6 | 0
2025-06-21 17:00 | 77.87 | 110.23 | 77.87 | 0 | 0 | 0 | 0 | 32.36 | 0
2025-06-21 18:00 | 74.09 | 84.98 | 74.09 | 0 | 0 | 0 | 0 | 10.88 | 0
2025-06-21 19:00 | 71.73 | 20.53 | 20.53 | 51.2 | 0 | 0 | 0 | 0 | 0
2025-06-21 20:00 | 67.8 | 0 | 0 | 67.8 | 0 | 0 | 0 | 0 | 0
2025-06-21 21:00 | 65.1 | 0 | 0 | 65.1 | 0 | 0 | 0 | 0 | 0
2025-06-21 22:00 | 60.09 | 0 | 0 | 60.09 | 0 | 0 | 0 | 0 | 0
2025-06-21 23:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 0 | 0 | 0
2025-06-22 | 53.86 | 0 | 0 | 53.86 | 0 | 0 | 0 | 0 | 0
2025-06-22 01:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 0 | 0 | 0
2025-06-22 02:00 | 50.26 | 0 | 0 | 50.26 | 0 | 0 | 0 | 0 | 0
2025-06-22 03:00 | 50.25 | 0 | 0 | 50.25 | 0 | 0 | 0 | 0 | 0
2025-06-22 04:00 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 0 | 0 | 0
2025-06-22 05:00 | 52.38 | 8.82 | 8.82 | 43.56 | 0 | 0 | 0 | 0 | 0
2025-06-22 06:00 | 54.09 | 49.29 | 49.29 | 4.81 | 0 | 0 | 0 | 0 | 0
2025-06-22 07:00 | 56.27 | 27.74 | 27.74 | 28.53 | 0 | 0 | 0 | 0 | 0
2025-06-22 08:00 | 60.6 | 62.99 | 60.6 | 0 | 0 | 0 | 0 | 2.39 | 0
2025-06-22 09:00 | 62.61 | 92.17 | 62.61 | 0 | 0 | 0 | 0 | 29.56 | 0
2025-06-22 10:00 | 66.79 | 91.21 | 66.79 | 0 | 0 | 0 | 0 | 24.42 | 0
2025-06-22 11:00 | 68.89 | 97.39 | 68.89 | 0 | 0 | 0 | 0 | 28.5 | 0
2025-06-22 12:00 | 72.43 | 92.7 | 72.43 | 0 | 0 | 0 | 0 | 20.27 | 0
2025-06-22 13:00 | 73.81 | 96.58 | 73.81 | 0 | 0 | 0 | 0 | 22.77 | 0
2025-06-22 14:00 | 74.06 | 108.73 | 74.06 | 0 | 0 | 0 | 0 | 34.67 | 0
2025-06-22 15:00 | 74.48 | 79.6 | 74.48 | 0 | 0 | 0 | 0 | 5.12 | 0
2025-06-22 16:00 | 74.86 | 88.4 | 74.86 | 0 | 0 | 0 | 0 | 13.54 | 0
2025-06-22 17:00 | 73.31 | 63.14 | 63.14 | 10.17 | 0 | 0 | 0 | 0 | 0
2025-06-22 18:00 | 71.55 | 11.07 | 11.07 | 60.47 | 0 | 0 | 0 | 0 | 0
2025-06-22 19:00 | 69.87 | 2.67 | 2.67 | 67.2 | 0 | 0 | 0 | 0 | 0
2025-06-22 20:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 0 | 0 | 0
2025-06-22 21:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 0 | 0 | 0
2025-06-22 22:00 | 60.54 | 0 | 0 | 60.54 | 0 | 0 | 0 | 0 | 0
2025-06-22 23:00 | 57.41 | 0 | 0 | 57.41 | 0 | 0 | 0 | 0 | 0
2025-06-23 | 54.27 | 0 | 0 | 54.27 | 0 | 0 | 0 | 0 | 0
2025-06-23 01:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 0 | 0 | 0
2025-06-23 02:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0 | 0 | 0
2025-06-23 03:00 | 50.03 | 0 | 0 | 50.03 | 0 | 0 | 0 | 0 | 0
2025-06-23 04:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 0 | 0 | 0
2025-06-23 05:00 | 52.25 | 8.74 | 8.74 | 43.52 | 0 | 0 | 0 | 0 | 0
2025-06-23 06:00 | 54.38 | 39.08 | 39.08 | 15.3 | 0 | 0 | 0 | 0 | 0
2025-06-23 07:00 | 57.39 | 57.81 | 57.39 | 0 | 0 | 0 | 0 | 0.42 | 0
2025-06-23 08:00 | 59.06 | 61.35 | 59.06 | 0 | 0 | 0 | 0 | 2.29 | 0
2025-06-23 09:00 | 62.33 | 74.41 | 62.33 | 0 | 0 | 0 | 0 | 12.08 | 0
2025-06-23 10:00 | 65.14 | 108.2 | 65.14 | 0 | 0 | 0 | 0 | 43.05 | 0
2025-06-23 11:00 | 66.94 | 115.94 | 66.94 | 0 | 0 | 0 | 0 | 49 | 0
2025-06-23 12:00 | 69.79 | 116.05 | 69.79 | 0 | 0 | 0 | 0 | 46.25 | 0
2025-06-23 13:00 | 70.82 | 99.38 | 70.82 | 0 | 0 | 0 | 0 | 28.56 | 0
2025-06-23 14:00 | 71.28 | 97.38 | 71.28 | 0 | 0 | 0 | 0 | 26.1 | 0
2025-06-23 15:00 | 72.29 | 92.9 | 72.29 | 0 | 0 | 0 | 0 | 20.61 | 0
2025-06-23 16:00 | 70.38 | 55.51 | 55.51 | 14.88 | 0 | 0 | 0 | 0 | 0
2025-06-23 17:00 | 70.36 | 50.25 | 50.25 | 20.11 | 0 | 0 | 0 | 0 | 0
2025-06-23 18:00 | 69.26 | 20.26 | 20.26 | 49 | 0 | 0 | 0 | 0 | 0
2025-06-23 19:00 | 66.83 | 6.24 | 6.24 | 60.59 | 0 | 0 | 0 | 0 | 0
2025-06-23 20:00 | 65.2 | 0 | 0 | 65.2 | 0 | 0 | 0 | 0 | 0
2025-06-23 21:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 0 | 0 | 0
2025-06-23 22:00 | 60 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0
2025-06-23 23:00 | 57.4 | 0 | 0 | 57.4 | 0 | 0 | 0 | 0 | 0
2025-06-24 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 0 | 0 | 0
2025-06-24 01:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0 | 0 | 0
2025-06-24 02:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 0 | 0 | 0
2025-06-24 03:00 | 50.91 | 0 | 0 | 50.91 | 0 | 0 | 0 | 0 | 0
2025-06-24 04:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 0 | 0 | 0
2025-06-24 05:00 | 51.05 | 21.29 | 21.29 | 29.76 | 0 | 0 | 0 | 0 | 0
2025-06-24 06:00 | 55.04 | 73.65 | 55.04 | 0 | 0 | 0 | 0 | 18.61 | 0
2025-06-24 07:00 | 57.01 | 92.31 | 57.01 | 0 | 0 | 0 | 0 | 35.3 | 0
2025-06-24 08:00 | 59.31 | 102.51 | 59.31 | 0 | 0 | 0 | 0 | 43.2 | 0
2025-06-24 09:00 | 62.99 | 107.06 | 62.99 | 0 | 0 | 0 | 0 | 44.06 | 0
2025-06-24 10:00 | 64.73 | 103.39 | 64.73 | 0 | 0 | 0 | 0 | 38.66 | 0
2025-06-24 11:00 | 66.93 | 102.34 | 66.93 | 0 | 0 | 0 | 0 | 35.41 | 0
2025-06-24 12:00 | 69.21 | 103.38 | 69.21 | 0 | 0 | 0 | 0 | 34.17 | 0
2025-06-24 13:00 | 71.17 | 102.41 | 71.17 | 0 | 0 | 0 | 0 | 31.23 | 0
2025-06-24 14:00 | 71.84 | 106.34 | 71.84 | 0 | 0 | 0 | 0 | 34.5 | 0
2025-06-24 15:00 | 71.46 | 110.41 | 71.46 | 0 | 0 | 0 | 0 | 38.95 | 0
2025-06-24 16:00 | 71.26 | 96.48 | 71.26 | 0 | 0 | 0 | 0 | 25.22 | 0
2025-06-24 17:00 | 70.68 | 77.93 | 70.68 | 0 | 0 | 0 | 0 | 7.25 | 0
2025-06-24 18:00 | 68.4 | 64.02 | 64.02 | 4.38 | 0 | 0 | 0 | 0 | 0
2025-06-24 19:00 | 67.6 | 12.92 | 12.92 | 54.68 | 0 | 0 | 0 | 0 | 0
2025-06-24 20:00 | 64.7 | 0 | 0 | 64.7 | 0 | 0 | 0 | 0 | 0
2025-06-24 21:00 | 62.65 | 0 | 0 | 62.65 | 0 | 0 | 0 | 0 | 0
2025-06-24 22:00 | 59.6 | 0 | 0 | 59.6 | 0 | 0 | 0 | 0 | 0
2025-06-24 23:00 | 57.2 | 0 | 0 | 57.2 | 0 | 0 | 0 | 0 | 0
2025-06-25 | 54.71 | 0 | 0 | 54.71 | 0 | 0 | 0 | 0 | 0
2025-06-25 01:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 0 | 0 | 0
2025-06-25 02:00 | 51.24 | 0 | 0 | 51.24 | 0 | 0 | 0 | 0 | 0
2025-06-25 03:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 0 | 0 | 0
2025-06-25 04:00 | 51.37 | 0 | 0 | 51.37 | 0 | 0 | 0 | 0 | 0
2025-06-25 05:00 | 52.44 | 2.55 | 2.55 | 49.9 | 0 | 0 | 0 | 0 | 0
2025-06-25 06:00 | 55.47 | 9.48 | 9.48 | 45.99 | 0 | 0 | 0 | 0 | 0
2025-06-25 07:00 | 57.63 | 22.43 | 22.43 | 35.19 | 0 | 0 | 0 | 0 | 0
2025-06-25 08:00 | 61 | 30.7 | 30.7 | 30.3 | 0 | 0 | 0 | 0 | 0
2025-06-25 09:00 | 64.88 | 36.5 | 36.5 | 28.38 | 0 | 0 | 0 | 0 | 0
2025-06-25 10:00 | 68.14 | 38.23 | 38.23 | 29.91 | 0 | 0 | 0 | 0 | 0
2025-06-25 11:00 | 70.9 | 40.85 | 40.85 | 30.05 | 0 | 0 | 0 | 0 | 0
2025-06-25 12:00 | 73.06 | 59.97 | 59.97 | 13.08 | 0 | 0 | 0 | 0 | 0
2025-06-25 13:00 | 76.3 | 55.71 | 55.71 | 20.58 | 0 | 0 | 0 | 0 | 0
2025-06-25 14:00 | 78.34 | 45.82 | 45.82 | 32.52 | 0 | 0 | 0 | 0 | 0
2025-06-25 15:00 | 78.27 | 82.1 | 78.27 | 0 | 0 | 0 | 0 | 3.83 | 0
2025-06-25 16:00 | 78.36 | 66 | 66 | 12.36 | 0 | 0 | 0 | 0 | 0
2025-06-25 17:00 | 76.61 | 70.2 | 70.2 | 6.41 | 0 | 0 | 0 | 0 | 0
2025-06-25 18:00 | 74.92 | 80.9 | 74.92 | 0 | 0 | 0 | 0 | 5.98 | 0
2025-06-25 19:00 | 71.2 | 24.3 | 24.3 | 46.9 | 0 | 0 | 0 | 0 | 0
2025-06-25 20:00 | 68.2 | 0 | 0 | 68.2 | 0 | 0 | 0 | 0 | 0
2025-06-25 21:00 | 64.61 | 0 | 0 | 64.61 | 0 | 0 | 0 | 0 | 0
2025-06-25 22:00 | 61.53 | 0 | 0 | 61.53 | 0 | 0 | 0 | 0 | 0
2025-06-25 23:00 | 56.62 | 0 | 0 | 56.62 | 0 | 0 | 0 | 0 | 0
2025-06-26 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 0 | 0 | 0
2025-06-26 01:00 | 53.02 | 0 | 0 | 53.02 | 0 | 0 | 0 | 0 | 0
2025-06-26 02:00 | 51.99 | 0 | 0 | 51.99 | 0 | 0 | 0 | 0 | 0
2025-06-26 03:00 | 50.87 | 0 | 0 | 50.87 | 0 | 0 | 0 | 0 | 0
2025-06-26 04:00 | 51.07 | 0 | 0 | 51.07 | 0 | 0 | 0 | 0 | 0
2025-06-26 05:00 | 52.97 | 3.21 | 3.21 | 49.76 | 0 | 0 | 0 | 0 | 0
2025-06-26 06:00 | 55.31 | 13.27 | 13.27 | 42.03 | 0 | 0 | 0 | 0 | 0
2025-06-26 07:00 | 57.8 | 24.88 | 24.88 | 32.93 | 0 | 0 | 0 | 0 | 0
2025-06-26 08:00 | 61.98 | 41.01 | 41.01 | 20.97 | 0 | 0 | 0 | 0 | 0
2025-06-26 09:00 | 66.77 | 46.1 | 46.1 | 20.66 | 0 | 0 | 0 | 0 | 0
2025-06-26 10:00 | 71.74 | 59.35 | 59.35 | 12.39 | 0 | 0 | 0 | 0 | 0
2025-06-26 11:00 | 75.7 | 73.27 | 73.27 | 2.43 | 0 | 0 | 0 | 0 | 0
2025-06-26 12:00 | 79.42 | 55.26 | 55.26 | 24.16 | 0 | 0 | 0 | 0 | 0
2025-06-26 13:00 | 82.61 | 45.37 | 45.37 | 37.24 | 0 | 0 | 0 | 0 | 0
2025-06-26 14:00 | 85 | 52.88 | 52.88 | 32.12 | 0 | 0 | 0 | 0 | 0
2025-06-26 15:00 | 85.38 | 42.62 | 42.62 | 42.77 | 0 | 0 | 0 | 0 | 0
2025-06-26 16:00 | 84.82 | 21.94 | 21.94 | 62.88 | 0 | 0 | 0 | 0 | 0
2025-06-26 17:00 | 82.11 | 12.1 | 12.1 | 70.01 | 0 | 0 | 0 | 0 | 0
2025-06-26 18:00 | 80.05 | 5.22 | 5.22 | 74.83 | 0 | 0 | 0 | 0 | 0
2025-06-26 19:00 | 74.76 | 0 | 0 | 74.76 | 0 | 0 | 0 | 0 | 0
2025-06-26 20:00 | 70.58 | 0 | 0 | 70.58 | 0 | 0 | 0 | 0 | 0
2025-06-26 21:00 | 66.22 | 0 | 0 | 66.22 | 0 | 0 | 0 | 0 | 0
2025-06-26 22:00 | 62.81 | 0 | 0 | 62.81 | 0 | 0 | 0 | 0 | 0
2025-06-26 23:00 | 57.77 | 0 | 0 | 57.77 | 0 | 0 | 0 | 0 | 0
2025-06-27 | 54.46 | 0 | 0 | 54.46 | 0 | 0 | 0 | 0 | 0
2025-06-27 01:00 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 0 | 0 | 0
2025-06-27 02:00 | 52.1 | 0 | 0 | 52.1 | 0 | 0 | 0 | 0 | 0
2025-06-27 03:00 | 49.41 | 0 | 0 | 49.41 | 0 | 0 | 0 | 0 | 0
2025-06-27 04:00 | 50.77 | 0 | 0 | 50.77 | 0 | 0 | 0 | 0 | 0
2025-06-27 05:00 | 54 | 30.67 | 30.67 | 23.32 | 0 | 0 | 0 | 0 | 0
2025-06-27 06:00 | 55.09 | 89.48 | 55.09 | 0 | 0 | 0 | 0 | 34.39 | 0
2025-06-27 07:00 | 57.08 | 111.4 | 57.08 | 0 | 0 | 0 | 0 | 54.32 | 0
2025-06-27 08:00 | 60.94 | 119.75 | 60.94 | 0 | 0 | 0 | 0 | 58.81 | 0
2025-06-27 09:00 | 64.59 | 120.52 | 64.59 | 0 | 0 | 0 | 0 | 55.93 | 0
2025-06-27 10:00 | 68.6 | 120.22 | 68.6 | 0 | 0 | 0 | 0 | 51.62 | 0
2025-06-27 11:00 | 72.5 | 117.71 | 72.5 | 0 | 0 | 0 | 0 | 45.21 | 0
2025-06-27 12:00 | 74.71 | 115.41 | 74.71 | 0 | 0 | 0 | 0 | 40.7 | 0
2025-06-27 13:00 | 76.51 | 116.03 | 76.51 | 0 | 0 | 0 | 0 | 39.53 | 0
2025-06-27 14:00 | 78.6 | 116.62 | 78.6 | 0 | 0 | 0 | 0 | 38.03 | 0
2025-06-27 15:00 | 78.34 | 116.12 | 78.34 | 0 | 0 | 0 | 0 | 37.77 | 0
2025-06-27 16:00 | 77.69 | 113.85 | 77.69 | 0 | 0 | 0 | 0 | 36.16 | 0
2025-06-27 17:00 | 75.9 | 100.84 | 75.9 | 0 | 0 | 0 | 0 | 24.95 | 0
2025-06-27 18:00 | 73.73 | 78.94 | 73.73 | 0 | 0 | 0 | 0 | 5.21 | 0
2025-06-27 19:00 | 71.13 | 20.66 | 20.66 | 50.47 | 0 | 0 | 0 | 0 | 0
2025-06-27 20:00 | 67.59 | 0 | 0 | 67.59 | 0 | 0 | 0 | 0 | 0
2025-06-27 21:00 | 64.71 | 0 | 0 | 64.71 | 0 | 0 | 0 | 0 | 0
2025-06-27 22:00 | 60.36 | 0 | 0 | 60.36 | 0 | 0 | 0 | 0 | 0
2025-06-27 23:00 | 56.06 | 0 | 0 | 56.06 | 0 | 0 | 0 | 0 | 0
2025-06-28 | 54.32 | 0 | 0 | 54.32 | 0 | 0 | 0 | 0 | 0
2025-06-28 01:00 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 0 | 0 | 0
2025-06-28 02:00 | 51.03 | 0 | 0 | 51.03 | 0 | 0 | 0 | 0 | 0
2025-06-28 03:00 | 51.63 | 0 | 0 | 51.63 | 0 | 0 | 0 | 0 | 0
2025-06-28 04:00 | 51.03 | 0 | 0 | 51.03 | 0 | 0 | 0 | 0 | 0
2025-06-28 05:00 | 53.13 | 33.71 | 33.71 | 19.42 | 0 | 0 | 0 | 0 | 0
2025-06-28 06:00 | 54.83 | 86.86 | 54.83 | 0 | 0 | 0 | 0 | 32.03 | 0
2025-06-28 07:00 | 57.61 | 108.02 | 57.61 | 0 | 0 | 0 | 0 | 50.41 | 0
2025-06-28 08:00 | 60.45 | 113.88 | 60.45 | 0 | 0 | 0 | 0 | 53.43 | 0
2025-06-28 09:00 | 64.29 | 82.11 | 64.29 | 0 | 0 | 0 | 0 | 17.82 | 0
2025-06-28 10:00 | 67.37 | 11.75 | 11.75 | 55.62 | 0 | 0 | 0 | 0 | 0
2025-06-28 11:00 | 71.02 | 31.07 | 31.07 | 39.95 | 0 | 0 | 0 | 0 | 0
2025-06-28 12:00 | 73.53 | 48.46 | 48.46 | 25.08 | 0 | 0 | 0 | 0 | 0
2025-06-28 13:00 | 75.26 | 55.63 | 55.63 | 19.63 | 0 | 0 | 0 | 0 | 0
2025-06-28 14:00 | 77.53 | 104.32 | 77.53 | 0 | 0 | 0 | 0 | 26.79 | 0
2025-06-28 15:00 | 77.69 | 86.45 | 77.69 | 0 | 0 | 0 | 0 | 8.76 | 0
2025-06-28 16:00 | 76.81 | 122.89 | 76.81 | 0 | 0 | 0 | 0 | 46.09 | 0
2025-06-28 17:00 | 75.8 | 125.64 | 75.8 | 0 | 0 | 0 | 0 | 49.84 | 0
2025-06-28 18:00 | 73.61 | 103.5 | 73.61 | 0 | 0 | 0 | 0 | 29.89 | 0
2025-06-28 19:00 | 70.5 | 21.41 | 21.41 | 49.09 | 0 | 0 | 0 | 0 | 0
2025-06-28 20:00 | 67.79 | 0 | 0 | 67.79 | 0 | 0 | 0 | 0 | 0
2025-06-28 21:00 | 64.01 | 0 | 0 | 64.01 | 0 | 0 | 0 | 0 | 0
2025-06-28 22:00 | 60.39 | 0 | 0 | 60.39 | 0 | 0 | 0 | 0 | 0
2025-06-28 23:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 0 | 0 | 0
2025-06-29 | 54.77 | 0 | 0 | 54.77 | 0 | 0 | 0 | 0 | 0
2025-06-29 01:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 0 | 0 | 0
2025-06-29 02:00 | 51.05 | 0 | 0 | 51.05 | 0 | 0 | 0 | 0 | 0
2025-06-29 03:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0 | 0 | 0
2025-06-29 04:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 0 | 0 | 0
2025-06-29 05:00 | 53.41 | 30.43 | 30.43 | 22.99 | 0 | 0 | 0 | 0 | 0
2025-06-29 06:00 | 55.35 | 91.12 | 55.35 | 0 | 0 | 0 | 0 | 35.77 | 0
2025-06-29 07:00 | 58.76 | 111.16 | 58.76 | 0 | 0 | 0 | 0 | 52.41 | 0
2025-06-29 08:00 | 60.83 | 120.18 | 60.83 | 0 | 0 | 0 | 0 | 59.35 | 0
2025-06-29 09:00 | 63.63 | 121.68 | 63.63 | 0 | 0 | 0 | 0 | 58.05 | 0
2025-06-29 10:00 | 68.42 | 119.62 | 68.42 | 0 | 0 | 0 | 0 | 51.2 | 0
2025-06-29 11:00 | 72.45 | 118.28 | 72.45 | 0 | 0 | 0 | 0 | 45.83 | 0
2025-06-29 12:00 | 75.3 | 116 | 75.3 | 0 | 0 | 0 | 0 | 40.7 | 0
2025-06-29 13:00 | 77.73 | 117.48 | 77.73 | 0 | 0 | 0 | 0 | 39.75 | 0
2025-06-29 14:00 | 79.75 | 118.1 | 79.75 | 0 | 0 | 0 | 0 | 38.35 | 0
2025-06-29 15:00 | 79.79 | 118.03 | 79.79 | 0 | 0 | 0 | 0 | 38.24 | 0
2025-06-29 16:00 | 79.48 | 113.45 | 79.48 | 0 | 0 | 0 | 0 | 33.97 | 0
2025-06-29 17:00 | 77.12 | 104.38 | 77.12 | 0 | 0 | 0 | 0 | 27.26 | 0
2025-06-29 18:00 | 74.68 | 84.08 | 74.68 | 0 | 0 | 0 | 0 | 9.4 | 0
2025-06-29 19:00 | 72.97 | 21.36 | 21.36 | 51.61 | 0 | 0 | 0 | 0 | 0
2025-06-29 20:00 | 68.7 | 0 | 0 | 68.7 | 0 | 0 | 0 | 0 | 0
2025-06-29 21:00 | 64.6 | 0 | 0 | 64.6 | 0 | 0 | 0 | 0 | 0
2025-06-29 22:00 | 60.91 | 0 | 0 | 60.91 | 0 | 0 | 0 | 0 | 0
2025-06-29 23:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 0 | 0 | 0
2025-06-30 | 54.77 | 0 | 0 | 54.77 | 0 | 0 | 0 | 0 | 0
2025-06-30 01:00 | 52.2 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0
2025-06-30 02:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0 | 0 | 0
2025-06-30 03:00 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 0 | 0 | 0
2025-06-30 04:00 | 51.15 | 0 | 0 | 51.15 | 0 | 0 | 0 | 0 | 0
2025-06-30 05:00 | 53.4 | 24.92 | 24.92 | 28.48 | 0 | 0 | 0 | 0 | 0
2025-06-30 06:00 | 55.27 | 87.22 | 55.27 | 0 | 0 | 0 | 0 | 31.95 | 0
2025-06-30 07:00 | 58.35 | 100.18 | 58.35 | 0 | 0 | 0 | 0 | 41.82 | 0
2025-06-30 08:00 | 61.63 | 119.41 | 61.63 | 0 | 0 | 0 | 0 | 57.78 | 0
2025-06-30 09:00 | 66.2 | 140.67 | 66.2 | 0 | 0 | 0 | 0 | 74.47 | 0
2025-06-30 10:00 | 70.92 | 133.34 | 70.92 | 0 | 0 | 0 | 0 | 62.42 | 0
2025-06-30 11:00 | 75.47 | 81.76 | 75.47 | 0 | 0 | 0 | 0 | 6.29 | 0
2025-06-30 12:00 | 78.96 | 79.1 | 78.96 | 0 | 0 | 0 | 0 | 0.14 | 0
2025-06-30 13:00 | 82.63 | 61.87 | 61.87 | 20.76 | 0 | 0 | 0 | 0 | 0
2025-06-30 14:00 | 84.08 | 70.99 | 70.99 | 13.09 | 0 | 0 | 0 | 0 | 0
2025-06-30 15:00 | 85.15 | 66.72 | 66.72 | 18.43 | 0 | 0 | 0 | 0 | 0
2025-06-30 16:00 | 83.83 | 56.76 | 56.76 | 27.07 | 0 | 0 | 0 | 0 | 0
2025-06-30 17:00 | 81.19 | 47.29 | 47.29 | 33.9 | 0 | 0 | 0 | 0 | 0
2025-06-30 18:00 | 79.14 | 20.78 | 20.78 | 58.37 | 0 | 0 | 0 | 0 | 0
2025-06-30 19:00 | 75.47 | 5.22 | 5.22 | 70.25 | 0 | 0 | 0 | 0 | 0
2025-06-30 20:00 | 71.03 | 0 | 0 | 71.03 | 0 | 0 | 0 | 0 | 0
2025-06-30 21:00 | 66.47 | 0 | 0 | 66.47 | 0 | 0 | 0 | 0 | 0
2025-06-30 22:00 | 61.82 | 0 | 0 | 61.82 | 0 | 0 | 0 | 0 | 0
2025-06-30 23:00 | 57.82 | 0 | 0 | 57.82 | 0 | 0 | 0 | 0 | 0
2025-07-01 | 55.35 | 0 | 0 | 55.35 | 0 | 0 | 0 | 0 | 0
2025-07-01 01:00 | 53.09 | 0 | 0 | 53.09 | 0 | 0 | 0 | 0 | 0
2025-07-01 02:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0 | 0 | 0
2025-07-01 03:00 | 51.59 | 0 | 0 | 51.59 | 0 | 0 | 0 | 0 | 0
2025-07-01 04:00 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 0 | 0 | 0
2025-07-01 05:00 | 52.59 | 20.34 | 20.34 | 32.25 | 0 | 0 | 0 | 0 | 0
2025-07-01 06:00 | 55.89 | 37.41 | 37.41 | 18.48 | 0 | 0 | 0 | 0 | 0
2025-07-01 07:00 | 58.39 | 71.05 | 58.39 | 0 | 0 | 0 | 0 | 12.65 | 0
2025-07-01 08:00 | 61.17 | 89.48 | 61.17 | 0 | 0 | 0 | 0 | 28.31 | 0
2025-07-01 09:00 | 65.16 | 107.57 | 65.16 | 0 | 0 | 0 | 0 | 42.41 | 0
2025-07-01 10:00 | 68.8 | 108.89 | 68.8 | 0 | 0 | 0 | 0 | 40.09 | 0
2025-07-01 11:00 | 70.84 | 112.96 | 70.84 | 0 | 0 | 0 | 0 | 42.12 | 0
2025-07-01 12:00 | 74.78 | 102.5 | 74.78 | 0 | 0 | 0 | 0 | 27.72 | 0
2025-07-01 13:00 | 77.54 | 112.8 | 77.54 | 0 | 0 | 0 | 0 | 35.26 | 0
2025-07-01 14:00 | 78.86 | 114.77 | 78.86 | 0 | 0 | 0 | 0 | 35.91 | 0
2025-07-01 15:00 | 79.66 | 123.8 | 79.66 | 0 | 0 | 0 | 0 | 44.14 | 0
2025-07-01 16:00 | 79.6 | 124.96 | 79.6 | 0 | 0 | 0 | 0 | 45.36 | 0
2025-07-01 17:00 | 77.4 | 120.71 | 77.4 | 0 | 0 | 0 | 0 | 43.31 | 0
2025-07-01 18:00 | 74.7 | 100.34 | 74.7 | 0 | 0 | 0 | 0 | 25.63 | 0
2025-07-01 19:00 | 72.37 | 27.1 | 27.1 | 45.27 | 0 | 0 | 0 | 0 | 0
2025-07-01 20:00 | 68.56 | 0 | 0 | 68.56 | 0 | 0 | 0 | 0 | 0
2025-07-01 21:00 | 64.94 | 0 | 0 | 64.94 | 0 | 0 | 0 | 0 | 0
2025-07-01 22:00 | 61.2 | 0 | 0 | 61.2 | 0 | 0 | 0 | 0 | 0
2025-07-01 23:00 | 59.08 | 0 | 0 | 59.08 | 0 | 0 | 0 | 0 | 0
2025-07-02 | 53.95 | 0 | 0 | 53.95 | 0 | 0 | 0 | 0 | 0
2025-07-02 01:00 | 52.72 | 0 | 0 | 52.72 | 0 | 0 | 0 | 0 | 0
2025-07-02 02:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0 | 0 | 0
2025-07-02 03:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0 | 0 | 0
2025-07-02 04:00 | 52 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0
2025-07-02 05:00 | 53.33 | 30.42 | 30.42 | 22.9 | 0 | 0 | 0 | 0 | 0
2025-07-02 06:00 | 55.05 | 96.84 | 55.05 | 0 | 0 | 0 | 0 | 41.79 | 0
2025-07-02 07:00 | 57.7 | 118.62 | 57.7 | 0 | 0 | 0 | 0 | 60.92 | 0
2025-07-02 08:00 | 60.94 | 128.52 | 60.94 | 0 | 0 | 0 | 0 | 67.58 | 0
2025-07-02 09:00 | 64.27 | 130.92 | 64.27 | 0 | 0 | 0 | 0 | 66.65 | 0
2025-07-02 10:00 | 67.55 | 130.13 | 67.55 | 0 | 0 | 0 | 0 | 62.58 | 0
2025-07-02 11:00 | 70.47 | 128.14 | 70.47 | 0 | 0 | 0 | 0 | 57.67 | 0
2025-07-02 12:00 | 73.2 | 96.02 | 73.2 | 0 | 0 | 0 | 0 | 22.82 | 0
2025-07-02 13:00 | 75.35 | 84.02 | 75.35 | 0 | 0 | 0 | 0 | 8.68 | 0
2025-07-02 14:00 | 75.53 | 123.56 | 75.53 | 0 | 0 | 0 | 0 | 48.02 | 0
2025-07-02 15:00 | 76.02 | 111.71 | 76.02 | 0 | 0 | 0 | 0 | 35.69 | 0
2025-07-02 16:00 | 75.27 | 124.52 | 75.27 | 0 | 0 | 0 | 0 | 49.25 | 0
2025-07-02 17:00 | 75.4 | 114.56 | 75.4 | 0 | 0 | 0 | 0 | 39.15 | 0
2025-07-02 18:00 | 73.2 | 83.57 | 73.2 | 0 | 0 | 0 | 0 | 10.37 | 0
2025-07-02 19:00 | 70.82 | 17.3 | 17.3 | 53.52 | 0 | 0 | 0 | 0 | 0
2025-07-02 20:00 | 66.87 | 0 | 0 | 66.87 | 0 | 0 | 0 | 0 | 0
2025-07-02 21:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 0 | 0 | 0
2025-07-02 22:00 | 60.69 | 0 | 0 | 60.69 | 0 | 0 | 0 | 0 | 0
2025-07-02 23:00 | 57.92 | 0 | 0 | 57.92 | 0 | 0 | 0 | 0 | 0
2025-07-03 | 55.72 | 0 | 0 | 55.72 | 0 | 0 | 0 | 0 | 0
2025-07-03 01:00 | 52.51 | 0 | 0 | 52.51 | 0 | 0 | 0 | 0 | 0
2025-07-03 02:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 0 | 0 | 0
2025-07-03 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0 | 0 | 0
2025-07-03 04:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 0 | 0 | 0
2025-07-03 05:00 | 53.16 | 26.82 | 26.82 | 26.33 | 0 | 0 | 0 | 0 | 0
2025-07-03 06:00 | 56.09 | 87.85 | 56.09 | 0 | 0 | 0 | 0 | 31.75 | 0
2025-07-03 07:00 | 58.97 | 109.3 | 58.97 | 0 | 0 | 0 | 0 | 50.32 | 0
2025-07-03 08:00 | 62.29 | 118.65 | 62.29 | 0 | 0 | 0 | 0 | 56.36 | 0
2025-07-03 09:00 | 65.8 | 120.39 | 65.8 | 0 | 0 | 0 | 0 | 54.59 | 0
2025-07-03 10:00 | 71.19 | 120.48 | 71.19 | 0 | 0 | 0 | 0 | 49.29 | 0
2025-07-03 11:00 | 74.15 | 118.63 | 74.15 | 0 | 0 | 0 | 0 | 44.48 | 0
2025-07-03 12:00 | 79.46 | 116.22 | 79.46 | 0 | 0 | 0 | 0 | 36.76 | 0
2025-07-03 13:00 | 81.73 | 116.89 | 81.73 | 0 | 0 | 0 | 0 | 35.16 | 0
2025-07-03 14:00 | 82.21 | 118.15 | 82.21 | 0 | 0 | 0 | 0 | 35.94 | 0
2025-07-03 15:00 | 84.02 | 117.56 | 84.02 | 0 | 0 | 0 | 0 | 33.54 | 0
2025-07-03 16:00 | 83.86 | 114.26 | 83.86 | 0 | 0 | 0 | 0 | 30.4 | 0
2025-07-03 17:00 | 81.51 | 103.72 | 81.51 | 0 | 0 | 0 | 0 | 22.21 | 0
2025-07-03 18:00 | 79.02 | 82.43 | 79.02 | 0 | 0 | 0 | 0 | 3.41 | 0
2025-07-03 19:00 | 74.47 | 20.04 | 20.04 | 54.44 | 0 | 0 | 0 | 0 | 0
2025-07-03 20:00 | 70.01 | 0 | 0 | 70.01 | 0 | 0 | 0 | 0 | 0
2025-07-03 21:00 | 66.26 | 0 | 0 | 66.26 | 0 | 0 | 0 | 0 | 0
2025-07-03 22:00 | 62.12 | 0 | 0 | 62.12 | 0 | 0 | 0 | 0 | 0
2025-07-03 23:00 | 58.2 | 0 | 0 | 58.2 | 0 | 0 | 0 | 0 | 0
2025-07-04 | 55.89 | 0 | 0 | 55.89 | 0 | 0 | 0 | 0 | 0
2025-07-04 01:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 0 | 0 | 0
2025-07-04 02:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0 | 0 | 0
2025-07-04 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0 | 0 | 0
2025-07-04 04:00 | 50.87 | 0 | 0 | 50.87 | 0 | 0 | 0 | 0 | 0
2025-07-04 05:00 | 52.38 | 21.79 | 21.79 | 30.6 | 0 | 0 | 0 | 0 | 0
2025-07-04 06:00 | 55.28 | 75.2 | 55.28 | 0 | 0 | 0 | 0 | 19.92 | 0
2025-07-04 07:00 | 59.21 | 99.26 | 59.21 | 0 | 0 | 0 | 0 | 40.04 | 0
2025-07-04 08:00 | 62.01 | 110.72 | 62.01 | 0 | 0 | 0 | 0 | 48.71 | 0
2025-07-04 09:00 | 64.67 | 117.28 | 64.67 | 0 | 0 | 0 | 0 | 52.62 | 0
2025-07-04 10:00 | 67.86 | 117.04 | 67.86 | 0 | 0 | 0 | 0 | 49.17 | 0
2025-07-04 11:00 | 73.47 | 112.27 | 73.47 | 0 | 0 | 0 | 0 | 38.79 | 0
2025-07-04 12:00 | 76.27 | 111.41 | 76.27 | 0 | 0 | 0 | 0 | 35.14 | 0
2025-07-04 13:00 | 79.39 | 111.17 | 79.39 | 0 | 0 | 0 | 0 | 31.78 | 0
2025-07-04 14:00 | 79.96 | 110.18 | 79.96 | 0 | 0 | 0 | 0 | 30.21 | 0
2025-07-04 15:00 | 81.12 | 107.73 | 81.12 | 0 | 0 | 0 | 0 | 26.61 | 0
2025-07-04 16:00 | 80.83 | 102.02 | 80.83 | 0 | 0 | 0 | 0 | 21.19 | 0
2025-07-04 17:00 | 78.6 | 93.09 | 78.6 | 0 | 0 | 0 | 0 | 14.49 | 0
2025-07-04 18:00 | 76.11 | 64.7 | 64.7 | 11.41 | 0 | 0 | 0 | 0 | 0
2025-07-04 19:00 | 73.12 | 16.37 | 16.37 | 56.75 | 0 | 0 | 0 | 0 | 0
2025-07-04 20:00 | 69.69 | 0 | 0 | 69.69 | 0 | 0 | 0 | 0 | 0
2025-07-04 21:00 | 65.52 | 0 | 0 | 65.52 | 0 | 0 | 0 | 0 | 0
2025-07-04 22:00 | 62.2 | 0 | 0 | 62.2 | 0 | 0 | 0 | 0 | 0
2025-07-04 23:00 | 57.99 | 0 | 0 | 57.99 | 0 | 0 | 0 | 0 | 0
2025-07-05 | 54.78 | 0 | 0 | 54.78 | 0 | 0 | 0 | 0 | 0
2025-07-05 01:00 | 54.1 | 0 | 0 | 54.1 | 0 | 0 | 0 | 0 | 0
2025-07-05 02:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-07-05 03:00 | 50.94 | 0 | 0 | 50.94 | 0 | 0 | 0 | 0 | 0
2025-07-05 04:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 0 | 0 | 0
2025-07-05 05:00 | 53.15 | 1.6 | 1.6 | 51.55 | 0 | 0 | 0 | 0 | 0
2025-07-05 06:00 | 55.25 | 38.61 | 38.61 | 16.64 | 0 | 0 | 0 | 0 | 0
2025-07-05 07:00 | 58.62 | 39.13 | 39.13 | 19.49 | 0 | 0 | 0 | 0 | 0
2025-07-05 08:00 | 62.52 | 38.64 | 38.64 | 23.89 | 0 | 0 | 0 | 0 | 0
2025-07-05 09:00 | 67.08 | 57.27 | 57.27 | 9.81 | 0 | 0 | 0 | 0 | 0
2025-07-05 10:00 | 70.51 | 75.94 | 70.51 | 0 | 0 | 0 | 0 | 5.43 | 0
2025-07-05 11:00 | 77.25 | 93.21 | 77.25 | 0 | 0 | 0 | 0 | 15.96 | 0
2025-07-05 12:00 | 80.37 | 105.11 | 80.37 | 0 | 0 | 0 | 0 | 24.73 | 0
2025-07-05 13:00 | 84.02 | 115.43 | 84.02 | 0 | 0 | 0 | 0 | 31.41 | 0
2025-07-05 14:00 | 85.16 | 67.77 | 67.77 | 17.39 | 0 | 0 | 0 | 0 | 0
2025-07-05 15:00 | 86.34 | 63.96 | 63.96 | 22.39 | 0 | 0 | 0 | 0 | 0
2025-07-05 16:00 | 85.51 | 81.43 | 81.43 | 4.09 | 0 | 0 | 0 | 0 | 0
2025-07-05 17:00 | 84.47 | 58.47 | 58.47 | 26 | 0 | 0 | 0 | 0 | 0
2025-07-05 18:00 | 80.15 | 3.54 | 3.54 | 76.61 | 0 | 0 | 0 | 0 | 0
2025-07-05 19:00 | 76.69 | 1.92 | 1.92 | 74.77 | 0 | 0 | 0 | 0 | 0
2025-07-05 20:00 | 71.37 | 0 | 0 | 71.37 | 0 | 0 | 0 | 0 | 0
2025-07-05 21:00 | 66.76 | 0 | 0 | 66.76 | 0 | 0 | 0 | 0 | 0
2025-07-05 22:00 | 62.42 | 0 | 0 | 62.42 | 0 | 0 | 0 | 0 | 0
2025-07-05 23:00 | 59.27 | 0 | 0 | 59.27 | 0 | 0 | 0 | 0 | 0
2025-07-06 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 0 | 0 | 0
2025-07-06 01:00 | 52.47 | 0 | 0 | 52.47 | 0 | 0 | 0 | 0 | 0
2025-07-06 02:00 | 50.77 | 0 | 0 | 50.77 | 0 | 0 | 0 | 0 | 0
2025-07-06 03:00 | 50.72 | 0 | 0 | 50.72 | 0 | 0 | 0 | 0 | 0
2025-07-06 04:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 0 | 0 | 0
2025-07-06 05:00 | 52.33 | 24.8 | 24.8 | 27.52 | 0 | 0 | 0 | 0 | 0
2025-07-06 06:00 | 54.99 | 91.6 | 54.99 | 0 | 0 | 0 | 0 | 36.61 | 0
2025-07-06 07:00 | 57.26 | 106.19 | 57.26 | 0 | 0 | 0 | 0 | 48.93 | 0
2025-07-06 08:00 | 61.17 | 109.66 | 61.17 | 0 | 0 | 0 | 0 | 48.48 | 0
2025-07-06 09:00 | 65.98 | 83.41 | 65.98 | 0 | 0 | 0 | 0 | 17.43 | 0
2025-07-06 10:00 | 69.3 | 62.04 | 62.04 | 7.27 | 0 | 0 | 0 | 0 | 0
2025-07-06 11:00 | 72.7 | 83.31 | 72.7 | 0 | 0 | 0 | 0 | 10.61 | 0
2025-07-06 12:00 | 75.13 | 55.54 | 55.54 | 19.59 | 0 | 0 | 0 | 0 | 0
2025-07-06 13:00 | 77.2 | 59.91 | 59.91 | 17.29 | 0 | 0 | 0 | 0 | 0
2025-07-06 14:00 | 78.87 | 86.98 | 78.87 | 0 | 0 | 0 | 0 | 8.11 | 0
2025-07-06 15:00 | 79.92 | 88.53 | 79.92 | 0 | 0 | 0 | 0 | 8.61 | 0
2025-07-06 16:00 | 79.87 | 79.43 | 79.43 | 0.44 | 0 | 0 | 0 | 0 | 0
2025-07-06 17:00 | 78.42 | 68.97 | 68.97 | 9.44 | 0 | 0 | 0 | 0 | 0
2025-07-06 18:00 | 75.94 | 61.51 | 61.51 | 14.44 | 0 | 0 | 0 | 0 | 0
2025-07-06 19:00 | 72.23 | 20.65 | 20.65 | 51.59 | 0 | 0 | 0 | 0 | 0
2025-07-06 20:00 | 69.12 | 0 | 0 | 69.12 | 0 | 0 | 0 | 0 | 0
2025-07-06 21:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 0 | 0 | 0
2025-07-06 22:00 | 61.58 | 0 | 0 | 61.58 | 0 | 0 | 0 | 0 | 0
2025-07-06 23:00 | 59.28 | 0 | 0 | 59.28 | 0 | 0 | 0 | 0 | 0
2025-07-07 | 54.37 | 0 | 0 | 54.37 | 0 | 0 | 0 | 0 | 0
2025-07-07 01:00 | 53.03 | 0 | 0 | 53.03 | 0 | 0 | 0 | 0 | 0
2025-07-07 02:00 | 52.39 | 0 | 0 | 52.39 | 0 | 0 | 0 | 0 | 0
2025-07-07 03:00 | 50.58 | 0 | 0 | 50.58 | 0 | 0 | 0 | 0 | 0
2025-07-07 04:00 | 51.46 | 0 | 0 | 51.46 | 0 | 0 | 0 | 0 | 0
2025-07-07 05:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 0 | 0 | 0
2025-07-07 06:00 | 55.14 | 10.02 | 10.02 | 45.12 | 0 | 0 | 0 | 0 | 0
2025-07-07 07:00 | 57.08 | 26.98 | 26.98 | 30.1 | 0 | 0 | 0 | 0 | 0
2025-07-07 08:00 | 61.07 | 36.2 | 36.2 | 24.88 | 0 | 0 | 0 | 0 | 0
2025-07-07 09:00 | 64.02 | 42.95 | 42.95 | 21.07 | 0 | 0 | 0 | 0 | 0
2025-07-07 10:00 | 66.64 | 43.59 | 43.59 | 23.05 | 0 | 0 | 0 | 0 | 0
2025-07-07 11:00 | 68.29 | 60.61 | 60.61 | 7.68 | 0 | 0 | 0 | 0 | 0
2025-07-07 12:00 | 70.63 | 90.38 | 70.63 | 0 | 0 | 0 | 0 | 19.74 | 0
2025-07-07 13:00 | 71.48 | 122.54 | 71.48 | 0 | 0 | 0 | 0 | 51.07 | 0
2025-07-07 14:00 | 72.56 | 118.81 | 72.56 | 0 | 0 | 0 | 0 | 46.24 | 0
2025-07-07 15:00 | 74.07 | 109.64 | 74.07 | 0 | 0 | 0 | 0 | 35.57 | 0
2025-07-07 16:00 | 72.78 | 116.84 | 72.78 | 0 | 0 | 0 | 0 | 44.07 | 0
2025-07-07 17:00 | 71.33 | 50.87 | 50.87 | 20.46 | 0 | 0 | 0 | 0 | 0
2025-07-07 18:00 | 70.68 | 29.85 | 29.85 | 40.83 | 0 | 0 | 0 | 0 | 0
2025-07-07 19:00 | 68.05 | 11.12 | 11.12 | 56.93 | 0 | 0 | 0 | 0 | 0
2025-07-07 20:00 | 65.79 | 0 | 0 | 65.79 | 0 | 0 | 0 | 0 | 0
2025-07-07 21:00 | 63.17 | 0 | 0 | 63.17 | 0 | 0 | 0 | 0 | 0
2025-07-07 22:00 | 60.55 | 0 | 0 | 60.55 | 0 | 0 | 0 | 0 | 0
2025-07-07 23:00 | 58.35 | 0 | 0 | 58.35 | 0 | 0 | 0 | 0 | 0
2025-07-08 | 55.57 | 0 | 0 | 55.57 | 0 | 0 | 0 | 0 | 0
2025-07-08 01:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 0 | 0 | 0
2025-07-08 02:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0 | 0 | 0
2025-07-08 03:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0
2025-07-08 04:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 0 | 0 | 0
2025-07-08 05:00 | 52.87 | 20.87 | 20.87 | 32 | 0 | 0 | 0 | 0 | 0
2025-07-08 06:00 | 55.14 | 82.04 | 55.14 | 0 | 0 | 0 | 0 | 26.9 | 0
2025-07-08 07:00 | 58.11 | 109.06 | 58.11 | 0 | 0 | 0 | 0 | 50.95 | 0
2025-07-08 08:00 | 60.56 | 121.36 | 60.56 | 0 | 0 | 0 | 0 | 60.81 | 0
2025-07-08 09:00 | 63.68 | 124.07 | 63.68 | 0 | 0 | 0 | 0 | 60.39 | 0
2025-07-08 10:00 | 66.97 | 119.53 | 66.97 | 0 | 0 | 0 | 0 | 52.56 | 0
2025-07-08 11:00 | 68.3 | 7.29 | 7.29 | 61.02 | 0 | 0 | 0 | 0 | 0
2025-07-08 12:00 | 70.73 | 93.7 | 70.73 | 0 | 0 | 0 | 0 | 22.98 | 0
2025-07-08 13:00 | 71.66 | 123.66 | 71.66 | 0 | 0 | 0 | 0 | 52 | 0
2025-07-08 14:00 | 71.38 | 6.52 | 6.52 | 64.86 | 0 | 0 | 0 | 0 | 0
2025-07-08 15:00 | 71.8 | 119.8 | 71.8 | 0 | 0 | 0 | 0 | 48 | 0
2025-07-08 16:00 | 71.7 | 120.51 | 71.7 | 0 | 0 | 0 | 0 | 48.81 | 0
2025-07-08 17:00 | 70.95 | 107.59 | 70.95 | 0 | 0 | 0 | 0 | 36.64 | 0
2025-07-08 18:00 | 70.09 | 80.46 | 70.09 | 0 | 0 | 0 | 0 | 10.37 | 0
2025-07-08 19:00 | 68.7 | 17.89 | 17.89 | 50.8 | 0 | 0 | 0 | 0 | 0
2025-07-08 20:00 | 66.8 | 0 | 0 | 66.8 | 0 | 0 | 0 | 0 | 0
2025-07-08 21:00 | 63.72 | 0 | 0 | 63.72 | 0 | 0 | 0 | 0 | 0
2025-07-08 22:00 | 60.51 | 0 | 0 | 60.51 | 0 | 0 | 0 | 0 | 0
2025-07-08 23:00 | 56.85 | 0 | 0 | 56.85 | 0 | 0 | 0 | 0 | 0
2025-07-09 | 55.69 | 0 | 0 | 55.69 | 0 | 0 | 0 | 0 | 0
2025-07-09 01:00 | 53.3 | 0 | 0 | 53.3 | 0 | 0 | 0 | 0 | 0
2025-07-09 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0 | 0 | 0
2025-07-09 03:00 | 52.44 | 0 | 0 | 52.44 | 0 | 0 | 0 | 0 | 0
2025-07-09 04:00 | 52.48 | 0 | 0 | 52.48 | 0 | 0 | 0 | 0 | 0
2025-07-09 05:00 | 53.68 | 10.75 | 10.75 | 42.93 | 0 | 0 | 0 | 0 | 0
2025-07-09 06:00 | 55.17 | 64.79 | 55.17 | 0 | 0 | 0 | 0 | 9.61 | 0
2025-07-09 07:00 | 58.63 | 98.08 | 58.63 | 0 | 0 | 0 | 0 | 39.45 | 0
2025-07-09 08:00 | 62.82 | 90.46 | 62.82 | 0 | 0 | 0 | 0 | 27.64 | 0
2025-07-09 09:00 | 67.03 | 100.18 | 67.03 | 0 | 0 | 0 | 0 | 33.15 | 0
2025-07-09 10:00 | 72.5 | 119.47 | 72.5 | 0 | 0 | 0 | 0 | 46.97 | 0
2025-07-09 11:00 | 77.17 | 109.21 | 77.17 | 0 | 0 | 0 | 0 | 32.04 | 0
2025-07-09 12:00 | 80.72 | 102.1 | 80.72 | 0 | 0 | 0 | 0 | 21.38 | 0
2025-07-09 13:00 | 85.26 | 87.94 | 85.26 | 0 | 0 | 0 | 0 | 2.68 | 0
2025-07-09 14:00 | 86.9 | 76.35 | 76.35 | 10.55 | 0 | 0 | 0 | 0 | 0
2025-07-09 15:00 | 86.74 | 56.23 | 56.23 | 30.51 | 0 | 0 | 0 | 0 | 0
2025-07-09 16:00 | 86.83 | 56.84 | 56.84 | 29.98 | 0 | 0 | 0 | 0 | 0
2025-07-09 17:00 | 84.8 | 48.59 | 48.59 | 36.21 | 0 | 0 | 0 | 0 | 0
2025-07-09 18:00 | 81.75 | 12.03 | 12.03 | 69.72 | 0 | 0 | 0 | 0 | 0
2025-07-09 19:00 | 76.83 | 1.01 | 1.01 | 75.81 | 0 | 0 | 0 | 0 | 0
2025-07-09 20:00 | 72.66 | 0 | 0 | 72.66 | 0 | 0 | 0 | 0 | 0
2025-07-09 21:00 | 67.52 | 0 | 0 | 67.52 | 0 | 0 | 0 | 0 | 0
2025-07-09 22:00 | 62.22 | 0 | 0 | 62.22 | 0 | 0 | 0 | 0 | 0
2025-07-09 23:00 | 58.18 | 0 | 0 | 58.18 | 0 | 0 | 0 | 0 | 0
2025-07-10 | 56.26 | 0 | 0 | 56.26 | 0 | 0 | 0 | 0 | 0
2025-07-10 01:00 | 53.93 | 0 | 0 | 53.93 | 0 | 0 | 0 | 0 | 0
2025-07-10 02:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 0 | 0 | 0
2025-07-10 03:00 | 52.17 | 0 | 0 | 52.17 | 0 | 0 | 0 | 0 | 0
2025-07-10 04:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 0 | 0 | 0
2025-07-10 05:00 | 53.67 | 15.9 | 15.9 | 37.77 | 0 | 0 | 0 | 0 | 0
2025-07-10 06:00 | 55.24 | 70.16 | 55.24 | 0 | 0 | 0 | 0 | 14.91 | 0
2025-07-10 07:00 | 59.82 | 97.88 | 59.82 | 0 | 0 | 0 | 0 | 38.05 | 0
2025-07-10 08:00 | 63.24 | 107.27 | 63.24 | 0 | 0 | 0 | 0 | 44.03 | 0
2025-07-10 09:00 | 67.38 | 105.47 | 67.38 | 0 | 0 | 0 | 0 | 38.09 | 0
2025-07-10 10:00 | 72.13 | 109.26 | 72.13 | 0 | 0 | 0 | 0 | 37.13 | 0
2025-07-10 11:00 | 77.41 | 108.47 | 77.41 | 0 | 0 | 0 | 0 | 31.06 | 0
2025-07-10 12:00 | 80.78 | 107.02 | 80.78 | 0 | 0 | 0 | 0 | 26.23 | 0
2025-07-10 13:00 | 85.42 | 108.99 | 85.42 | 0 | 0 | 0 | 0 | 23.57 | 0
2025-07-10 14:00 | 86.82 | 109.97 | 86.82 | 0 | 0 | 0 | 0 | 23.15 | 0
2025-07-10 15:00 | 88.26 | 109.52 | 88.26 | 0 | 0 | 0 | 0 | 21.26 | 0
2025-07-10 16:00 | 87.04 | 102.26 | 87.04 | 0 | 0 | 0 | 0 | 15.22 | 0
2025-07-10 17:00 | 84.94 | 81.87 | 81.87 | 3.07 | 0 | 0 | 0 | 0 | 0
2025-07-10 18:00 | 81.24 | 61 | 61 | 20.24 | 0 | 0 | 0 | 0 | 0
2025-07-10 19:00 | 77.2 | 15.27 | 15.27 | 61.93 | 0 | 0 | 0 | 0 | 0
2025-07-10 20:00 | 73.41 | 0 | 0 | 73.41 | 0 | 0 | 0 | 0 | 0
2025-07-10 21:00 | 68.27 | 0 | 0 | 68.27 | 0 | 0 | 0 | 0 | 0
2025-07-10 22:00 | 63.15 | 0 | 0 | 63.15 | 0 | 0 | 0 | 0 | 0
2025-07-10 23:00 | 58.94 | 0 | 0 | 58.94 | 0 | 0 | 0 | 0 | 0
2025-07-11 | 55.96 | 0 | 0 | 55.96 | 0 | 0 | 0 | 0 | 0
2025-07-11 01:00 | 53.89 | 0 | 0 | 53.89 | 0 | 0 | 0 | 0 | 0
2025-07-11 02:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 0 | 0 | 0
2025-07-11 03:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 0 | 0 | 0
2025-07-11 04:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 0 | 0 | 0
2025-07-11 05:00 | 53.88 | 1.51 | 1.51 | 52.38 | 0 | 0 | 0 | 0 | 0
2025-07-11 06:00 | 56.57 | 10.44 | 10.44 | 46.13 | 0 | 0 | 0 | 0 | 0
2025-07-11 07:00 | 58.44 | 12.22 | 12.22 | 46.22 | 0 | 0 | 0 | 0 | 0
2025-07-11 08:00 | 60.65 | 26.25 | 26.25 | 34.4 | 0 | 0 | 0 | 0 | 0
2025-07-11 09:00 | 65.54 | 43.08 | 43.08 | 22.46 | 0 | 0 | 0 | 0 | 0
2025-07-11 10:00 | 68.28 | 49.52 | 49.52 | 18.76 | 0 | 0 | 0 | 0 | 0
2025-07-11 11:00 | 71.62 | 52.27 | 52.27 | 19.36 | 0 | 0 | 0 | 0 | 0
2025-07-11 12:00 | 75.02 | 73.95 | 73.95 | 1.07 | 0 | 0 | 0 | 0 | 0
2025-07-11 13:00 | 76.93 | 78.18 | 76.93 | 0 | 0 | 0 | 0 | 1.25 | 0
2025-07-11 14:00 | 77.87 | 53.67 | 53.67 | 24.21 | 0 | 0 | 0 | 0 | 0
2025-07-11 15:00 | 78.24 | 26.63 | 26.63 | 51.61 | 0 | 0 | 0 | 0 | 0
2025-07-11 16:00 | 78.18 | 4.22 | 4.22 | 73.96 | 0 | 0 | 0 | 0 | 0
2025-07-11 17:00 | 76.6 | 3.12 | 3.12 | 73.48 | 0 | 0 | 0 | 0 | 0
2025-07-11 18:00 | 74.15 | 8.42 | 8.42 | 65.74 | 0 | 0 | 0 | 0 | 0
2025-07-11 19:00 | 71.79 | 1.32 | 1.32 | 70.47 | 0 | 0 | 0 | 0 | 0
2025-07-11 20:00 | 68.9 | 0 | 0 | 68.9 | 0 | 0 | 0 | 0 | 0
2025-07-11 21:00 | 65.15 | 0 | 0 | 65.15 | 0 | 0 | 0 | 0 | 0
2025-07-11 22:00 | 61 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0
2025-07-11 23:00 | 58.89 | 0 | 0 | 58.89 | 0 | 0 | 0 | 0 | 0
2025-07-12 | 54.18 | 0 | 0 | 54.18 | 0 | 0 | 0 | 0 | 0
2025-07-12 01:00 | 53.13 | 0 | 0 | 53.13 | 0 | 0 | 0 | 0 | 0
2025-07-12 02:00 | 51.65 | 0 | 0 | 51.65 | 0 | 0 | 0 | 0 | 0
2025-07-12 03:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0 | 0 | 0
2025-07-12 04:00 | 52.24 | 0 | 0 | 52.24 | 0 | 0 | 0 | 0 | 0
2025-07-12 05:00 | 53.91 | 18.4 | 18.4 | 35.51 | 0 | 0 | 0 | 0 | 0
2025-07-12 06:00 | 55.19 | 77.63 | 55.19 | 0 | 0 | 0 | 0 | 22.44 | 0
2025-07-12 07:00 | 58.67 | 91.5 | 58.67 | 0 | 0 | 0 | 0 | 32.83 | 0
2025-07-12 08:00 | 61.71 | 105.15 | 61.71 | 0 | 0 | 0 | 0 | 43.44 | 0
2025-07-12 09:00 | 64.17 | 108.86 | 64.17 | 0 | 0 | 0 | 0 | 44.69 | 0
2025-07-12 10:00 | 69.33 | 111.08 | 69.33 | 0 | 0 | 0 | 0 | 41.75 | 0
2025-07-12 11:00 | 70.72 | 109.46 | 70.72 | 0 | 0 | 0 | 0 | 38.74 | 0
2025-07-12 12:00 | 74.23 | 106.16 | 74.23 | 0 | 0 | 0 | 0 | 31.93 | 0
2025-07-12 13:00 | 76.17 | 107.32 | 76.17 | 0 | 0 | 0 | 0 | 31.15 | 0
2025-07-12 14:00 | 77.33 | 108.22 | 77.33 | 0 | 0 | 0 | 0 | 30.88 | 0
2025-07-12 15:00 | 77.36 | 101.46 | 77.36 | 0 | 0 | 0 | 0 | 24.1 | 0
2025-07-12 16:00 | 77.61 | 96.32 | 77.61 | 0 | 0 | 0 | 0 | 18.71 | 0
2025-07-12 17:00 | 75.2 | 85.72 | 75.2 | 0 | 0 | 0 | 0 | 10.52 | 0
2025-07-12 18:00 | 73.99 | 75.41 | 73.99 | 0 | 0 | 0 | 0 | 1.42 | 0
2025-07-12 19:00 | 71.16 | 15.51 | 15.51 | 55.65 | 0 | 0 | 0 | 0 | 0
2025-07-12 20:00 | 68.04 | 0 | 0 | 68.04 | 0 | 0 | 0 | 0 | 0
2025-07-12 21:00 | 65.24 | 0 | 0 | 65.24 | 0 | 0 | 0 | 0 | 0
2025-07-12 22:00 | 62.15 | 0 | 0 | 62.15 | 0 | 0 | 0 | 0 | 0
2025-07-12 23:00 | 58.2 | 0 | 0 | 58.2 | 0 | 0 | 0 | 0 | 0
2025-07-13 | 56.17 | 0 | 0 | 56.17 | 0 | 0 | 0 | 0 | 0
2025-07-13 01:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 0 | 0 | 0
2025-07-13 02:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 0 | 0 | 0
2025-07-13 03:00 | 51.38 | 0 | 0 | 51.38 | 0 | 0 | 0 | 0 | 0
2025-07-13 04:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 0 | 0 | 0
2025-07-13 05:00 | 53.08 | 17.9 | 17.9 | 35.18 | 0 | 0 | 0 | 0 | 0
2025-07-13 06:00 | 56 | 81.16 | 56 | 0 | 0 | 0 | 0 | 25.16 | 0
2025-07-13 07:00 | 59.11 | 105.58 | 59.11 | 0 | 0 | 0 | 0 | 46.47 | 0
2025-07-13 08:00 | 62.14 | 115.26 | 62.14 | 0 | 0 | 0 | 0 | 53.12 | 0
2025-07-13 09:00 | 66.58 | 118.5 | 66.58 | 0 | 0 | 0 | 0 | 51.92 | 0
2025-07-13 10:00 | 72.34 | 118.46 | 72.34 | 0 | 0 | 0 | 0 | 46.12 | 0
2025-07-13 11:00 | 76.34 | 115.63 | 76.34 | 0 | 0 | 0 | 0 | 39.29 | 0
2025-07-13 12:00 | 81.03 | 114.14 | 81.03 | 0 | 0 | 0 | 0 | 33.11 | 0
2025-07-13 13:00 | 84.55 | 115.4 | 84.55 | 0 | 0 | 0 | 0 | 30.85 | 0
2025-07-13 14:00 | 85.64 | 115.11 | 85.64 | 0 | 0 | 0 | 0 | 29.47 | 0
2025-07-13 15:00 | 86.3 | 114.6 | 86.3 | 0 | 0 | 0 | 0 | 28.3 | 0
2025-07-13 16:00 | 87.11 | 109.53 | 87.11 | 0 | 0 | 0 | 0 | 22.42 | 0
2025-07-13 17:00 | 84.34 | 94.03 | 84.34 | 0 | 0 | 0 | 0 | 9.69 | 0
2025-07-13 18:00 | 80.67 | 68.65 | 68.65 | 12.02 | 0 | 0 | 0 | 0 | 0
2025-07-13 19:00 | 76.28 | 13.55 | 13.55 | 62.73 | 0 | 0 | 0 | 0 | 0
2025-07-13 20:00 | 71.87 | 0 | 0 | 71.87 | 0 | 0 | 0 | 0 | 0
2025-07-13 21:00 | 66.81 | 0 | 0 | 66.81 | 0 | 0 | 0 | 0 | 0
2025-07-13 22:00 | 63.38 | 0 | 0 | 63.38 | 0 | 0 | 0 | 0 | 0
2025-07-13 23:00 | 58.61 | 0 | 0 | 58.61 | 0 | 0 | 0 | 0 | 0
2025-07-14 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 0 | 0 | 0
2025-07-14 01:00 | 53.19 | 0 | 0 | 53.19 | 0 | 0 | 0 | 0 | 0
2025-07-14 02:00 | 51.49 | 0 | 0 | 51.49 | 0 | 0 | 0 | 0 | 0
2025-07-14 03:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 0 | 0 | 0
2025-07-14 04:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0 | 0 | 0
2025-07-14 05:00 | 53.33 | 17.51 | 17.51 | 35.82 | 0 | 0 | 0 | 0 | 0
2025-07-14 06:00 | 55.45 | 76.77 | 55.45 | 0 | 0 | 0 | 0 | 21.32 | 0
2025-07-14 07:00 | 58.63 | 95.94 | 58.63 | 0 | 0 | 0 | 0 | 37.31 | 0
2025-07-14 08:00 | 60.25 | 107.74 | 60.25 | 0 | 0 | 0 | 0 | 47.49 | 0
2025-07-14 09:00 | 64.78 | 112.55 | 64.78 | 0 | 0 | 0 | 0 | 47.77 | 0
2025-07-14 10:00 | 67.43 | 114.01 | 67.43 | 0 | 0 | 0 | 0 | 46.58 | 0
2025-07-14 11:00 | 70.11 | 112.24 | 70.11 | 0 | 0 | 0 | 0 | 42.13 | 0
2025-07-14 12:00 | 71.44 | 112.96 | 71.44 | 0 | 0 | 0 | 0 | 41.53 | 0
2025-07-14 13:00 | 73.41 | 114.59 | 73.41 | 0 | 0 | 0 | 0 | 41.18 | 0
2025-07-14 14:00 | 73.04 | 118.09 | 73.04 | 0 | 0 | 0 | 0 | 45.05 | 0
2025-07-14 15:00 | 74.42 | 120.46 | 74.42 | 0 | 0 | 0 | 0 | 46.04 | 0
2025-07-14 16:00 | 73.39 | 117.68 | 73.39 | 0 | 0 | 0 | 0 | 44.29 | 0
2025-07-14 17:00 | 72.08 | 109.92 | 72.08 | 0 | 0 | 0 | 0 | 37.84 | 0
2025-07-14 18:00 | 70.9 | 91.74 | 70.9 | 0 | 0 | 0 | 0 | 20.84 | 0
2025-07-14 19:00 | 69.49 | 19.59 | 19.59 | 49.89 | 0 | 0 | 0 | 0 | 0
2025-07-14 20:00 | 66.61 | 0 | 0 | 66.61 | 0 | 0 | 0 | 0 | 0
2025-07-14 21:00 | 64.39 | 0 | 0 | 64.39 | 0 | 0 | 0 | 0 | 0
2025-07-14 22:00 | 60.29 | 0 | 0 | 60.29 | 0 | 0 | 0 | 0 | 0
2025-07-14 23:00 | 57.15 | 0 | 0 | 57.15 | 0 | 0 | 0 | 0 | 0
2025-07-15 | 56.27 | 0 | 0 | 56.27 | 0 | 0 | 0 | 0 | 0
2025-07-15 01:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 0 | 0 | 0
2025-07-15 02:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 0 | 0 | 0
2025-07-15 03:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0 | 0 | 0
2025-07-15 04:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 0 | 0 | 0
2025-07-15 05:00 | 53.63 | 15.52 | 15.52 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-07-15 06:00 | 55.66 | 76.23 | 55.66 | 0 | 0 | 0 | 0 | 20.57 | 0
2025-07-15 07:00 | 58.86 | 99.21 | 58.86 | 0 | 0 | 0 | 0 | 40.35 | 0
2025-07-15 08:00 | 61.01 | 112.53 | 61.01 | 0 | 0 | 0 | 0 | 51.52 | 0
2025-07-15 09:00 | 64.52 | 115.29 | 64.52 | 0 | 0 | 0 | 0 | 50.77 | 0
2025-07-15 10:00 | 67.48 | 116.91 | 67.48 | 0 | 0 | 0 | 0 | 49.43 | 0
2025-07-15 11:00 | 70 | 116.37 | 70 | 0 | 0 | 0 | 0 | 46.37 | 0
2025-07-15 12:00 | 72.1 | 115.64 | 72.1 | 0 | 0 | 0 | 0 | 43.54 | 0
2025-07-15 13:00 | 73.93 | 116.96 | 73.93 | 0 | 0 | 0 | 0 | 43.03 | 0
2025-07-15 14:00 | 74.88 | 116.46 | 74.88 | 0 | 0 | 0 | 0 | 41.58 | 0
2025-07-15 15:00 | 74.67 | 115.88 | 74.67 | 0 | 0 | 0 | 0 | 41.21 | 0
2025-07-15 16:00 | 75.27 | 110.2 | 75.27 | 0 | 0 | 0 | 0 | 34.94 | 0
2025-07-15 17:00 | 73.4 | 95.62 | 73.4 | 0 | 0 | 0 | 0 | 22.21 | 0
2025-07-15 18:00 | 72.19 | 75.88 | 72.19 | 0 | 0 | 0 | 0 | 3.69 | 0
2025-07-15 19:00 | 69.99 | 14.69 | 14.69 | 55.3 | 0 | 0 | 0 | 0 | 0
2025-07-15 20:00 | 67.67 | 0 | 0 | 67.67 | 0 | 0 | 0 | 0 | 0
2025-07-15 21:00 | 63.45 | 0 | 0 | 63.45 | 0 | 0 | 0 | 0 | 0
2025-07-15 22:00 | 61.82 | 0 | 0 | 61.82 | 0 | 0 | 0 | 0 | 0
2025-07-15 23:00 | 57.98 | 0 | 0 | 57.98 | 0 | 0 | 0 | 0 | 0
2025-07-16 | 56.39 | 0 | 0 | 56.39 | 0 | 0 | 0 | 0 | 0
2025-07-16 01:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 0 | 0 | 0
2025-07-16 02:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 0 | 0 | 0
2025-07-16 03:00 | 52.53 | 0 | 0 | 52.53 | 0 | 0 | 0 | 0 | 0
2025-07-16 04:00 | 51.92 | 0 | 0 | 51.92 | 0 | 0 | 0 | 0 | 0
2025-07-16 05:00 | 54.1 | 10.09 | 10.09 | 44.01 | 0 | 0 | 0 | 0 | 0
2025-07-16 06:00 | 55.8 | 22 | 22 | 33.8 | 0 | 0 | 0 | 0 | 0
2025-07-16 07:00 | 59.04 | 37.18 | 37.18 | 21.86 | 0 | 0 | 0 | 0 | 0
2025-07-16 08:00 | 62.51 | 70.97 | 62.51 | 0 | 0 | 0 | 0 | 8.46 | 0
2025-07-16 09:00 | 66.92 | 122.33 | 66.92 | 0 | 0 | 0 | 0 | 55.41 | 0
2025-07-16 10:00 | 70.28 | 89 | 70.28 | 0 | 0 | 0 | 0 | 18.72 | 0
2025-07-16 11:00 | 74.08 | 96.06 | 74.08 | 0 | 0 | 0 | 0 | 21.98 | 0
2025-07-16 12:00 | 77.71 | 101.3 | 77.71 | 0 | 0 | 0 | 0 | 23.59 | 0
2025-07-16 13:00 | 80.78 | 104.37 | 80.78 | 0 | 0 | 0 | 0 | 23.59 | 0
2025-07-16 14:00 | 82.34 | 85.66 | 82.34 | 0 | 0 | 0 | 0 | 3.32 | 0
2025-07-16 15:00 | 83.4 | 83.84 | 83.4 | 0 | 0 | 0 | 0 | 0.43 | 0
2025-07-16 16:00 | 83.11 | 64.15 | 64.15 | 18.95 | 0 | 0 | 0 | 0 | 0
2025-07-16 17:00 | 80.25 | 15.72 | 15.72 | 64.53 | 0 | 0 | 0 | 0 | 0
2025-07-16 18:00 | 77.66 | 10.6 | 10.6 | 67.06 | 0 | 0 | 0 | 0 | 0
2025-07-16 19:00 | 73.85 | 1.34 | 1.34 | 72.51 | 0 | 0 | 0 | 0 | 0
2025-07-16 20:00 | 71.64 | 0 | 0 | 71.64 | 0 | 0 | 0 | 0 | 0
2025-07-16 21:00 | 66.65 | 0 | 0 | 66.65 | 0 | 0 | 0 | 0 | 0
2025-07-16 22:00 | 62.72 | 0 | 0 | 62.72 | 0 | 0 | 0 | 0 | 0
2025-07-16 23:00 | 58.16 | 0 | 0 | 58.16 | 0 | 0 | 0 | 0 | 0
2025-07-17 | 55.69 | 0 | 0 | 55.69 | 0 | 0 | 0 | 0 | 0
2025-07-17 01:00 | 53.73 | 0 | 0 | 53.73 | 0 | 0 | 0 | 0 | 0
2025-07-17 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0 | 0 | 0
2025-07-17 03:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 0 | 0 | 0
2025-07-17 04:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0 | 0 | 0
2025-07-17 05:00 | 53 | 10.28 | 10.28 | 42.73 | 0 | 0 | 0 | 0 | 0
2025-07-17 06:00 | 55.18 | 48.68 | 48.68 | 6.5 | 0 | 0 | 0 | 0 | 0
2025-07-17 07:00 | 58.09 | 89.81 | 58.09 | 0 | 0 | 0 | 0 | 31.72 | 0
2025-07-17 08:00 | 62.59 | 79.56 | 62.59 | 0 | 0 | 0 | 0 | 16.97 | 0
2025-07-17 09:00 | 65.73 | 96.06 | 65.73 | 0 | 0 | 0 | 0 | 30.33 | 0
2025-07-17 10:00 | 68.5 | 101.09 | 68.5 | 0 | 0 | 0 | 0 | 32.59 | 0
2025-07-17 11:00 | 71.66 | 109.39 | 71.66 | 0 | 0 | 0 | 0 | 37.73 | 0
2025-07-17 12:00 | 73.82 | 96.28 | 73.82 | 0 | 0 | 0 | 0 | 22.45 | 0
2025-07-17 13:00 | 76.63 | 97.83 | 76.63 | 0 | 0 | 0 | 0 | 21.2 | 0
2025-07-17 14:00 | 77.22 | 101.76 | 77.22 | 0 | 0 | 0 | 0 | 24.54 | 0
2025-07-17 15:00 | 77.69 | 88.57 | 77.69 | 0 | 0 | 0 | 0 | 10.88 | 0
2025-07-17 16:00 | 77.71 | 91 | 77.71 | 0 | 0 | 0 | 0 | 13.29 | 0
2025-07-17 17:00 | 76.1 | 86.47 | 76.1 | 0 | 0 | 0 | 0 | 10.37 | 0
2025-07-17 18:00 | 74.11 | 76.18 | 74.11 | 0 | 0 | 0 | 0 | 2.07 | 0
2025-07-17 19:00 | 71.65 | 11.17 | 11.17 | 60.48 | 0 | 0 | 0 | 0 | 0
2025-07-17 20:00 | 68.97 | 0 | 0 | 68.97 | 0 | 0 | 0 | 0 | 0
2025-07-17 21:00 | 66.03 | 0 | 0 | 66.03 | 0 | 0 | 0 | 0 | 0
2025-07-17 22:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 0 | 0 | 0
2025-07-17 23:00 | 58.93 | 0 | 0 | 58.93 | 0 | 0 | 0 | 0 | 0
2025-07-18 | 55.65 | 0 | 0 | 55.65 | 0 | 0 | 0 | 0 | 0
2025-07-18 01:00 | 53.15 | 0 | 0 | 53.15 | 0 | 0 | 0 | 0 | 0
2025-07-18 02:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 0 | 0 | 0
2025-07-18 03:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 0 | 0 | 0
2025-07-18 04:00 | 51.38 | 0 | 0 | 51.38 | 0 | 0 | 0 | 0 | 0
2025-07-18 05:00 | 53.34 | 12.91 | 12.91 | 40.43 | 0 | 0 | 0 | 0 | 0
2025-07-18 06:00 | 55.71 | 76.14 | 55.71 | 0 | 0 | 0 | 0 | 20.43 | 0
2025-07-18 07:00 | 58.42 | 97.39 | 58.42 | 0 | 0 | 0 | 0 | 38.97 | 0
2025-07-18 08:00 | 62.82 | 110.96 | 62.82 | 0 | 0 | 0 | 0 | 48.14 | 0
2025-07-18 09:00 | 65.97 | 113.72 | 65.97 | 0 | 0 | 0 | 0 | 47.74 | 0
2025-07-18 10:00 | 70.07 | 114.14 | 70.07 | 0 | 0 | 0 | 0 | 44.07 | 0
2025-07-18 11:00 | 72.92 | 114.88 | 72.92 | 0 | 0 | 0 | 0 | 41.96 | 0
2025-07-18 12:00 | 75.75 | 112.98 | 75.75 | 0 | 0 | 0 | 0 | 37.23 | 0
2025-07-18 13:00 | 77.48 | 115.3 | 77.48 | 0 | 0 | 0 | 0 | 37.81 | 0
2025-07-18 14:00 | 79.37 | 115.89 | 79.37 | 0 | 0 | 0 | 0 | 36.52 | 0
2025-07-18 15:00 | 79.85 | 114.02 | 79.85 | 0 | 0 | 0 | 0 | 34.17 | 0
2025-07-18 16:00 | 78.68 | 107.69 | 78.68 | 0 | 0 | 0 | 0 | 29.02 | 0
2025-07-18 17:00 | 77.68 | 94.82 | 77.68 | 0 | 0 | 0 | 0 | 17.13 | 0
2025-07-18 18:00 | 75.55 | 68.09 | 68.09 | 7.46 | 0 | 0 | 0 | 0 | 0
2025-07-18 19:00 | 73 | 11.85 | 11.85 | 61.15 | 0 | 0 | 0 | 0 | 0
2025-07-18 20:00 | 69.62 | 0 | 0 | 69.62 | 0 | 0 | 0 | 0 | 0
2025-07-18 21:00 | 65.44 | 0 | 0 | 65.44 | 0 | 0 | 0 | 0 | 0
2025-07-18 22:00 | 62.31 | 0 | 0 | 62.31 | 0 | 0 | 0 | 0 | 0
2025-07-18 23:00 | 58.58 | 0 | 0 | 58.58 | 0 | 0 | 0 | 0 | 0
2025-07-19 | 54.32 | 0 | 0 | 54.32 | 0 | 0 | 0 | 0 | 0
2025-07-19 01:00 | 53.27 | 0 | 0 | 53.27 | 0 | 0 | 0 | 0 | 0
2025-07-19 02:00 | 52.65 | 0 | 0 | 52.65 | 0 | 0 | 0 | 0 | 0
2025-07-19 03:00 | 50.79 | 0 | 0 | 50.79 | 0 | 0 | 0 | 0 | 0
2025-07-19 04:00 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 0 | 0 | 0
2025-07-19 05:00 | 54.31 | 11.78 | 11.78 | 42.53 | 0 | 0 | 0 | 0 | 0
2025-07-19 06:00 | 55.37 | 72.05 | 55.37 | 0 | 0 | 0 | 0 | 16.68 | 0
2025-07-19 07:00 | 58.64 | 97.88 | 58.64 | 0 | 0 | 0 | 0 | 39.24 | 0
2025-07-19 08:00 | 61.34 | 111.66 | 61.34 | 0 | 0 | 0 | 0 | 50.32 | 0
2025-07-19 09:00 | 66.37 | 117.26 | 66.37 | 0 | 0 | 0 | 0 | 50.89 | 0
2025-07-19 10:00 | 69.05 | 117.77 | 69.05 | 0 | 0 | 0 | 0 | 48.72 | 0
2025-07-19 11:00 | 72.39 | 115.41 | 72.39 | 0 | 0 | 0 | 0 | 43.02 | 0
2025-07-19 12:00 | 75.83 | 116.32 | 75.83 | 0 | 0 | 0 | 0 | 40.49 | 0
2025-07-19 13:00 | 77.61 | 116.04 | 77.61 | 0 | 0 | 0 | 0 | 38.43 | 0
2025-07-19 14:00 | 78.18 | 116.36 | 78.18 | 0 | 0 | 0 | 0 | 38.18 | 0
2025-07-19 15:00 | 78.75 | 116.51 | 78.75 | 0 | 0 | 0 | 0 | 37.77 | 0
2025-07-19 16:00 | 78.86 | 113.79 | 78.86 | 0 | 0 | 0 | 0 | 34.93 | 0
2025-07-19 17:00 | 76.97 | 103.88 | 76.97 | 0 | 0 | 0 | 0 | 26.9 | 0
2025-07-19 18:00 | 74.1 | 77.99 | 74.1 | 0 | 0 | 0 | 0 | 3.9 | 0
2025-07-19 19:00 | 72.34 | 12.55 | 12.55 | 59.79 | 0 | 0 | 0 | 0 | 0
2025-07-19 20:00 | 68.35 | 0 | 0 | 68.35 | 0 | 0 | 0 | 0 | 0
2025-07-19 21:00 | 66.37 | 0 | 0 | 66.37 | 0 | 0 | 0 | 0 | 0
2025-07-19 22:00 | 62.08 | 0 | 0 | 62.08 | 0 | 0 | 0 | 0 | 0
2025-07-19 23:00 | 58.19 | 0 | 0 | 58.19 | 0 | 0 | 0 | 0 | 0
2025-07-20 | 55.47 | 0 | 0 | 55.47 | 0 | 0 | 0 | 0 | 0
2025-07-20 01:00 | 52.6 | 0 | 0 | 52.6 | 0 | 0 | 0 | 0 | 0
2025-07-20 02:00 | 51.57 | 0 | 0 | 51.57 | 0 | 0 | 0 | 0 | 0
2025-07-20 03:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 0 | 0 | 0
2025-07-20 04:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 0 | 0 | 0
2025-07-20 05:00 | 53.9 | 12.13 | 12.13 | 41.78 | 0 | 0 | 0 | 0 | 0
2025-07-20 06:00 | 55.77 | 76.65 | 55.77 | 0 | 0 | 0 | 0 | 20.88 | 0
2025-07-20 07:00 | 58.6 | 101.3 | 58.6 | 0 | 0 | 0 | 0 | 42.7 | 0
2025-07-20 08:00 | 61.88 | 114.14 | 61.88 | 0 | 0 | 0 | 0 | 52.26 | 0
2025-07-20 09:00 | 67.24 | 116.53 | 67.24 | 0 | 0 | 0 | 0 | 49.29 | 0
2025-07-20 10:00 | 70.03 | 116.92 | 70.03 | 0 | 0 | 0 | 0 | 46.89 | 0
2025-07-20 11:00 | 74.88 | 114.67 | 74.88 | 0 | 0 | 0 | 0 | 39.78 | 0
2025-07-20 12:00 | 77.74 | 113.78 | 77.74 | 0 | 0 | 0 | 0 | 36.04 | 0
2025-07-20 13:00 | 78.66 | 114.47 | 78.66 | 0 | 0 | 0 | 0 | 35.81 | 0
2025-07-20 14:00 | 80.78 | 115.82 | 80.78 | 0 | 0 | 0 | 0 | 35.04 | 0
2025-07-20 15:00 | 81.32 | 114.5 | 81.32 | 0 | 0 | 0 | 0 | 33.19 | 0
2025-07-20 16:00 | 81.07 | 110.93 | 81.07 | 0 | 0 | 0 | 0 | 29.85 | 0
2025-07-20 17:00 | 79.5 | 97.36 | 79.5 | 0 | 0 | 0 | 0 | 17.85 | 0
2025-07-20 18:00 | 78.54 | 70.65 | 70.65 | 7.89 | 0 | 0 | 0 | 0 | 0
2025-07-20 19:00 | 73.29 | 11.16 | 11.16 | 62.12 | 0 | 0 | 0 | 0 | 0
2025-07-20 20:00 | 70.24 | 0 | 0 | 70.24 | 0 | 0 | 0 | 0 | 0
2025-07-20 21:00 | 66.52 | 0 | 0 | 66.52 | 0 | 0 | 0 | 0 | 0
2025-07-20 22:00 | 62.36 | 0 | 0 | 62.36 | 0 | 0 | 0 | 0 | 0
2025-07-20 23:00 | 58.88 | 0 | 0 | 58.88 | 0 | 0 | 0 | 0 | 0
2025-07-21 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 0 | 0 | 0
2025-07-21 01:00 | 53.63 | 0 | 0 | 53.63 | 0 | 0 | 0 | 0 | 0
2025-07-21 02:00 | 52.39 | 0 | 0 | 52.39 | 0 | 0 | 0 | 0 | 0
2025-07-21 03:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0 | 0 | 0
2025-07-21 04:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 0 | 0 | 0
2025-07-21 05:00 | 54.28 | 10.48 | 10.48 | 43.8 | 0 | 0 | 0 | 0 | 0
2025-07-21 06:00 | 56.42 | 66.4 | 56.42 | 0 | 0 | 0 | 0 | 9.98 | 0
2025-07-21 07:00 | 59.21 | 90.83 | 59.21 | 0 | 0 | 0 | 0 | 31.62 | 0
2025-07-21 08:00 | 62.54 | 107.84 | 62.54 | 0 | 0 | 0 | 0 | 45.3 | 0
2025-07-21 09:00 | 67.3 | 110.26 | 67.3 | 0 | 0 | 0 | 0 | 42.96 | 0
2025-07-21 10:00 | 72.2 | 114.16 | 72.2 | 0 | 0 | 0 | 0 | 41.96 | 0
2025-07-21 11:00 | 77.04 | 111.88 | 77.04 | 0 | 0 | 0 | 0 | 34.85 | 0
2025-07-21 12:00 | 80.8 | 111.03 | 80.8 | 0 | 0 | 0 | 0 | 30.23 | 0
2025-07-21 13:00 | 83.84 | 111.56 | 83.84 | 0 | 0 | 0 | 0 | 27.72 | 0
2025-07-21 14:00 | 85.81 | 109.78 | 85.81 | 0 | 0 | 0 | 0 | 23.98 | 0
2025-07-21 15:00 | 86.3 | 105.19 | 86.3 | 0 | 0 | 0 | 0 | 18.88 | 0
2025-07-21 16:00 | 86.29 | 97.47 | 86.29 | 0 | 0 | 0 | 0 | 11.18 | 0
2025-07-21 17:00 | 83.57 | 81.36 | 81.36 | 2.21 | 0 | 0 | 0 | 0 | 0
2025-07-21 18:00 | 80.54 | 58.34 | 58.34 | 22.19 | 0 | 0 | 0 | 0 | 0
2025-07-21 19:00 | 76.72 | 9.35 | 9.35 | 67.37 | 0 | 0 | 0 | 0 | 0
2025-07-21 20:00 | 71.64 | 0 | 0 | 71.64 | 0 | 0 | 0 | 0 | 0
2025-07-21 21:00 | 67.79 | 0 | 0 | 67.79 | 0 | 0 | 0 | 0 | 0
2025-07-21 22:00 | 63.49 | 0 | 0 | 63.49 | 0 | 0 | 0 | 0 | 0
2025-07-21 23:00 | 58.9 | 0 | 0 | 58.9 | 0 | 0 | 0 | 0 | 0
2025-07-22 | 55.59 | 0 | 0 | 55.59 | 0 | 0 | 0 | 0 | 0
2025-07-22 01:00 | 53.82 | 0 | 0 | 53.82 | 0 | 0 | 0 | 0 | 0
2025-07-22 02:00 | 51.78 | 0 | 0 | 51.78 | 0 | 0 | 0 | 0 | 0
2025-07-22 03:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0 | 0 | 0
2025-07-22 04:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 0 | 0 | 0
2025-07-22 05:00 | 54 | 9.79 | 9.79 | 44.21 | 0 | 0 | 0 | 0 | 0
2025-07-22 06:00 | 56.11 | 62.41 | 56.11 | 0 | 0 | 0 | 0 | 6.29 | 0
2025-07-22 07:00 | 59.23 | 85.18 | 59.23 | 0 | 0 | 0 | 0 | 25.96 | 0
2025-07-22 08:00 | 61.23 | 104.86 | 61.23 | 0 | 0 | 0 | 0 | 43.63 | 0
2025-07-22 09:00 | 66.61 | 108.84 | 66.61 | 0 | 0 | 0 | 0 | 42.23 | 0
2025-07-22 10:00 | 69.86 | 109.91 | 69.86 | 0 | 0 | 0 | 0 | 40.05 | 0
2025-07-22 11:00 | 73.66 | 104.89 | 73.66 | 0 | 0 | 0 | 0 | 31.23 | 0
2025-07-22 12:00 | 76.36 | 102.65 | 76.36 | 0 | 0 | 0 | 0 | 26.29 | 0
2025-07-22 13:00 | 78.5 | 103.8 | 78.5 | 0 | 0 | 0 | 0 | 25.3 | 0
2025-07-22 14:00 | 79.8 | 104.84 | 79.8 | 0 | 0 | 0 | 0 | 25.03 | 0
2025-07-22 15:00 | 80.62 | 102.73 | 80.62 | 0 | 0 | 0 | 0 | 22.11 | 0
2025-07-22 16:00 | 79.78 | 91.61 | 79.78 | 0 | 0 | 0 | 0 | 11.83 | 0
2025-07-22 17:00 | 78.91 | 77.74 | 77.74 | 1.18 | 0 | 0 | 0 | 0 | 0
2025-07-22 18:00 | 75.37 | 56.05 | 56.05 | 19.33 | 0 | 0 | 0 | 0 | 0
2025-07-22 19:00 | 72.89 | 8.94 | 8.94 | 63.95 | 0 | 0 | 0 | 0 | 0
2025-07-22 20:00 | 70.69 | 0 | 0 | 70.69 | 0 | 0 | 0 | 0 | 0
2025-07-22 21:00 | 65.62 | 0 | 0 | 65.62 | 0 | 0 | 0 | 0 | 0
2025-07-22 22:00 | 62.1 | 0 | 0 | 62.1 | 0 | 0 | 0 | 0 | 0
2025-07-22 23:00 | 58.32 | 0 | 0 | 58.32 | 0 | 0 | 0 | 0 | 0
2025-07-23 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 0 | 0 | 0
2025-07-23 01:00 | 53.21 | 0 | 0 | 53.21 | 0 | 0 | 0 | 0 | 0
2025-07-23 02:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 0 | 0 | 0
2025-07-23 03:00 | 52.09 | 0 | 0 | 52.09 | 0 | 0 | 0 | 0 | 0
2025-07-23 04:00 | 51.8 | 0 | 0 | 51.8 | 0 | 0 | 0 | 0 | 0
2025-07-23 05:00 | 53.97 | 8.99 | 8.99 | 44.98 | 0 | 0 | 0 | 0 | 0
2025-07-23 06:00 | 56.29 | 64.98 | 56.29 | 0 | 0 | 0 | 0 | 8.69 | 0
2025-07-23 07:00 | 59.48 | 92.82 | 59.48 | 0 | 0 | 0 | 0 | 33.34 | 0
2025-07-23 08:00 | 62.68 | 107.68 | 62.68 | 0 | 0 | 0 | 0 | 45 | 0
2025-07-23 09:00 | 68.27 | 113.52 | 68.27 | 0 | 0 | 0 | 0 | 45.25 | 0
2025-07-23 10:00 | 71.32 | 115.36 | 71.32 | 0 | 0 | 0 | 0 | 44.04 | 0
2025-07-23 11:00 | 74.92 | 114.39 | 74.92 | 0 | 0 | 0 | 0 | 39.47 | 0
2025-07-23 12:00 | 77.8 | 112.57 | 77.8 | 0 | 0 | 0 | 0 | 34.78 | 0
2025-07-23 13:00 | 80.9 | 113.31 | 80.9 | 0 | 0 | 0 | 0 | 32.41 | 0
2025-07-23 14:00 | 83.39 | 114.04 | 83.39 | 0 | 0 | 0 | 0 | 30.65 | 0
2025-07-23 15:00 | 84.13 | 112.66 | 84.13 | 0 | 0 | 0 | 0 | 28.54 | 0
2025-07-23 16:00 | 83.42 | 105.26 | 83.42 | 0 | 0 | 0 | 0 | 21.84 | 0
2025-07-23 17:00 | 81.34 | 91.44 | 81.34 | 0 | 0 | 0 | 0 | 10.1 | 0
2025-07-23 18:00 | 77.6 | 65.4 | 65.4 | 12.21 | 0 | 0 | 0 | 0 | 0
2025-07-23 19:00 | 75 | 8.54 | 8.54 | 66.46 | 0 | 0 | 0 | 0 | 0
2025-07-23 20:00 | 70.17 | 0 | 0 | 70.17 | 0 | 0 | 0 | 0 | 0
2025-07-23 21:00 | 65.9 | 0 | 0 | 65.9 | 0 | 0 | 0 | 0 | 0
2025-07-23 22:00 | 62.73 | 0 | 0 | 62.73 | 0 | 0 | 0 | 0 | 0
2025-07-23 23:00 | 59.21 | 0 | 0 | 59.21 | 0 | 0 | 0 | 0 | 0
2025-07-24 | 56.04 | 0 | 0 | 56.04 | 0 | 0 | 0 | 0 | 0
2025-07-24 01:00 | 53.76 | 0 | 0 | 53.76 | 0 | 0 | 0 | 0 | 0
2025-07-24 02:00 | 52.41 | 0 | 0 | 52.41 | 0 | 0 | 0 | 0 | 0
2025-07-24 03:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 0 | 0 | 0
2025-07-24 04:00 | 52.09 | 0 | 0 | 52.09 | 0 | 0 | 0 | 0 | 0
2025-07-24 05:00 | 52.76 | 6.73 | 6.73 | 46.03 | 0 | 0 | 0 | 0 | 0
2025-07-24 06:00 | 54.59 | 60.36 | 54.59 | 0 | 0 | 0 | 0 | 5.77 | 0
2025-07-24 07:00 | 58.46 | 87.78 | 58.46 | 0 | 0 | 0 | 0 | 29.32 | 0
2025-07-24 08:00 | 60.35 | 101.23 | 60.35 | 0 | 0 | 0 | 0 | 40.88 | 0
2025-07-24 09:00 | 63.65 | 105.31 | 63.65 | 0 | 0 | 0 | 0 | 41.65 | 0
2025-07-24 10:00 | 65.91 | 108.4 | 65.91 | 0 | 0 | 0 | 0 | 42.5 | 0
2025-07-24 11:00 | 66.72 | 104.11 | 66.72 | 0 | 0 | 0 | 0 | 37.38 | 0
2025-07-24 12:00 | 68.53 | 100.8 | 68.53 | 0 | 0 | 0 | 0 | 32.27 | 0
2025-07-24 13:00 | 68.67 | 101.92 | 68.67 | 0 | 0 | 0 | 0 | 33.26 | 0
2025-07-24 14:00 | 68.49 | 106.57 | 68.49 | 0 | 0 | 0 | 0 | 38.08 | 0
2025-07-24 15:00 | 69.6 | 103.99 | 69.6 | 0 | 0 | 0 | 0 | 34.38 | 0
2025-07-24 16:00 | 69.18 | 95.65 | 69.18 | 0 | 0 | 0 | 0 | 26.47 | 0
2025-07-24 17:00 | 68.78 | 83.98 | 68.78 | 0 | 0 | 0 | 0 | 15.21 | 0
2025-07-24 18:00 | 69.22 | 62.72 | 62.72 | 6.5 | 0 | 0 | 0 | 0 | 0
2025-07-24 19:00 | 66.27 | 7.61 | 7.61 | 58.66 | 0 | 0 | 0 | 0 | 0
2025-07-24 20:00 | 65.55 | 0 | 0 | 65.55 | 0 | 0 | 0 | 0 | 0
2025-07-24 21:00 | 62.72 | 0 | 0 | 62.72 | 0 | 0 | 0 | 0 | 0
2025-07-24 22:00 | 61.18 | 0 | 0 | 61.18 | 0 | 0 | 0 | 0 | 0
2025-07-24 23:00 | 58.24 | 0 | 0 | 58.24 | 0 | 0 | 0 | 0 | 0
2025-07-25 | 56 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0
2025-07-25 01:00 | 53.09 | 0 | 0 | 53.09 | 0 | 0 | 0 | 0 | 0
2025-07-25 02:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 0 | 0 | 0
2025-07-25 03:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 0 | 0 | 0
2025-07-25 04:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 0 | 0 | 0
2025-07-25 05:00 | 53.8 | 8.71 | 8.71 | 45.09 | 0 | 0 | 0 | 0 | 0
2025-07-25 06:00 | 55.36 | 78.4 | 55.36 | 0 | 0 | 0 | 0 | 23.04 | 0
2025-07-25 07:00 | 58.9 | 106.63 | 58.9 | 0 | 0 | 0 | 0 | 47.72 | 0
2025-07-25 08:00 | 63.35 | 119.37 | 63.35 | 0 | 0 | 0 | 0 | 56.02 | 0
2025-07-25 09:00 | 65.82 | 120.68 | 65.82 | 0 | 0 | 0 | 0 | 54.86 | 0
2025-07-25 10:00 | 70.13 | 120.73 | 70.13 | 0 | 0 | 0 | 0 | 50.6 | 0
2025-07-25 11:00 | 72.41 | 118.24 | 72.41 | 0 | 0 | 0 | 0 | 45.83 | 0
2025-07-25 12:00 | 75.65 | 116.39 | 75.65 | 0 | 0 | 0 | 0 | 40.74 | 0
2025-07-25 13:00 | 78.2 | 117.4 | 78.2 | 0 | 0 | 0 | 0 | 39.2 | 0
2025-07-25 14:00 | 79.48 | 118.64 | 79.48 | 0 | 0 | 0 | 0 | 39.17 | 0
2025-07-25 15:00 | 79.37 | 119.6 | 79.37 | 0 | 0 | 0 | 0 | 40.23 | 0
2025-07-25 16:00 | 78.87 | 116.75 | 78.87 | 0 | 0 | 0 | 0 | 37.88 | 0
2025-07-25 17:00 | 78.38 | 105.49 | 78.38 | 0 | 0 | 0 | 0 | 27.11 | 0
2025-07-25 18:00 | 76.27 | 78.95 | 76.27 | 0 | 0 | 0 | 0 | 2.69 | 0
2025-07-25 19:00 | 73.53 | 8.2 | 8.2 | 65.34 | 0 | 0 | 0 | 0 | 0
2025-07-25 20:00 | 70.3 | 0 | 0 | 70.3 | 0 | 0 | 0 | 0 | 0
2025-07-25 21:00 | 65.84 | 0 | 0 | 65.84 | 0 | 0 | 0 | 0 | 0
2025-07-25 22:00 | 61.98 | 0 | 0 | 61.98 | 0 | 0 | 0 | 0 | 0
2025-07-25 23:00 | 59.41 | 0 | 0 | 59.41 | 0 | 0 | 0 | 0 | 0
2025-07-26 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 0 | 0 | 0
2025-07-26 01:00 | 53.05 | 0 | 0 | 53.05 | 0 | 0 | 0 | 0 | 0
2025-07-26 02:00 | 51.63 | 0 | 0 | 51.63 | 0 | 0 | 0 | 0 | 0
2025-07-26 03:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 0 | 0 | 0
2025-07-26 04:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 0 | 0 | 0
2025-07-26 05:00 | 53.53 | 9.93 | 9.93 | 43.6 | 0 | 0 | 0 | 0 | 0
2025-07-26 06:00 | 56.26 | 8.9 | 8.9 | 47.36 | 0 | 0 | 0 | 0 | 0
2025-07-26 07:00 | 58.86 | 55.83 | 55.83 | 3.03 | 0 | 0 | 0 | 0 | 0
2025-07-26 08:00 | 62.24 | 95.9 | 62.24 | 0 | 0 | 0 | 0 | 33.66 | 0
2025-07-26 09:00 | 63.79 | 111.69 | 63.79 | 0 | 0 | 0 | 0 | 47.9 | 0
2025-07-26 10:00 | 67.92 | 104.11 | 67.92 | 0 | 0 | 0 | 0 | 36.19 | 0
2025-07-26 11:00 | 70.84 | 85.09 | 70.84 | 0 | 0 | 0 | 0 | 14.25 | 0
2025-07-26 12:00 | 71.95 | 45.58 | 45.58 | 26.37 | 0 | 0 | 0 | 0 | 0
2025-07-26 13:00 | 74.03 | 26.67 | 26.67 | 47.36 | 0 | 0 | 0 | 0 | 0
2025-07-26 14:00 | 74.94 | 111.76 | 74.94 | 0 | 0 | 0 | 0 | 36.82 | 0
2025-07-26 15:00 | 75.71 | 42.52 | 42.52 | 33.18 | 0 | 0 | 0 | 0 | 0
2025-07-26 16:00 | 76.17 | 36.28 | 36.28 | 39.9 | 0 | 0 | 0 | 0 | 0
2025-07-26 17:00 | 75.37 | 18.04 | 18.04 | 57.33 | 0 | 0 | 0 | 0 | 0
2025-07-26 18:00 | 72.31 | 0.85 | 0.85 | 71.46 | 0 | 0 | 0 | 0 | 0
2025-07-26 19:00 | 70.76 | 10.68 | 10.68 | 60.08 | 0 | 0 | 0 | 0 | 0
2025-07-26 20:00 | 68.07 | 0 | 0 | 68.07 | 0 | 0 | 0 | 0 | 0
2025-07-26 21:00 | 64.95 | 0 | 0 | 64.95 | 0 | 0 | 0 | 0 | 0
2025-07-26 22:00 | 61.77 | 0 | 0 | 61.77 | 0 | 0 | 0 | 0 | 0
2025-07-26 23:00 | 58.63 | 0 | 0 | 58.63 | 0 | 0 | 0 | 0 | 0
2025-07-27 | 56.52 | 0 | 0 | 56.52 | 0 | 0 | 0 | 0 | 0
2025-07-27 01:00 | 54.08 | 0 | 0 | 54.08 | 0 | 0 | 0 | 0 | 0
2025-07-27 02:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 0 | 0 | 0
2025-07-27 03:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 0 | 0 | 0
2025-07-27 04:00 | 52.59 | 0 | 0 | 52.59 | 0 | 0 | 0 | 0 | 0
2025-07-27 05:00 | 53.69 | 7.23 | 7.23 | 46.46 | 0 | 0 | 0 | 0 | 0
2025-07-27 06:00 | 56.24 | 74.55 | 56.24 | 0 | 0 | 0 | 0 | 18.3 | 0
2025-07-27 07:00 | 58.45 | 102.17 | 58.45 | 0 | 0 | 0 | 0 | 43.72 | 0
2025-07-27 08:00 | 61.41 | 112.7 | 61.41 | 0 | 0 | 0 | 0 | 51.29 | 0
2025-07-27 09:00 | 64.33 | 116.54 | 64.33 | 0 | 0 | 0 | 0 | 52.21 | 0
2025-07-27 10:00 | 66.02 | 116.2 | 66.02 | 0 | 0 | 0 | 0 | 50.18 | 0
2025-07-27 11:00 | 69.37 | 113.6 | 69.37 | 0 | 0 | 0 | 0 | 44.23 | 0
2025-07-27 12:00 | 70.98 | 111.26 | 70.98 | 0 | 0 | 0 | 0 | 40.28 | 0
2025-07-27 13:00 | 72.09 | 112.72 | 72.09 | 0 | 0 | 0 | 0 | 40.64 | 0
2025-07-27 14:00 | 74.22 | 114.53 | 74.22 | 0 | 0 | 0 | 0 | 40.31 | 0
2025-07-27 15:00 | 74.03 | 115.06 | 74.03 | 0 | 0 | 0 | 0 | 41.03 | 0
2025-07-27 16:00 | 73.49 | 112.18 | 73.49 | 0 | 0 | 0 | 0 | 38.7 | 0
2025-07-27 17:00 | 72.4 | 102.36 | 72.4 | 0 | 0 | 0 | 0 | 29.96 | 0
2025-07-27 18:00 | 71.46 | 76.27 | 71.46 | 0 | 0 | 0 | 0 | 4.81 | 0
2025-07-27 19:00 | 69.91 | 6.88 | 6.88 | 63.03 | 0 | 0 | 0 | 0 | 0
2025-07-27 20:00 | 66.62 | 0 | 0 | 66.62 | 0 | 0 | 0 | 0 | 0
2025-07-27 21:00 | 64.27 | 0 | 0 | 64.27 | 0 | 0 | 0 | 0 | 0
2025-07-27 22:00 | 61.74 | 0 | 0 | 61.74 | 0 | 0 | 0 | 0 | 0
2025-07-27 23:00 | 57.39 | 0 | 0 | 57.39 | 0 | 0 | 0 | 0 | 0
2025-07-28 | 55.68 | 0 | 0 | 55.68 | 0 | 0 | 0 | 0 | 0
2025-07-28 01:00 | 53.32 | 0 | 0 | 53.32 | 0 | 0 | 0 | 0 | 0
2025-07-28 02:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 0 | 0 | 0
2025-07-28 03:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 0 | 0 | 0
2025-07-28 04:00 | 52.21 | 0 | 0 | 52.21 | 0 | 0 | 0 | 0 | 0
2025-07-28 05:00 | 54.5 | 1.76 | 1.76 | 52.74 | 0 | 0 | 0 | 0 | 0
2025-07-28 06:00 | 55.55 | 34.42 | 34.42 | 21.12 | 0 | 0 | 0 | 0 | 0
2025-07-28 07:00 | 58.6 | 72.48 | 58.6 | 0 | 0 | 0 | 0 | 13.88 | 0
2025-07-28 08:00 | 62.53 | 104.53 | 62.53 | 0 | 0 | 0 | 0 | 41.99 | 0
2025-07-28 09:00 | 64.42 | 107.54 | 64.42 | 0 | 0 | 0 | 0 | 43.12 | 0
2025-07-28 10:00 | 68.61 | 90.78 | 68.61 | 0 | 0 | 0 | 0 | 22.17 | 0
2025-07-28 11:00 | 70.38 | 92.16 | 70.38 | 0 | 0 | 0 | 0 | 21.78 | 0
2025-07-28 12:00 | 73.46 | 69.64 | 69.64 | 3.82 | 0 | 0 | 0 | 0 | 0
2025-07-28 13:00 | 74.56 | 67.42 | 67.42 | 7.14 | 0 | 0 | 0 | 0 | 0
2025-07-28 14:00 | 75.32 | 70.45 | 70.45 | 4.87 | 0 | 0 | 0 | 0 | 0
2025-07-28 15:00 | 75.47 | 88.94 | 75.47 | 0 | 0 | 0 | 0 | 13.48 | 0
2025-07-28 16:00 | 74.86 | 110.59 | 74.86 | 0 | 0 | 0 | 0 | 35.73 | 0
2025-07-28 17:00 | 74.22 | 116.87 | 74.22 | 0 | 0 | 0 | 0 | 42.65 | 0
2025-07-28 18:00 | 73.02 | 92.69 | 73.02 | 0 | 0 | 0 | 0 | 19.68 | 0
2025-07-28 19:00 | 70.37 | 10.98 | 10.98 | 59.39 | 0 | 0 | 0 | 0 | 0
2025-07-28 20:00 | 67.55 | 0 | 0 | 67.55 | 0 | 0 | 0 | 0 | 0
2025-07-28 21:00 | 64.57 | 0 | 0 | 64.57 | 0 | 0 | 0 | 0 | 0
2025-07-28 22:00 | 62.03 | 0 | 0 | 62.03 | 0 | 0 | 0 | 0 | 0
2025-07-28 23:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 0 | 0 | 0
2025-07-29 | 55.42 | 0 | 0 | 55.42 | 0 | 0 | 0 | 0 | 0
2025-07-29 01:00 | 53.2 | 0 | 0 | 53.2 | 0 | 0 | 0 | 0 | 0
2025-07-29 02:00 | 52.32 | 0 | 0 | 52.32 | 0 | 0 | 0 | 0 | 0
2025-07-29 03:00 | 52.41 | 0 | 0 | 52.41 | 0 | 0 | 0 | 0 | 0
2025-07-29 04:00 | 52.7 | 0 | 0 | 52.7 | 0 | 0 | 0 | 0 | 0
2025-07-29 05:00 | 52.91 | 0.87 | 0.87 | 52.04 | 0 | 0 | 0 | 0 | 0
2025-07-29 06:00 | 55.63 | 55.55 | 55.55 | 0.07 | 0 | 0 | 0 | 0 | 0
2025-07-29 07:00 | 58.15 | 115.14 | 58.15 | 0 | 0 | 0 | 0 | 56.99 | 0
2025-07-29 08:00 | 61.77 | 117.4 | 61.77 | 0 | 0 | 0 | 0 | 55.63 | 0
2025-07-29 09:00 | 66.18 | 90.38 | 66.18 | 0 | 0 | 0 | 0 | 24.2 | 0
2025-07-29 10:00 | 68.08 | 87.19 | 68.08 | 0 | 0 | 0 | 0 | 19.11 | 0
2025-07-29 11:00 | 71.11 | 66.03 | 66.03 | 5.08 | 0 | 0 | 0 | 0 | 0
2025-07-29 12:00 | 74.16 | 87.75 | 74.16 | 0 | 0 | 0 | 0 | 13.59 | 0
2025-07-29 13:00 | 76.72 | 20.34 | 20.34 | 56.38 | 0 | 0 | 0 | 0 | 0
2025-07-29 14:00 | 78.14 | 7.29 | 7.29 | 70.85 | 0 | 0 | 0 | 0 | 0
2025-07-29 15:00 | 78.47 | 21.16 | 21.16 | 57.31 | 0 | 0 | 0 | 0 | 0
2025-07-29 16:00 | 78.42 | 4.23 | 4.23 | 74.19 | 0 | 0 | 0 | 0 | 0
2025-07-29 17:00 | 75.7 | 2.37 | 2.37 | 73.32 | 0 | 0 | 0 | 0 | 0
2025-07-29 18:00 | 75.16 | 0.72 | 0.72 | 74.44 | 0 | 0 | 0 | 0 | 0
2025-07-29 19:00 | 71.77 | 0 | 0 | 71.77 | 0 | 0 | 0 | 0 | 0
2025-07-29 20:00 | 69.16 | 0 | 0 | 69.16 | 0 | 0 | 0 | 0 | 0
2025-07-29 21:00 | 64.72 | 0 | 0 | 64.72 | 0 | 0 | 0 | 0 | 0
2025-07-29 22:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 0 | 0 | 0
2025-07-29 23:00 | 58.74 | 0 | 0 | 58.74 | 0 | 0 | 0 | 0 | 0
2025-07-30 | 56.46 | 0 | 0 | 56.46 | 0 | 0 | 0 | 0 | 0
2025-07-30 01:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 0 | 0 | 0
2025-07-30 02:00 | 52.14 | 0 | 0 | 52.14 | 0 | 0 | 0 | 0 | 0
2025-07-30 03:00 | 51.1 | 0 | 0 | 51.1 | 0 | 0 | 0 | 0 | 0
2025-07-30 04:00 | 52.38 | 0 | 0 | 52.38 | 0 | 0 | 0 | 0 | 0
2025-07-30 05:00 | 53.94 | 0.02 | 0.02 | 53.93 | 0 | 0 | 0 | 0 | 0
2025-07-30 06:00 | 56.53 | 15.89 | 15.89 | 40.63 | 0 | 0 | 0 | 0 | 0
2025-07-30 07:00 | 58.74 | 9.34 | 9.34 | 49.4 | 0 | 0 | 0 | 0 | 0
2025-07-30 08:00 | 63.23 | 64.1 | 63.23 | 0 | 0 | 0 | 0 | 0.87 | 0
2025-07-30 09:00 | 67.63 | 68.63 | 67.63 | 0 | 0 | 0 | 0 | 1 | 0
2025-07-30 10:00 | 70.47 | 14.56 | 14.56 | 55.92 | 0 | 0 | 0 | 0 | 0
2025-07-30 11:00 | 75.79 | 7.51 | 7.51 | 68.28 | 0 | 0 | 0 | 0 | 0
2025-07-30 12:00 | 79.67 | 39.52 | 39.52 | 40.15 | 0 | 0 | 0 | 0 | 0
2025-07-30 13:00 | 81.97 | 94.27 | 81.97 | 0 | 0 | 0 | 0 | 12.3 | 0
2025-07-30 14:00 | 83.35 | 93.09 | 83.35 | 0 | 0 | 0 | 0 | 9.74 | 0
2025-07-30 15:00 | 85.07 | 5.87 | 5.87 | 79.2 | 0 | 0 | 0 | 0 | 0
2025-07-30 16:00 | 83.36 | 88.06 | 83.36 | 0 | 0 | 0 | 0 | 4.7 | 0
2025-07-30 17:00 | 82.01 | 96.7 | 82.01 | 0 | 0 | 0 | 0 | 14.69 | 0
2025-07-30 18:00 | 79.17 | 59.22 | 59.22 | 19.95 | 0 | 0 | 0 | 0 | 0
2025-07-30 19:00 | 75.84 | 2.83 | 2.83 | 73.01 | 0 | 0 | 0 | 0 | 0
2025-07-30 20:00 | 70.98 | 0 | 0 | 70.98 | 0 | 0 | 0 | 0 | 0
2025-07-30 21:00 | 66.61 | 0 | 0 | 66.61 | 0 | 0 | 0 | 0 | 0
2025-07-30 22:00 | 62.81 | 0 | 0 | 62.81 | 0 | 0 | 0 | 0 | 0
2025-07-30 23:00 | 59.51 | 0 | 0 | 59.51 | 0 | 0 | 0 | 0 | 0
2025-07-31 | 56.77 | 0 | 0 | 56.77 | 0 | 0 | 0 | 0 | 0
2025-07-31 01:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 0 | 0 | 0
2025-07-31 02:00 | 52.26 | 0 | 0 | 52.26 | 0 | 0 | 0 | 0 | 0
2025-07-31 03:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0
2025-07-31 04:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 0 | 0 | 0
2025-07-31 05:00 | 53.02 | 8.51 | 8.51 | 44.51 | 0 | 0 | 0 | 0 | 0
2025-07-31 06:00 | 55.29 | 82.69 | 55.29 | 0 | 0 | 0 | 0 | 27.41 | 0
2025-07-31 07:00 | 57.98 | 105.96 | 57.98 | 0 | 0 | 0 | 0 | 47.98 | 0
2025-07-31 08:00 | 61.14 | 130.17 | 61.14 | 0 | 0 | 0 | 0 | 69.03 | 0
2025-07-31 09:00 | 64.24 | 132.89 | 64.24 | 0 | 0 | 0 | 0 | 68.65 | 0
2025-07-31 10:00 | 66.99 | 131.21 | 66.99 | 0 | 0 | 0 | 0 | 64.22 | 0
2025-07-31 11:00 | 69.03 | 93.86 | 69.03 | 0 | 0 | 0 | 0 | 24.82 | 0
2025-07-31 12:00 | 70.18 | 59.59 | 59.59 | 10.59 | 0 | 0 | 0 | 0 | 0
2025-07-31 13:00 | 72.5 | 68.13 | 68.13 | 4.36 | 0 | 0 | 0 | 0 | 0
2025-07-31 14:00 | 72.87 | 53.84 | 53.84 | 19.04 | 0 | 0 | 0 | 0 | 0
2025-07-31 15:00 | 73.73 | 53.47 | 53.47 | 20.26 | 0 | 0 | 0 | 0 | 0
2025-07-31 16:00 | 72.54 | 13.78 | 13.78 | 58.76 | 0 | 0 | 0 | 0 | 0
2025-07-31 17:00 | 71.33 | 6.93 | 6.93 | 64.4 | 0 | 0 | 0 | 0 | 0
2025-07-31 18:00 | 70.83 | 0.78 | 0.78 | 70.05 | 0 | 0 | 0 | 0 | 0
2025-07-31 19:00 | 69.68 | 0 | 0 | 69.68 | 0 | 0 | 0 | 0 | 0
2025-07-31 20:00 | 66.83 | 0 | 0 | 66.83 | 0 | 0 | 0 | 0 | 0
2025-07-31 21:00 | 63.98 | 0 | 0 | 63.98 | 0 | 0 | 0 | 0 | 0
2025-07-31 22:00 | 60.74 | 0 | 0 | 60.74 | 0 | 0 | 0 | 0 | 0
2025-07-31 23:00 | 59.15 | 0 | 0 | 59.15 | 0 | 0 | 0 | 0 | 0
2025-08-01 | 55.24 | 0 | 0 | 55.24 | 0 | 0 | 0 | 0 | 0
2025-08-01 01:00 | 53.14 | 0 | 0 | 53.14 | 0 | 0 | 0 | 0 | 0
2025-08-01 02:00 | 52.38 | 0 | 0 | 52.38 | 0 | 0 | 0 | 0 | 0
2025-08-01 03:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 0 | 0 | 0
2025-08-01 04:00 | 52.73 | 0 | 0 | 52.73 | 0 | 0 | 0 | 0 | 0
2025-08-01 05:00 | 53.82 | 0.03 | 0.03 | 53.78 | 0 | 0 | 0 | 0 | 0
2025-08-01 06:00 | 56.2 | 9.5 | 9.5 | 46.7 | 0 | 0 | 0 | 0 | 0
2025-08-01 07:00 | 58.96 | 30.39 | 30.39 | 28.58 | 0 | 0 | 0 | 0 | 0
2025-08-01 08:00 | 62.02 | 64.65 | 62.02 | 0 | 0 | 0 | 0 | 2.62 | 0
2025-08-01 09:00 | 65.25 | 55.41 | 55.41 | 9.84 | 0 | 0 | 0 | 0 | 0
2025-08-01 10:00 | 69.39 | 48.7 | 48.7 | 20.69 | 0 | 0 | 0 | 0 | 0
2025-08-01 11:00 | 72.4 | 41.39 | 41.39 | 31.02 | 0 | 0 | 0 | 0 | 0
2025-08-01 12:00 | 76.09 | 8.05 | 8.05 | 68.04 | 0 | 0 | 0 | 0 | 0
2025-08-01 13:00 | 78.51 | 8.05 | 8.05 | 70.47 | 0 | 0 | 0 | 0 | 0
2025-08-01 14:00 | 80.27 | 20.11 | 20.11 | 60.16 | 0 | 0 | 0 | 0 | 0
2025-08-01 15:00 | 80.21 | 24.2 | 24.2 | 56.01 | 0 | 0 | 0 | 0 | 0
2025-08-01 16:00 | 80 | 14.48 | 14.48 | 65.52 | 0 | 0 | 0 | 0 | 0
2025-08-01 17:00 | 77.96 | 11.6 | 11.6 | 66.36 | 0 | 0 | 0 | 0 | 0
2025-08-01 18:00 | 75.6 | 2.03 | 2.03 | 73.57 | 0 | 0 | 0 | 0 | 0
2025-08-01 19:00 | 73.13 | 0 | 0 | 73.13 | 0 | 0 | 0 | 0 | 0
2025-08-01 20:00 | 69.26 | 0 | 0 | 69.26 | 0 | 0 | 0 | 0 | 0
2025-08-01 21:00 | 65.91 | 0 | 0 | 65.91 | 0 | 0 | 0 | 0 | 0
2025-08-01 22:00 | 61.57 | 0 | 0 | 61.57 | 0 | 0 | 0 | 0 | 0
2025-08-01 23:00 | 58.24 | 0 | 0 | 58.24 | 0 | 0 | 0 | 0 | 0
2025-08-02 | 56 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0
2025-08-02 01:00 | 53.92 | 0 | 0 | 53.92 | 0 | 0 | 0 | 0 | 0
2025-08-02 02:00 | 51.58 | 0 | 0 | 51.58 | 0 | 0 | 0 | 0 | 0
2025-08-02 03:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 0 | 0 | 0
2025-08-02 04:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0 | 0 | 0
2025-08-02 05:00 | 53.48 | 1.68 | 1.68 | 51.81 | 0 | 0 | 0 | 0 | 0
2025-08-02 06:00 | 56.39 | 20.79 | 20.79 | 35.6 | 0 | 0 | 0 | 0 | 0
2025-08-02 07:00 | 58.9 | 38.09 | 38.09 | 20.82 | 0 | 0 | 0 | 0 | 0
2025-08-02 08:00 | 62.12 | 72.48 | 62.12 | 0 | 0 | 0 | 0 | 10.36 | 0
2025-08-02 09:00 | 66.05 | 101.7 | 66.05 | 0 | 0 | 0 | 0 | 35.65 | 0
2025-08-02 10:00 | 68.04 | 106.4 | 68.04 | 0 | 0 | 0 | 0 | 38.36 | 0
2025-08-02 11:00 | 70.89 | 88.94 | 70.89 | 0 | 0 | 0 | 0 | 18.04 | 0
2025-08-02 12:00 | 73.54 | 86.72 | 73.54 | 0 | 0 | 0 | 0 | 13.18 | 0
2025-08-02 13:00 | 75.67 | 87.77 | 75.67 | 0 | 0 | 0 | 0 | 12.11 | 0
2025-08-02 14:00 | 75.79 | 100.46 | 75.79 | 0 | 0 | 0 | 0 | 24.67 | 0
2025-08-02 15:00 | 77.26 | 69.25 | 69.25 | 8.01 | 0 | 0 | 0 | 0 | 0
2025-08-02 16:00 | 76.7 | 57.18 | 57.18 | 19.51 | 0 | 0 | 0 | 0 | 0
2025-08-02 17:00 | 76.19 | 38.14 | 38.14 | 38.04 | 0 | 0 | 0 | 0 | 0
2025-08-02 18:00 | 74.08 | 27.25 | 27.25 | 46.82 | 0 | 0 | 0 | 0 | 0
2025-08-02 19:00 | 71.08 | 2.48 | 2.48 | 68.61 | 0 | 0 | 0 | 0 | 0
2025-08-02 20:00 | 68.68 | 0 | 0 | 68.68 | 0 | 0 | 0 | 0 | 0
2025-08-02 21:00 | 65.46 | 0 | 0 | 65.46 | 0 | 0 | 0 | 0 | 0
2025-08-02 22:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 0 | 0 | 0
2025-08-02 23:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 0 | 0 | 0
2025-08-03 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 0 | 0 | 0
2025-08-03 01:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 0 | 0 | 0
2025-08-03 02:00 | 51.69 | 0 | 0 | 51.69 | 0 | 0 | 0 | 0 | 0
2025-08-03 03:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 0 | 0 | 0
2025-08-03 04:00 | 51.58 | 0 | 0 | 51.58 | 0 | 0 | 0 | 0 | 0
2025-08-03 05:00 | 53.2 | 3.55 | 3.55 | 49.65 | 0 | 0 | 0 | 0 | 0
2025-08-03 06:00 | 55.06 | 71.57 | 55.06 | 0 | 0 | 0 | 0 | 16.51 | 0
2025-08-03 07:00 | 58.61 | 113.33 | 58.61 | 0 | 0 | 0 | 0 | 54.72 | 0
2025-08-03 08:00 | 62.01 | 126.72 | 62.01 | 0 | 0 | 0 | 0 | 64.71 | 0
2025-08-03 09:00 | 65.46 | 124.76 | 65.46 | 0 | 0 | 0 | 0 | 59.3 | 0
2025-08-03 10:00 | 68.68 | 116.48 | 68.68 | 0 | 0 | 0 | 0 | 47.81 | 0
2025-08-03 11:00 | 71.02 | 55.64 | 55.64 | 15.38 | 0 | 0 | 0 | 0 | 0
2025-08-03 12:00 | 74.13 | 75.94 | 74.13 | 0 | 0 | 0 | 0 | 1.82 | 0
2025-08-03 13:00 | 76.24 | 75.27 | 75.27 | 0.97 | 0 | 0 | 0 | 0 | 0
2025-08-03 14:00 | 77.49 | 65.24 | 65.24 | 12.25 | 0 | 0 | 0 | 0 | 0
2025-08-03 15:00 | 78.15 | 64.68 | 64.68 | 13.48 | 0 | 0 | 0 | 0 | 0
2025-08-03 16:00 | 78.4 | 47.8 | 47.8 | 30.6 | 0 | 0 | 0 | 0 | 0
2025-08-03 17:00 | 76.85 | 32.05 | 32.05 | 44.8 | 0 | 0 | 0 | 0 | 0
2025-08-03 18:00 | 73.94 | 16.1 | 16.1 | 57.84 | 0 | 0 | 0 | 0 | 0
2025-08-03 19:00 | 72.13 | 1.2 | 1.2 | 70.94 | 0 | 0 | 0 | 0 | 0
2025-08-03 20:00 | 68.99 | 0 | 0 | 68.99 | 0 | 0 | 0 | 0 | 0
2025-08-03 21:00 | 64.86 | 0 | 0 | 64.86 | 0 | 0 | 0 | 0 | 0
2025-08-03 22:00 | 62.22 | 0 | 0 | 62.22 | 0 | 0 | 0 | 0 | 0
2025-08-03 23:00 | 58.44 | 0 | 0 | 58.44 | 0 | 0 | 0 | 0 | 0
2025-08-04 | 55.09 | 0 | 0 | 55.09 | 0 | 0 | 0 | 0 | 0
2025-08-04 01:00 | 53.69 | 0 | 0 | 53.69 | 0 | 0 | 0 | 0 | 0
2025-08-04 02:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 0 | 0 | 0
2025-08-04 03:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 0 | 0 | 0
2025-08-04 04:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 0 | 0 | 0
2025-08-04 05:00 | 53.11 | 2.68 | 2.68 | 50.43 | 0 | 0 | 0 | 0 | 0
2025-08-04 06:00 | 56.1 | 57.25 | 56.1 | 0 | 0 | 0 | 0 | 1.16 | 0
2025-08-04 07:00 | 58.9 | 91.65 | 58.9 | 0 | 0 | 0 | 0 | 32.75 | 0
2025-08-04 08:00 | 62.78 | 103.52 | 62.78 | 0 | 0 | 0 | 0 | 40.74 | 0
2025-08-04 09:00 | 67.09 | 111.52 | 67.09 | 0 | 0 | 0 | 0 | 44.43 | 0
2025-08-04 10:00 | 70.73 | 110.2 | 70.73 | 0 | 0 | 0 | 0 | 39.48 | 0
2025-08-04 11:00 | 75.1 | 111.82 | 75.1 | 0 | 0 | 0 | 0 | 36.73 | 0
2025-08-04 12:00 | 78.2 | 108.56 | 78.2 | 0 | 0 | 0 | 0 | 30.35 | 0
2025-08-04 13:00 | 82.55 | 106.04 | 82.55 | 0 | 0 | 0 | 0 | 23.49 | 0
2025-08-04 14:00 | 83.56 | 105.9 | 83.56 | 0 | 0 | 0 | 0 | 22.34 | 0
2025-08-04 15:00 | 84.88 | 104.83 | 84.88 | 0 | 0 | 0 | 0 | 19.95 | 0
2025-08-04 16:00 | 84.35 | 103.73 | 84.35 | 0 | 0 | 0 | 0 | 19.39 | 0
2025-08-04 17:00 | 82.57 | 82.17 | 82.17 | 0.4 | 0 | 0 | 0 | 0 | 0
2025-08-04 18:00 | 78.71 | 49.7 | 49.7 | 29.01 | 0 | 0 | 0 | 0 | 0
2025-08-04 19:00 | 75.51 | 2.49 | 2.49 | 73.02 | 0 | 0 | 0 | 0 | 0
2025-08-04 20:00 | 72.14 | 0 | 0 | 72.14 | 0 | 0 | 0 | 0 | 0
2025-08-04 21:00 | 67.77 | 0 | 0 | 67.77 | 0 | 0 | 0 | 0 | 0
2025-08-04 22:00 | 63.19 | 0 | 0 | 63.19 | 0 | 0 | 0 | 0 | 0
2025-08-04 23:00 | 59.09 | 0 | 0 | 59.09 | 0 | 0 | 0 | 0 | 0
2025-08-05 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 0 | 0 | 0
2025-08-05 01:00 | 53.79 | 0 | 0 | 53.79 | 0 | 0 | 0 | 0 | 0
2025-08-05 02:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 0 | 0 | 0
2025-08-05 03:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0 | 0 | 0
2025-08-05 04:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 0 | 0 | 0
2025-08-05 05:00 | 53.34 | 1.82 | 1.82 | 51.52 | 0 | 0 | 0 | 0 | 0
2025-08-05 06:00 | 55.79 | 48.65 | 48.65 | 7.14 | 0 | 0 | 0 | 0 | 0
2025-08-05 07:00 | 58.86 | 81.38 | 58.86 | 0 | 0 | 0 | 0 | 22.51 | 0
2025-08-05 08:00 | 62.58 | 94.12 | 62.58 | 0 | 0 | 0 | 0 | 31.53 | 0
2025-08-05 09:00 | 65.99 | 99.43 | 65.99 | 0 | 0 | 0 | 0 | 33.43 | 0
2025-08-05 10:00 | 69.65 | 104.29 | 69.65 | 0 | 0 | 0 | 0 | 34.64 | 0
2025-08-05 11:00 | 74.98 | 104.69 | 74.98 | 0 | 0 | 0 | 0 | 29.71 | 0
2025-08-05 12:00 | 78.78 | 101.65 | 78.78 | 0 | 0 | 0 | 0 | 22.87 | 0
2025-08-05 13:00 | 80.38 | 103.22 | 80.38 | 0 | 0 | 0 | 0 | 22.83 | 0
2025-08-05 14:00 | 81.16 | 105.53 | 81.16 | 0 | 0 | 0 | 0 | 24.37 | 0
2025-08-05 15:00 | 82.01 | 106.68 | 82.01 | 0 | 0 | 0 | 0 | 24.67 | 0
2025-08-05 16:00 | 82.08 | 95.23 | 82.08 | 0 | 0 | 0 | 0 | 13.15 | 0
2025-08-05 17:00 | 80.83 | 75.42 | 75.42 | 5.41 | 0 | 0 | 0 | 0 | 0
2025-08-05 18:00 | 76.93 | 38.1 | 38.1 | 38.83 | 0 | 0 | 0 | 0 | 0
2025-08-05 19:00 | 74.11 | 1.83 | 1.83 | 72.28 | 0 | 0 | 0 | 0 | 0
2025-08-05 20:00 | 70.42 | 0 | 0 | 70.42 | 0 | 0 | 0 | 0 | 0
2025-08-05 21:00 | 66.72 | 0 | 0 | 66.72 | 0 | 0 | 0 | 0 | 0
2025-08-05 22:00 | 62.16 | 0 | 0 | 62.16 | 0 | 0 | 0 | 0 | 0
2025-08-05 23:00 | 57.96 | 0 | 0 | 57.96 | 0 | 0 | 0 | 0 | 0
2025-08-06 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 0 | 0 | 0
2025-08-06 01:00 | 53.98 | 0 | 0 | 53.98 | 0 | 0 | 0 | 0 | 0
2025-08-06 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0 | 0 | 0
2025-08-06 03:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0 | 0 | 0
2025-08-06 04:00 | 51.75 | 0 | 0 | 51.75 | 0 | 0 | 0 | 0 | 0
2025-08-06 05:00 | 53 | 3.05 | 3.05 | 49.95 | 0 | 0 | 0 | 0 | 0
2025-08-06 06:00 | 56.28 | 71.84 | 56.28 | 0 | 0 | 0 | 0 | 15.56 | 0
2025-08-06 07:00 | 59.15 | 114.68 | 59.15 | 0 | 0 | 0 | 0 | 55.53 | 0
2025-08-06 08:00 | 63.1 | 125.67 | 63.1 | 0 | 0 | 0 | 0 | 62.57 | 0
2025-08-06 09:00 | 68 | 127.84 | 68 | 0 | 0 | 0 | 0 | 59.84 | 0
2025-08-06 10:00 | 71.35 | 126.04 | 71.35 | 0 | 0 | 0 | 0 | 54.69 | 0
2025-08-06 11:00 | 76.11 | 119.86 | 76.11 | 0 | 0 | 0 | 0 | 43.75 | 0
2025-08-06 12:00 | 80.5 | 121.21 | 80.5 | 0 | 0 | 0 | 0 | 40.7 | 0
2025-08-06 13:00 | 83.34 | 122.61 | 83.34 | 0 | 0 | 0 | 0 | 39.28 | 0
2025-08-06 14:00 | 86.06 | 76.11 | 76.11 | 9.95 | 0 | 0 | 0 | 0 | 0
2025-08-06 15:00 | 86.28 | 26.62 | 26.62 | 59.66 | 0 | 0 | 0 | 0 | 0
2025-08-06 16:00 | 85.17 | 108.05 | 85.17 | 0 | 0 | 0 | 0 | 22.88 | 0
2025-08-06 17:00 | 83.65 | 60.44 | 60.44 | 23.21 | 0 | 0 | 0 | 0 | 0
2025-08-06 18:00 | 80.51 | 44.02 | 44.02 | 36.48 | 0 | 0 | 0 | 0 | 0
2025-08-06 19:00 | 76.86 | 4.46 | 4.46 | 72.4 | 0 | 0 | 0 | 0 | 0
2025-08-06 20:00 | 72.07 | 0 | 0 | 72.07 | 0 | 0 | 0 | 0 | 0
2025-08-06 21:00 | 67.48 | 0 | 0 | 67.48 | 0 | 0 | 0 | 0 | 0
2025-08-06 22:00 | 63.01 | 0 | 0 | 63.01 | 0 | 0 | 0 | 0 | 0
2025-08-06 23:00 | 58.86 | 0 | 0 | 58.86 | 0 | 0 | 0 | 0 | 0
2025-08-07 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 0 | 0 | 0
2025-08-07 01:00 | 53.5 | 0 | 0 | 53.5 | 0 | 0 | 0 | 0 | 0
2025-08-07 02:00 | 51.79 | 0 | 0 | 51.79 | 0 | 0 | 0 | 0 | 0
2025-08-07 03:00 | 52.32 | 0 | 0 | 52.32 | 0 | 0 | 0 | 0 | 0
2025-08-07 04:00 | 52.63 | 0 | 0 | 52.63 | 0 | 0 | 0 | 0 | 0
2025-08-07 05:00 | 53.67 | 1.34 | 1.34 | 52.33 | 0 | 0 | 0 | 0 | 0
2025-08-07 06:00 | 55.76 | 35.2 | 35.2 | 20.56 | 0 | 0 | 0 | 0 | 0
2025-08-07 07:00 | 58.4 | 82.91 | 58.4 | 0 | 0 | 0 | 0 | 24.5 | 0
2025-08-07 08:00 | 61.14 | 101.54 | 61.14 | 0 | 0 | 0 | 0 | 40.39 | 0
2025-08-07 09:00 | 65.21 | 105.79 | 65.21 | 0 | 0 | 0 | 0 | 40.58 | 0
2025-08-07 10:00 | 68.88 | 107.88 | 68.88 | 0 | 0 | 0 | 0 | 39 | 0
2025-08-07 11:00 | 72.2 | 102.86 | 72.2 | 0 | 0 | 0 | 0 | 30.66 | 0
2025-08-07 12:00 | 75.1 | 95.51 | 75.1 | 0 | 0 | 0 | 0 | 20.41 | 0
2025-08-07 13:00 | 77.44 | 94.52 | 77.44 | 0 | 0 | 0 | 0 | 17.08 | 0
2025-08-07 14:00 | 77.96 | 96.74 | 77.96 | 0 | 0 | 0 | 0 | 18.78 | 0
2025-08-07 15:00 | 78.42 | 78.55 | 78.42 | 0 | 0 | 0 | 0 | 0.13 | 0
2025-08-07 16:00 | 79.04 | 77.44 | 77.44 | 1.6 | 0 | 0 | 0 | 0 | 0
2025-08-07 17:00 | 77.37 | 64.61 | 64.61 | 12.76 | 0 | 0 | 0 | 0 | 0
2025-08-07 18:00 | 74.67 | 35.99 | 35.99 | 38.68 | 0 | 0 | 0 | 0 | 0
2025-08-07 19:00 | 72.03 | 1.14 | 1.14 | 70.89 | 0 | 0 | 0 | 0 | 0
2025-08-07 20:00 | 68.78 | 0 | 0 | 68.78 | 0 | 0 | 0 | 0 | 0
2025-08-07 21:00 | 65.33 | 0 | 0 | 65.33 | 0 | 0 | 0 | 0 | 0
2025-08-07 22:00 | 62.01 | 0 | 0 | 62.01 | 0 | 0 | 0 | 0 | 0
2025-08-07 23:00 | 59.71 | 0 | 0 | 59.71 | 0 | 0 | 0 | 0 | 0
2025-08-08 | 55.57 | 0 | 0 | 55.57 | 0 | 0 | 0 | 0 | 0
2025-08-08 01:00 | 53.64 | 0 | 0 | 53.64 | 0 | 0 | 0 | 0 | 0
2025-08-08 02:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0
2025-08-08 03:00 | 51.21 | 0 | 0 | 51.21 | 0 | 0 | 0 | 0 | 0
2025-08-08 04:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 0 | 0 | 0
2025-08-08 05:00 | 53.51 | 2.9 | 2.9 | 50.62 | 0 | 0 | 0 | 0 | 0
2025-08-08 06:00 | 53.28 | 32.28 | 32.28 | 21 | 0 | 0 | 0 | 0 | 0
2025-08-08 07:00 | 58.57 | 29.11 | 29.11 | 29.46 | 0 | 0 | 0 | 0 | 0
2025-08-08 08:00 | 62.31 | 55.4 | 55.4 | 6.91 | 0 | 0 | 0 | 0 | 0
2025-08-08 09:00 | 63.58 | 107.68 | 63.58 | 0 | 0 | 0 | 0 | 44.09 | 0
2025-08-08 10:00 | 68.46 | 134.54 | 68.46 | 0 | 0 | 0 | 0 | 66.08 | 0
2025-08-08 11:00 | 69.1 | 119.27 | 69.1 | 0 | 0 | 0 | 0 | 50.17 | 0
2025-08-08 12:00 | 73.28 | 54.22 | 54.22 | 19.06 | 0 | 0 | 0 | 0 | 0
2025-08-08 13:00 | 74.53 | 9.08 | 9.08 | 65.45 | 0 | 0 | 0 | 0 | 0
2025-08-08 14:00 | 74.43 | 8.18 | 8.18 | 66.24 | 0 | 0 | 0 | 0 | 0
2025-08-08 15:00 | 76.18 | 17.96 | 17.96 | 58.22 | 0 | 0 | 0 | 0 | 0
2025-08-08 16:00 | 76.18 | 53.71 | 53.71 | 22.46 | 0 | 0 | 0 | 0 | 0
2025-08-08 17:00 | 74.72 | 62.09 | 62.09 | 12.63 | 0 | 0 | 0 | 0 | 0
2025-08-08 18:00 | 73.1 | 63.25 | 63.25 | 9.85 | 0 | 0 | 0 | 0 | 0
2025-08-08 19:00 | 70.28 | 2.28 | 2.28 | 68 | 0 | 0 | 0 | 0 | 0
2025-08-08 20:00 | 66.76 | 0 | 0 | 66.76 | 0 | 0 | 0 | 0 | 0
2025-08-08 21:00 | 64.93 | 0 | 0 | 64.93 | 0 | 0 | 0 | 0 | 0
2025-08-08 22:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 0 | 0 | 0
2025-08-08 23:00 | 58.8 | 0 | 0 | 58.8 | 0 | 0 | 0 | 0 | 0
2025-08-09 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 0 | 0 | 0
2025-08-09 01:00 | 52.53 | 0 | 0 | 52.53 | 0 | 0 | 0 | 0 | 0
2025-08-09 02:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0 | 0 | 0
2025-08-09 03:00 | 50.62 | 0 | 0 | 50.62 | 0 | 0 | 0 | 0 | 0
2025-08-09 04:00 | 51.92 | 0 | 0 | 51.92 | 0 | 0 | 0 | 0 | 0
2025-08-09 05:00 | 53.48 | 0.06 | 0.06 | 53.43 | 0 | 0 | 0 | 0 | 0
2025-08-09 06:00 | 54.78 | 7.34 | 7.34 | 47.44 | 0 | 0 | 0 | 0 | 0
2025-08-09 07:00 | 58.73 | 11.16 | 11.16 | 47.57 | 0 | 0 | 0 | 0 | 0
2025-08-09 08:00 | 61.93 | 17.12 | 17.12 | 44.81 | 0 | 0 | 0 | 0 | 0
2025-08-09 09:00 | 64.85 | 37.63 | 37.63 | 27.22 | 0 | 0 | 0 | 0 | 0
2025-08-09 10:00 | 68.49 | 66.1 | 66.1 | 2.39 | 0 | 0 | 0 | 0 | 0
2025-08-09 11:00 | 70.79 | 44.63 | 44.63 | 26.16 | 0 | 0 | 0 | 0 | 0
2025-08-09 12:00 | 74.31 | 54.55 | 54.55 | 19.75 | 0 | 0 | 0 | 0 | 0
2025-08-09 13:00 | 76.54 | 63.43 | 63.43 | 13.11 | 0 | 0 | 0 | 0 | 0
2025-08-09 14:00 | 77.91 | 59.23 | 59.23 | 18.68 | 0 | 0 | 0 | 0 | 0
2025-08-09 15:00 | 78.45 | 45.1 | 45.1 | 33.35 | 0 | 0 | 0 | 0 | 0
2025-08-09 16:00 | 77.95 | 22.63 | 22.63 | 55.32 | 0 | 0 | 0 | 0 | 0
2025-08-09 17:00 | 76.4 | 9.81 | 9.81 | 66.6 | 0 | 0 | 0 | 0 | 0
2025-08-09 18:00 | 74.62 | 0 | 0 | 74.62 | 0 | 0 | 0 | 0 | 0
2025-08-09 19:00 | 72.27 | 0 | 0 | 72.27 | 0 | 0 | 0 | 0 | 0
2025-08-09 20:00 | 68.53 | 0 | 0 | 68.53 | 0 | 0 | 0 | 0 | 0
2025-08-09 21:00 | 65.28 | 0 | 0 | 65.28 | 0 | 0 | 0 | 0 | 0
2025-08-09 22:00 | 61.54 | 0 | 0 | 61.54 | 0 | 0 | 0 | 0 | 0
2025-08-09 23:00 | 58.02 | 0 | 0 | 58.02 | 0 | 0 | 0 | 0 | 0
2025-08-10 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 0 | 0 | 0
2025-08-10 01:00 | 52.98 | 0 | 0 | 52.98 | 0 | 0 | 0 | 0 | 0
2025-08-10 02:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 0 | 0 | 0
2025-08-10 03:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-08-10 04:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0 | 0 | 0
2025-08-10 05:00 | 53.1 | 1.02 | 1.02 | 52.08 | 0 | 0 | 0 | 0 | 0
2025-08-10 06:00 | 55.25 | 66.56 | 55.25 | 0 | 0 | 0 | 0 | 11.32 | 0
2025-08-10 07:00 | 57.62 | 111.57 | 57.62 | 0 | 0 | 0 | 0 | 53.95 | 0
2025-08-10 08:00 | 62.09 | 121.92 | 62.09 | 0 | 0 | 0 | 0 | 59.83 | 0
2025-08-10 09:00 | 65.77 | 123.12 | 65.77 | 0 | 0 | 0 | 0 | 57.35 | 0
2025-08-10 10:00 | 69.87 | 120.86 | 69.87 | 0 | 0 | 0 | 0 | 50.99 | 0
2025-08-10 11:00 | 72.75 | 117.57 | 72.75 | 0 | 0 | 0 | 0 | 44.82 | 0
2025-08-10 12:00 | 77.05 | 115.54 | 77.05 | 0 | 0 | 0 | 0 | 38.48 | 0
2025-08-10 13:00 | 78.31 | 116.64 | 78.31 | 0 | 0 | 0 | 0 | 38.33 | 0
2025-08-10 14:00 | 79.57 | 119.19 | 79.57 | 0 | 0 | 0 | 0 | 39.62 | 0
2025-08-10 15:00 | 80.03 | 120.22 | 80.03 | 0 | 0 | 0 | 0 | 40.19 | 0
2025-08-10 16:00 | 79.14 | 118.19 | 79.14 | 0 | 0 | 0 | 0 | 39.05 | 0
2025-08-10 17:00 | 79.27 | 107.48 | 79.27 | 0 | 0 | 0 | 0 | 28.21 | 0
2025-08-10 18:00 | 76.79 | 62.66 | 62.66 | 14.13 | 0 | 0 | 0 | 0 | 0
2025-08-10 19:00 | 73.31 | 0.89 | 0.89 | 72.42 | 0 | 0 | 0 | 0 | 0
2025-08-10 20:00 | 68.99 | 0 | 0 | 68.99 | 0 | 0 | 0 | 0 | 0
2025-08-10 21:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 0 | 0 | 0
2025-08-10 22:00 | 61.72 | 0 | 0 | 61.72 | 0 | 0 | 0 | 0 | 0
2025-08-10 23:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 0 | 0 | 0
2025-08-11 | 56.17 | 0 | 0 | 56.17 | 0 | 0 | 0 | 0 | 0
2025-08-11 01:00 | 53.55 | 0 | 0 | 53.55 | 0 | 0 | 0 | 0 | 0
2025-08-11 02:00 | 52.92 | 0 | 0 | 52.92 | 0 | 0 | 0 | 0 | 0
2025-08-11 03:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0 | 0 | 0
2025-08-11 04:00 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 0 | 0 | 0
2025-08-11 05:00 | 52.91 | 0.92 | 0.92 | 51.99 | 0 | 0 | 0 | 0 | 0
2025-08-11 06:00 | 54.52 | 47.79 | 47.79 | 6.74 | 0 | 0 | 0 | 0 | 0
2025-08-11 07:00 | 58.23 | 65.95 | 58.23 | 0 | 0 | 0 | 0 | 7.72 | 0
2025-08-11 08:00 | 62.37 | 97.16 | 62.37 | 0 | 0 | 0 | 0 | 34.78 | 0
2025-08-11 09:00 | 65.8 | 87.26 | 65.8 | 0 | 0 | 0 | 0 | 21.45 | 0
2025-08-11 10:00 | 69.25 | 97.06 | 69.25 | 0 | 0 | 0 | 0 | 27.81 | 0
2025-08-11 11:00 | 72.25 | 111.28 | 72.25 | 0 | 0 | 0 | 0 | 39.03 | 0
2025-08-11 12:00 | 75.9 | 124.36 | 75.9 | 0 | 0 | 0 | 0 | 48.46 | 0
2025-08-11 13:00 | 78.63 | 124.52 | 78.63 | 0 | 0 | 0 | 0 | 45.89 | 0
2025-08-11 14:00 | 79.82 | 128.06 | 79.82 | 0 | 0 | 0 | 0 | 48.25 | 0
2025-08-11 15:00 | 80.19 | 129.49 | 80.19 | 0 | 0 | 0 | 0 | 49.3 | 0
2025-08-11 16:00 | 79.2 | 127.28 | 79.2 | 0 | 0 | 0 | 0 | 48.08 | 0
2025-08-11 17:00 | 78.56 | 116.18 | 78.56 | 0 | 0 | 0 | 0 | 37.62 | 0
2025-08-11 18:00 | 74.22 | 69.63 | 69.63 | 4.59 | 0 | 0 | 0 | 0 | 0
2025-08-11 19:00 | 72.94 | 1.86 | 1.86 | 71.09 | 0 | 0 | 0 | 0 | 0
2025-08-11 20:00 | 70.53 | 0 | 0 | 70.53 | 0 | 0 | 0 | 0 | 0
2025-08-11 21:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 0 | 0 | 0
2025-08-11 22:00 | 61.68 | 0 | 0 | 61.68 | 0 | 0 | 0 | 0 | 0
2025-08-11 23:00 | 58.37 | 0 | 0 | 58.37 | 0 | 0 | 0 | 0 | 0
2025-08-12 | 55.04 | 0 | 0 | 55.04 | 0 | 0 | 0 | 0 | 0
2025-08-12 01:00 | 53.67 | 0 | 0 | 53.67 | 0 | 0 | 0 | 0 | 0
2025-08-12 02:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 0 | 0 | 0
2025-08-12 03:00 | 51.39 | 0 | 0 | 51.39 | 0 | 0 | 0 | 0 | 0
2025-08-12 04:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 0 | 0 | 0
2025-08-12 05:00 | 53.16 | 0.77 | 0.77 | 52.39 | 0 | 0 | 0 | 0 | 0
2025-08-12 06:00 | 56.86 | 48.65 | 48.65 | 8.21 | 0 | 0 | 0 | 0 | 0
2025-08-12 07:00 | 58 | 92.58 | 58 | 0 | 0 | 0 | 0 | 34.58 | 0
2025-08-12 08:00 | 60.97 | 108.95 | 60.97 | 0 | 0 | 0 | 0 | 47.98 | 0
2025-08-12 09:00 | 63.01 | 113.12 | 63.01 | 0 | 0 | 0 | 0 | 50.11 | 0
2025-08-12 10:00 | 66.4 | 110.61 | 66.4 | 0 | 0 | 0 | 0 | 44.21 | 0
2025-08-12 11:00 | 69.69 | 109.43 | 69.69 | 0 | 0 | 0 | 0 | 39.74 | 0
2025-08-12 12:00 | 70.43 | 107.87 | 70.43 | 0 | 0 | 0 | 0 | 37.44 | 0
2025-08-12 13:00 | 71.46 | 108.52 | 71.46 | 0 | 0 | 0 | 0 | 37.07 | 0
2025-08-12 14:00 | 73.42 | 109.97 | 73.42 | 0 | 0 | 0 | 0 | 36.55 | 0
2025-08-12 15:00 | 74.38 | 111.29 | 74.38 | 0 | 0 | 0 | 0 | 36.91 | 0
2025-08-12 16:00 | 73.43 | 108.28 | 73.43 | 0 | 0 | 0 | 0 | 34.85 | 0
2025-08-12 17:00 | 72.37 | 92.48 | 72.37 | 0 | 0 | 0 | 0 | 20.11 | 0
2025-08-12 18:00 | 70.17 | 47.84 | 47.84 | 22.33 | 0 | 0 | 0 | 0 | 0
2025-08-12 19:00 | 69.34 | 0.64 | 0.64 | 68.71 | 0 | 0 | 0 | 0 | 0
2025-08-12 20:00 | 67 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0
2025-08-12 21:00 | 62.97 | 0 | 0 | 62.97 | 0 | 0 | 0 | 0 | 0
2025-08-12 22:00 | 61.44 | 0 | 0 | 61.44 | 0 | 0 | 0 | 0 | 0
2025-08-12 23:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 0 | 0 | 0
2025-08-13 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 0 | 0 | 0
2025-08-13 01:00 | 53.42 | 0 | 0 | 53.42 | 0 | 0 | 0 | 0 | 0
2025-08-13 02:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 0 | 0 | 0
2025-08-13 03:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 0 | 0 | 0
2025-08-13 04:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 0 | 0 | 0
2025-08-13 05:00 | 52.22 | 0.62 | 0.62 | 51.61 | 0 | 0 | 0 | 0 | 0
2025-08-13 06:00 | 54.59 | 13.18 | 13.18 | 41.41 | 0 | 0 | 0 | 0 | 0
2025-08-13 07:00 | 57.87 | 2.23 | 2.23 | 55.64 | 0 | 0 | 0 | 0 | 0
2025-08-13 08:00 | 61.55 | 21.47 | 21.47 | 40.09 | 0 | 0 | 0 | 0 | 0
2025-08-13 09:00 | 65.46 | 23.96 | 23.96 | 41.5 | 0 | 0 | 0 | 0 | 0
2025-08-13 10:00 | 69.08 | 44.7 | 44.7 | 24.38 | 0 | 0 | 0 | 0 | 0
2025-08-13 11:00 | 72.9 | 37.2 | 37.2 | 35.7 | 0 | 0 | 0 | 0 | 0
2025-08-13 12:00 | 75.87 | 81 | 75.87 | 0 | 0 | 0 | 0 | 5.13 | 0
2025-08-13 13:00 | 77.13 | 129.61 | 77.13 | 0 | 0 | 0 | 0 | 52.48 | 0
2025-08-13 14:00 | 79.11 | 124.17 | 79.11 | 0 | 0 | 0 | 0 | 45.06 | 0
2025-08-13 15:00 | 79.06 | 124.52 | 79.06 | 0 | 0 | 0 | 0 | 45.47 | 0
2025-08-13 16:00 | 78.9 | 99.67 | 78.9 | 0 | 0 | 0 | 0 | 20.77 | 0
2025-08-13 17:00 | 77.72 | 45.69 | 45.69 | 32.03 | 0 | 0 | 0 | 0 | 0
2025-08-13 18:00 | 73.59 | 20.63 | 20.63 | 52.96 | 0 | 0 | 0 | 0 | 0
2025-08-13 19:00 | 73.55 | 0.13 | 0.13 | 73.42 | 0 | 0 | 0 | 0 | 0
2025-08-13 20:00 | 69.2 | 0 | 0 | 69.2 | 0 | 0 | 0 | 0 | 0
2025-08-13 21:00 | 64.96 | 0 | 0 | 64.96 | 0 | 0 | 0 | 0 | 0
2025-08-13 22:00 | 62.58 | 0 | 0 | 62.58 | 0 | 0 | 0 | 0 | 0
2025-08-13 23:00 | 58.06 | 0 | 0 | 58.06 | 0 | 0 | 0 | 0 | 0
2025-08-14 | 55.37 | 0 | 0 | 55.37 | 0 | 0 | 0 | 0 | 0
2025-08-14 01:00 | 52.84 | 0 | 0 | 52.84 | 0 | 0 | 0 | 0 | 0
2025-08-14 02:00 | 52.52 | 0 | 0 | 52.52 | 0 | 0 | 0 | 0 | 0
2025-08-14 03:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 0 | 0 | 0
2025-08-14 04:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 0 | 0 | 0
2025-08-14 05:00 | 53.69 | 0.53 | 0.53 | 53.16 | 0 | 0 | 0 | 0 | 0
2025-08-14 06:00 | 55.6 | 55.05 | 55.05 | 0.55 | 0 | 0 | 0 | 0 | 0
2025-08-14 07:00 | 58.2 | 103.93 | 58.2 | 0 | 0 | 0 | 0 | 45.73 | 0
2025-08-14 08:00 | 62.2 | 115.2 | 62.2 | 0 | 0 | 0 | 0 | 53 | 0
2025-08-14 09:00 | 66.63 | 117 | 66.63 | 0 | 0 | 0 | 0 | 50.37 | 0
2025-08-14 10:00 | 69.27 | 115.36 | 69.27 | 0 | 0 | 0 | 0 | 46.09 | 0
2025-08-14 11:00 | 72.7 | 112.78 | 72.7 | 0 | 0 | 0 | 0 | 40.08 | 0
2025-08-14 12:00 | 75.78 | 110.89 | 75.78 | 0 | 0 | 0 | 0 | 35.1 | 0
2025-08-14 13:00 | 78.71 | 112.3 | 78.71 | 0 | 0 | 0 | 0 | 33.59 | 0
2025-08-14 14:00 | 79.25 | 114.07 | 79.25 | 0 | 0 | 0 | 0 | 34.82 | 0
2025-08-14 15:00 | 79.92 | 113.71 | 79.92 | 0 | 0 | 0 | 0 | 33.78 | 0
2025-08-14 16:00 | 78.78 | 112.54 | 78.78 | 0 | 0 | 0 | 0 | 33.75 | 0
2025-08-14 17:00 | 77.47 | 98.56 | 77.47 | 0 | 0 | 0 | 0 | 21.09 | 0
2025-08-14 18:00 | 75.44 | 50.58 | 50.58 | 24.85 | 0 | 0 | 0 | 0 | 0
2025-08-14 19:00 | 72.61 | 0.33 | 0.33 | 72.28 | 0 | 0 | 0 | 0 | 0
2025-08-14 20:00 | 69.99 | 0 | 0 | 69.99 | 0 | 0 | 0 | 0 | 0
2025-08-14 21:00 | 65.63 | 0 | 0 | 65.63 | 0 | 0 | 0 | 0 | 0
2025-08-14 22:00 | 61.19 | 0 | 0 | 61.19 | 0 | 0 | 0 | 0 | 0
2025-08-14 23:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 0 | 0 | 0
2025-08-15 | 56.18 | 0 | 0 | 56.18 | 0 | 0 | 0 | 0 | 0
2025-08-15 01:00 | 53.65 | 0 | 0 | 53.65 | 0 | 0 | 0 | 0 | 0
2025-08-15 02:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 0 | 0 | 0
2025-08-15 03:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 0 | 0 | 0
2025-08-15 04:00 | 52.22 | 0 | 0 | 52.22 | 0 | 0 | 0 | 0 | 0
2025-08-15 05:00 | 52.59 | 0.43 | 0.43 | 52.17 | 0 | 0 | 0 | 0 | 0
2025-08-15 06:00 | 55.69 | 45.74 | 45.74 | 9.95 | 0 | 0 | 0 | 0 | 0
2025-08-15 07:00 | 60.01 | 93.33 | 60.01 | 0 | 0 | 0 | 0 | 33.32 | 0
2025-08-15 08:00 | 63.24 | 107.21 | 63.24 | 0 | 0 | 0 | 0 | 43.97 | 0
2025-08-15 09:00 | 67.74 | 109.66 | 67.74 | 0 | 0 | 0 | 0 | 41.92 | 0
2025-08-15 10:00 | 73.74 | 110.22 | 73.74 | 0 | 0 | 0 | 0 | 36.48 | 0
2025-08-15 11:00 | 78.72 | 105.34 | 78.72 | 0 | 0 | 0 | 0 | 26.62 | 0
2025-08-15 12:00 | 83.19 | 103.48 | 83.19 | 0 | 0 | 0 | 0 | 20.29 | 0
2025-08-15 13:00 | 88.22 | 107.01 | 88.22 | 0 | 0 | 0 | 0 | 18.79 | 0
2025-08-15 14:00 | 91 | 109.73 | 91 | 0 | 0 | 0 | 0 | 18.73 | 0
2025-08-15 15:00 | 91.18 | 108.42 | 91.18 | 0 | 0 | 0 | 0 | 17.24 | 0
2025-08-15 16:00 | 90.25 | 102.98 | 90.25 | 0 | 0 | 0 | 0 | 12.73 | 0
2025-08-15 17:00 | 87.38 | 86.28 | 86.28 | 1.1 | 0 | 0 | 0 | 0 | 0
2025-08-15 18:00 | 83.82 | 38.55 | 38.55 | 45.27 | 0 | 0 | 0 | 0 | 0
2025-08-15 19:00 | 78.67 | 0.24 | 0.24 | 78.43 | 0 | 0 | 0 | 0 | 0
2025-08-15 20:00 | 73.03 | 0 | 0 | 73.03 | 0 | 0 | 0 | 0 | 0
2025-08-15 21:00 | 69.08 | 0 | 0 | 69.08 | 0 | 0 | 0 | 0 | 0
2025-08-15 22:00 | 63.38 | 0 | 0 | 63.38 | 0 | 0 | 0 | 0 | 0
2025-08-15 23:00 | 59.16 | 0 | 0 | 59.16 | 0 | 0 | 0 | 0 | 0
2025-08-16 | 55.81 | 0 | 0 | 55.81 | 0 | 0 | 0 | 0 | 0
2025-08-16 01:00 | 53.41 | 0 | 0 | 53.41 | 0 | 0 | 0 | 0 | 0
2025-08-16 02:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-08-16 03:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0 | 0 | 0
2025-08-16 04:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0 | 0 | 0
2025-08-16 05:00 | 53.24 | 0.34 | 0.34 | 52.9 | 0 | 0 | 0 | 0 | 0
2025-08-16 06:00 | 55.54 | 44.03 | 44.03 | 11.51 | 0 | 0 | 0 | 0 | 0
2025-08-16 07:00 | 58.42 | 93.76 | 58.42 | 0 | 0 | 0 | 0 | 35.34 | 0
2025-08-16 08:00 | 61.96 | 104.89 | 61.96 | 0 | 0 | 0 | 0 | 42.93 | 0
2025-08-16 09:00 | 67.32 | 110.06 | 67.32 | 0 | 0 | 0 | 0 | 42.74 | 0
2025-08-16 10:00 | 72.07 | 105.17 | 72.07 | 0 | 0 | 0 | 0 | 33.1 | 0
2025-08-16 11:00 | 76.1 | 98.33 | 76.1 | 0 | 0 | 0 | 0 | 22.23 | 0
2025-08-16 12:00 | 81.7 | 100.72 | 81.7 | 0 | 0 | 0 | 0 | 19.02 | 0
2025-08-16 13:00 | 85.44 | 101.44 | 85.44 | 0 | 0 | 0 | 0 | 16 | 0
2025-08-16 14:00 | 88.49 | 102.03 | 88.49 | 0 | 0 | 0 | 0 | 13.54 | 0
2025-08-16 15:00 | 87.82 | 94.62 | 87.82 | 0 | 0 | 0 | 0 | 6.8 | 0
2025-08-16 16:00 | 86.96 | 87.17 | 86.96 | 0 | 0 | 0 | 0 | 0.21 | 0
2025-08-16 17:00 | 84.41 | 74.99 | 74.99 | 9.42 | 0 | 0 | 0 | 0 | 0
2025-08-16 18:00 | 81.55 | 33.37 | 33.37 | 48.18 | 0 | 0 | 0 | 0 | 0
2025-08-16 19:00 | 77.15 | 0.13 | 0.13 | 77.02 | 0 | 0 | 0 | 0 | 0
2025-08-16 20:00 | 71.77 | 0 | 0 | 71.77 | 0 | 0 | 0 | 0 | 0
2025-08-16 21:00 | 67.16 | 0 | 0 | 67.16 | 0 | 0 | 0 | 0 | 0
2025-08-16 22:00 | 61.64 | 0 | 0 | 61.64 | 0 | 0 | 0 | 0 | 0
2025-08-16 23:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 0 | 0 | 0
2025-08-17 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 0 | 0 | 0
2025-08-17 01:00 | 52.89 | 0 | 0 | 52.89 | 0 | 0 | 0 | 0 | 0
2025-08-17 02:00 | 50.84 | 0 | 0 | 50.84 | 0 | 0 | 0 | 0 | 0
2025-08-17 03:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 0 | 0 | 0
2025-08-17 04:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 0 | 0 | 0
2025-08-17 05:00 | 52.9 | 0.26 | 0.26 | 52.64 | 0 | 0 | 0 | 0 | 0
2025-08-17 06:00 | 55.26 | 40.8 | 40.8 | 14.47 | 0 | 0 | 0 | 0 | 0
2025-08-17 07:00 | 58.42 | 85.78 | 58.42 | 0 | 0 | 0 | 0 | 27.36 | 0
2025-08-17 08:00 | 61.06 | 101.54 | 61.06 | 0 | 0 | 0 | 0 | 40.48 | 0
2025-08-17 09:00 | 64.26 | 108.75 | 64.26 | 0 | 0 | 0 | 0 | 44.49 | 0
2025-08-17 10:00 | 67.44 | 109.31 | 67.44 | 0 | 0 | 0 | 0 | 41.87 | 0
2025-08-17 11:00 | 69.62 | 106.78 | 69.62 | 0 | 0 | 0 | 0 | 37.17 | 0
2025-08-17 12:00 | 71.46 | 107.25 | 71.46 | 0 | 0 | 0 | 0 | 35.79 | 0
2025-08-17 13:00 | 73.57 | 108.72 | 73.57 | 0 | 0 | 0 | 0 | 35.15 | 0
2025-08-17 14:00 | 74.57 | 110.81 | 74.57 | 0 | 0 | 0 | 0 | 36.24 | 0
2025-08-17 15:00 | 74.68 | 107.07 | 74.68 | 0 | 0 | 0 | 0 | 32.39 | 0
2025-08-17 16:00 | 73.31 | 98.26 | 73.31 | 0 | 0 | 0 | 0 | 24.96 | 0
2025-08-17 17:00 | 72.64 | 84.7 | 72.64 | 0 | 0 | 0 | 0 | 12.05 | 0
2025-08-17 18:00 | 71.34 | 35.13 | 35.13 | 36.21 | 0 | 0 | 0 | 0 | 0
2025-08-17 19:00 | 69.72 | 0 | 0 | 69.72 | 0 | 0 | 0 | 0 | 0
2025-08-17 20:00 | 66.71 | 0 | 0 | 66.71 | 0 | 0 | 0 | 0 | 0
2025-08-17 21:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 0 | 0 | 0
2025-08-17 22:00 | 61.35 | 0 | 0 | 61.35 | 0 | 0 | 0 | 0 | 0
2025-08-17 23:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 0 | 0 | 0
2025-08-18 | 55.62 | 0 | 0 | 55.62 | 0 | 0 | 0 | 0 | 0
2025-08-18 01:00 | 52.35 | 0 | 0 | 52.35 | 0 | 0 | 0 | 0 | 0
2025-08-18 02:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 0 | 0 | 0
2025-08-18 03:00 | 50.73 | 0 | 0 | 50.73 | 0 | 0 | 0 | 0 | 0
2025-08-18 04:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 0 | 0 | 0
2025-08-18 05:00 | 52.72 | 0.07 | 0.07 | 52.65 | 0 | 0 | 0 | 0 | 0
2025-08-18 06:00 | 55.68 | 33.84 | 33.84 | 21.84 | 0 | 0 | 0 | 0 | 0
2025-08-18 07:00 | 58.03 | 95.61 | 58.03 | 0 | 0 | 0 | 0 | 37.58 | 0
2025-08-18 08:00 | 62.01 | 116.35 | 62.01 | 0 | 0 | 0 | 0 | 54.34 | 0
2025-08-18 09:00 | 64.48 | 120.73 | 64.48 | 0 | 0 | 0 | 0 | 56.25 | 0
2025-08-18 10:00 | 68.96 | 99.4 | 68.96 | 0 | 0 | 0 | 0 | 30.44 | 0
2025-08-18 11:00 | 70.89 | 100.74 | 70.89 | 0 | 0 | 0 | 0 | 29.85 | 0
2025-08-18 12:00 | 73.42 | 77.99 | 73.42 | 0 | 0 | 0 | 0 | 4.57 | 0
2025-08-18 13:00 | 74.75 | 21.99 | 21.99 | 52.76 | 0 | 0 | 0 | 0 | 0
2025-08-18 14:00 | 77.18 | 91.35 | 77.18 | 0 | 0 | 0 | 0 | 14.17 | 0
2025-08-18 15:00 | 76.79 | 78.59 | 76.79 | 0 | 0 | 0 | 0 | 1.8 | 0
2025-08-18 16:00 | 76.3 | 113.98 | 76.3 | 0 | 0 | 0 | 0 | 37.69 | 0
2025-08-18 17:00 | 76.03 | 95.56 | 76.03 | 0 | 0 | 0 | 0 | 19.53 | 0
2025-08-18 18:00 | 73.99 | 39.38 | 39.38 | 34.6 | 0 | 0 | 0 | 0 | 0
2025-08-18 19:00 | 71.37 | 0.09 | 0.09 | 71.28 | 0 | 0 | 0 | 0 | 0
2025-08-18 20:00 | 67.55 | 0 | 0 | 67.55 | 0 | 0 | 0 | 0 | 0
2025-08-18 21:00 | 64.37 | 0 | 0 | 64.37 | 0 | 0 | 0 | 0 | 0
2025-08-18 22:00 | 60.97 | 0 | 0 | 60.97 | 0 | 0 | 0 | 0 | 0
2025-08-18 23:00 | 58.19 | 0 | 0 | 58.19 | 0 | 0 | 0 | 0 | 0
2025-08-19 | 55.61 | 0 | 0 | 55.61 | 0 | 0 | 0 | 0 | 0
2025-08-19 01:00 | 52.97 | 0 | 0 | 52.97 | 0 | 0 | 0 | 0 | 0
2025-08-19 02:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 0 | 0 | 0
2025-08-19 03:00 | 51.43 | 0 | 0 | 51.43 | 0 | 0 | 0 | 0 | 0
2025-08-19 04:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 0 | 0 | 0
2025-08-19 05:00 | 53.2 | 0 | 0 | 53.2 | 0 | 0 | 0 | 0 | 0
2025-08-19 06:00 | 55.69 | 6.37 | 6.37 | 49.31 | 0 | 0 | 0 | 0 | 0
2025-08-19 07:00 | 58.37 | 29.57 | 29.57 | 28.8 | 0 | 0 | 0 | 0 | 0
2025-08-19 08:00 | 60.72 | 75.18 | 60.72 | 0 | 0 | 0 | 0 | 14.46 | 0
2025-08-19 09:00 | 62.87 | 70.01 | 62.87 | 0 | 0 | 0 | 0 | 7.15 | 0
2025-08-19 10:00 | 65.23 | 73.23 | 65.23 | 0 | 0 | 0 | 0 | 8 | 0
2025-08-19 11:00 | 67.73 | 88.45 | 67.73 | 0 | 0 | 0 | 0 | 20.72 | 0
2025-08-19 12:00 | 69.91 | 89.1 | 69.91 | 0 | 0 | 0 | 0 | 19.19 | 0
2025-08-19 13:00 | 70.44 | 89.57 | 70.44 | 0 | 0 | 0 | 0 | 19.13 | 0
2025-08-19 14:00 | 71.13 | 96.25 | 71.13 | 0 | 0 | 0 | 0 | 25.12 | 0
2025-08-19 15:00 | 71.15 | 67.61 | 67.61 | 3.54 | 0 | 0 | 0 | 0 | 0
2025-08-19 16:00 | 70.74 | 86.4 | 70.74 | 0 | 0 | 0 | 0 | 15.66 | 0
2025-08-19 17:00 | 70.14 | 94.62 | 70.14 | 0 | 0 | 0 | 0 | 24.47 | 0
2025-08-19 18:00 | 69.14 | 37.53 | 37.53 | 31.62 | 0 | 0 | 0 | 0 | 0
2025-08-19 19:00 | 68.3 | 0 | 0 | 68.3 | 0 | 0 | 0 | 0 | 0
2025-08-19 20:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 0 | 0 | 0
2025-08-19 21:00 | 62.88 | 0 | 0 | 62.88 | 0 | 0 | 0 | 0 | 0
2025-08-19 22:00 | 59.7 | 0 | 0 | 59.7 | 0 | 0 | 0 | 0 | 0
2025-08-19 23:00 | 57.73 | 0 | 0 | 57.73 | 0 | 0 | 0 | 0 | 0
2025-08-20 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 0 | 0 | 0
2025-08-20 01:00 | 53.55 | 0 | 0 | 53.55 | 0 | 0 | 0 | 0 | 0
2025-08-20 02:00 | 51.49 | 0 | 0 | 51.49 | 0 | 0 | 0 | 0 | 0
2025-08-20 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0 | 0 | 0
2025-08-20 04:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 0 | 0 | 0
2025-08-20 05:00 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 0 | 0 | 0
2025-08-20 06:00 | 55.02 | 27.23 | 27.23 | 27.78 | 0 | 0 | 0 | 0 | 0
2025-08-20 07:00 | 57.59 | 60.54 | 57.59 | 0 | 0 | 0 | 0 | 2.95 | 0
2025-08-20 08:00 | 60.7 | 72.78 | 60.7 | 0 | 0 | 0 | 0 | 12.08 | 0
2025-08-20 09:00 | 64.06 | 82.12 | 64.06 | 0 | 0 | 0 | 0 | 18.06 | 0
2025-08-20 10:00 | 66.79 | 92.7 | 66.79 | 0 | 0 | 0 | 0 | 25.91 | 0
2025-08-20 11:00 | 69.63 | 94.4 | 69.63 | 0 | 0 | 0 | 0 | 24.77 | 0
2025-08-20 12:00 | 72.94 | 96.22 | 72.94 | 0 | 0 | 0 | 0 | 23.28 | 0
2025-08-20 13:00 | 75.2 | 94.74 | 75.2 | 0 | 0 | 0 | 0 | 19.54 | 0
2025-08-20 14:00 | 74.33 | 101.89 | 74.33 | 0 | 0 | 0 | 0 | 27.57 | 0
2025-08-20 15:00 | 74.67 | 100.08 | 74.67 | 0 | 0 | 0 | 0 | 25.41 | 0
2025-08-20 16:00 | 74.45 | 104.43 | 74.45 | 0 | 0 | 0 | 0 | 29.98 | 0
2025-08-20 17:00 | 73.79 | 85.74 | 73.79 | 0 | 0 | 0 | 0 | 11.95 | 0
2025-08-20 18:00 | 72.54 | 30.92 | 30.92 | 41.62 | 0 | 0 | 0 | 0 | 0
2025-08-20 19:00 | 70.04 | 0 | 0 | 70.04 | 0 | 0 | 0 | 0 | 0
2025-08-20 20:00 | 67.03 | 0 | 0 | 67.03 | 0 | 0 | 0 | 0 | 0
2025-08-20 21:00 | 64.1 | 0 | 0 | 64.1 | 0 | 0 | 0 | 0 | 0
2025-08-20 22:00 | 60.29 | 0 | 0 | 60.29 | 0 | 0 | 0 | 0 | 0
2025-08-20 23:00 | 57.44 | 0 | 0 | 57.44 | 0 | 0 | 0 | 0 | 0
2025-08-21 | 54.87 | 0 | 0 | 54.87 | 0 | 0 | 0 | 0 | 0
2025-08-21 01:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 0 | 0 | 0
2025-08-21 02:00 | 50.75 | 0 | 0 | 50.75 | 0 | 0 | 0 | 0 | 0
2025-08-21 03:00 | 50.31 | 0 | 0 | 50.31 | 0 | 0 | 0 | 0 | 0
2025-08-21 04:00 | 51.72 | 0 | 0 | 51.72 | 0 | 0 | 0 | 0 | 0
2025-08-21 05:00 | 52.82 | 0.18 | 0.18 | 52.64 | 0 | 0 | 0 | 0 | 0
2025-08-21 06:00 | 55.19 | 57.49 | 55.19 | 0 | 0 | 0 | 0 | 2.3 | 0
2025-08-21 07:00 | 56.84 | 118.97 | 56.84 | 0 | 0 | 0 | 0 | 62.13 | 0
2025-08-21 08:00 | 60.42 | 129.4 | 60.42 | 0 | 0 | 0 | 0 | 68.98 | 0
2025-08-21 09:00 | 65.18 | 130.71 | 65.18 | 0 | 0 | 0 | 0 | 65.53 | 0
2025-08-21 10:00 | 67.2 | 128.06 | 67.2 | 0 | 0 | 0 | 0 | 60.85 | 0
2025-08-21 11:00 | 72.74 | 124.36 | 72.74 | 0 | 0 | 0 | 0 | 51.63 | 0
2025-08-21 12:00 | 74.29 | 122.26 | 74.29 | 0 | 0 | 0 | 0 | 47.98 | 0
2025-08-21 13:00 | 78 | 115.29 | 78 | 0 | 0 | 0 | 0 | 37.29 | 0
2025-08-21 14:00 | 78.64 | 19.95 | 19.95 | 58.69 | 0 | 0 | 0 | 0 | 0
2025-08-21 15:00 | 80.12 | 5.51 | 5.51 | 74.62 | 0 | 0 | 0 | 0 | 0
2025-08-21 16:00 | 80.69 | 3.66 | 3.66 | 77.03 | 0 | 0 | 0 | 0 | 0
2025-08-21 17:00 | 76.44 | 1.77 | 1.77 | 74.67 | 0 | 0 | 0 | 0 | 0
2025-08-21 18:00 | 75.55 | 0 | 0 | 75.55 | 0 | 0 | 0 | 0 | 0
2025-08-21 19:00 | 71.22 | 0 | 0 | 71.22 | 0 | 0 | 0 | 0 | 0
2025-08-21 20:00 | 68.81 | 0 | 0 | 68.81 | 0 | 0 | 0 | 0 | 0
2025-08-21 21:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 0 | 0 | 0
2025-08-21 22:00 | 61.22 | 0 | 0 | 61.22 | 0 | 0 | 0 | 0 | 0
2025-08-21 23:00 | 57.31 | 0 | 0 | 57.31 | 0 | 0 | 0 | 0 | 0
2025-08-22 | 55.3 | 0 | 0 | 55.3 | 0 | 0 | 0 | 0 | 0
2025-08-22 01:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 0 | 0 | 0
2025-08-22 02:00 | 51.9 | 0 | 0 | 51.9 | 0 | 0 | 0 | 0 | 0
2025-08-22 03:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 0 | 0 | 0
2025-08-22 04:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 0 | 0 | 0
2025-08-22 05:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 0 | 0 | 0
2025-08-22 06:00 | 54.87 | 39.71 | 39.71 | 15.16 | 0 | 0 | 0 | 0 | 0
2025-08-22 07:00 | 58.91 | 89.19 | 58.91 | 0 | 0 | 0 | 0 | 30.28 | 0
2025-08-22 08:00 | 62.27 | 23.77 | 23.77 | 38.5 | 0 | 0 | 0 | 0 | 0
2025-08-22 09:00 | 65.43 | 48.49 | 48.49 | 16.94 | 0 | 0 | 0 | 0 | 0
2025-08-22 10:00 | 70.16 | 123.87 | 70.16 | 0 | 0 | 0 | 0 | 53.71 | 0
2025-08-22 11:00 | 74.51 | 96.28 | 74.51 | 0 | 0 | 0 | 0 | 21.77 | 0
2025-08-22 12:00 | 78.99 | 96.27 | 78.99 | 0 | 0 | 0 | 0 | 17.28 | 0
2025-08-22 13:00 | 81.43 | 94.9 | 81.43 | 0 | 0 | 0 | 0 | 13.46 | 0
2025-08-22 14:00 | 83.22 | 71.77 | 71.77 | 11.45 | 0 | 0 | 0 | 0 | 0
2025-08-22 15:00 | 83.69 | 9.79 | 9.79 | 73.9 | 0 | 0 | 0 | 0 | 0
2025-08-22 16:00 | 83.11 | 17.92 | 17.92 | 65.18 | 0 | 0 | 0 | 0 | 0
2025-08-22 17:00 | 81.87 | 3.88 | 3.88 | 77.99 | 0 | 0 | 0 | 0 | 0
2025-08-22 18:00 | 78.23 | 0 | 0 | 78.23 | 0 | 0 | 0 | 0 | 0
2025-08-22 19:00 | 74.25 | 0 | 0 | 74.25 | 0 | 0 | 0 | 0 | 0
2025-08-22 20:00 | 69.92 | 0 | 0 | 69.92 | 0 | 0 | 0 | 0 | 0
2025-08-22 21:00 | 65.55 | 0 | 0 | 65.55 | 0 | 0 | 0 | 0 | 0
2025-08-22 22:00 | 60.96 | 0 | 0 | 60.96 | 0 | 0 | 0 | 0 | 0
2025-08-22 23:00 | 57.58 | 0 | 0 | 57.58 | 0 | 0 | 0 | 0 | 0
2025-08-23 | 55.38 | 0 | 0 | 55.38 | 0 | 0 | 0 | 0 | 0
2025-08-23 01:00 | 52.44 | 0 | 0 | 52.44 | 0 | 0 | 0 | 0 | 0
2025-08-23 02:00 | 51.56 | 0 | 0 | 51.56 | 0 | 0 | 0 | 0 | 0
2025-08-23 03:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0 | 0 | 0
2025-08-23 04:00 | 51.5 | 0 | 0 | 51.5 | 0 | 0 | 0 | 0 | 0
2025-08-23 05:00 | 52.46 | 0 | 0 | 52.46 | 0 | 0 | 0 | 0 | 0
2025-08-23 06:00 | 54.39 | 42.23 | 42.23 | 12.16 | 0 | 0 | 0 | 0 | 0
2025-08-23 07:00 | 57.37 | 104.42 | 57.37 | 0 | 0 | 0 | 0 | 47.05 | 0
2025-08-23 08:00 | 60.03 | 86.74 | 60.03 | 0 | 0 | 0 | 0 | 26.72 | 0
2025-08-23 09:00 | 62.31 | 68.01 | 62.31 | 0 | 0 | 0 | 0 | 5.7 | 0
2025-08-23 10:00 | 66.81 | 116.99 | 66.81 | 0 | 0 | 0 | 0 | 50.18 | 0
2025-08-23 11:00 | 69.14 | 105.25 | 69.14 | 0 | 0 | 0 | 0 | 36.11 | 0
2025-08-23 12:00 | 71.07 | 90.29 | 71.07 | 0 | 0 | 0 | 0 | 19.23 | 0
2025-08-23 13:00 | 72.38 | 84.26 | 72.38 | 0 | 0 | 0 | 0 | 11.88 | 0
2025-08-23 14:00 | 73.14 | 80.67 | 73.14 | 0 | 0 | 0 | 0 | 7.53 | 0
2025-08-23 15:00 | 74.33 | 50.83 | 50.83 | 23.5 | 0 | 0 | 0 | 0 | 0
2025-08-23 16:00 | 74.68 | 67.71 | 67.71 | 6.98 | 0 | 0 | 0 | 0 | 0
2025-08-23 17:00 | 72.97 | 68.41 | 68.41 | 4.56 | 0 | 0 | 0 | 0 | 0
2025-08-23 18:00 | 70.53 | 29.35 | 29.35 | 41.18 | 0 | 0 | 0 | 0 | 0
2025-08-23 19:00 | 69.13 | 0 | 0 | 69.13 | 0 | 0 | 0 | 0 | 0
2025-08-23 20:00 | 66.32 | 0 | 0 | 66.32 | 0 | 0 | 0 | 0 | 0
2025-08-23 21:00 | 63.8 | 0 | 0 | 63.8 | 0 | 0 | 0 | 0 | 0
2025-08-23 22:00 | 60.58 | 0 | 0 | 60.58 | 0 | 0 | 0 | 0 | 0
2025-08-23 23:00 | 55.79 | 0 | 0 | 55.79 | 0 | 0 | 0 | 0 | 0
2025-08-24 | 54.84 | 0 | 0 | 54.84 | 0 | 0 | 0 | 0 | 0
2025-08-24 01:00 | 51.98 | 0 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0
2025-08-24 02:00 | 50.44 | 0 | 0 | 50.44 | 0 | 0 | 0 | 0 | 0
2025-08-24 03:00 | 50.59 | 0 | 0 | 50.59 | 0 | 0 | 0 | 0 | 0
2025-08-24 04:00 | 51.35 | 0 | 0 | 51.35 | 0 | 0 | 0 | 0 | 0
2025-08-24 05:00 | 51.66 | 0 | 0 | 51.66 | 0 | 0 | 0 | 0 | 0
2025-08-24 06:00 | 54.91 | 40.69 | 40.69 | 14.23 | 0 | 0 | 0 | 0 | 0
2025-08-24 07:00 | 57.6 | 99.28 | 57.6 | 0 | 0 | 0 | 0 | 41.68 | 0
2025-08-24 08:00 | 60.25 | 112.93 | 60.25 | 0 | 0 | 0 | 0 | 52.67 | 0
2025-08-24 09:00 | 62.92 | 115.57 | 62.92 | 0 | 0 | 0 | 0 | 52.65 | 0
2025-08-24 10:00 | 65.89 | 112.67 | 65.89 | 0 | 0 | 0 | 0 | 46.78 | 0
2025-08-24 11:00 | 69.61 | 109.47 | 69.61 | 0 | 0 | 0 | 0 | 39.86 | 0
2025-08-24 12:00 | 70.6 | 105.79 | 70.6 | 0 | 0 | 0 | 0 | 35.19 | 0
2025-08-24 13:00 | 73.58 | 107.74 | 73.58 | 0 | 0 | 0 | 0 | 34.16 | 0
2025-08-24 14:00 | 74 | 109.88 | 74 | 0 | 0 | 0 | 0 | 35.87 | 0
2025-08-24 15:00 | 74.39 | 107.95 | 74.39 | 0 | 0 | 0 | 0 | 33.56 | 0
2025-08-24 16:00 | 73.23 | 101.54 | 73.23 | 0 | 0 | 0 | 0 | 28.31 | 0
2025-08-24 17:00 | 72.97 | 84.4 | 72.97 | 0 | 0 | 0 | 0 | 11.42 | 0
2025-08-24 18:00 | 71.66 | 25.64 | 25.64 | 46.02 | 0 | 0 | 0 | 0 | 0
2025-08-24 19:00 | 68.43 | 0 | 0 | 68.43 | 0 | 0 | 0 | 0 | 0
2025-08-24 20:00 | 66.63 | 0 | 0 | 66.63 | 0 | 0 | 0 | 0 | 0
2025-08-24 21:00 | 63.4 | 0 | 0 | 63.4 | 0 | 0 | 0 | 0 | 0
2025-08-24 22:00 | 59.91 | 0 | 0 | 59.91 | 0 | 0 | 0 | 0 | 0
2025-08-24 23:00 | 57.65 | 0 | 0 | 57.65 | 0 | 0 | 0 | 0 | 0
2025-08-25 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0 | 0 | 0
2025-08-25 01:00 | 52.55 | 0 | 0 | 52.55 | 0 | 0 | 0 | 0 | 0
2025-08-25 02:00 | 51.89 | 0 | 0 | 51.89 | 0 | 0 | 0 | 0 | 0
2025-08-25 03:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 0 | 0 | 0
2025-08-25 04:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0 | 0 | 0
2025-08-25 05:00 | 52.22 | 0 | 0 | 52.22 | 0 | 0 | 0 | 0 | 0
2025-08-25 06:00 | 54.01 | 8.14 | 8.14 | 45.87 | 0 | 0 | 0 | 0 | 0
2025-08-25 07:00 | 56.53 | 25.2 | 25.2 | 31.33 | 0 | 0 | 0 | 0 | 0
2025-08-25 08:00 | 59.41 | 44.44 | 44.44 | 14.98 | 0 | 0 | 0 | 0 | 0
2025-08-25 09:00 | 61.04 | 59 | 59 | 2.04 | 0 | 0 | 0 | 0 | 0
2025-08-25 10:00 | 63.78 | 55.38 | 55.38 | 8.4 | 0 | 0 | 0 | 0 | 0
2025-08-25 11:00 | 65.98 | 46.07 | 46.07 | 19.91 | 0 | 0 | 0 | 0 | 0
2025-08-25 12:00 | 65.94 | 40.17 | 40.17 | 25.76 | 0 | 0 | 0 | 0 | 0
2025-08-25 13:00 | 65.96 | 38.68 | 38.68 | 27.27 | 0 | 0 | 0 | 0 | 0
2025-08-25 14:00 | 66.3 | 20.43 | 20.43 | 45.87 | 0 | 0 | 0 | 0 | 0
2025-08-25 15:00 | 67.47 | 24.53 | 24.53 | 42.94 | 0 | 0 | 0 | 0 | 0
2025-08-25 16:00 | 66.94 | 15.38 | 15.38 | 51.57 | 0 | 0 | 0 | 0 | 0
2025-08-25 17:00 | 67.07 | 8.02 | 8.02 | 59.04 | 0 | 0 | 0 | 0 | 0
2025-08-25 18:00 | 65.7 | 0 | 0 | 65.7 | 0 | 0 | 0 | 0 | 0
2025-08-25 19:00 | 65.33 | 0 | 0 | 65.33 | 0 | 0 | 0 | 0 | 0
2025-08-25 20:00 | 63.32 | 0 | 0 | 63.32 | 0 | 0 | 0 | 0 | 0
2025-08-25 21:00 | 61.08 | 0 | 0 | 61.08 | 0 | 0 | 0 | 0 | 0
2025-08-25 22:00 | 58.94 | 0 | 0 | 58.94 | 0 | 0 | 0 | 0 | 0
2025-08-25 23:00 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 0 | 0 | 0
2025-08-26 | 55.45 | 0 | 0 | 55.45 | 0 | 0 | 0 | 0 | 0
2025-08-26 01:00 | 52.3 | 0 | 0 | 52.3 | 0 | 0 | 0 | 0 | 0
2025-08-26 02:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 0 | 0 | 0
2025-08-26 03:00 | 50.29 | 0 | 0 | 50.29 | 0 | 0 | 0 | 0 | 0
2025-08-26 04:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 0 | 0 | 0
2025-08-26 05:00 | 52.23 | 0 | 0 | 52.23 | 0 | 0 | 0 | 0 | 0
2025-08-26 06:00 | 55.01 | 30.93 | 30.93 | 24.08 | 0 | 0 | 0 | 0 | 0
2025-08-26 07:00 | 56.93 | 78.34 | 56.93 | 0 | 0 | 0 | 0 | 21.41 | 0
2025-08-26 08:00 | 59.92 | 17.57 | 17.57 | 42.36 | 0 | 0 | 0 | 0 | 0
2025-08-26 09:00 | 63.8 | 42.46 | 42.46 | 21.34 | 0 | 0 | 0 | 0 | 0
2025-08-26 10:00 | 67.32 | 81.44 | 67.32 | 0 | 0 | 0 | 0 | 14.12 | 0
2025-08-26 11:00 | 70.99 | 97.95 | 70.99 | 0 | 0 | 0 | 0 | 26.96 | 0
2025-08-26 12:00 | 72.98 | 70.36 | 70.36 | 2.62 | 0 | 0 | 0 | 0 | 0
2025-08-26 13:00 | 75.14 | 63.73 | 63.73 | 11.4 | 0 | 0 | 0 | 0 | 0
2025-08-26 14:00 | 76.44 | 97.88 | 76.44 | 0 | 0 | 0 | 0 | 21.45 | 0
2025-08-26 15:00 | 75.93 | 92.38 | 75.93 | 0 | 0 | 0 | 0 | 16.45 | 0
2025-08-26 16:00 | 75.6 | 107.22 | 75.6 | 0 | 0 | 0 | 0 | 31.62 | 0
2025-08-26 17:00 | 74.27 | 83.94 | 74.27 | 0 | 0 | 0 | 0 | 9.67 | 0
2025-08-26 18:00 | 72.14 | 23.39 | 23.39 | 48.74 | 0 | 0 | 0 | 0 | 0
2025-08-26 19:00 | 70.56 | 0 | 0 | 70.56 | 0 | 0 | 0 | 0 | 0
2025-08-26 20:00 | 67.22 | 0 | 0 | 67.22 | 0 | 0 | 0 | 0 | 0
2025-08-26 21:00 | 63.77 | 0 | 0 | 63.77 | 0 | 0 | 0 | 0 | 0
2025-08-26 22:00 | 59.06 | 0 | 0 | 59.06 | 0 | 0 | 0 | 0 | 0
2025-08-26 23:00 | 58.22 | 0 | 0 | 58.22 | 0 | 0 | 0 | 0 | 0
2025-08-27 | 53.83 | 0 | 0 | 53.83 | 0 | 0 | 0 | 0 | 0
2025-08-27 01:00 | 53.28 | 0 | 0 | 53.28 | 0 | 0 | 0 | 0 | 0
2025-08-27 02:00 | 50.22 | 0 | 0 | 50.22 | 0 | 0 | 0 | 0 | 0
2025-08-27 03:00 | 50.08 | 0 | 0 | 50.08 | 0 | 0 | 0 | 0 | 0
2025-08-27 04:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 0 | 0 | 0
2025-08-27 05:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 0 | 0 | 0
2025-08-27 06:00 | 53.73 | 30.22 | 30.22 | 23.51 | 0 | 0 | 0 | 0 | 0
2025-08-27 07:00 | 56.29 | 106.58 | 56.29 | 0 | 0 | 0 | 0 | 50.29 | 0
2025-08-27 08:00 | 58.97 | 110.94 | 58.97 | 0 | 0 | 0 | 0 | 51.97 | 0
2025-08-27 09:00 | 62.92 | 127.06 | 62.92 | 0 | 0 | 0 | 0 | 64.14 | 0
2025-08-27 10:00 | 65.59 | 119.26 | 65.59 | 0 | 0 | 0 | 0 | 53.67 | 0
2025-08-27 11:00 | 68.5 | 7.65 | 7.65 | 60.85 | 0 | 0 | 0 | 0 | 0
2025-08-27 12:00 | 69.17 | 119.15 | 69.17 | 0 | 0 | 0 | 0 | 49.98 | 0
2025-08-27 13:00 | 71.01 | 120.28 | 71.01 | 0 | 0 | 0 | 0 | 49.27 | 0
2025-08-27 14:00 | 71.1 | 69.98 | 69.98 | 1.12 | 0 | 0 | 0 | 0 | 0
2025-08-27 15:00 | 71.86 | 34.58 | 34.58 | 37.28 | 0 | 0 | 0 | 0 | 0
2025-08-27 16:00 | 71.49 | 108.26 | 71.49 | 0 | 0 | 0 | 0 | 36.77 | 0
2025-08-27 17:00 | 71.13 | 1.44 | 1.44 | 69.7 | 0 | 0 | 0 | 0 | 0
2025-08-27 18:00 | 70.02 | 0 | 0 | 70.02 | 0 | 0 | 0 | 0 | 0
2025-08-27 19:00 | 68.09 | 0 | 0 | 68.09 | 0 | 0 | 0 | 0 | 0
2025-08-27 20:00 | 64.81 | 0 | 0 | 64.81 | 0 | 0 | 0 | 0 | 0
2025-08-27 21:00 | 63.03 | 0 | 0 | 63.03 | 0 | 0 | 0 | 0 | 0
2025-08-27 22:00 | 59.64 | 0 | 0 | 59.64 | 0 | 0 | 0 | 0 | 0
2025-08-27 23:00 | 56.67 | 0 | 0 | 56.67 | 0 | 0 | 0 | 0 | 0
2025-08-28 | 53.9 | 0 | 0 | 53.9 | 0 | 0 | 0 | 0 | 0
2025-08-28 01:00 | 51.9 | 0 | 0 | 51.9 | 0 | 0 | 0 | 0 | 0
2025-08-28 02:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 0 | 0 | 0
2025-08-28 03:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 0 | 0 | 0
2025-08-28 04:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 0 | 0 | 0
2025-08-28 05:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 0 | 0 | 0
2025-08-28 06:00 | 55.47 | 36.39 | 36.39 | 19.09 | 0 | 0 | 0 | 0 | 0
2025-08-28 07:00 | 57.54 | 79.22 | 57.54 | 0 | 0 | 0 | 0 | 21.68 | 0
2025-08-28 08:00 | 59.54 | 99.28 | 59.54 | 0 | 0 | 0 | 0 | 39.74 | 0
2025-08-28 09:00 | 62.91 | 47.38 | 47.38 | 15.53 | 0 | 0 | 0 | 0 | 0
2025-08-28 10:00 | 66.01 | 119.02 | 66.01 | 0 | 0 | 0 | 0 | 53.01 | 0
2025-08-28 11:00 | 68.97 | 83.28 | 68.97 | 0 | 0 | 0 | 0 | 14.31 | 0
2025-08-28 12:00 | 70.87 | 85.22 | 70.87 | 0 | 0 | 0 | 0 | 14.34 | 0
2025-08-28 13:00 | 73.19 | 48.13 | 48.13 | 25.06 | 0 | 0 | 0 | 0 | 0
2025-08-28 14:00 | 74.78 | 61.46 | 61.46 | 13.32 | 0 | 0 | 0 | 0 | 0
2025-08-28 15:00 | 73.76 | 120.36 | 73.76 | 0 | 0 | 0 | 0 | 46.6 | 0
2025-08-28 16:00 | 73.49 | 74.92 | 73.49 | 0 | 0 | 0 | 0 | 1.44 | 0
2025-08-28 17:00 | 72.73 | 34.77 | 34.77 | 37.96 | 0 | 0 | 0 | 0 | 0
2025-08-28 18:00 | 71 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0
2025-08-28 19:00 | 69.89 | 0 | 0 | 69.89 | 0 | 0 | 0 | 0 | 0
2025-08-28 20:00 | 66.62 | 0 | 0 | 66.62 | 0 | 0 | 0 | 0 | 0
2025-08-28 21:00 | 63.52 | 0 | 0 | 63.52 | 0 | 0 | 0 | 0 | 0
2025-08-28 22:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 0 | 0 | 0
2025-08-28 23:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 0 | 0 | 0
2025-08-29 | 53.4 | 0 | 0 | 53.4 | 0 | 0 | 0 | 0 | 0
2025-08-29 01:00 | 52.49 | 0 | 0 | 52.49 | 0 | 0 | 0 | 0 | 0
2025-08-29 02:00 | 51.04 | 0 | 0 | 51.04 | 0 | 0 | 0 | 0 | 0
2025-08-29 03:00 | 50.99 | 0 | 0 | 50.99 | 0 | 0 | 0 | 0 | 0
2025-08-29 04:00 | 50.69 | 0 | 0 | 50.69 | 0 | 0 | 0 | 0 | 0
2025-08-29 05:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 0 | 0 | 0
2025-08-29 06:00 | 54.21 | 33.8 | 33.8 | 20.41 | 0 | 0 | 0 | 0 | 0
2025-08-29 07:00 | 57.14 | 79.69 | 57.14 | 0 | 0 | 0 | 0 | 22.55 | 0
2025-08-29 08:00 | 58.83 | 120.22 | 58.83 | 0 | 0 | 0 | 0 | 61.39 | 0
2025-08-29 09:00 | 62.88 | 123.19 | 62.88 | 0 | 0 | 0 | 0 | 60.3 | 0
2025-08-29 10:00 | 65.32 | 118.77 | 65.32 | 0 | 0 | 0 | 0 | 53.45 | 0
2025-08-29 11:00 | 67.29 | 66.29 | 66.29 | 1 | 0 | 0 | 0 | 0 | 0
2025-08-29 12:00 | 68.82 | 66.24 | 66.24 | 2.58 | 0 | 0 | 0 | 0 | 0
2025-08-29 13:00 | 71.3 | 63.09 | 63.09 | 8.21 | 0 | 0 | 0 | 0 | 0
2025-08-29 14:00 | 73.02 | 51.11 | 51.11 | 21.91 | 0 | 0 | 0 | 0 | 0
2025-08-29 15:00 | 73.44 | 61.91 | 61.91 | 11.53 | 0 | 0 | 0 | 0 | 0
2025-08-29 16:00 | 72.47 | 35.22 | 35.22 | 37.25 | 0 | 0 | 0 | 0 | 0
2025-08-29 17:00 | 72.35 | 27.94 | 27.94 | 44.41 | 0 | 0 | 0 | 0 | 0
2025-08-29 18:00 | 69.84 | 6.98 | 6.98 | 62.86 | 0 | 0 | 0 | 0 | 0
2025-08-29 19:00 | 68.3 | 0 | 0 | 68.3 | 0 | 0 | 0 | 0 | 0
2025-08-29 20:00 | 65.1 | 0 | 0 | 65.1 | 0 | 0 | 0 | 0 | 0
2025-08-29 21:00 | 62.26 | 0 | 0 | 62.26 | 0 | 0 | 0 | 0 | 0
2025-08-29 22:00 | 59.23 | 0 | 0 | 59.23 | 0 | 0 | 0 | 0 | 0
2025-08-29 23:00 | 55.66 | 0 | 0 | 55.66 | 0 | 0 | 0 | 0 | 0
2025-08-30 | 54.76 | 0 | 0 | 54.76 | 0 | 0 | 0 | 0 | 0
2025-08-30 01:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0 | 0 | 0
2025-08-30 02:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 0 | 0 | 0
2025-08-30 03:00 | 49.68 | 0 | 0 | 49.68 | 0 | 0 | 0 | 0 | 0
2025-08-30 04:00 | 50.62 | 0 | 0 | 50.62 | 0 | 0 | 0 | 0 | 0
2025-08-30 05:00 | 52.92 | 0 | 0 | 52.92 | 0 | 0 | 0 | 0 | 0
2025-08-30 06:00 | 55.16 | 24.11 | 24.11 | 31.05 | 0 | 0 | 0 | 0 | 0
2025-08-30 07:00 | 55.99 | 83.31 | 55.99 | 0 | 0 | 0 | 0 | 27.32 | 0
2025-08-30 08:00 | 59.79 | 101.86 | 59.79 | 0 | 0 | 0 | 0 | 42.07 | 0
2025-08-30 09:00 | 62.8 | 106.67 | 62.8 | 0 | 0 | 0 | 0 | 43.87 | 0
2025-08-30 10:00 | 67.16 | 105.28 | 67.16 | 0 | 0 | 0 | 0 | 38.13 | 0
2025-08-30 11:00 | 69.9 | 104.1 | 69.9 | 0 | 0 | 0 | 0 | 34.2 | 0
2025-08-30 12:00 | 72.09 | 101.73 | 72.09 | 0 | 0 | 0 | 0 | 29.64 | 0
2025-08-30 13:00 | 74.48 | 104.41 | 74.48 | 0 | 0 | 0 | 0 | 29.93 | 0
2025-08-30 14:00 | 75.47 | 109.77 | 75.47 | 0 | 0 | 0 | 0 | 34.3 | 0
2025-08-30 15:00 | 76.95 | 111.25 | 76.95 | 0 | 0 | 0 | 0 | 34.3 | 0
2025-08-30 16:00 | 75.98 | 107.5 | 75.98 | 0 | 0 | 0 | 0 | 31.51 | 0
2025-08-30 17:00 | 74.77 | 87.22 | 74.77 | 0 | 0 | 0 | 0 | 12.44 | 0
2025-08-30 18:00 | 71.08 | 18.3 | 18.3 | 52.78 | 0 | 0 | 0 | 0 | 0
2025-08-30 19:00 | 69.73 | 0 | 0 | 69.73 | 0 | 0 | 0 | 0 | 0
2025-08-30 20:00 | 67.7 | 0 | 0 | 67.7 | 0 | 0 | 0 | 0 | 0
2025-08-30 21:00 | 63.98 | 0 | 0 | 63.98 | 0 | 0 | 0 | 0 | 0
2025-08-30 22:00 | 59.04 | 0 | 0 | 59.04 | 0 | 0 | 0 | 0 | 0
2025-08-30 23:00 | 56.67 | 0 | 0 | 56.67 | 0 | 0 | 0 | 0 | 0
2025-08-31 | 53.26 | 0 | 0 | 53.26 | 0 | 0 | 0 | 0 | 0
2025-08-31 01:00 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 0 | 0 | 0
2025-08-31 02:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 0 | 0 | 0
2025-08-31 03:00 | 49.81 | 0 | 0 | 49.81 | 0 | 0 | 0 | 0 | 0
2025-08-31 04:00 | 50.66 | 0 | 0 | 50.66 | 0 | 0 | 0 | 0 | 0
2025-08-31 05:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 0 | 0 | 0
2025-08-31 06:00 | 53.31 | 0 | 0 | 53.31 | 0 | 0 | 0 | 0 | 0
2025-08-31 07:00 | 56.25 | 18.63 | 18.63 | 37.61 | 0 | 0 | 0 | 0 | 0
2025-08-31 08:00 | 59.19 | 36.53 | 36.53 | 22.67 | 0 | 0 | 0 | 0 | 0
2025-08-31 09:00 | 60.26 | 58.13 | 58.13 | 2.13 | 0 | 0 | 0 | 0 | 0
2025-08-31 10:00 | 63.22 | 61.47 | 61.47 | 1.74 | 0 | 0 | 0 | 0 | 0
2025-08-31 11:00 | 65.69 | 84.31 | 65.69 | 0 | 0 | 0 | 0 | 18.61 | 0
2025-08-31 12:00 | 65.8 | 80.85 | 65.8 | 0 | 0 | 0 | 0 | 15.05 | 0
2025-08-31 13:00 | 67.55 | 78.76 | 67.55 | 0 | 0 | 0 | 0 | 11.21 | 0
2025-08-31 14:00 | 67.98 | 52.85 | 52.85 | 15.13 | 0 | 0 | 0 | 0 | 0
2025-08-31 15:00 | 68.97 | 29.01 | 29.01 | 39.96 | 0 | 0 | 0 | 0 | 0
2025-08-31 16:00 | 67.83 | 28.95 | 28.95 | 38.88 | 0 | 0 | 0 | 0 | 0
2025-08-31 17:00 | 67.34 | 5.42 | 5.42 | 61.93 | 0 | 0 | 0 | 0 | 0
2025-08-31 18:00 | 66.95 | 0.72 | 0.72 | 66.23 | 0 | 0 | 0 | 0 | 0
2025-08-31 19:00 | 64.53 | 0 | 0 | 64.53 | 0 | 0 | 0 | 0 | 0
2025-08-31 20:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 0 | 0 | 0
2025-08-31 21:00 | 61 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0
2025-08-31 22:00 | 58.7 | 0 | 0 | 58.7 | 0 | 0 | 0 | 0 | 0
2025-08-31 23:00 | 56.65 | 0 | 0 | 56.65 | 0 | 0 | 0 | 0 | 0
2025-09-01 | 54.07 | 0 | 0 | 54.07 | 0 | 0 | 0 | 0 | 0
2025-09-01 01:00 | 51.46 | 0 | 0 | 51.46 | 0 | 0 | 0 | 0 | 0
2025-09-01 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 0 | 0 | 0
2025-09-01 03:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 0 | 0 | 0
2025-09-01 04:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0 | 0 | 0
2025-09-01 05:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 0 | 0 | 0
2025-09-01 06:00 | 53.7 | 9.3 | 9.3 | 44.39 | 0 | 0 | 0 | 0 | 0
2025-09-01 07:00 | 56.18 | 12.15 | 12.15 | 44.03 | 0 | 0 | 0 | 0 | 0
2025-09-01 08:00 | 58.03 | 35.63 | 35.63 | 22.4 | 0 | 0 | 0 | 0 | 0
2025-09-01 09:00 | 62.15 | 63.49 | 62.15 | 0 | 0 | 0 | 0 | 1.34 | 0
2025-09-01 10:00 | 63.43 | 70.28 | 63.43 | 0 | 0 | 0 | 0 | 6.85 | 0
2025-09-01 11:00 | 66.33 | 69.37 | 66.33 | 0 | 0 | 0 | 0 | 3.04 | 0
2025-09-01 12:00 | 67.06 | 73.5 | 67.06 | 0 | 0 | 0 | 0 | 6.44 | 0
2025-09-01 13:00 | 68.16 | 70.81 | 68.16 | 0 | 0 | 0 | 0 | 2.65 | 0
2025-09-01 14:00 | 69.72 | 55.64 | 55.64 | 14.07 | 0 | 0 | 0 | 0 | 0
2025-09-01 15:00 | 69.82 | 87.64 | 69.82 | 0 | 0 | 0 | 0 | 17.82 | 0
2025-09-01 16:00 | 69.22 | 99.96 | 69.22 | 0 | 0 | 0 | 0 | 30.74 | 0
2025-09-01 17:00 | 68.85 | 48.13 | 48.13 | 20.72 | 0 | 0 | 0 | 0 | 0
2025-09-01 18:00 | 67.23 | 14.3 | 14.3 | 52.93 | 0 | 0 | 0 | 0 | 0
2025-09-01 19:00 | 65.81 | 0 | 0 | 65.81 | 0 | 0 | 0 | 0 | 0
2025-09-01 20:00 | 63.48 | 0 | 0 | 63.48 | 0 | 0 | 0 | 0 | 0
2025-09-01 21:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 0 | 0 | 0
2025-09-01 22:00 | 58.5 | 0 | 0 | 58.5 | 0 | 0 | 0 | 0 | 0
2025-09-01 23:00 | 56.95 | 0 | 0 | 56.95 | 0 | 0 | 0 | 0 | 0
2025-09-02 | 53.9 | 0 | 0 | 53.9 | 0 | 0 | 0 | 0 | 0
2025-09-02 01:00 | 51.83 | 0 | 0 | 51.83 | 0 | 0 | 0 | 0 | 0
2025-09-02 02:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 0 | 0 | 0
2025-09-02 03:00 | 50.05 | 0 | 0 | 50.05 | 0 | 0 | 0 | 0 | 0
2025-09-02 04:00 | 50.34 | 0 | 0 | 50.34 | 0 | 0 | 0 | 0 | 0
2025-09-02 05:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0 | 0 | 0
2025-09-02 06:00 | 54.5 | 27.57 | 27.57 | 26.93 | 0 | 0 | 0 | 0 | 0
2025-09-02 07:00 | 56.83 | 96.82 | 56.83 | 0 | 0 | 0 | 0 | 40 | 0
2025-09-02 08:00 | 60.97 | 114.8 | 60.97 | 0 | 0 | 0 | 0 | 53.82 | 0
2025-09-02 09:00 | 65.53 | 119.21 | 65.53 | 0 | 0 | 0 | 0 | 53.68 | 0
2025-09-02 10:00 | 70.77 | 115.88 | 70.77 | 0 | 0 | 0 | 0 | 45.1 | 0
2025-09-02 11:00 | 75.08 | 111.76 | 75.08 | 0 | 0 | 0 | 0 | 36.68 | 0
2025-09-02 12:00 | 80.38 | 103.39 | 80.38 | 0 | 0 | 0 | 0 | 23.02 | 0
2025-09-02 13:00 | 82.87 | 53.46 | 53.46 | 29.41 | 0 | 0 | 0 | 0 | 0
2025-09-02 14:00 | 85.08 | 111.59 | 85.08 | 0 | 0 | 0 | 0 | 26.51 | 0
2025-09-02 15:00 | 85.89 | 64.9 | 64.9 | 21 | 0 | 0 | 0 | 0 | 0
2025-09-02 16:00 | 84.54 | 2.35 | 2.35 | 82.19 | 0 | 0 | 0 | 0 | 0
2025-09-02 17:00 | 82.43 | 0.78 | 0.78 | 81.65 | 0 | 0 | 0 | 0 | 0
2025-09-02 18:00 | 79.21 | 0 | 0 | 79.21 | 0 | 0 | 0 | 0 | 0
2025-09-02 19:00 | 75.7 | 0 | 0 | 75.7 | 0 | 0 | 0 | 0 | 0
2025-09-02 20:00 | 70.32 | 0 | 0 | 70.32 | 0 | 0 | 0 | 0 | 0
2025-09-02 21:00 | 65.28 | 0 | 0 | 65.28 | 0 | 0 | 0 | 0 | 0
2025-09-02 22:00 | 61.65 | 0 | 0 | 61.65 | 0 | 0 | 0 | 0 | 0
2025-09-02 23:00 | 57.93 | 0 | 0 | 57.93 | 0 | 0 | 0 | 0 | 0
2025-09-03 | 54.24 | 0 | 0 | 54.24 | 0 | 0 | 0 | 0 | 0
2025-09-03 01:00 | 51.24 | 0 | 0 | 51.24 | 0 | 0 | 0 | 0 | 0
2025-09-03 02:00 | 50.15 | 0 | 0 | 50.15 | 0 | 0 | 0 | 0 | 0
2025-09-03 03:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 0 | 0 | 0
2025-09-03 04:00 | 50.52 | 0 | 0 | 50.52 | 0 | 0 | 0 | 0 | 0
2025-09-03 05:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 0 | 0 | 0
2025-09-03 06:00 | 53.98 | 24.11 | 24.11 | 29.86 | 0 | 0 | 0 | 0 | 0
2025-09-03 07:00 | 56.55 | 86.88 | 56.55 | 0 | 0 | 0 | 0 | 30.33 | 0
2025-09-03 08:00 | 58.43 | 100.83 | 58.43 | 0 | 0 | 0 | 0 | 42.4 | 0
2025-09-03 09:00 | 61.5 | 103.78 | 61.5 | 0 | 0 | 0 | 0 | 42.28 | 0
2025-09-03 10:00 | 64.33 | 107.03 | 64.33 | 0 | 0 | 0 | 0 | 42.71 | 0
2025-09-03 11:00 | 65.4 | 101.38 | 65.4 | 0 | 0 | 0 | 0 | 35.98 | 0
2025-09-03 12:00 | 67.67 | 99.62 | 67.67 | 0 | 0 | 0 | 0 | 31.95 | 0
2025-09-03 13:00 | 68.32 | 98.89 | 68.32 | 0 | 0 | 0 | 0 | 30.57 | 0
2025-09-03 14:00 | 69.1 | 103.35 | 69.1 | 0 | 0 | 0 | 0 | 34.25 | 0
2025-09-03 15:00 | 69.55 | 100.8 | 69.55 | 0 | 0 | 0 | 0 | 31.25 | 0
2025-09-03 16:00 | 69.83 | 90.98 | 69.83 | 0 | 0 | 0 | 0 | 21.15 | 0
2025-09-03 17:00 | 68.71 | 68.23 | 68.23 | 0.49 | 0 | 0 | 0 | 0 | 0
2025-09-03 18:00 | 67.34 | 9.54 | 9.54 | 57.81 | 0 | 0 | 0 | 0 | 0
2025-09-03 19:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 0 | 0 | 0
2025-09-03 20:00 | 63.29 | 0 | 0 | 63.29 | 0 | 0 | 0 | 0 | 0
2025-09-03 21:00 | 61.61 | 0 | 0 | 61.61 | 0 | 0 | 0 | 0 | 0
2025-09-03 22:00 | 59.29 | 0 | 0 | 59.29 | 0 | 0 | 0 | 0 | 0
2025-09-03 23:00 | 56.01 | 0 | 0 | 56.01 | 0 | 0 | 0 | 0 | 0
2025-09-04 | 53.44 | 0 | 0 | 53.44 | 0 | 0 | 0 | 0 | 0
2025-09-04 01:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 0 | 0 | 0
2025-09-04 02:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 0 | 0 | 0
2025-09-04 03:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0 | 0 | 0
2025-09-04 04:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 0 | 0 | 0
2025-09-04 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 0 | 0 | 0
2025-09-04 06:00 | 53.48 | 25.44 | 25.44 | 28.03 | 0 | 0 | 0 | 0 | 0
2025-09-04 07:00 | 56.37 | 89.22 | 56.37 | 0 | 0 | 0 | 0 | 32.85 | 0
2025-09-04 08:00 | 59.54 | 109.36 | 59.54 | 0 | 0 | 0 | 0 | 49.82 | 0
2025-09-04 09:00 | 61.96 | 110.94 | 61.96 | 0 | 0 | 0 | 0 | 48.98 | 0
2025-09-04 10:00 | 62.99 | 107.6 | 62.99 | 0 | 0 | 0 | 0 | 44.61 | 0
2025-09-04 11:00 | 66.61 | 103.09 | 66.61 | 0 | 0 | 0 | 0 | 36.49 | 0
2025-09-04 12:00 | 69.43 | 101.58 | 69.43 | 0 | 0 | 0 | 0 | 32.15 | 0
2025-09-04 13:00 | 69.78 | 102.57 | 69.78 | 0 | 0 | 0 | 0 | 32.79 | 0
2025-09-04 14:00 | 69.69 | 104.55 | 69.69 | 0 | 0 | 0 | 0 | 34.86 | 0
2025-09-04 15:00 | 70.68 | 104.85 | 70.68 | 0 | 0 | 0 | 0 | 34.17 | 0
2025-09-04 16:00 | 69.63 | 95.95 | 69.63 | 0 | 0 | 0 | 0 | 26.32 | 0
2025-09-04 17:00 | 70.09 | 74.41 | 70.09 | 0 | 0 | 0 | 0 | 4.32 | 0
2025-09-04 18:00 | 67.67 | 8.92 | 8.92 | 58.75 | 0 | 0 | 0 | 0 | 0
2025-09-04 19:00 | 66.36 | 0 | 0 | 66.36 | 0 | 0 | 0 | 0 | 0
2025-09-04 20:00 | 63.64 | 0 | 0 | 63.64 | 0 | 0 | 0 | 0 | 0
2025-09-04 21:00 | 61.2 | 0 | 0 | 61.2 | 0 | 0 | 0 | 0 | 0
2025-09-04 22:00 | 59.46 | 0 | 0 | 59.46 | 0 | 0 | 0 | 0 | 0
2025-09-04 23:00 | 56.04 | 0 | 0 | 56.04 | 0 | 0 | 0 | 0 | 0
2025-09-05 | 53.44 | 0 | 0 | 53.44 | 0 | 0 | 0 | 0 | 0
2025-09-05 01:00 | 50.97 | 0 | 0 | 50.97 | 0 | 0 | 0 | 0 | 0
2025-09-05 02:00 | 49.29 | 0 | 0 | 49.29 | 0 | 0 | 0 | 0 | 0
2025-09-05 03:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 0 | 0 | 0
2025-09-05 04:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0 | 0 | 0
2025-09-05 05:00 | 52.04 | 0 | 0 | 52.04 | 0 | 0 | 0 | 0 | 0
2025-09-05 06:00 | 53.44 | 22.76 | 22.76 | 30.68 | 0 | 0 | 0 | 0 | 0
2025-09-05 07:00 | 57.51 | 87.82 | 57.51 | 0 | 0 | 0 | 0 | 30.31 | 0
2025-09-05 08:00 | 60.09 | 107.42 | 60.09 | 0 | 0 | 0 | 0 | 47.33 | 0
2025-09-05 09:00 | 64.6 | 110.1 | 64.6 | 0 | 0 | 0 | 0 | 45.5 | 0
2025-09-05 10:00 | 68.73 | 107.97 | 68.73 | 0 | 0 | 0 | 0 | 39.24 | 0
2025-09-05 11:00 | 74.27 | 104.39 | 74.27 | 0 | 0 | 0 | 0 | 30.12 | 0
2025-09-05 12:00 | 78.88 | 101.41 | 78.88 | 0 | 0 | 0 | 0 | 22.52 | 0
2025-09-05 13:00 | 80.19 | 103.39 | 80.19 | 0 | 0 | 0 | 0 | 23.2 | 0
2025-09-05 14:00 | 82.99 | 105.68 | 82.99 | 0 | 0 | 0 | 0 | 22.68 | 0
2025-09-05 15:00 | 84.52 | 104.89 | 84.52 | 0 | 0 | 0 | 0 | 20.38 | 0
2025-09-05 16:00 | 82.44 | 97.7 | 82.44 | 0 | 0 | 0 | 0 | 15.26 | 0
2025-09-05 17:00 | 81.36 | 76.46 | 76.46 | 4.9 | 0 | 0 | 0 | 0 | 0
2025-09-05 18:00 | 78.44 | 7.71 | 7.71 | 70.73 | 0 | 0 | 0 | 0 | 0
2025-09-05 19:00 | 73.81 | 0 | 0 | 73.81 | 0 | 0 | 0 | 0 | 0
2025-09-05 20:00 | 69.55 | 0 | 0 | 69.55 | 0 | 0 | 0 | 0 | 0
2025-09-05 21:00 | 65.6 | 0 | 0 | 65.6 | 0 | 0 | 0 | 0 | 0
2025-09-05 22:00 | 61.42 | 0 | 0 | 61.42 | 0 | 0 | 0 | 0 | 0
2025-09-05 23:00 | 56.7 | 0 | 0 | 56.7 | 0 | 0 | 0 | 0 | 0
2025-09-06 | 53.46 | 0 | 0 | 53.46 | 0 | 0 | 0 | 0 | 0
2025-09-06 01:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 0 | 0 | 0
2025-09-06 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 0 | 0 | 0
2025-09-06 03:00 | 49.02 | 0 | 0 | 49.02 | 0 | 0 | 0 | 0 | 0
2025-09-06 04:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 0 | 0 | 0
2025-09-06 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 0 | 0 | 0
2025-09-06 06:00 | 53.47 | 0.85 | 0.85 | 52.62 | 0 | 0 | 0 | 0 | 0
2025-09-06 07:00 | 57.05 | 8.48 | 8.48 | 48.57 | 0 | 0 | 0 | 0 | 0
2025-09-06 08:00 | 62.27 | 51.05 | 51.05 | 11.22 | 0 | 0 | 0 | 0 | 0
2025-09-06 09:00 | 65.73 | 57.74 | 57.74 | 7.99 | 0 | 0 | 0 | 0 | 0
2025-09-06 10:00 | 70.82 | 63.02 | 63.02 | 7.8 | 0 | 0 | 0 | 0 | 0
2025-09-06 11:00 | 76.84 | 34.32 | 34.32 | 42.52 | 0 | 0 | 0 | 0 | 0
2025-09-06 12:00 | 81.3 | 53.7 | 53.7 | 27.6 | 0 | 0 | 0 | 0 | 0
2025-09-06 13:00 | 85.82 | 39.17 | 39.17 | 46.66 | 0 | 0 | 0 | 0 | 0
2025-09-06 14:00 | 87.73 | 113.53 | 87.73 | 0 | 0 | 0 | 0 | 25.79 | 0
2025-09-06 15:00 | 88.41 | 109.47 | 88.41 | 0 | 0 | 0 | 0 | 21.06 | 0
2025-09-06 16:00 | 86.76 | 98.04 | 86.76 | 0 | 0 | 0 | 0 | 11.28 | 0
2025-09-06 17:00 | 84.29 | 42.73 | 42.73 | 41.56 | 0 | 0 | 0 | 0 | 0
2025-09-06 18:00 | 80.26 | 1.08 | 1.08 | 79.19 | 0 | 0 | 0 | 0 | 0
2025-09-06 19:00 | 76.52 | 0 | 0 | 76.52 | 0 | 0 | 0 | 0 | 0
2025-09-06 20:00 | 70.35 | 0 | 0 | 70.35 | 0 | 0 | 0 | 0 | 0
2025-09-06 21:00 | 66.41 | 0 | 0 | 66.41 | 0 | 0 | 0 | 0 | 0
2025-09-06 22:00 | 61 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0
2025-09-06 23:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 0 | 0 | 0
2025-09-07 | 52.8 | 0 | 0 | 52.8 | 0 | 0 | 0 | 0 | 0
2025-09-07 01:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0
2025-09-07 02:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 0 | 0 | 0
2025-09-07 03:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 0 | 0 | 0
2025-09-07 04:00 | 50.64 | 0 | 0 | 50.64 | 0 | 0 | 0 | 0 | 0
2025-09-07 05:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0 | 0 | 0
2025-09-07 06:00 | 53.1 | 14.2 | 14.2 | 38.9 | 0 | 0 | 0 | 0 | 0
2025-09-07 07:00 | 55.95 | 64.13 | 55.95 | 0 | 0 | 0 | 0 | 8.18 | 0
2025-09-07 08:00 | 58.29 | 77.38 | 58.29 | 0 | 0 | 0 | 0 | 19.09 | 0
2025-09-07 09:00 | 61.16 | 83.27 | 61.16 | 0 | 0 | 0 | 0 | 22.12 | 0
2025-09-07 10:00 | 63.06 | 75.39 | 63.06 | 0 | 0 | 0 | 0 | 12.33 | 0
2025-09-07 11:00 | 66.67 | 79.8 | 66.67 | 0 | 0 | 0 | 0 | 13.13 | 0
2025-09-07 12:00 | 67.08 | 95.54 | 67.08 | 0 | 0 | 0 | 0 | 28.45 | 0
2025-09-07 13:00 | 69.41 | 95.25 | 69.41 | 0 | 0 | 0 | 0 | 25.84 | 0
2025-09-07 14:00 | 69.29 | 99.94 | 69.29 | 0 | 0 | 0 | 0 | 30.65 | 0
2025-09-07 15:00 | 70.04 | 86.64 | 70.04 | 0 | 0 | 0 | 0 | 16.6 | 0
2025-09-07 16:00 | 69.75 | 106.64 | 69.75 | 0 | 0 | 0 | 0 | 36.88 | 0
2025-09-07 17:00 | 69.2 | 79.8 | 69.2 | 0 | 0 | 0 | 0 | 10.6 | 0
2025-09-07 18:00 | 66.95 | 9.15 | 9.15 | 57.8 | 0 | 0 | 0 | 0 | 0
2025-09-07 19:00 | 66.17 | 0 | 0 | 66.17 | 0 | 0 | 0 | 0 | 0
2025-09-07 20:00 | 64.39 | 0 | 0 | 64.39 | 0 | 0 | 0 | 0 | 0
2025-09-07 21:00 | 60.83 | 0 | 0 | 60.83 | 0 | 0 | 0 | 0 | 0
2025-09-07 22:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 0 | 0 | 0
2025-09-07 23:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 0 | 0 | 0
2025-09-08 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 0 | 0 | 0
2025-09-08 01:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 0 | 0 | 0
2025-09-08 02:00 | 49.45 | 0 | 0 | 49.45 | 0 | 0 | 0 | 0 | 0
2025-09-08 03:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0 | 0 | 0
2025-09-08 04:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 0 | 0 | 0
2025-09-08 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 0 | 0 | 0
2025-09-08 06:00 | 54.25 | 1.21 | 1.21 | 53.03 | 0 | 0 | 0 | 0 | 0
2025-09-08 07:00 | 55.51 | 2.45 | 2.45 | 53.06 | 0 | 0 | 0 | 0 | 0
2025-09-08 08:00 | 58.72 | 19.34 | 19.34 | 39.37 | 0 | 0 | 0 | 0 | 0
2025-09-08 09:00 | 61.4 | 71.93 | 61.4 | 0 | 0 | 0 | 0 | 10.53 | 0
2025-09-08 10:00 | 64.82 | 101.38 | 64.82 | 0 | 0 | 0 | 0 | 36.55 | 0
2025-09-08 11:00 | 66.63 | 111.5 | 66.63 | 0 | 0 | 0 | 0 | 44.87 | 0
2025-09-08 12:00 | 70.2 | 100.92 | 70.2 | 0 | 0 | 0 | 0 | 30.72 | 0
2025-09-08 13:00 | 71.78 | 69.45 | 69.45 | 2.34 | 0 | 0 | 0 | 0 | 0
2025-09-08 14:00 | 72.69 | 10.43 | 10.43 | 62.26 | 0 | 0 | 0 | 0 | 0
2025-09-08 15:00 | 72.9 | 8.68 | 8.68 | 64.22 | 0 | 0 | 0 | 0 | 0
2025-09-08 16:00 | 72.28 | 2.34 | 2.34 | 69.93 | 0 | 0 | 0 | 0 | 0
2025-09-08 17:00 | 71.99 | 0.75 | 0.75 | 71.23 | 0 | 0 | 0 | 0 | 0
2025-09-08 18:00 | 69.27 | 1.49 | 1.49 | 67.78 | 0 | 0 | 0 | 0 | 0
2025-09-08 19:00 | 67.77 | 0 | 0 | 67.77 | 0 | 0 | 0 | 0 | 0
2025-09-08 20:00 | 65.79 | 0 | 0 | 65.79 | 0 | 0 | 0 | 0 | 0
2025-09-08 21:00 | 62.47 | 0 | 0 | 62.47 | 0 | 0 | 0 | 0 | 0
2025-09-08 22:00 | 57.9 | 0 | 0 | 57.9 | 0 | 0 | 0 | 0 | 0
2025-09-08 23:00 | 55.46 | 0 | 0 | 55.46 | 0 | 0 | 0 | 0 | 0
2025-09-09 | 53.36 | 0 | 0 | 53.36 | 0 | 0 | 0 | 0 | 0
2025-09-09 01:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 0 | 0 | 0
2025-09-09 02:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 0 | 0 | 0
2025-09-09 03:00 | 49.63 | 0 | 0 | 49.63 | 0 | 0 | 0 | 0 | 0
2025-09-09 04:00 | 49.86 | 0 | 0 | 49.86 | 0 | 0 | 0 | 0 | 0
2025-09-09 05:00 | 52.08 | 0 | 0 | 52.08 | 0 | 0 | 0 | 0 | 0
2025-09-09 06:00 | 53.02 | 17.02 | 17.02 | 36 | 0 | 0 | 0 | 0 | 0
2025-09-09 07:00 | 56.39 | 83.09 | 56.39 | 0 | 0 | 0 | 0 | 26.7 | 0
2025-09-09 08:00 | 58.32 | 85.11 | 58.32 | 0 | 0 | 0 | 0 | 26.79 | 0
2025-09-09 09:00 | 61.86 | 98.58 | 61.86 | 0 | 0 | 0 | 0 | 36.72 | 0
2025-09-09 10:00 | 66.21 | 98.28 | 66.21 | 0 | 0 | 0 | 0 | 32.07 | 0
2025-09-09 11:00 | 69.68 | 93.14 | 69.68 | 0 | 0 | 0 | 0 | 23.46 | 0
2025-09-09 12:00 | 71.52 | 89.32 | 71.52 | 0 | 0 | 0 | 0 | 17.8 | 0
2025-09-09 13:00 | 74.22 | 93.94 | 74.22 | 0 | 0 | 0 | 0 | 19.72 | 0
2025-09-09 14:00 | 74.92 | 98.28 | 74.92 | 0 | 0 | 0 | 0 | 23.36 | 0
2025-09-09 15:00 | 76 | 90.09 | 76 | 0 | 0 | 0 | 0 | 14.09 | 0
2025-09-09 16:00 | 76.03 | 87.46 | 76.03 | 0 | 0 | 0 | 0 | 11.44 | 0
2025-09-09 17:00 | 73.99 | 54.75 | 54.75 | 19.24 | 0 | 0 | 0 | 0 | 0
2025-09-09 18:00 | 71.87 | 3.21 | 3.21 | 68.66 | 0 | 0 | 0 | 0 | 0
2025-09-09 19:00 | 68.57 | 0 | 0 | 68.57 | 0 | 0 | 0 | 0 | 0
2025-09-09 20:00 | 65.53 | 0 | 0 | 65.53 | 0 | 0 | 0 | 0 | 0
2025-09-09 21:00 | 63.26 | 0 | 0 | 63.26 | 0 | 0 | 0 | 0 | 0
2025-09-09 22:00 | 58.99 | 0 | 0 | 58.99 | 0 | 0 | 0 | 0 | 0
2025-09-09 23:00 | 55.31 | 0 | 0 | 55.31 | 0 | 0 | 0 | 0 | 0
2025-09-10 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 0 | 0 | 0
2025-09-10 01:00 | 50.25 | 0 | 0 | 50.25 | 0 | 0 | 0 | 0 | 0
2025-09-10 02:00 | 49.26 | 0 | 0 | 49.26 | 0 | 0 | 0 | 0 | 0
2025-09-10 03:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 0 | 0 | 0
2025-09-10 04:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 0 | 0 | 0
2025-09-10 05:00 | 52 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0
2025-09-10 06:00 | 53.12 | 14.61 | 14.61 | 38.51 | 0 | 0 | 0 | 0 | 0
2025-09-10 07:00 | 56.06 | 61.79 | 56.06 | 0 | 0 | 0 | 0 | 5.73 | 0
2025-09-10 08:00 | 59.99 | 89.07 | 59.99 | 0 | 0 | 0 | 0 | 29.08 | 0
2025-09-10 09:00 | 62.44 | 91.68 | 62.44 | 0 | 0 | 0 | 0 | 29.24 | 0
2025-09-10 10:00 | 68.24 | 87.37 | 68.24 | 0 | 0 | 0 | 0 | 19.12 | 0
2025-09-10 11:00 | 72.42 | 96.81 | 72.42 | 0 | 0 | 0 | 0 | 24.39 | 0
2025-09-10 12:00 | 77.07 | 93.66 | 77.07 | 0 | 0 | 0 | 0 | 16.59 | 0
2025-09-10 13:00 | 79.9 | 87.58 | 79.9 | 0 | 0 | 0 | 0 | 7.69 | 0
2025-09-10 14:00 | 80.84 | 63.45 | 63.45 | 17.39 | 0 | 0 | 0 | 0 | 0
2025-09-10 15:00 | 82.71 | 47.44 | 47.44 | 35.28 | 0 | 0 | 0 | 0 | 0
2025-09-10 16:00 | 81.27 | 16.67 | 16.67 | 64.6 | 0 | 0 | 0 | 0 | 0
2025-09-10 17:00 | 78.96 | 0.2 | 0.2 | 78.76 | 0 | 0 | 0 | 0 | 0
2025-09-10 18:00 | 76.42 | 0.24 | 0.24 | 76.18 | 0 | 0 | 0 | 0 | 0
2025-09-10 19:00 | 72.35 | 0 | 0 | 72.35 | 0 | 0 | 0 | 0 | 0
2025-09-10 20:00 | 68.91 | 0 | 0 | 68.91 | 0 | 0 | 0 | 0 | 0
2025-09-10 21:00 | 63.94 | 0 | 0 | 63.94 | 0 | 0 | 0 | 0 | 0
2025-09-10 22:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 0 | 0 | 0
2025-09-10 23:00 | 56.52 | 0 | 0 | 56.52 | 0 | 0 | 0 | 0 | 0
2025-09-11 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 0 | 0 | 0
2025-09-11 01:00 | 51.28 | 0 | 0 | 51.28 | 0 | 0 | 0 | 0 | 0
2025-09-11 02:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 0 | 0 | 0
2025-09-11 03:00 | 49.55 | 0 | 0 | 49.55 | 0 | 0 | 0 | 0 | 0
2025-09-11 04:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0 | 0 | 0
2025-09-11 05:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 0 | 0 | 0
2025-09-11 06:00 | 52.75 | 8.89 | 8.89 | 43.86 | 0 | 0 | 0 | 0 | 0
2025-09-11 07:00 | 55.2 | 91.62 | 55.2 | 0 | 0 | 0 | 0 | 36.42 | 0
2025-09-11 08:00 | 58.71 | 86.72 | 58.71 | 0 | 0 | 0 | 0 | 28.01 | 0
2025-09-11 09:00 | 61.38 | 63.38 | 61.38 | 0 | 0 | 0 | 0 | 2.01 | 0
2025-09-11 10:00 | 63.13 | 70.5 | 63.13 | 0 | 0 | 0 | 0 | 7.37 | 0
2025-09-11 11:00 | 65.17 | 80.74 | 65.17 | 0 | 0 | 0 | 0 | 15.57 | 0
2025-09-11 12:00 | 67.97 | 72.33 | 67.97 | 0 | 0 | 0 | 0 | 4.36 | 0
2025-09-11 13:00 | 68.98 | 82.42 | 68.98 | 0 | 0 | 0 | 0 | 13.44 | 0
2025-09-11 14:00 | 69.56 | 78.67 | 69.56 | 0 | 0 | 0 | 0 | 9.11 | 0
2025-09-11 15:00 | 69.52 | 72.18 | 69.52 | 0 | 0 | 0 | 0 | 2.67 | 0
2025-09-11 16:00 | 69.57 | 35.72 | 35.72 | 33.85 | 0 | 0 | 0 | 0 | 0
2025-09-11 17:00 | 68.57 | 11.91 | 11.91 | 56.67 | 0 | 0 | 0 | 0 | 0
2025-09-11 18:00 | 66.9 | 0.84 | 0.84 | 66.06 | 0 | 0 | 0 | 0 | 0
2025-09-11 19:00 | 65.46 | 0 | 0 | 65.46 | 0 | 0 | 0 | 0 | 0
2025-09-11 20:00 | 63.27 | 0 | 0 | 63.27 | 0 | 0 | 0 | 0 | 0
2025-09-11 21:00 | 60.38 | 0 | 0 | 60.38 | 0 | 0 | 0 | 0 | 0
2025-09-11 22:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 0 | 0 | 0
2025-09-11 23:00 | 55.83 | 0 | 0 | 55.83 | 0 | 0 | 0 | 0 | 0
2025-09-12 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0 | 0 | 0
2025-09-12 01:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 0 | 0 | 0
2025-09-12 02:00 | 49.95 | 0 | 0 | 49.95 | 0 | 0 | 0 | 0 | 0
2025-09-12 03:00 | 49.19 | 0 | 0 | 49.19 | 0 | 0 | 0 | 0 | 0
2025-09-12 04:00 | 48.96 | 0 | 0 | 48.96 | 0 | 0 | 0 | 0 | 0
2025-09-12 05:00 | 51.14 | 0 | 0 | 51.14 | 0 | 0 | 0 | 0 | 0
2025-09-12 06:00 | 52.82 | 13.19 | 13.19 | 39.63 | 0 | 0 | 0 | 0 | 0
2025-09-12 07:00 | 56.56 | 85.9 | 56.56 | 0 | 0 | 0 | 0 | 29.34 | 0
2025-09-12 08:00 | 58.89 | 105.5 | 58.89 | 0 | 0 | 0 | 0 | 46.62 | 0
2025-09-12 09:00 | 61.59 | 105.4 | 61.59 | 0 | 0 | 0 | 0 | 43.81 | 0
2025-09-12 10:00 | 64.39 | 94.96 | 64.39 | 0 | 0 | 0 | 0 | 30.56 | 0
2025-09-12 11:00 | 67.15 | 92.63 | 67.15 | 0 | 0 | 0 | 0 | 25.48 | 0
2025-09-12 12:00 | 68.94 | 92.33 | 68.94 | 0 | 0 | 0 | 0 | 23.39 | 0
2025-09-12 13:00 | 70.38 | 95.38 | 70.38 | 0 | 0 | 0 | 0 | 25 | 0
2025-09-12 14:00 | 71.95 | 96.77 | 71.95 | 0 | 0 | 0 | 0 | 24.83 | 0
2025-09-12 15:00 | 72.74 | 99.01 | 72.74 | 0 | 0 | 0 | 0 | 26.27 | 0
2025-09-12 16:00 | 71.33 | 92.01 | 71.33 | 0 | 0 | 0 | 0 | 20.68 | 0
2025-09-12 17:00 | 70.98 | 56.97 | 56.97 | 14.01 | 0 | 0 | 0 | 0 | 0
2025-09-12 18:00 | 69.32 | 1.58 | 1.58 | 67.74 | 0 | 0 | 0 | 0 | 0
2025-09-12 19:00 | 66.96 | 0 | 0 | 66.96 | 0 | 0 | 0 | 0 | 0
2025-09-12 20:00 | 63.94 | 0 | 0 | 63.94 | 0 | 0 | 0 | 0 | 0
2025-09-12 21:00 | 61.06 | 0 | 0 | 61.06 | 0 | 0 | 0 | 0 | 0
2025-09-12 22:00 | 59.02 | 0 | 0 | 59.02 | 0 | 0 | 0 | 0 | 0
2025-09-12 23:00 | 55.59 | 0 | 0 | 55.59 | 0 | 0 | 0 | 0 | 0
2025-09-13 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 0 | 0 | 0
2025-09-13 01:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 0 | 0 | 0
2025-09-13 02:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 0 | 0 | 0
2025-09-13 03:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 0 | 0 | 0
2025-09-13 04:00 | 49.09 | 0 | 0 | 49.09 | 0 | 0 | 0 | 0 | 0
2025-09-13 05:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0 | 0 | 0
2025-09-13 06:00 | 52.52 | 5.94 | 5.94 | 46.57 | 0 | 0 | 0 | 0 | 0
2025-09-13 07:00 | 54.86 | 3.52 | 3.52 | 51.34 | 0 | 0 | 0 | 0 | 0
2025-09-13 08:00 | 58.61 | 12.02 | 12.02 | 46.59 | 0 | 0 | 0 | 0 | 0
2025-09-13 09:00 | 62.26 | 31.91 | 31.91 | 30.34 | 0 | 0 | 0 | 0 | 0
2025-09-13 10:00 | 64.89 | 47.53 | 47.53 | 17.36 | 0 | 0 | 0 | 0 | 0
2025-09-13 11:00 | 69.39 | 51.23 | 51.23 | 18.16 | 0 | 0 | 0 | 0 | 0
2025-09-13 12:00 | 72.96 | 80.68 | 72.96 | 0 | 0 | 0 | 0 | 7.73 | 0
2025-09-13 13:00 | 75.19 | 74.77 | 74.77 | 0.42 | 0 | 0 | 0 | 0 | 0
2025-09-13 14:00 | 77.64 | 85.94 | 77.64 | 0 | 0 | 0 | 0 | 8.31 | 0
2025-09-13 15:00 | 77.68 | 116.18 | 77.68 | 0 | 0 | 0 | 0 | 38.5 | 0
2025-09-13 16:00 | 77.24 | 113.73 | 77.24 | 0 | 0 | 0 | 0 | 36.49 | 0
2025-09-13 17:00 | 76.36 | 70.59 | 70.59 | 5.77 | 0 | 0 | 0 | 0 | 0
2025-09-13 18:00 | 72.9 | 1.35 | 1.35 | 71.56 | 0 | 0 | 0 | 0 | 0
2025-09-13 19:00 | 69.49 | 0 | 0 | 69.49 | 0 | 0 | 0 | 0 | 0
2025-09-13 20:00 | 66.36 | 0 | 0 | 66.36 | 0 | 0 | 0 | 0 | 0
2025-09-13 21:00 | 61.92 | 0 | 0 | 61.92 | 0 | 0 | 0 | 0 | 0
2025-09-13 22:00 | 58.68 | 0 | 0 | 58.68 | 0 | 0 | 0 | 0 | 0
2025-09-13 23:00 | 55.09 | 0 | 0 | 55.09 | 0 | 0 | 0 | 0 | 0
2025-09-14 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 0 | 0 | 0
2025-09-14 01:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0 | 0 | 0
2025-09-14 02:00 | 49.03 | 0 | 0 | 49.03 | 0 | 0 | 0 | 0 | 0
2025-09-14 03:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 0 | 0 | 0
2025-09-14 04:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 0 | 0 | 0
2025-09-14 05:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 0 | 0 | 0
2025-09-14 06:00 | 51.85 | 6.99 | 6.99 | 44.85 | 0 | 0 | 0 | 0 | 0
2025-09-14 07:00 | 54.61 | 66.16 | 54.61 | 0 | 0 | 0 | 0 | 11.55 | 0
2025-09-14 08:00 | 57.83 | 64.43 | 57.83 | 0 | 0 | 0 | 0 | 6.61 | 0
2025-09-14 09:00 | 61.85 | 112.56 | 61.85 | 0 | 0 | 0 | 0 | 50.71 | 0
2025-09-14 10:00 | 65.19 | 85.38 | 65.19 | 0 | 0 | 0 | 0 | 20.19 | 0
2025-09-14 11:00 | 68.88 | 47.66 | 47.66 | 21.22 | 0 | 0 | 0 | 0 | 0
2025-09-14 12:00 | 71.57 | 54 | 54 | 17.57 | 0 | 0 | 0 | 0 | 0
2025-09-14 13:00 | 73.94 | 37.34 | 37.34 | 36.61 | 0 | 0 | 0 | 0 | 0
2025-09-14 14:00 | 75.11 | 37.44 | 37.44 | 37.67 | 0 | 0 | 0 | 0 | 0
2025-09-14 15:00 | 75.39 | 35.46 | 35.46 | 39.93 | 0 | 0 | 0 | 0 | 0
2025-09-14 16:00 | 75.36 | 75.48 | 75.36 | 0 | 0 | 0 | 0 | 0.12 | 0
2025-09-14 17:00 | 73.86 | 43.27 | 43.27 | 30.59 | 0 | 0 | 0 | 0 | 0
2025-09-14 18:00 | 71.38 | 1 | 1 | 70.38 | 0 | 0 | 0 | 0 | 0
2025-09-14 19:00 | 68.98 | 0 | 0 | 68.98 | 0 | 0 | 0 | 0 | 0
2025-09-14 20:00 | 63.91 | 0 | 0 | 63.91 | 0 | 0 | 0 | 0 | 0
2025-09-14 21:00 | 61.5 | 0 | 0 | 61.5 | 0 | 0 | 0 | 0 | 0
2025-09-14 22:00 | 58.12 | 0 | 0 | 58.12 | 0 | 0 | 0 | 0 | 0
2025-09-14 23:00 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 0 | 0 | 0
2025-09-15 | 53.16 | 0 | 0 | 53.16 | 0 | 0 | 0 | 0 | 0
2025-09-15 01:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0 | 0 | 0
2025-09-15 02:00 | 49.98 | 0 | 0 | 49.98 | 0 | 0 | 0 | 0 | 0
2025-09-15 03:00 | 48.27 | 0 | 0 | 48.27 | 0 | 0 | 0 | 0 | 0
2025-09-15 04:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 0 | 0 | 0
2025-09-15 05:00 | 50.36 | 0 | 0 | 50.36 | 0 | 0 | 0 | 0 | 0
2025-09-15 06:00 | 52.22 | 13.78 | 13.78 | 38.44 | 0 | 0 | 0 | 0 | 0
2025-09-15 07:00 | 54.04 | 88.49 | 54.04 | 0 | 0 | 0 | 0 | 34.45 | 0
2025-09-15 08:00 | 57.95 | 108.03 | 57.95 | 0 | 0 | 0 | 0 | 50.08 | 0
2025-09-15 09:00 | 60.92 | 111.73 | 60.92 | 0 | 0 | 0 | 0 | 50.8 | 0
2025-09-15 10:00 | 64.01 | 107.36 | 64.01 | 0 | 0 | 0 | 0 | 43.34 | 0
2025-09-15 11:00 | 65.92 | 102.52 | 65.92 | 0 | 0 | 0 | 0 | 36.6 | 0
2025-09-15 12:00 | 68.36 | 100.36 | 68.36 | 0 | 0 | 0 | 0 | 32 | 0
2025-09-15 13:00 | 70.06 | 103.28 | 70.06 | 0 | 0 | 0 | 0 | 33.22 | 0
2025-09-15 14:00 | 71.97 | 105.83 | 71.97 | 0 | 0 | 0 | 0 | 33.86 | 0
2025-09-15 15:00 | 70.07 | 52.43 | 52.43 | 17.64 | 0 | 0 | 0 | 0 | 0
2025-09-15 16:00 | 70.65 | 8.44 | 8.44 | 62.21 | 0 | 0 | 0 | 0 | 0
2025-09-15 17:00 | 70.08 | 0.03 | 0.03 | 70.04 | 0 | 0 | 0 | 0 | 0
2025-09-15 18:00 | 67.84 | 0 | 0 | 67.84 | 0 | 0 | 0 | 0 | 0
2025-09-15 19:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 0 | 0 | 0
2025-09-15 20:00 | 63.42 | 0 | 0 | 63.42 | 0 | 0 | 0 | 0 | 0
2025-09-15 21:00 | 60.26 | 0 | 0 | 60.26 | 0 | 0 | 0 | 0 | 0
2025-09-15 22:00 | 57.66 | 0 | 0 | 57.66 | 0 | 0 | 0 | 0 | 0
2025-09-15 23:00 | 55.14 | 0 | 0 | 55.14 | 0 | 0 | 0 | 0 | 0
2025-09-16 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 0 | 0 | 0
2025-09-16 01:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0 | 0 | 0
2025-09-16 02:00 | 49.08 | 0 | 0 | 49.08 | 0 | 0 | 0 | 0 | 0
2025-09-16 03:00 | 48.75 | 0 | 0 | 48.75 | 0 | 0 | 0 | 0 | 0
2025-09-16 04:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 0 | 0 | 0
2025-09-16 05:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 0 | 0 | 0
2025-09-16 06:00 | 52.05 | 2.17 | 2.17 | 49.89 | 0 | 0 | 0 | 0 | 0
2025-09-16 07:00 | 55.38 | 1.7 | 1.7 | 53.69 | 0 | 0 | 0 | 0 | 0
2025-09-16 08:00 | 57.91 | 36.39 | 36.39 | 21.52 | 0 | 0 | 0 | 0 | 0
2025-09-16 09:00 | 61.26 | 32.29 | 32.29 | 28.97 | 0 | 0 | 0 | 0 | 0
2025-09-16 10:00 | 63.21 | 59.74 | 59.74 | 3.47 | 0 | 0 | 0 | 0 | 0
2025-09-16 11:00 | 66.34 | 58.98 | 58.98 | 7.36 | 0 | 0 | 0 | 0 | 0
2025-09-16 12:00 | 68.31 | 52.3 | 52.3 | 16.01 | 0 | 0 | 0 | 0 | 0
2025-09-16 13:00 | 70.41 | 58.51 | 58.51 | 11.9 | 0 | 0 | 0 | 0 | 0
2025-09-16 14:00 | 72.54 | 64.73 | 64.73 | 7.81 | 0 | 0 | 0 | 0 | 0
2025-09-16 15:00 | 73.05 | 107.2 | 73.05 | 0 | 0 | 0 | 0 | 34.16 | 0
2025-09-16 16:00 | 71.34 | 103.44 | 71.34 | 0 | 0 | 0 | 0 | 32.1 | 0
2025-09-16 17:00 | 70.53 | 59.11 | 59.11 | 11.42 | 0 | 0 | 0 | 0 | 0
2025-09-16 18:00 | 68.89 | 1.21 | 1.21 | 67.68 | 0 | 0 | 0 | 0 | 0
2025-09-16 19:00 | 66.82 | 0 | 0 | 66.82 | 0 | 0 | 0 | 0 | 0
2025-09-16 20:00 | 62.83 | 0 | 0 | 62.83 | 0 | 0 | 0 | 0 | 0
2025-09-16 21:00 | 59.87 | 0 | 0 | 59.87 | 0 | 0 | 0 | 0 | 0
2025-09-16 22:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 0 | 0 | 0
2025-09-16 23:00 | 53.78 | 0 | 0 | 53.78 | 0 | 0 | 0 | 0 | 0
2025-09-17 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0 | 0 | 0
2025-09-17 01:00 | 50.31 | 0 | 0 | 50.31 | 0 | 0 | 0 | 0 | 0
2025-09-17 02:00 | 49.27 | 0 | 0 | 49.27 | 0 | 0 | 0 | 0 | 0
2025-09-17 03:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0 | 0 | 0
2025-09-17 04:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 0 | 0 | 0
2025-09-17 05:00 | 50.66 | 0 | 0 | 50.66 | 0 | 0 | 0 | 0 | 0
2025-09-17 06:00 | 52.18 | 2 | 2 | 50.18 | 0 | 0 | 0 | 0 | 0
2025-09-17 07:00 | 53.95 | 79.82 | 53.95 | 0 | 0 | 0 | 0 | 25.86 | 0
2025-09-17 08:00 | 56.74 | 55.29 | 55.29 | 1.45 | 0 | 0 | 0 | 0 | 0
2025-09-17 09:00 | 59.35 | 19.2 | 19.2 | 40.15 | 0 | 0 | 0 | 0 | 0
2025-09-17 10:00 | 62.25 | 56.33 | 56.33 | 5.92 | 0 | 0 | 0 | 0 | 0
2025-09-17 11:00 | 63.69 | 20.16 | 20.16 | 43.53 | 0 | 0 | 0 | 0 | 0
2025-09-17 12:00 | 65.4 | 27.89 | 27.89 | 37.51 | 0 | 0 | 0 | 0 | 0
2025-09-17 13:00 | 65.56 | 37.07 | 37.07 | 28.49 | 0 | 0 | 0 | 0 | 0
2025-09-17 14:00 | 66.23 | 85.52 | 66.23 | 0 | 0 | 0 | 0 | 19.29 | 0
2025-09-17 15:00 | 66.58 | 65.97 | 65.97 | 0.61 | 0 | 0 | 0 | 0 | 0
2025-09-17 16:00 | 66.42 | 26.07 | 26.07 | 40.35 | 0 | 0 | 0 | 0 | 0
2025-09-17 17:00 | 65.36 | 9.98 | 9.98 | 55.38 | 0 | 0 | 0 | 0 | 0
2025-09-17 18:00 | 65.43 | 0 | 0 | 65.43 | 0 | 0 | 0 | 0 | 0
2025-09-17 19:00 | 63.74 | 0 | 0 | 63.74 | 0 | 0 | 0 | 0 | 0
2025-09-17 20:00 | 61.24 | 0 | 0 | 61.24 | 0 | 0 | 0 | 0 | 0
2025-09-17 21:00 | 59.48 | 0 | 0 | 59.48 | 0 | 0 | 0 | 0 | 0
2025-09-17 22:00 | 56.84 | 0 | 0 | 56.84 | 0 | 0 | 0 | 0 | 0
2025-09-17 23:00 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 0 | 0 | 0
2025-09-18 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 0 | 0 | 0
2025-09-18 01:00 | 50.07 | 0 | 0 | 50.07 | 0 | 0 | 0 | 0 | 0
2025-09-18 02:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 0 | 0 | 0
2025-09-18 03:00 | 48.86 | 0 | 0 | 48.86 | 0 | 0 | 0 | 0 | 0
2025-09-18 04:00 | 48.64 | 0 | 0 | 48.64 | 0 | 0 | 0 | 0 | 0
2025-09-18 05:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 0 | 0 | 0
2025-09-18 06:00 | 51.48 | 0.68 | 0.68 | 50.8 | 0 | 0 | 0 | 0 | 0
2025-09-18 07:00 | 54.41 | 3.53 | 3.53 | 50.88 | 0 | 0 | 0 | 0 | 0
2025-09-18 08:00 | 57.27 | 17.23 | 17.23 | 40.05 | 0 | 0 | 0 | 0 | 0
2025-09-18 09:00 | 61.05 | 65.54 | 61.05 | 0 | 0 | 0 | 0 | 4.49 | 0
2025-09-18 10:00 | 63.43 | 51.69 | 51.69 | 11.75 | 0 | 0 | 0 | 0 | 0
2025-09-18 11:00 | 65.89 | 81.04 | 65.89 | 0 | 0 | 0 | 0 | 15.16 | 0
2025-09-18 12:00 | 68.13 | 27.86 | 27.86 | 40.27 | 0 | 0 | 0 | 0 | 0
2025-09-18 13:00 | 70.45 | 20.76 | 20.76 | 49.68 | 0 | 0 | 0 | 0 | 0
2025-09-18 14:00 | 70.69 | 38.88 | 38.88 | 31.81 | 0 | 0 | 0 | 0 | 0
2025-09-18 15:00 | 71.29 | 3.41 | 3.41 | 67.88 | 0 | 0 | 0 | 0 | 0
2025-09-18 16:00 | 70.44 | 14.17 | 14.17 | 56.28 | 0 | 0 | 0 | 0 | 0
2025-09-18 17:00 | 70.6 | 11.46 | 11.46 | 59.14 | 0 | 0 | 0 | 0 | 0
2025-09-18 18:00 | 68.34 | 0 | 0 | 68.34 | 0 | 0 | 0 | 0 | 0
2025-09-18 19:00 | 65.49 | 0 | 0 | 65.49 | 0 | 0 | 0 | 0 | 0
2025-09-18 20:00 | 63.09 | 0 | 0 | 63.09 | 0 | 0 | 0 | 0 | 0
2025-09-18 21:00 | 60.46 | 0 | 0 | 60.46 | 0 | 0 | 0 | 0 | 0
2025-09-18 22:00 | 57.11 | 0 | 0 | 57.11 | 0 | 0 | 0 | 0 | 0
2025-09-18 23:00 | 54.18 | 0 | 0 | 54.18 | 0 | 0 | 0 | 0 | 0
2025-09-19 | 51.56 | 0 | 0 | 51.56 | 0 | 0 | 0 | 0 | 0
2025-09-19 01:00 | 50.19 | 0 | 0 | 50.19 | 0 | 0 | 0 | 0 | 0
2025-09-19 02:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 0 | 0 | 0
2025-09-19 03:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 0 | 0 | 0
2025-09-19 04:00 | 48.18 | 0 | 0 | 48.18 | 0 | 0 | 0 | 0 | 0
2025-09-19 05:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 0 | 0 | 0
2025-09-19 06:00 | 51.8 | 4.81 | 4.81 | 46.98 | 0 | 0 | 0 | 0 | 0
2025-09-19 07:00 | 54.13 | 69.84 | 54.13 | 0 | 0 | 0 | 0 | 15.71 | 0
2025-09-19 08:00 | 57.16 | 80.36 | 57.16 | 0 | 0 | 0 | 0 | 23.19 | 0
2025-09-19 09:00 | 60.37 | 84.17 | 60.37 | 0 | 0 | 0 | 0 | 23.8 | 0
2025-09-19 10:00 | 63.25 | 93.04 | 63.25 | 0 | 0 | 0 | 0 | 29.8 | 0
2025-09-19 11:00 | 65.84 | 94.36 | 65.84 | 0 | 0 | 0 | 0 | 28.53 | 0
2025-09-19 12:00 | 67.71 | 77.63 | 67.71 | 0 | 0 | 0 | 0 | 9.93 | 0
2025-09-19 13:00 | 69.26 | 76.04 | 69.26 | 0 | 0 | 0 | 0 | 6.77 | 0
2025-09-19 14:00 | 70.1 | 62.65 | 62.65 | 7.45 | 0 | 0 | 0 | 0 | 0
2025-09-19 15:00 | 70.69 | 52.74 | 52.74 | 17.95 | 0 | 0 | 0 | 0 | 0
2025-09-19 16:00 | 70.63 | 31.13 | 31.13 | 39.5 | 0 | 0 | 0 | 0 | 0
2025-09-19 17:00 | 69.15 | 3.71 | 3.71 | 65.44 | 0 | 0 | 0 | 0 | 0
2025-09-19 18:00 | 67.87 | 0 | 0 | 67.87 | 0 | 0 | 0 | 0 | 0
2025-09-19 19:00 | 65.08 | 0 | 0 | 65.08 | 0 | 0 | 0 | 0 | 0
2025-09-19 20:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 0 | 0 | 0
2025-09-19 21:00 | 60.41 | 0 | 0 | 60.41 | 0 | 0 | 0 | 0 | 0
2025-09-19 22:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 0 | 0 | 0
2025-09-19 23:00 | 53.87 | 0 | 0 | 53.87 | 0 | 0 | 0 | 0 | 0
2025-09-20 | 51.26 | 0 | 0 | 51.26 | 0 | 0 | 0 | 0 | 0
2025-09-20 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 0 | 0 | 0
2025-09-20 02:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0 | 0 | 0
2025-09-20 03:00 | 48.14 | 0 | 0 | 48.14 | 0 | 0 | 0 | 0 | 0
2025-09-20 04:00 | 48.63 | 0 | 0 | 48.63 | 0 | 0 | 0 | 0 | 0
2025-09-20 05:00 | 50.45 | 0 | 0 | 50.45 | 0 | 0 | 0 | 0 | 0
2025-09-20 06:00 | 50.9 | 1.89 | 1.89 | 49.01 | 0 | 0 | 0 | 0 | 0
2025-09-20 07:00 | 55.26 | 37.72 | 37.72 | 17.54 | 0 | 0 | 0 | 0 | 0
2025-09-20 08:00 | 58.41 | 52.02 | 52.02 | 6.39 | 0 | 0 | 0 | 0 | 0
2025-09-20 09:00 | 58.99 | 56.89 | 56.89 | 2.1 | 0 | 0 | 0 | 0 | 0
2025-09-20 10:00 | 63.48 | 50.64 | 50.64 | 12.85 | 0 | 0 | 0 | 0 | 0
2025-09-20 11:00 | 66.17 | 31.02 | 31.02 | 35.15 | 0 | 0 | 0 | 0 | 0
2025-09-20 12:00 | 69 | 31.14 | 31.14 | 37.86 | 0 | 0 | 0 | 0 | 0
2025-09-20 13:00 | 70.93 | 39.58 | 39.58 | 31.35 | 0 | 0 | 0 | 0 | 0
2025-09-20 14:00 | 72.82 | 24.83 | 24.83 | 47.98 | 0 | 0 | 0 | 0 | 0
2025-09-20 15:00 | 72.79 | 20.76 | 20.76 | 52.02 | 0 | 0 | 0 | 0 | 0
2025-09-20 16:00 | 71.95 | 7.37 | 7.37 | 64.58 | 0 | 0 | 0 | 0 | 0
2025-09-20 17:00 | 71.05 | 0.02 | 0.02 | 71.03 | 0 | 0 | 0 | 0 | 0
2025-09-20 18:00 | 69.39 | 0 | 0 | 69.39 | 0 | 0 | 0 | 0 | 0
2025-09-20 19:00 | 65.94 | 0 | 0 | 65.94 | 0 | 0 | 0 | 0 | 0
2025-09-20 20:00 | 62.71 | 0 | 0 | 62.71 | 0 | 0 | 0 | 0 | 0
2025-09-20 21:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 0 | 0 | 0
2025-09-20 22:00 | 56.87 | 0 | 0 | 56.87 | 0 | 0 | 0 | 0 | 0
2025-09-20 23:00 | 54.21 | 0 | 0 | 54.21 | 0 | 0 | 0 | 0 | 0
2025-09-21 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-09-21 01:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 0 | 0 | 0
2025-09-21 02:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0 | 0 | 0
2025-09-21 03:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 0 | 0 | 0
2025-09-21 04:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0 | 0 | 0
2025-09-21 05:00 | 49.09 | 0 | 0 | 49.09 | 0 | 0 | 0 | 0 | 0
2025-09-21 06:00 | 51.4 | 4.9 | 4.9 | 46.5 | 0 | 0 | 0 | 0 | 0
2025-09-21 07:00 | 53.79 | 84.62 | 53.79 | 0 | 0 | 0 | 0 | 30.83 | 0
2025-09-21 08:00 | 55.71 | 108.55 | 55.71 | 0 | 0 | 0 | 0 | 52.84 | 0
2025-09-21 09:00 | 59.74 | 111.65 | 59.74 | 0 | 0 | 0 | 0 | 51.91 | 0
2025-09-21 10:00 | 61.47 | 86.61 | 61.47 | 0 | 0 | 0 | 0 | 25.14 | 0
2025-09-21 11:00 | 65.19 | 86.7 | 65.19 | 0 | 0 | 0 | 0 | 21.51 | 0
2025-09-21 12:00 | 67.38 | 78.3 | 67.38 | 0 | 0 | 0 | 0 | 10.92 | 0
2025-09-21 13:00 | 67.87 | 74.34 | 67.87 | 0 | 0 | 0 | 0 | 6.46 | 0
2025-09-21 14:00 | 69.16 | 38.15 | 38.15 | 31.01 | 0 | 0 | 0 | 0 | 0
2025-09-21 15:00 | 68.64 | 18.71 | 18.71 | 49.94 | 0 | 0 | 0 | 0 | 0
2025-09-21 16:00 | 69.25 | 13.4 | 13.4 | 55.86 | 0 | 0 | 0 | 0 | 0
2025-09-21 17:00 | 67.75 | 0 | 0 | 67.75 | 0 | 0 | 0 | 0 | 0
2025-09-21 18:00 | 65.93 | 0 | 0 | 65.93 | 0 | 0 | 0 | 0 | 0
2025-09-21 19:00 | 64.3 | 0 | 0 | 64.3 | 0 | 0 | 0 | 0 | 0
2025-09-21 20:00 | 61.78 | 0 | 0 | 61.78 | 0 | 0 | 0 | 0 | 0
2025-09-21 21:00 | 59.17 | 0 | 0 | 59.17 | 0 | 0 | 0 | 0 | 0
2025-09-21 22:00 | 57.04 | 0 | 0 | 57.04 | 0 | 0 | 0 | 0 | 0
2025-09-21 23:00 | 53.53 | 0 | 0 | 53.53 | 0 | 0 | 0 | 0 | 0
2025-09-22 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 0 | 0 | 0
2025-09-22 01:00 | 49.02 | 0 | 0 | 49.02 | 0 | 0 | 0 | 0 | 0
2025-09-22 02:00 | 49.32 | 0 | 0 | 49.32 | 0 | 0 | 0 | 0 | 0
2025-09-22 03:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 0 | 0 | 0
2025-09-22 04:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 0 | 0 | 0
2025-09-22 05:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 0 | 0 | 0
2025-09-22 06:00 | 51.39 | 0.08 | 0.08 | 51.31 | 0 | 0 | 0 | 0 | 0
2025-09-22 07:00 | 54.45 | 1.67 | 1.67 | 52.78 | 0 | 0 | 0 | 0 | 0
2025-09-22 08:00 | 57.74 | 10.92 | 10.92 | 46.82 | 0 | 0 | 0 | 0 | 0
2025-09-22 09:00 | 60.81 | 13.96 | 13.96 | 46.85 | 0 | 0 | 0 | 0 | 0
2025-09-22 10:00 | 63.31 | 45.95 | 45.95 | 17.36 | 0 | 0 | 0 | 0 | 0
2025-09-22 11:00 | 66.73 | 68.94 | 66.73 | 0 | 0 | 0 | 0 | 2.22 | 0
2025-09-22 12:00 | 68.97 | 80.77 | 68.97 | 0 | 0 | 0 | 0 | 11.8 | 0
2025-09-22 13:00 | 70.99 | 98.68 | 70.99 | 0 | 0 | 0 | 0 | 27.68 | 0
2025-09-22 14:00 | 72.26 | 56.19 | 56.19 | 16.07 | 0 | 0 | 0 | 0 | 0
2025-09-22 15:00 | 73.08 | 37.66 | 37.66 | 35.43 | 0 | 0 | 0 | 0 | 0
2025-09-22 16:00 | 72.96 | 27.06 | 27.06 | 45.9 | 0 | 0 | 0 | 0 | 0
2025-09-22 17:00 | 70.53 | 19.96 | 19.96 | 50.58 | 0 | 0 | 0 | 0 | 0
2025-09-22 18:00 | 69.34 | 0 | 0 | 69.34 | 0 | 0 | 0 | 0 | 0
2025-09-22 19:00 | 67.39 | 0 | 0 | 67.39 | 0 | 0 | 0 | 0 | 0
2025-09-22 20:00 | 64.07 | 0 | 0 | 64.07 | 0 | 0 | 0 | 0 | 0
2025-09-22 21:00 | 59.92 | 0 | 0 | 59.92 | 0 | 0 | 0 | 0 | 0
2025-09-22 22:00 | 56.29 | 0 | 0 | 56.29 | 0 | 0 | 0 | 0 | 0
2025-09-22 23:00 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 0 | 0 | 0
2025-09-23 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 0 | 0 | 0
2025-09-23 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 0 | 0 | 0
2025-09-23 02:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 0 | 0 | 0
2025-09-23 03:00 | 48.92 | 0 | 0 | 48.92 | 0 | 0 | 0 | 0 | 0
2025-09-23 04:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0 | 0 | 0
2025-09-23 05:00 | 50.03 | 0 | 0 | 50.03 | 0 | 0 | 0 | 0 | 0
2025-09-23 06:00 | 51.42 | 3.23 | 3.23 | 48.2 | 0 | 0 | 0 | 0 | 0
2025-09-23 07:00 | 53.87 | 37.52 | 37.52 | 16.35 | 0 | 0 | 0 | 0 | 0
2025-09-23 08:00 | 56.44 | 70.44 | 56.44 | 0 | 0 | 0 | 0 | 13.99 | 0
2025-09-23 09:00 | 60.88 | 86.04 | 60.88 | 0 | 0 | 0 | 0 | 25.16 | 0
2025-09-23 10:00 | 64.52 | 89.14 | 64.52 | 0 | 0 | 0 | 0 | 24.62 | 0
2025-09-23 11:00 | 68.55 | 92.03 | 68.55 | 0 | 0 | 0 | 0 | 23.48 | 0
2025-09-23 12:00 | 71.25 | 90.28 | 71.25 | 0 | 0 | 0 | 0 | 19.03 | 0
2025-09-23 13:00 | 72.88 | 87.62 | 72.88 | 0 | 0 | 0 | 0 | 14.74 | 0
2025-09-23 14:00 | 74.23 | 89.98 | 74.23 | 0 | 0 | 0 | 0 | 15.75 | 0
2025-09-23 15:00 | 74.58 | 82.45 | 74.58 | 0 | 0 | 0 | 0 | 7.87 | 0
2025-09-23 16:00 | 75.46 | 66.38 | 66.38 | 9.08 | 0 | 0 | 0 | 0 | 0
2025-09-23 17:00 | 72.78 | 18.77 | 18.77 | 54.02 | 0 | 0 | 0 | 0 | 0
2025-09-23 18:00 | 71.49 | 0 | 0 | 71.49 | 0 | 0 | 0 | 0 | 0
2025-09-23 19:00 | 67.92 | 0 | 0 | 67.92 | 0 | 0 | 0 | 0 | 0
2025-09-23 20:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 0 | 0 | 0
2025-09-23 21:00 | 60.43 | 0 | 0 | 60.43 | 0 | 0 | 0 | 0 | 0
2025-09-23 22:00 | 57.46 | 0 | 0 | 57.46 | 0 | 0 | 0 | 0 | 0
2025-09-23 23:00 | 54.03 | 0 | 0 | 54.03 | 0 | 0 | 0 | 0 | 0
2025-09-24 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0 | 0 | 0
2025-09-24 01:00 | 49.78 | 0 | 0 | 49.78 | 0 | 0 | 0 | 0 | 0
2025-09-24 02:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 0 | 0 | 0
2025-09-24 03:00 | 47.5 | 0 | 0 | 47.5 | 0 | 0 | 0 | 0 | 0
2025-09-24 04:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 0 | 0 | 0
2025-09-24 05:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 0 | 0 | 0
2025-09-24 06:00 | 51.51 | 1.68 | 1.68 | 49.83 | 0 | 0 | 0 | 0 | 0
2025-09-24 07:00 | 53.43 | 24.19 | 24.19 | 29.24 | 0 | 0 | 0 | 0 | 0
2025-09-24 08:00 | 55.86 | 59.81 | 55.86 | 0 | 0 | 0 | 0 | 3.95 | 0
2025-09-24 09:00 | 60.37 | 87.49 | 60.37 | 0 | 0 | 0 | 0 | 27.12 | 0
2025-09-24 10:00 | 63.33 | 95.03 | 63.33 | 0 | 0 | 0 | 0 | 31.7 | 0
2025-09-24 11:00 | 65.87 | 81.53 | 65.87 | 0 | 0 | 0 | 0 | 15.66 | 0
2025-09-24 12:00 | 67.71 | 78.54 | 67.71 | 0 | 0 | 0 | 0 | 10.83 | 0
2025-09-24 13:00 | 69.66 | 91.04 | 69.66 | 0 | 0 | 0 | 0 | 21.38 | 0
2025-09-24 14:00 | 71.71 | 92.12 | 71.71 | 0 | 0 | 0 | 0 | 20.41 | 0
2025-09-24 15:00 | 71.25 | 68.22 | 68.22 | 3.03 | 0 | 0 | 0 | 0 | 0
2025-09-24 16:00 | 70.7 | 48.26 | 48.26 | 22.44 | 0 | 0 | 0 | 0 | 0
2025-09-24 17:00 | 70.75 | 11.91 | 11.91 | 58.84 | 0 | 0 | 0 | 0 | 0
2025-09-24 18:00 | 67.88 | 0 | 0 | 67.88 | 0 | 0 | 0 | 0 | 0
2025-09-24 19:00 | 66.31 | 0 | 0 | 66.31 | 0 | 0 | 0 | 0 | 0
2025-09-24 20:00 | 61.86 | 0 | 0 | 61.86 | 0 | 0 | 0 | 0 | 0
2025-09-24 21:00 | 59.76 | 0 | 0 | 59.76 | 0 | 0 | 0 | 0 | 0
2025-09-24 22:00 | 57.5 | 0 | 0 | 57.5 | 0 | 0 | 0 | 0 | 0
2025-09-24 23:00 | 53.68 | 0 | 0 | 53.68 | 0 | 0 | 0 | 0 | 0
2025-09-25 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 0 | 0 | 0
2025-09-25 01:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 0 | 0 | 0
2025-09-25 02:00 | 48.71 | 0 | 0 | 48.71 | 0 | 0 | 0 | 0 | 0
2025-09-25 03:00 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 0 | 0 | 0
2025-09-25 04:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 0 | 0 | 0
2025-09-25 05:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 0 | 0 | 0
2025-09-25 06:00 | 51.92 | 1.95 | 1.95 | 49.98 | 0 | 0 | 0 | 0 | 0
2025-09-25 07:00 | 54.14 | 28.47 | 28.47 | 25.67 | 0 | 0 | 0 | 0 | 0
2025-09-25 08:00 | 56.39 | 43.44 | 43.44 | 12.95 | 0 | 0 | 0 | 0 | 0
2025-09-25 09:00 | 58.93 | 57.82 | 57.82 | 1.11 | 0 | 0 | 0 | 0 | 0
2025-09-25 10:00 | 63.43 | 77.58 | 63.43 | 0 | 0 | 0 | 0 | 14.15 | 0
2025-09-25 11:00 | 65.46 | 76.12 | 65.46 | 0 | 0 | 0 | 0 | 10.66 | 0
2025-09-25 12:00 | 67.68 | 68.38 | 67.68 | 0 | 0 | 0 | 0 | 0.7 | 0
2025-09-25 13:00 | 69.36 | 82.01 | 69.36 | 0 | 0 | 0 | 0 | 12.64 | 0
2025-09-25 14:00 | 71.19 | 98.44 | 71.19 | 0 | 0 | 0 | 0 | 27.25 | 0
2025-09-25 15:00 | 71.22 | 96.93 | 71.22 | 0 | 0 | 0 | 0 | 25.71 | 0
2025-09-25 16:00 | 71.2 | 80.92 | 71.2 | 0 | 0 | 0 | 0 | 9.72 | 0
2025-09-25 17:00 | 70.61 | 27.44 | 27.44 | 43.18 | 0 | 0 | 0 | 0 | 0
2025-09-25 18:00 | 68.04 | 0 | 0 | 68.04 | 0 | 0 | 0 | 0 | 0
2025-09-25 19:00 | 65.82 | 0 | 0 | 65.82 | 0 | 0 | 0 | 0 | 0
2025-09-25 20:00 | 62.3 | 0 | 0 | 62.3 | 0 | 0 | 0 | 0 | 0
2025-09-25 21:00 | 59.54 | 0 | 0 | 59.54 | 0 | 0 | 0 | 0 | 0
2025-09-25 22:00 | 57.37 | 0 | 0 | 57.37 | 0 | 0 | 0 | 0 | 0
2025-09-25 23:00 | 53.38 | 0 | 0 | 53.38 | 0 | 0 | 0 | 0 | 0
2025-09-26 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 0 | 0 | 0
2025-09-26 01:00 | 48.4 | 0 | 0 | 48.4 | 0 | 0 | 0 | 0 | 0
2025-09-26 02:00 | 48.82 | 0 | 0 | 48.82 | 0 | 0 | 0 | 0 | 0
2025-09-26 03:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0 | 0 | 0
2025-09-26 04:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0 | 0 | 0
2025-09-26 05:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 0 | 0 | 0
2025-09-26 06:00 | 51.29 | 0.32 | 0.32 | 50.97 | 0 | 0 | 0 | 0 | 0
2025-09-26 07:00 | 53.66 | 7.83 | 7.83 | 45.83 | 0 | 0 | 0 | 0 | 0
2025-09-26 08:00 | 55.84 | 34.77 | 34.77 | 21.07 | 0 | 0 | 0 | 0 | 0
2025-09-26 09:00 | 59.55 | 43.82 | 43.82 | 15.73 | 0 | 0 | 0 | 0 | 0
2025-09-26 10:00 | 61.58 | 48.14 | 48.14 | 13.43 | 0 | 0 | 0 | 0 | 0
2025-09-26 11:00 | 65.1 | 48.29 | 48.29 | 16.81 | 0 | 0 | 0 | 0 | 0
2025-09-26 12:00 | 66.89 | 55.01 | 55.01 | 11.88 | 0 | 0 | 0 | 0 | 0
2025-09-26 13:00 | 69.09 | 35.83 | 35.83 | 33.26 | 0 | 0 | 0 | 0 | 0
2025-09-26 14:00 | 69.83 | 22.12 | 22.12 | 47.71 | 0 | 0 | 0 | 0 | 0
2025-09-26 15:00 | 70.48 | 2.43 | 2.43 | 68.04 | 0 | 0 | 0 | 0 | 0
2025-09-26 16:00 | 69.52 | 1.01 | 1.01 | 68.51 | 0 | 0 | 0 | 0 | 0
2025-09-26 17:00 | 69.04 | 0.42 | 0.42 | 68.62 | 0 | 0 | 0 | 0 | 0
2025-09-26 18:00 | 67.11 | 0 | 0 | 67.11 | 0 | 0 | 0 | 0 | 0
2025-09-26 19:00 | 64.45 | 0 | 0 | 64.45 | 0 | 0 | 0 | 0 | 0
2025-09-26 20:00 | 61.93 | 0 | 0 | 61.93 | 0 | 0 | 0 | 0 | 0
2025-09-26 21:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 0 | 0 | 0
2025-09-26 22:00 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 0 | 0 | 0
2025-09-26 23:00 | 53.26 | 0 | 0 | 53.26 | 0 | 0 | 0 | 0 | 0
2025-09-27 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 0 | 0 | 0
2025-09-27 01:00 | 50.23 | 0 | 0 | 50.23 | 0 | 0 | 0 | 0 | 0
2025-09-27 02:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 0 | 0 | 0
2025-09-27 03:00 | 47.69 | 0 | 0 | 47.69 | 0 | 0 | 0 | 0 | 0
2025-09-27 04:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 0 | 0 | 0
2025-09-27 05:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0 | 0 | 0
2025-09-27 06:00 | 49.56 | 0.5 | 0.5 | 49.06 | 0 | 0 | 0 | 0 | 0
2025-09-27 07:00 | 52.96 | 9.5 | 9.5 | 43.46 | 0 | 0 | 0 | 0 | 0
2025-09-27 08:00 | 55.17 | 13.31 | 13.31 | 41.85 | 0 | 0 | 0 | 0 | 0
2025-09-27 09:00 | 58.64 | 31.85 | 31.85 | 26.79 | 0 | 0 | 0 | 0 | 0
2025-09-27 10:00 | 61.76 | 28.66 | 28.66 | 33.1 | 0 | 0 | 0 | 0 | 0
2025-09-27 11:00 | 64.82 | 22.67 | 22.67 | 42.15 | 0 | 0 | 0 | 0 | 0
2025-09-27 12:00 | 66.11 | 55.31 | 55.31 | 10.8 | 0 | 0 | 0 | 0 | 0
2025-09-27 13:00 | 68.65 | 76.42 | 68.65 | 0 | 0 | 0 | 0 | 7.77 | 0
2025-09-27 14:00 | 69.58 | 83.08 | 69.58 | 0 | 0 | 0 | 0 | 13.5 | 0
2025-09-27 15:00 | 70.13 | 87.86 | 70.13 | 0 | 0 | 0 | 0 | 17.73 | 0
2025-09-27 16:00 | 69.31 | 83.01 | 69.31 | 0 | 0 | 0 | 0 | 13.7 | 0
2025-09-27 17:00 | 69.15 | 26.07 | 26.07 | 43.08 | 0 | 0 | 0 | 0 | 0
2025-09-27 18:00 | 66.62 | 0 | 0 | 66.62 | 0 | 0 | 0 | 0 | 0
2025-09-27 19:00 | 65.24 | 0 | 0 | 65.24 | 0 | 0 | 0 | 0 | 0
2025-09-27 20:00 | 61.26 | 0 | 0 | 61.26 | 0 | 0 | 0 | 0 | 0
2025-09-27 21:00 | 59.13 | 0 | 0 | 59.13 | 0 | 0 | 0 | 0 | 0
2025-09-27 22:00 | 55.83 | 0 | 0 | 55.83 | 0 | 0 | 0 | 0 | 0
2025-09-27 23:00 | 52.99 | 0 | 0 | 52.99 | 0 | 0 | 0 | 0 | 0
2025-09-28 | 50.95 | 0 | 0 | 50.95 | 0 | 0 | 0 | 0 | 0
2025-09-28 01:00 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 0 | 0 | 0
2025-09-28 02:00 | 46.49 | 0 | 0 | 46.49 | 0 | 0 | 0 | 0 | 0
2025-09-28 03:00 | 45.91 | 0 | 0 | 45.91 | 0 | 0 | 0 | 0 | 0
2025-09-28 04:00 | 48.46 | 0 | 0 | 48.46 | 0 | 0 | 0 | 0 | 0
2025-09-28 05:00 | 49.53 | 0 | 0 | 49.53 | 0 | 0 | 0 | 0 | 0
2025-09-28 06:00 | 51.58 | 0.81 | 0.81 | 50.77 | 0 | 0 | 0 | 0 | 0
2025-09-28 07:00 | 52.81 | 0.03 | 0.03 | 52.78 | 0 | 0 | 0 | 0 | 0
2025-09-28 08:00 | 54.64 | 32.07 | 32.07 | 22.57 | 0 | 0 | 0 | 0 | 0
2025-09-28 09:00 | 57.63 | 19.01 | 19.01 | 38.62 | 0 | 0 | 0 | 0 | 0
2025-09-28 10:00 | 60.3 | 37.36 | 37.36 | 22.94 | 0 | 0 | 0 | 0 | 0
2025-09-28 11:00 | 61.99 | 52.84 | 52.84 | 9.14 | 0 | 0 | 0 | 0 | 0
2025-09-28 12:00 | 65.14 | 45.17 | 45.17 | 19.96 | 0 | 0 | 0 | 0 | 0
2025-09-28 13:00 | 66.79 | 91.9 | 66.79 | 0 | 0 | 0 | 0 | 25.12 | 0
2025-09-28 14:00 | 66.74 | 83.23 | 66.74 | 0 | 0 | 0 | 0 | 16.49 | 0
2025-09-28 15:00 | 66.78 | 32.84 | 32.84 | 33.94 | 0 | 0 | 0 | 0 | 0
2025-09-28 16:00 | 65.86 | 58.63 | 58.63 | 7.23 | 0 | 0 | 0 | 0 | 0
2025-09-28 17:00 | 66.44 | 20.18 | 20.18 | 46.26 | 0 | 0 | 0 | 0 | 0
2025-09-28 18:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 0 | 0 | 0
2025-09-28 19:00 | 62.35 | 0 | 0 | 62.35 | 0 | 0 | 0 | 0 | 0
2025-09-28 20:00 | 60.53 | 0 | 0 | 60.53 | 0 | 0 | 0 | 0 | 0
2025-09-28 21:00 | 57.54 | 0 | 0 | 57.54 | 0 | 0 | 0 | 0 | 0
2025-09-28 22:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 0 | 0 | 0
2025-09-28 23:00 | 52.1 | 0 | 0 | 52.1 | 0 | 0 | 0 | 0 | 0
2025-09-29 | 51.13 | 0 | 0 | 51.13 | 0 | 0 | 0 | 0 | 0
2025-09-29 01:00 | 48.76 | 0 | 0 | 48.76 | 0 | 0 | 0 | 0 | 0
2025-09-29 02:00 | 48.28 | 0 | 0 | 48.28 | 0 | 0 | 0 | 0 | 0
2025-09-29 03:00 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 0 | 0 | 0
2025-09-29 04:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0 | 0 | 0
2025-09-29 05:00 | 48.2 | 0 | 0 | 48.2 | 0 | 0 | 0 | 0 | 0
2025-09-29 06:00 | 50.96 | 0.92 | 0.92 | 50.04 | 0 | 0 | 0 | 0 | 0
2025-09-29 07:00 | 52.48 | 50.94 | 50.94 | 1.54 | 0 | 0 | 0 | 0 | 0
2025-09-29 08:00 | 55.43 | 58.8 | 55.43 | 0 | 0 | 0 | 0 | 3.37 | 0
2025-09-29 09:00 | 58.67 | 67.58 | 58.67 | 0 | 0 | 0 | 0 | 8.91 | 0
2025-09-29 10:00 | 61.77 | 70.38 | 61.77 | 0 | 0 | 0 | 0 | 8.61 | 0
2025-09-29 11:00 | 63.72 | 56.93 | 56.93 | 6.8 | 0 | 0 | 0 | 0 | 0
2025-09-29 12:00 | 66.96 | 50.46 | 50.46 | 16.5 | 0 | 0 | 0 | 0 | 0
2025-09-29 13:00 | 69.4 | 55.09 | 55.09 | 14.31 | 0 | 0 | 0 | 0 | 0
2025-09-29 14:00 | 70.04 | 42.32 | 42.32 | 27.72 | 0 | 0 | 0 | 0 | 0
2025-09-29 15:00 | 70.53 | 44.02 | 44.02 | 26.51 | 0 | 0 | 0 | 0 | 0
2025-09-29 16:00 | 70.31 | 70.74 | 70.31 | 0 | 0 | 0 | 0 | 0.43 | 0
2025-09-29 17:00 | 68.94 | 23.15 | 23.15 | 45.79 | 0 | 0 | 0 | 0 | 0
2025-09-29 18:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 0 | 0 | 0
2025-09-29 19:00 | 64.56 | 0 | 0 | 64.56 | 0 | 0 | 0 | 0 | 0
2025-09-29 20:00 | 62.21 | 0 | 0 | 62.21 | 0 | 0 | 0 | 0 | 0
2025-09-29 21:00 | 58.14 | 0 | 0 | 58.14 | 0 | 0 | 0 | 0 | 0
2025-09-29 22:00 | 55.49 | 0 | 0 | 55.49 | 0 | 0 | 0 | 0 | 0
2025-09-29 23:00 | 52.23 | 0 | 0 | 52.23 | 0 | 0 | 0 | 0 | 0
2025-09-30 | 50.88 | 0 | 0 | 50.88 | 0 | 0 | 0 | 0 | 0
2025-09-30 01:00 | 48.63 | 0 | 0 | 48.63 | 0 | 0 | 0 | 0 | 0
2025-09-30 02:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 0 | 0 | 0
2025-09-30 03:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 0 | 0 | 0
2025-09-30 04:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 0 | 0 | 0
2025-09-30 05:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0 | 0 | 0
2025-09-30 06:00 | 49.68 | 1.18 | 1.18 | 48.49 | 0 | 0 | 0 | 0 | 0
2025-09-30 07:00 | 52.12 | 49.43 | 49.43 | 2.69 | 0 | 0 | 0 | 0 | 0
2025-09-30 08:00 | 55.95 | 64.59 | 55.95 | 0 | 0 | 0 | 0 | 8.64 | 0
2025-09-30 09:00 | 57.69 | 82.71 | 57.69 | 0 | 0 | 0 | 0 | 25.02 | 0
2025-09-30 10:00 | 61.07 | 85.65 | 61.07 | 0 | 0 | 0 | 0 | 24.58 | 0
2025-09-30 11:00 | 62.99 | 80.61 | 62.99 | 0 | 0 | 0 | 0 | 17.62 | 0
2025-09-30 12:00 | 65.99 | 77.23 | 65.99 | 0 | 0 | 0 | 0 | 11.23 | 0
2025-09-30 13:00 | 66.79 | 80.38 | 66.79 | 0 | 0 | 0 | 0 | 13.59 | 0
2025-09-30 14:00 | 68.38 | 89.78 | 68.38 | 0 | 0 | 0 | 0 | 21.4 | 0
2025-09-30 15:00 | 68.74 | 87.36 | 68.74 | 0 | 0 | 0 | 0 | 18.62 | 0
2025-09-30 16:00 | 69.52 | 68.03 | 68.03 | 1.5 | 0 | 0 | 0 | 0 | 0
2025-09-30 17:00 | 67.61 | 18.34 | 18.34 | 49.28 | 0 | 0 | 0 | 0 | 0
2025-09-30 18:00 | 65.32 | 0 | 0 | 65.32 | 0 | 0 | 0 | 0 | 0
2025-09-30 19:00 | 63.75 | 0 | 0 | 63.75 | 0 | 0 | 0 | 0 | 0
2025-09-30 20:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 0 | 0 | 0
2025-09-30 21:00 | 57.24 | 0 | 0 | 57.24 | 0 | 0 | 0 | 0 | 0
2025-09-30 22:00 | 54.85 | 0 | 0 | 54.85 | 0 | 0 | 0 | 0 | 0
2025-09-30 23:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 0 | 0 | 0
2025-10-01 | 50.24 | 0 | 0 | 50.24 | 0 | 0 | 0 | 0 | 0
2025-10-01 01:00 | 48.41 | 0 | 0 | 48.41 | 0 | 0 | 0 | 0 | 0
2025-10-01 02:00 | 46.81 | 0 | 0 | 46.81 | 0 | 0 | 0 | 0 | 0
2025-10-01 03:00 | 47.79 | 0 | 0 | 47.79 | 0 | 0 | 0 | 0 | 0
2025-10-01 04:00 | 46.75 | 0 | 0 | 46.75 | 0 | 0 | 0 | 0 | 0
2025-10-01 05:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 0 | 0 | 0
2025-10-01 06:00 | 50.97 | 0.84 | 0.84 | 50.13 | 0 | 0 | 0 | 0 | 0
2025-10-01 07:00 | 53.02 | 51.23 | 51.23 | 1.79 | 0 | 0 | 0 | 0 | 0
2025-10-01 08:00 | 55.77 | 90.39 | 55.77 | 0 | 0 | 0 | 0 | 34.62 | 0
2025-10-01 09:00 | 59.32 | 95.21 | 59.32 | 0 | 0 | 0 | 0 | 35.88 | 0
2025-10-01 10:00 | 63.89 | 92.94 | 63.89 | 0 | 0 | 0 | 0 | 29.05 | 0
2025-10-01 11:00 | 67.6 | 86.1 | 67.6 | 0 | 0 | 0 | 0 | 18.5 | 0
2025-10-01 12:00 | 71.69 | 86.91 | 71.69 | 0 | 0 | 0 | 0 | 15.22 | 0
2025-10-01 13:00 | 73.78 | 88.57 | 73.78 | 0 | 0 | 0 | 0 | 14.79 | 0
2025-10-01 14:00 | 76.75 | 90.98 | 76.75 | 0 | 0 | 0 | 0 | 14.23 | 0
2025-10-01 15:00 | 77.05 | 87.02 | 77.05 | 0 | 0 | 0 | 0 | 9.97 | 0
2025-10-01 16:00 | 76.44 | 76.38 | 76.38 | 0.06 | 0 | 0 | 0 | 0 | 0
2025-10-01 17:00 | 75.2 | 16.36 | 16.36 | 58.84 | 0 | 0 | 0 | 0 | 0
2025-10-01 18:00 | 71.37 | 0 | 0 | 71.37 | 0 | 0 | 0 | 0 | 0
2025-10-01 19:00 | 67.62 | 0 | 0 | 67.62 | 0 | 0 | 0 | 0 | 0
2025-10-01 20:00 | 63.73 | 0 | 0 | 63.73 | 0 | 0 | 0 | 0 | 0
2025-10-01 21:00 | 59.9 | 0 | 0 | 59.9 | 0 | 0 | 0 | 0 | 0
2025-10-01 22:00 | 56.22 | 0 | 0 | 56.22 | 0 | 0 | 0 | 0 | 0
2025-10-01 23:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 0 | 0 | 0
2025-10-02 | 49.24 | 0 | 0 | 49.24 | 0 | 0 | 0 | 0 | 0
2025-10-02 01:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0 | 0 | 0
2025-10-02 02:00 | 47.52 | 0 | 0 | 47.52 | 0 | 0 | 0 | 0 | 0
2025-10-02 03:00 | 47.04 | 0 | 0 | 47.04 | 0 | 0 | 0 | 0 | 0
2025-10-02 04:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0 | 0 | 0
2025-10-02 05:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0 | 0 | 0
2025-10-02 06:00 | 50.64 | 0.54 | 0.54 | 50.1 | 0 | 0 | 0 | 0 | 0
2025-10-02 07:00 | 53.43 | 26.33 | 26.33 | 27.1 | 0 | 0 | 0 | 0 | 0
2025-10-02 08:00 | 56.18 | 79.48 | 56.18 | 0 | 0 | 0 | 0 | 23.31 | 0
2025-10-02 09:00 | 60.12 | 51.43 | 51.43 | 8.7 | 0 | 0 | 0 | 0 | 0
2025-10-02 10:00 | 63.88 | 47.89 | 47.89 | 15.98 | 0 | 0 | 0 | 0 | 0
2025-10-02 11:00 | 67.04 | 60.96 | 60.96 | 6.08 | 0 | 0 | 0 | 0 | 0
2025-10-02 12:00 | 70.16 | 44.99 | 44.99 | 25.17 | 0 | 0 | 0 | 0 | 0
2025-10-02 13:00 | 72.28 | 76.99 | 72.28 | 0 | 0 | 0 | 0 | 4.71 | 0
2025-10-02 14:00 | 74.03 | 54.86 | 54.86 | 19.16 | 0 | 0 | 0 | 0 | 0
2025-10-02 15:00 | 74.45 | 92.81 | 74.45 | 0 | 0 | 0 | 0 | 18.36 | 0
2025-10-02 16:00 | 74.36 | 66.56 | 66.56 | 7.8 | 0 | 0 | 0 | 0 | 0
2025-10-02 17:00 | 72.03 | 1.4 | 1.4 | 70.63 | 0 | 0 | 0 | 0 | 0
2025-10-02 18:00 | 69.71 | 0 | 0 | 69.71 | 0 | 0 | 0 | 0 | 0
2025-10-02 19:00 | 65.39 | 0 | 0 | 65.39 | 0 | 0 | 0 | 0 | 0
2025-10-02 20:00 | 63.81 | 0 | 0 | 63.81 | 0 | 0 | 0 | 0 | 0
2025-10-02 21:00 | 59.16 | 0 | 0 | 59.16 | 0 | 0 | 0 | 0 | 0
2025-10-02 22:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 0 | 0 | 0
2025-10-02 23:00 | 53.47 | 0 | 0 | 53.47 | 0 | 0 | 0 | 0 | 0
2025-10-03 | 50.16 | 0 | 0 | 50.16 | 0 | 0 | 0 | 0 | 0
2025-10-03 01:00 | 49.01 | 0 | 0 | 49.01 | 0 | 0 | 0 | 0 | 0
2025-10-03 02:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0 | 0 | 0
2025-10-03 03:00 | 48.05 | 0 | 0 | 48.05 | 0 | 0 | 0 | 0 | 0
2025-10-03 04:00 | 47.76 | 0 | 0 | 47.76 | 0 | 0 | 0 | 0 | 0
2025-10-03 05:00 | 48.39 | 0 | 0 | 48.39 | 0 | 0 | 0 | 0 | 0
2025-10-03 06:00 | 50.72 | 0.48 | 0.48 | 50.25 | 0 | 0 | 0 | 0 | 0
2025-10-03 07:00 | 51.7 | 37.9 | 37.9 | 13.8 | 0 | 0 | 0 | 0 | 0
2025-10-03 08:00 | 54.83 | 74.66 | 54.83 | 0 | 0 | 0 | 0 | 19.83 | 0
2025-10-03 09:00 | 58.63 | 92.42 | 58.63 | 0 | 0 | 0 | 0 | 33.78 | 0
2025-10-03 10:00 | 59.96 | 89.66 | 59.96 | 0 | 0 | 0 | 0 | 29.7 | 0
2025-10-03 11:00 | 64 | 83.05 | 64 | 0 | 0 | 0 | 0 | 19.05 | 0
2025-10-03 12:00 | 66.44 | 81.07 | 66.44 | 0 | 0 | 0 | 0 | 14.63 | 0
2025-10-03 13:00 | 69.07 | 74.46 | 69.07 | 0 | 0 | 0 | 0 | 5.4 | 0
2025-10-03 14:00 | 68.5 | 70.19 | 68.5 | 0 | 0 | 0 | 0 | 1.68 | 0
2025-10-03 15:00 | 70.51 | 65.82 | 65.82 | 4.7 | 0 | 0 | 0 | 0 | 0
2025-10-03 16:00 | 69.01 | 36.7 | 36.7 | 32.32 | 0 | 0 | 0 | 0 | 0
2025-10-03 17:00 | 67.86 | 10.22 | 10.22 | 57.64 | 0 | 0 | 0 | 0 | 0
2025-10-03 18:00 | 65.56 | 0 | 0 | 65.56 | 0 | 0 | 0 | 0 | 0
2025-10-03 19:00 | 63.17 | 0 | 0 | 63.17 | 0 | 0 | 0 | 0 | 0
2025-10-03 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 0 | 0 | 0
2025-10-03 21:00 | 57.35 | 0 | 0 | 57.35 | 0 | 0 | 0 | 0 | 0
2025-10-03 22:00 | 55.34 | 0 | 0 | 55.34 | 0 | 0 | 0 | 0 | 0
2025-10-03 23:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0 | 0 | 0
2025-10-04 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 0 | 0 | 0
2025-10-04 01:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0 | 0 | 0
2025-10-04 02:00 | 47.26 | 0 | 0 | 47.26 | 0 | 0 | 0 | 0 | 0
2025-10-04 03:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0 | 0 | 0
2025-10-04 04:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 0 | 0 | 0
2025-10-04 05:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 0 | 0 | 0
2025-10-04 06:00 | 50.31 | 0.09 | 0.09 | 50.23 | 0 | 0 | 0 | 0 | 0
2025-10-04 07:00 | 51.69 | 25 | 25 | 26.69 | 0 | 0 | 0 | 0 | 0
2025-10-04 08:00 | 53.66 | 42.57 | 42.57 | 11.09 | 0 | 0 | 0 | 0 | 0
2025-10-04 09:00 | 56.64 | 15.96 | 15.96 | 40.68 | 0 | 0 | 0 | 0 | 0
2025-10-04 10:00 | 59.15 | 41.47 | 41.47 | 17.69 | 0 | 0 | 0 | 0 | 0
2025-10-04 11:00 | 60.26 | 48.33 | 48.33 | 11.93 | 0 | 0 | 0 | 0 | 0
2025-10-04 12:00 | 62.26 | 65.1 | 62.26 | 0 | 0 | 0 | 0 | 2.85 | 0
2025-10-04 13:00 | 63.61 | 78.25 | 63.61 | 0 | 0 | 0 | 0 | 14.63 | 0
2025-10-04 14:00 | 64.65 | 51.04 | 51.04 | 13.61 | 0 | 0 | 0 | 0 | 0
2025-10-04 15:00 | 64.64 | 42.25 | 42.25 | 22.39 | 0 | 0 | 0 | 0 | 0
2025-10-04 16:00 | 65.11 | 77.17 | 65.11 | 0 | 0 | 0 | 0 | 12.06 | 0
2025-10-04 17:00 | 63.17 | 15.21 | 15.21 | 47.97 | 0 | 0 | 0 | 0 | 0
2025-10-04 18:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 0 | 0 | 0
2025-10-04 19:00 | 60.82 | 0 | 0 | 60.82 | 0 | 0 | 0 | 0 | 0
2025-10-04 20:00 | 58.83 | 0 | 0 | 58.83 | 0 | 0 | 0 | 0 | 0
2025-10-04 21:00 | 55.87 | 0 | 0 | 55.87 | 0 | 0 | 0 | 0 | 0
2025-10-04 22:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 0 | 0 | 0
2025-10-04 23:00 | 51.65 | 0 | 0 | 51.65 | 0 | 0 | 0 | 0 | 0
2025-10-05 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 0 | 0 | 0
2025-10-05 01:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0 | 0 | 0
2025-10-05 02:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 0 | 0 | 0
2025-10-05 03:00 | 47.35 | 0 | 0 | 47.35 | 0 | 0 | 0 | 0 | 0
2025-10-05 04:00 | 47.21 | 0 | 0 | 47.21 | 0 | 0 | 0 | 0 | 0
2025-10-05 05:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0 | 0 | 0
2025-10-05 06:00 | 49.64 | 0.45 | 0.45 | 49.19 | 0 | 0 | 0 | 0 | 0
2025-10-05 07:00 | 51.66 | 39.65 | 39.65 | 12.01 | 0 | 0 | 0 | 0 | 0
2025-10-05 08:00 | 54.43 | 66.65 | 54.43 | 0 | 0 | 0 | 0 | 12.23 | 0
2025-10-05 09:00 | 55.77 | 76.46 | 55.77 | 0 | 0 | 0 | 0 | 20.7 | 0
2025-10-05 10:00 | 58.56 | 79.95 | 58.56 | 0 | 0 | 0 | 0 | 21.39 | 0
2025-10-05 11:00 | 60.03 | 65.72 | 60.03 | 0 | 0 | 0 | 0 | 5.69 | 0
2025-10-05 12:00 | 62.23 | 72.82 | 62.23 | 0 | 0 | 0 | 0 | 10.59 | 0
2025-10-05 13:00 | 63.2 | 39.24 | 39.24 | 23.96 | 0 | 0 | 0 | 0 | 0
2025-10-05 14:00 | 63.3 | 42.84 | 42.84 | 20.47 | 0 | 0 | 0 | 0 | 0
2025-10-05 15:00 | 63.29 | 66.87 | 63.29 | 0 | 0 | 0 | 0 | 3.58 | 0
2025-10-05 16:00 | 63.46 | 54.37 | 54.37 | 9.09 | 0 | 0 | 0 | 0 | 0
2025-10-05 17:00 | 62.47 | 1.65 | 1.65 | 60.82 | 0 | 0 | 0 | 0 | 0
2025-10-05 18:00 | 62.33 | 0 | 0 | 62.33 | 0 | 0 | 0 | 0 | 0
2025-10-05 19:00 | 60.05 | 0 | 0 | 60.05 | 0 | 0 | 0 | 0 | 0
2025-10-05 20:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 0 | 0 | 0
2025-10-05 21:00 | 55.84 | 0 | 0 | 55.84 | 0 | 0 | 0 | 0 | 0
2025-10-05 22:00 | 53.21 | 0 | 0 | 53.21 | 0 | 0 | 0 | 0 | 0
2025-10-05 23:00 | 51.88 | 0 | 0 | 51.88 | 0 | 0 | 0 | 0 | 0
2025-10-06 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 0 | 0 | 0
2025-10-06 01:00 | 48.45 | 0 | 0 | 48.45 | 0 | 0 | 0 | 0 | 0
2025-10-06 02:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 0 | 0 | 0
2025-10-06 03:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 0 | 0 | 0
2025-10-06 04:00 | 47.42 | 0 | 0 | 47.42 | 0 | 0 | 0 | 0 | 0
2025-10-06 05:00 | 46.82 | 0 | 0 | 46.82 | 0 | 0 | 0 | 0 | 0
2025-10-06 06:00 | 50.64 | 0 | 0 | 50.64 | 0 | 0 | 0 | 0 | 0
2025-10-06 07:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 0 | 0 | 0
2025-10-06 08:00 | 54.9 | 2.02 | 2.02 | 52.87 | 0 | 0 | 0 | 0 | 0
2025-10-06 09:00 | 58.31 | 3.7 | 3.7 | 54.61 | 0 | 0 | 0 | 0 | 0
2025-10-06 10:00 | 61.74 | 11.56 | 11.56 | 50.18 | 0 | 0 | 0 | 0 | 0
2025-10-06 11:00 | 64.77 | 13.91 | 13.91 | 50.86 | 0 | 0 | 0 | 0 | 0
2025-10-06 12:00 | 68.03 | 11 | 11 | 57.03 | 0 | 0 | 0 | 0 | 0
2025-10-06 13:00 | 70.09 | 65.33 | 65.33 | 4.76 | 0 | 0 | 0 | 0 | 0
2025-10-06 14:00 | 72.18 | 64.61 | 64.61 | 7.56 | 0 | 0 | 0 | 0 | 0
2025-10-06 15:00 | 72.06 | 44.34 | 44.34 | 27.72 | 0 | 0 | 0 | 0 | 0
2025-10-06 16:00 | 72.28 | 27.58 | 27.58 | 44.7 | 0 | 0 | 0 | 0 | 0
2025-10-06 17:00 | 70.28 | 3.7 | 3.7 | 66.58 | 0 | 0 | 0 | 0 | 0
2025-10-06 18:00 | 66.63 | 0 | 0 | 66.63 | 0 | 0 | 0 | 0 | 0
2025-10-06 19:00 | 65.94 | 0 | 0 | 65.94 | 0 | 0 | 0 | 0 | 0
2025-10-06 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 0 | 0 | 0
2025-10-06 21:00 | 58.77 | 0 | 0 | 58.77 | 0 | 0 | 0 | 0 | 0
2025-10-06 22:00 | 54.84 | 0 | 0 | 54.84 | 0 | 0 | 0 | 0 | 0
2025-10-06 23:00 | 52.51 | 0 | 0 | 52.51 | 0 | 0 | 0 | 0 | 0
2025-10-07 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0 | 0 | 0
2025-10-07 01:00 | 48.06 | 0 | 0 | 48.06 | 0 | 0 | 0 | 0 | 0
2025-10-07 02:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0 | 0 | 0
2025-10-07 03:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 0 | 0 | 0
2025-10-07 04:00 | 46.93 | 0 | 0 | 46.93 | 0 | 0 | 0 | 0 | 0
2025-10-07 05:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 0 | 0 | 0
2025-10-07 06:00 | 48.33 | 0.28 | 0.28 | 48.04 | 0 | 0 | 0 | 0 | 0
2025-10-07 07:00 | 51.55 | 41 | 41 | 10.54 | 0 | 0 | 0 | 0 | 0
2025-10-07 08:00 | 54.36 | 83.96 | 54.36 | 0 | 0 | 0 | 0 | 29.59 | 0
2025-10-07 09:00 | 57.05 | 93.19 | 57.05 | 0 | 0 | 0 | 0 | 36.14 | 0
2025-10-07 10:00 | 60.24 | 78.48 | 60.24 | 0 | 0 | 0 | 0 | 18.24 | 0
2025-10-07 11:00 | 62.23 | 48.21 | 48.21 | 14.02 | 0 | 0 | 0 | 0 | 0
2025-10-07 12:00 | 64.74 | 42.61 | 42.61 | 22.13 | 0 | 0 | 0 | 0 | 0
2025-10-07 13:00 | 67.09 | 64.61 | 64.61 | 2.48 | 0 | 0 | 0 | 0 | 0
2025-10-07 14:00 | 66.48 | 40.75 | 40.75 | 25.74 | 0 | 0 | 0 | 0 | 0
2025-10-07 15:00 | 68.3 | 27.14 | 27.14 | 41.17 | 0 | 0 | 0 | 0 | 0
2025-10-07 16:00 | 67.46 | 5.71 | 5.71 | 61.75 | 0 | 0 | 0 | 0 | 0
2025-10-07 17:00 | 66.04 | 0.82 | 0.82 | 65.22 | 0 | 0 | 0 | 0 | 0
2025-10-07 18:00 | 64.88 | 0 | 0 | 64.88 | 0 | 0 | 0 | 0 | 0
2025-10-07 19:00 | 63.03 | 0 | 0 | 63.03 | 0 | 0 | 0 | 0 | 0
2025-10-07 20:00 | 60.28 | 0 | 0 | 60.28 | 0 | 0 | 0 | 0 | 0
2025-10-07 21:00 | 56.87 | 0 | 0 | 56.87 | 0 | 0 | 0 | 0 | 0
2025-10-07 22:00 | 54.59 | 0 | 0 | 54.59 | 0 | 0 | 0 | 0 | 0
2025-10-07 23:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 0 | 0 | 0
2025-10-08 | 49.23 | 0 | 0 | 49.23 | 0 | 0 | 0 | 0 | 0
2025-10-08 01:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 0 | 0 | 0
2025-10-08 02:00 | 46.27 | 0 | 0 | 46.27 | 0 | 0 | 0 | 0 | 0
2025-10-08 03:00 | 46.66 | 0 | 0 | 46.66 | 0 | 0 | 0 | 0 | 0
2025-10-08 04:00 | 46.57 | 0 | 0 | 46.57 | 0 | 0 | 0 | 0 | 0
2025-10-08 05:00 | 47.1 | 0 | 0 | 47.1 | 0 | 0 | 0 | 0 | 0
2025-10-08 06:00 | 48.43 | 0 | 0 | 48.43 | 0 | 0 | 0 | 0 | 0
2025-10-08 07:00 | 51.89 | 46.8 | 46.8 | 5.09 | 0 | 0 | 0 | 0 | 0
2025-10-08 08:00 | 53.8 | 97.7 | 53.8 | 0 | 0 | 0 | 0 | 43.89 | 0
2025-10-08 09:00 | 57.09 | 99.25 | 57.09 | 0 | 0 | 0 | 0 | 42.16 | 0
2025-10-08 10:00 | 60.46 | 71.66 | 60.46 | 0 | 0 | 0 | 0 | 11.21 | 0
2025-10-08 11:00 | 61.95 | 21.42 | 21.42 | 40.53 | 0 | 0 | 0 | 0 | 0
2025-10-08 12:00 | 65 | 31.52 | 31.52 | 33.48 | 0 | 0 | 0 | 0 | 0
2025-10-08 13:00 | 66.81 | 60.65 | 60.65 | 6.16 | 0 | 0 | 0 | 0 | 0
2025-10-08 14:00 | 68.28 | 47.35 | 47.35 | 20.93 | 0 | 0 | 0 | 0 | 0
2025-10-08 15:00 | 69.12 | 58.01 | 58.01 | 11.11 | 0 | 0 | 0 | 0 | 0
2025-10-08 16:00 | 67.43 | 4.57 | 4.57 | 62.86 | 0 | 0 | 0 | 0 | 0
2025-10-08 17:00 | 67.18 | 0.03 | 0.03 | 67.16 | 0 | 0 | 0 | 0 | 0
2025-10-08 18:00 | 65.53 | 0 | 0 | 65.53 | 0 | 0 | 0 | 0 | 0
2025-10-08 19:00 | 62.51 | 0 | 0 | 62.51 | 0 | 0 | 0 | 0 | 0
2025-10-08 20:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 0 | 0 | 0
2025-10-08 21:00 | 57.14 | 0 | 0 | 57.14 | 0 | 0 | 0 | 0 | 0
2025-10-08 22:00 | 54.25 | 0 | 0 | 54.25 | 0 | 0 | 0 | 0 | 0
2025-10-08 23:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 0 | 0 | 0
2025-10-09 | 49.23 | 0 | 0 | 49.23 | 0 | 0 | 0 | 0 | 0
2025-10-09 01:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 0 | 0 | 0
2025-10-09 02:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 0 | 0 | 0
2025-10-09 03:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 0 | 0 | 0
2025-10-09 04:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 0 | 0 | 0
2025-10-09 05:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 0 | 0 | 0
2025-10-09 06:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 0 | 0 | 0
2025-10-09 07:00 | 50.89 | 0.1 | 0.1 | 50.79 | 0 | 0 | 0 | 0 | 0
2025-10-09 08:00 | 52.19 | 2.92 | 2.92 | 49.27 | 0 | 0 | 0 | 0 | 0
2025-10-09 09:00 | 54.49 | 4.84 | 4.84 | 49.65 | 0 | 0 | 0 | 0 | 0
2025-10-09 10:00 | 55.67 | 6.71 | 6.71 | 48.96 | 0 | 0 | 0 | 0 | 0
2025-10-09 11:00 | 58.06 | 8.17 | 8.17 | 49.9 | 0 | 0 | 0 | 0 | 0
2025-10-09 12:00 | 58.89 | 8.7 | 8.7 | 50.19 | 0 | 0 | 0 | 0 | 0
2025-10-09 13:00 | 58.69 | 7.48 | 7.48 | 51.21 | 0 | 0 | 0 | 0 | 0
2025-10-09 14:00 | 60.09 | 6.13 | 6.13 | 53.96 | 0 | 0 | 0 | 0 | 0
2025-10-09 15:00 | 60.02 | 3.69 | 3.69 | 56.33 | 0 | 0 | 0 | 0 | 0
2025-10-09 16:00 | 60.17 | 1.57 | 1.57 | 58.6 | 0 | 0 | 0 | 0 | 0
2025-10-09 17:00 | 59.32 | 0 | 0 | 59.32 | 0 | 0 | 0 | 0 | 0
2025-10-09 18:00 | 58.4 | 0 | 0 | 58.4 | 0 | 0 | 0 | 0 | 0
2025-10-09 19:00 | 57.37 | 0 | 0 | 57.37 | 0 | 0 | 0 | 0 | 0
2025-10-09 20:00 | 56.1 | 0 | 0 | 56.1 | 0 | 0 | 0 | 0 | 0
2025-10-09 21:00 | 54.68 | 0 | 0 | 54.68 | 0 | 0 | 0 | 0 | 0
2025-10-09 22:00 | 52.84 | 0 | 0 | 52.84 | 0 | 0 | 0 | 0 | 0
2025-10-09 23:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0 | 0 | 0
2025-10-10 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 0 | 0 | 0
2025-10-10 01:00 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 0 | 0 | 0
2025-10-10 02:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0 | 0 | 0
2025-10-10 03:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 0 | 0 | 0
2025-10-10 04:00 | 46.05 | 0 | 0 | 46.05 | 0 | 0 | 0 | 0 | 0
2025-10-10 05:00 | 49 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0
2025-10-10 06:00 | 49.22 | 0 | 0 | 49.21 | 0 | 0 | 0 | 0 | 0
2025-10-10 07:00 | 50.54 | 42.11 | 42.11 | 8.44 | 0 | 0 | 0 | 0 | 0
2025-10-10 08:00 | 54.33 | 90.9 | 54.33 | 0 | 0 | 0 | 0 | 36.57 | 0
2025-10-10 09:00 | 56.44 | 68.19 | 56.44 | 0 | 0 | 0 | 0 | 11.76 | 0
2025-10-10 10:00 | 60.44 | 35.1 | 35.1 | 25.35 | 0 | 0 | 0 | 0 | 0
2025-10-10 11:00 | 62.87 | 49.11 | 49.11 | 13.76 | 0 | 0 | 0 | 0 | 0
2025-10-10 12:00 | 65.4 | 52.62 | 52.62 | 12.78 | 0 | 0 | 0 | 0 | 0
2025-10-10 13:00 | 68.5 | 71.3 | 68.5 | 0 | 0 | 0 | 0 | 2.8 | 0
2025-10-10 14:00 | 69.31 | 90.4 | 69.31 | 0 | 0 | 0 | 0 | 21.1 | 0
2025-10-10 15:00 | 69.97 | 94.07 | 69.97 | 0 | 0 | 0 | 0 | 24.11 | 0
2025-10-10 16:00 | 69.24 | 70.16 | 69.24 | 0 | 0 | 0 | 0 | 0.91 | 0
2025-10-10 17:00 | 67.47 | 6.84 | 6.84 | 60.63 | 0 | 0 | 0 | 0 | 0
2025-10-10 18:00 | 65.92 | 0 | 0 | 65.92 | 0 | 0 | 0 | 0 | 0
2025-10-10 19:00 | 63.58 | 0 | 0 | 63.58 | 0 | 0 | 0 | 0 | 0
2025-10-10 20:00 | 60.06 | 0 | 0 | 60.06 | 0 | 0 | 0 | 0 | 0
2025-10-10 21:00 | 57.79 | 0 | 0 | 57.79 | 0 | 0 | 0 | 0 | 0
2025-10-10 22:00 | 54.34 | 0 | 0 | 54.34 | 0 | 0 | 0 | 0 | 0
2025-10-10 23:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 0 | 0 | 0
2025-10-11 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0 | 0 | 0
2025-10-11 01:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 0 | 0 | 0
2025-10-11 02:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 0 | 0 | 0
2025-10-11 03:00 | 45.82 | 0 | 0 | 45.82 | 0 | 0 | 0 | 0 | 0
2025-10-11 04:00 | 46.31 | 0 | 0 | 46.31 | 0 | 0 | 0 | 0 | 0
2025-10-11 05:00 | 47 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0
2025-10-11 06:00 | 48.99 | 0 | 0 | 48.99 | 0 | 0 | 0 | 0 | 0
2025-10-11 07:00 | 50.96 | 42.65 | 42.65 | 8.31 | 0 | 0 | 0 | 0 | 0
2025-10-11 08:00 | 53.87 | 89.36 | 53.87 | 0 | 0 | 0 | 0 | 35.5 | 0
2025-10-11 09:00 | 56.58 | 93.07 | 56.58 | 0 | 0 | 0 | 0 | 36.49 | 0
2025-10-11 10:00 | 59.15 | 87.26 | 59.15 | 0 | 0 | 0 | 0 | 28.11 | 0
2025-10-11 11:00 | 61.06 | 79.52 | 61.06 | 0 | 0 | 0 | 0 | 18.46 | 0
2025-10-11 12:00 | 64.97 | 79.53 | 64.97 | 0 | 0 | 0 | 0 | 14.56 | 0
2025-10-11 13:00 | 65.82 | 85.64 | 65.82 | 0 | 0 | 0 | 0 | 19.81 | 0
2025-10-11 14:00 | 67.01 | 91.97 | 67.01 | 0 | 0 | 0 | 0 | 24.96 | 0
2025-10-11 15:00 | 67.27 | 89.87 | 67.27 | 0 | 0 | 0 | 0 | 22.6 | 0
2025-10-11 16:00 | 66.8 | 67.4 | 66.8 | 0 | 0 | 0 | 0 | 0.59 | 0
2025-10-11 17:00 | 66.67 | 2.29 | 2.29 | 64.38 | 0 | 0 | 0 | 0 | 0
2025-10-11 18:00 | 64.77 | 0 | 0 | 64.77 | 0 | 0 | 0 | 0 | 0
2025-10-11 19:00 | 61.96 | 0 | 0 | 61.96 | 0 | 0 | 0 | 0 | 0
2025-10-11 20:00 | 59.01 | 0 | 0 | 59.01 | 0 | 0 | 0 | 0 | 0
2025-10-11 21:00 | 56.56 | 0 | 0 | 56.56 | 0 | 0 | 0 | 0 | 0
2025-10-11 22:00 | 53.52 | 0 | 0 | 53.52 | 0 | 0 | 0 | 0 | 0
2025-10-11 23:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 0 | 0 | 0
2025-10-12 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 0 | 0 | 0
2025-10-12 01:00 | 46.82 | 0 | 0 | 46.82 | 0 | 0 | 0 | 0 | 0
2025-10-12 02:00 | 46.2 | 0 | 0 | 46.2 | 0 | 0 | 0 | 0 | 0
2025-10-12 03:00 | 45.84 | 0 | 0 | 45.84 | 0 | 0 | 0 | 0 | 0
2025-10-12 04:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 0 | 0 | 0
2025-10-12 05:00 | 46.73 | 0 | 0 | 46.73 | 0 | 0 | 0 | 0 | 0
2025-10-12 06:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 0 | 0 | 0
2025-10-12 07:00 | 49.98 | 4.67 | 4.67 | 45.3 | 0 | 0 | 0 | 0 | 0
2025-10-12 08:00 | 52.23 | 35.51 | 35.51 | 16.72 | 0 | 0 | 0 | 0 | 0
2025-10-12 09:00 | 54.37 | 60.46 | 54.37 | 0 | 0 | 0 | 0 | 6.09 | 0
2025-10-12 10:00 | 56.08 | 68.84 | 56.08 | 0 | 0 | 0 | 0 | 12.76 | 0
2025-10-12 11:00 | 58.85 | 63.08 | 58.85 | 0 | 0 | 0 | 0 | 4.23 | 0
2025-10-12 12:00 | 59.25 | 65.41 | 59.25 | 0 | 0 | 0 | 0 | 6.16 | 0
2025-10-12 13:00 | 60.39 | 67.91 | 60.39 | 0 | 0 | 0 | 0 | 7.52 | 0
2025-10-12 14:00 | 61.98 | 77.76 | 61.98 | 0 | 0 | 0 | 0 | 15.78 | 0
2025-10-12 15:00 | 61.27 | 97.51 | 61.27 | 0 | 0 | 0 | 0 | 36.24 | 0
2025-10-12 16:00 | 61.26 | 72.36 | 61.26 | 0 | 0 | 0 | 0 | 11.1 | 0
2025-10-12 17:00 | 60.23 | 5.11 | 5.11 | 55.12 | 0 | 0 | 0 | 0 | 0
2025-10-12 18:00 | 60.15 | 0 | 0 | 60.15 | 0 | 0 | 0 | 0 | 0
2025-10-12 19:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 0 | 0 | 0
2025-10-12 20:00 | 56.98 | 0 | 0 | 56.98 | 0 | 0 | 0 | 0 | 0
2025-10-12 21:00 | 54.9 | 0 | 0 | 54.9 | 0 | 0 | 0 | 0 | 0
2025-10-12 22:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 0 | 0 | 0
2025-10-12 23:00 | 50.17 | 0 | 0 | 50.17 | 0 | 0 | 0 | 0 | 0
2025-10-13 | 48.04 | 0 | 0 | 48.04 | 0 | 0 | 0 | 0 | 0
2025-10-13 01:00 | 47.56 | 0 | 0 | 47.56 | 0 | 0 | 0 | 0 | 0
2025-10-13 02:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 0 | 0 | 0
2025-10-13 03:00 | 45.26 | 0 | 0 | 45.26 | 0 | 0 | 0 | 0 | 0
2025-10-13 04:00 | 45.96 | 0 | 0 | 45.96 | 0 | 0 | 0 | 0 | 0
2025-10-13 05:00 | 46.76 | 0 | 0 | 46.76 | 0 | 0 | 0 | 0 | 0
2025-10-13 06:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 0 | 0 | 0
2025-10-13 07:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 0 | 0 | 0
2025-10-13 08:00 | 52.43 | 1.63 | 1.63 | 50.8 | 0 | 0 | 0 | 0 | 0
2025-10-13 09:00 | 54.51 | 3.15 | 3.15 | 51.36 | 0 | 0 | 0 | 0 | 0
2025-10-13 10:00 | 56.54 | 4.6 | 4.6 | 51.94 | 0 | 0 | 0 | 0 | 0
2025-10-13 11:00 | 58.58 | 5.91 | 5.91 | 52.67 | 0 | 0 | 0 | 0 | 0
2025-10-13 12:00 | 60.93 | 6.61 | 6.61 | 54.32 | 0 | 0 | 0 | 0 | 0
2025-10-13 13:00 | 62.39 | 58.31 | 58.31 | 4.08 | 0 | 0 | 0 | 0 | 0
2025-10-13 14:00 | 62.82 | 57.25 | 57.25 | 5.56 | 0 | 0 | 0 | 0 | 0
2025-10-13 15:00 | 63.86 | 53.52 | 53.52 | 10.34 | 0 | 0 | 0 | 0 | 0
2025-10-13 16:00 | 63.22 | 37.62 | 37.62 | 25.6 | 0 | 0 | 0 | 0 | 0
2025-10-13 17:00 | 62.72 | 0.88 | 0.88 | 61.85 | 0 | 0 | 0 | 0 | 0
2025-10-13 18:00 | 61.02 | 0 | 0 | 61.02 | 0 | 0 | 0 | 0 | 0
2025-10-13 19:00 | 58.97 | 0 | 0 | 58.97 | 0 | 0 | 0 | 0 | 0
2025-10-13 20:00 | 57.34 | 0 | 0 | 57.34 | 0 | 0 | 0 | 0 | 0
2025-10-13 21:00 | 54.36 | 0 | 0 | 54.36 | 0 | 0 | 0 | 0 | 0
2025-10-13 22:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 0 | 0 | 0
2025-10-13 23:00 | 49.93 | 0 | 0 | 49.93 | 0 | 0 | 0 | 0 | 0
2025-10-14 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 0 | 0 | 0
2025-10-14 01:00 | 46.62 | 0 | 0 | 46.62 | 0 | 0 | 0 | 0 | 0
2025-10-14 02:00 | 46.34 | 0 | 0 | 46.34 | 0 | 0 | 0 | 0 | 0
2025-10-14 03:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 0 | 0 | 0
2025-10-14 04:00 | 45.48 | 0 | 0 | 45.48 | 0 | 0 | 0 | 0 | 0
2025-10-14 05:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 0 | 0 | 0
2025-10-14 06:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 0 | 0 | 0
2025-10-14 07:00 | 51.22 | 21.89 | 21.89 | 29.33 | 0 | 0 | 0 | 0 | 0
2025-10-14 08:00 | 52.82 | 78.45 | 52.82 | 0 | 0 | 0 | 0 | 25.63 | 0
2025-10-14 09:00 | 56.33 | 64.9 | 56.33 | 0 | 0 | 0 | 0 | 8.57 | 0
2025-10-14 10:00 | 57.92 | 36.55 | 36.55 | 21.36 | 0 | 0 | 0 | 0 | 0
2025-10-14 11:00 | 61.1 | 52.95 | 52.95 | 8.16 | 0 | 0 | 0 | 0 | 0
2025-10-14 12:00 | 62.24 | 68.24 | 62.24 | 0 | 0 | 0 | 0 | 5.99 | 0
2025-10-14 13:00 | 64.6 | 15.24 | 15.24 | 49.36 | 0 | 0 | 0 | 0 | 0
2025-10-14 14:00 | 64.27 | 8.45 | 8.45 | 55.83 | 0 | 0 | 0 | 0 | 0
2025-10-14 15:00 | 65.24 | 8.68 | 8.68 | 56.57 | 0 | 0 | 0 | 0 | 0
2025-10-14 16:00 | 65.68 | 0.66 | 0.66 | 65.02 | 0 | 0 | 0 | 0 | 0
2025-10-14 17:00 | 63.73 | 0 | 0 | 63.73 | 0 | 0 | 0 | 0 | 0
2025-10-14 18:00 | 62.93 | 0 | 0 | 62.93 | 0 | 0 | 0 | 0 | 0
2025-10-14 19:00 | 61.01 | 0 | 0 | 61.01 | 0 | 0 | 0 | 0 | 0
2025-10-14 20:00 | 57.81 | 0 | 0 | 57.81 | 0 | 0 | 0 | 0 | 0
2025-10-14 21:00 | 54.93 | 0 | 0 | 54.93 | 0 | 0 | 0 | 0 | 0
2025-10-14 22:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 0 | 0 | 0
2025-10-14 23:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 0 | 0 | 0
2025-10-15 | 48.12 | 0 | 0 | 48.12 | 0 | 0 | 0 | 0 | 0
2025-10-15 01:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 0 | 0 | 0
2025-10-15 02:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 0 | 0 | 0
2025-10-15 03:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 0 | 0 | 0
2025-10-15 04:00 | 45.32 | 0 | 0 | 45.32 | 0 | 0 | 0 | 0 | 0
2025-10-15 05:00 | 47.34 | 0 | 0 | 47.34 | 0 | 0 | 0 | 0 | 0
2025-10-15 06:00 | 47.65 | 0 | 0 | 47.65 | 0 | 0 | 0 | 0 | 0
2025-10-15 07:00 | 50.21 | 0 | 0 | 50.21 | 0 | 0 | 0 | 0 | 0
2025-10-15 08:00 | 53.09 | 25.93 | 25.93 | 27.17 | 0 | 0 | 0 | 0 | 0
2025-10-15 09:00 | 55.58 | 2.74 | 2.74 | 52.84 | 0 | 0 | 0 | 0 | 0
2025-10-15 10:00 | 57.31 | 13.57 | 13.57 | 43.74 | 0 | 0 | 0 | 0 | 0
2025-10-15 11:00 | 60.15 | 45.75 | 45.75 | 14.4 | 0 | 0 | 0 | 0 | 0
2025-10-15 12:00 | 62.1 | 56.7 | 56.7 | 5.41 | 0 | 0 | 0 | 0 | 0
2025-10-15 13:00 | 63.17 | 42.83 | 42.83 | 20.35 | 0 | 0 | 0 | 0 | 0
2025-10-15 14:00 | 64.73 | 75.01 | 64.73 | 0 | 0 | 0 | 0 | 10.28 | 0
2025-10-15 15:00 | 65.69 | 86.08 | 65.69 | 0 | 0 | 0 | 0 | 20.39 | 0
2025-10-15 16:00 | 64.66 | 32.6 | 32.6 | 32.06 | 0 | 0 | 0 | 0 | 0
2025-10-15 17:00 | 63.73 | 0.78 | 0.78 | 62.95 | 0 | 0 | 0 | 0 | 0
2025-10-15 18:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 0 | 0 | 0
2025-10-15 19:00 | 59.14 | 0 | 0 | 59.14 | 0 | 0 | 0 | 0 | 0
2025-10-15 20:00 | 57.75 | 0 | 0 | 57.75 | 0 | 0 | 0 | 0 | 0
2025-10-15 21:00 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 0 | 0 | 0
2025-10-15 22:00 | 52.21 | 0 | 0 | 52.21 | 0 | 0 | 0 | 0 | 0
2025-10-15 23:00 | 51.25 | 0 | 0 | 51.25 | 0 | 0 | 0 | 0 | 0
2025-10-16 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0 | 0 | 0
2025-10-16 01:00 | 46.13 | 0 | 0 | 46.13 | 0 | 0 | 0 | 0 | 0
2025-10-16 02:00 | 46.13 | 0 | 0 | 46.13 | 0 | 0 | 0 | 0 | 0
2025-10-16 03:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 0 | 0 | 0
2025-10-16 04:00 | 45.33 | 0 | 0 | 45.33 | 0 | 0 | 0 | 0 | 0
2025-10-16 05:00 | 47.12 | 0 | 0 | 47.12 | 0 | 0 | 0 | 0 | 0
2025-10-16 06:00 | 48.02 | 0 | 0 | 48.02 | 0 | 0 | 0 | 0 | 0
2025-10-16 07:00 | 49.14 | 8.93 | 8.93 | 40.21 | 0 | 0 | 0 | 0 | 0
2025-10-16 08:00 | 52.42 | 36.3 | 36.3 | 16.12 | 0 | 0 | 0 | 0 | 0
2025-10-16 09:00 | 54.3 | 54.54 | 54.3 | 0 | 0 | 0 | 0 | 0.25 | 0
2025-10-16 10:00 | 57.58 | 75.02 | 57.58 | 0 | 0 | 0 | 0 | 17.44 | 0
2025-10-16 11:00 | 58.64 | 64.46 | 58.64 | 0 | 0 | 0 | 0 | 5.82 | 0
2025-10-16 12:00 | 61.27 | 61.24 | 61.24 | 0.03 | 0 | 0 | 0 | 0 | 0
2025-10-16 13:00 | 63 | 50.54 | 50.54 | 12.46 | 0 | 0 | 0 | 0 | 0
2025-10-16 14:00 | 62.55 | 64.54 | 62.55 | 0 | 0 | 0 | 0 | 1.99 | 0
2025-10-16 15:00 | 63.16 | 80.77 | 63.16 | 0 | 0 | 0 | 0 | 17.6 | 0
2025-10-16 16:00 | 63.16 | 62.3 | 62.3 | 0.87 | 0 | 0 | 0 | 0 | 0
2025-10-16 17:00 | 61.69 | 1.59 | 1.59 | 60.1 | 0 | 0 | 0 | 0 | 0
2025-10-16 18:00 | 60.88 | 0 | 0 | 60.88 | 0 | 0 | 0 | 0 | 0
2025-10-16 19:00 | 58.83 | 0 | 0 | 58.83 | 0 | 0 | 0 | 0 | 0
2025-10-16 20:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 0 | 0 | 0
2025-10-16 21:00 | 54.52 | 0 | 0 | 54.52 | 0 | 0 | 0 | 0 | 0
2025-10-16 22:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 0 | 0 | 0
2025-10-16 23:00 | 50.01 | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0
2025-10-17 | 47.55 | 0 | 0 | 47.55 | 0 | 0 | 0 | 0 | 0
2025-10-17 01:00 | 46.08 | 0 | 0 | 46.08 | 0 | 0 | 0 | 0 | 0
2025-10-17 02:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 0 | 0 | 0
2025-10-17 03:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 0 | 0 | 0
2025-10-17 04:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 0 | 0 | 0
2025-10-17 05:00 | 46.52 | 0 | 0 | 46.52 | 0 | 0 | 0 | 0 | 0
2025-10-17 06:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 0 | 0 | 0
2025-10-17 07:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0 | 0 | 0
2025-10-17 08:00 | 51.9 | 3.42 | 3.42 | 48.48 | 0 | 0 | 0 | 0 | 0
2025-10-17 09:00 | 54.01 | 7.72 | 7.72 | 46.29 | 0 | 0 | 0 | 0 | 0
2025-10-17 10:00 | 57.64 | 7.61 | 7.61 | 50.03 | 0 | 0 | 0 | 0 | 0
2025-10-17 11:00 | 59.05 | 4.93 | 4.93 | 54.12 | 0 | 0 | 0 | 0 | 0
2025-10-17 12:00 | 61.02 | 8.17 | 8.17 | 52.85 | 0 | 0 | 0 | 0 | 0
2025-10-17 13:00 | 62.14 | 60.45 | 60.45 | 1.69 | 0 | 0 | 0 | 0 | 0
2025-10-17 14:00 | 63.28 | 61.58 | 61.58 | 1.7 | 0 | 0 | 0 | 0 | 0
2025-10-17 15:00 | 62.99 | 56.82 | 56.82 | 6.17 | 0 | 0 | 0 | 0 | 0
2025-10-17 16:00 | 63.2 | 37.69 | 37.69 | 25.52 | 0 | 0 | 0 | 0 | 0
2025-10-17 17:00 | 61.91 | 0.37 | 0.37 | 61.54 | 0 | 0 | 0 | 0 | 0
2025-10-17 18:00 | 60.79 | 0 | 0 | 60.79 | 0 | 0 | 0 | 0 | 0
2025-10-17 19:00 | 57.76 | 0 | 0 | 57.76 | 0 | 0 | 0 | 0 | 0
2025-10-17 20:00 | 56.26 | 0 | 0 | 56.26 | 0 | 0 | 0 | 0 | 0
2025-10-17 21:00 | 55.17 | 0 | 0 | 55.17 | 0 | 0 | 0 | 0 | 0
2025-10-17 22:00 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 0 | 0 | 0
2025-10-17 23:00 | 50.45 | 0 | 0 | 50.45 | 0 | 0 | 0 | 0 | 0
2025-10-18 | 48.38 | 0 | 0 | 48.38 | 0 | 0 | 0 | 0 | 0
2025-10-18 01:00 | 46.56 | 0 | 0 | 46.56 | 0 | 0 | 0 | 0 | 0
2025-10-18 02:00 | 45.06 | 0 | 0 | 45.06 | 0 | 0 | 0 | 0 | 0
2025-10-18 03:00 | 44.45 | 0 | 0 | 44.45 | 0 | 0 | 0 | 0 | 0
2025-10-18 04:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 0 | 0 | 0
2025-10-18 05:00 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 0 | 0 | 0
2025-10-18 06:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 0 | 0 | 0
2025-10-18 07:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 0 | 0 | 0
2025-10-18 08:00 | 52.76 | 7 | 7 | 45.76 | 0 | 0 | 0 | 0 | 0
2025-10-18 09:00 | 54.01 | 4.68 | 4.68 | 49.33 | 0 | 0 | 0 | 0 | 0
2025-10-18 10:00 | 57.05 | 3.94 | 3.94 | 53.11 | 0 | 0 | 0 | 0 | 0
2025-10-18 11:00 | 59.34 | 11.2 | 11.2 | 48.14 | 0 | 0 | 0 | 0 | 0
2025-10-18 12:00 | 59.77 | 67.57 | 59.77 | 0 | 0 | 0 | 0 | 7.8 | 0
2025-10-18 13:00 | 61.41 | 83.53 | 61.41 | 0 | 0 | 0 | 0 | 22.12 | 0
2025-10-18 14:00 | 61.98 | 92.96 | 61.98 | 0 | 0 | 0 | 0 | 30.97 | 0
2025-10-18 15:00 | 62.17 | 50.53 | 50.53 | 11.64 | 0 | 0 | 0 | 0 | 0
2025-10-18 16:00 | 62.83 | 47.32 | 47.32 | 15.51 | 0 | 0 | 0 | 0 | 0
2025-10-18 17:00 | 61.55 | 0.45 | 0.45 | 61.1 | 0 | 0 | 0 | 0 | 0
2025-10-18 18:00 | 60.31 | 0 | 0 | 60.31 | 0 | 0 | 0 | 0 | 0
2025-10-18 19:00 | 58.77 | 0 | 0 | 58.77 | 0 | 0 | 0 | 0 | 0
2025-10-18 20:00 | 55.46 | 0 | 0 | 55.46 | 0 | 0 | 0 | 0 | 0
2025-10-18 21:00 | 54.74 | 0 | 0 | 54.74 | 0 | 0 | 0 | 0 | 0
2025-10-18 22:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0
2025-10-18 23:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0 | 0 | 0
2025-10-19 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0 | 0 | 0
2025-10-19 01:00 | 46.77 | 0 | 0 | 46.77 | 0 | 0 | 0 | 0 | 0
2025-10-19 02:00 | 45.11 | 0 | 0 | 45.11 | 0 | 0 | 0 | 0 | 0
2025-10-19 03:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0 | 0 | 0
2025-10-19 04:00 | 45.19 | 0 | 0 | 45.19 | 0 | 0 | 0 | 0 | 0
2025-10-19 05:00 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 0 | 0 | 0
2025-10-19 06:00 | 47.04 | 0 | 0 | 47.04 | 0 | 0 | 0 | 0 | 0
2025-10-19 07:00 | 49.57 | 12.74 | 12.74 | 36.83 | 0 | 0 | 0 | 0 | 0
2025-10-19 08:00 | 51.58 | 14.99 | 14.99 | 36.59 | 0 | 0 | 0 | 0 | 0
2025-10-19 09:00 | 53.54 | 54.87 | 53.54 | 0 | 0 | 0 | 0 | 1.33 | 0
2025-10-19 10:00 | 57.01 | 66.98 | 57.01 | 0 | 0 | 0 | 0 | 9.97 | 0
2025-10-19 11:00 | 58.7 | 38.35 | 38.35 | 20.36 | 0 | 0 | 0 | 0 | 0
2025-10-19 12:00 | 60.78 | 27.86 | 27.86 | 32.92 | 0 | 0 | 0 | 0 | 0
2025-10-19 13:00 | 62.29 | 27.99 | 27.99 | 34.31 | 0 | 0 | 0 | 0 | 0
2025-10-19 14:00 | 64.11 | 13.3 | 13.3 | 50.82 | 0 | 0 | 0 | 0 | 0
2025-10-19 15:00 | 63.81 | 6.12 | 6.12 | 57.69 | 0 | 0 | 0 | 0 | 0
2025-10-19 16:00 | 63.54 | 5.28 | 5.28 | 58.25 | 0 | 0 | 0 | 0 | 0
2025-10-19 17:00 | 62.3 | 0 | 0 | 62.3 | 0 | 0 | 0 | 0 | 0
2025-10-19 18:00 | 61.22 | 0 | 0 | 61.22 | 0 | 0 | 0 | 0 | 0
2025-10-19 19:00 | 59.66 | 0 | 0 | 59.66 | 0 | 0 | 0 | 0 | 0
2025-10-19 20:00 | 57 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0
2025-10-19 21:00 | 54.55 | 0 | 0 | 54.55 | 0 | 0 | 0 | 0 | 0
2025-10-19 22:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 0 | 0 | 0
2025-10-19 23:00 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 0 | 0 | 0
2025-10-20 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 0 | 0 | 0
2025-10-20 01:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 0 | 0 | 0
2025-10-20 02:00 | 44.66 | 0 | 0 | 44.66 | 0 | 0 | 0 | 0 | 0
2025-10-20 03:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0 | 0 | 0
2025-10-20 04:00 | 44.09 | 0 | 0 | 44.09 | 0 | 0 | 0 | 0 | 0
2025-10-20 05:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 0 | 0 | 0
2025-10-20 06:00 | 47.37 | 0 | 0 | 47.37 | 0 | 0 | 0 | 0 | 0
2025-10-20 07:00 | 49.56 | 5.55 | 5.55 | 44.01 | 0 | 0 | 0 | 0 | 0
2025-10-20 08:00 | 51.76 | 24.88 | 24.88 | 26.88 | 0 | 0 | 0 | 0 | 0
2025-10-20 09:00 | 55.11 | 25.46 | 25.46 | 29.65 | 0 | 0 | 0 | 0 | 0
2025-10-20 10:00 | 57.93 | 23.04 | 23.04 | 34.89 | 0 | 0 | 0 | 0 | 0
2025-10-20 11:00 | 61.7 | 10.22 | 10.22 | 51.48 | 0 | 0 | 0 | 0 | 0
2025-10-20 12:00 | 63.78 | 15.31 | 15.31 | 48.47 | 0 | 0 | 0 | 0 | 0
2025-10-20 13:00 | 66.35 | 23.97 | 23.97 | 42.38 | 0 | 0 | 0 | 0 | 0
2025-10-20 14:00 | 67.48 | 31.36 | 31.36 | 36.12 | 0 | 0 | 0 | 0 | 0
2025-10-20 15:00 | 67.15 | 20.94 | 20.94 | 46.21 | 0 | 0 | 0 | 0 | 0
2025-10-20 16:00 | 67.33 | 8.59 | 8.59 | 58.74 | 0 | 0 | 0 | 0 | 0
2025-10-20 17:00 | 65.38 | 0 | 0 | 65.38 | 0 | 0 | 0 | 0 | 0
2025-10-20 18:00 | 63.8 | 0 | 0 | 63.8 | 0 | 0 | 0 | 0 | 0
2025-10-20 19:00 | 60.79 | 0 | 0 | 60.79 | 0 | 0 | 0 | 0 | 0
2025-10-20 20:00 | 58.34 | 0 | 0 | 58.34 | 0 | 0 | 0 | 0 | 0
2025-10-20 21:00 | 54.4 | 0 | 0 | 54.4 | 0 | 0 | 0 | 0 | 0
2025-10-20 22:00 | 52.17 | 0 | 0 | 52.17 | 0 | 0 | 0 | 0 | 0
2025-10-20 23:00 | 49.88 | 0 | 0 | 49.88 | 0 | 0 | 0 | 0 | 0
2025-10-21 | 47.51 | 0 | 0 | 47.51 | 0 | 0 | 0 | 0 | 0
2025-10-21 01:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 0 | 0 | 0
2025-10-21 02:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0 | 0 | 0
2025-10-21 03:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0 | 0 | 0
2025-10-21 04:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 0 | 0 | 0
2025-10-21 05:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 0 | 0 | 0
2025-10-21 06:00 | 46.6 | 0 | 0 | 46.6 | 0 | 0 | 0 | 0 | 0
2025-10-21 07:00 | 49.99 | 4.98 | 4.98 | 45.01 | 0 | 0 | 0 | 0 | 0
2025-10-21 08:00 | 50.01 | 19.07 | 19.07 | 30.94 | 0 | 0 | 0 | 0 | 0
2025-10-21 09:00 | 50.6 | 58.02 | 50.6 | 0 | 0 | 0 | 0 | 7.42 | 0
2025-10-21 10:00 | 52.38 | 50.37 | 50.37 | 2 | 0 | 0 | 0 | 0 | 0
2025-10-21 11:00 | 52.08 | 73.81 | 52.08 | 0 | 0 | 0 | 0 | 21.74 | 0
2025-10-21 12:00 | 54.07 | 74.73 | 54.07 | 0 | 0 | 0 | 0 | 20.67 | 0
2025-10-21 13:00 | 54.6 | 80.35 | 54.6 | 0 | 0 | 0 | 0 | 25.74 | 0
2025-10-21 14:00 | 53.84 | 85.91 | 53.84 | 0 | 0 | 0 | 0 | 32.07 | 0
2025-10-21 15:00 | 54.09 | 82.72 | 54.09 | 0 | 0 | 0 | 0 | 28.63 | 0
2025-10-21 16:00 | 54.76 | 42.29 | 42.29 | 12.48 | 0 | 0 | 0 | 0 | 0
2025-10-21 17:00 | 53.32 | 0.29 | 0.29 | 53.03 | 0 | 0 | 0 | 0 | 0
2025-10-21 18:00 | 53.28 | 0 | 0 | 53.28 | 0 | 0 | 0 | 0 | 0
2025-10-21 19:00 | 53.35 | 0 | 0 | 53.35 | 0 | 0 | 0 | 0 | 0
2025-10-21 20:00 | 52.29 | 0 | 0 | 52.29 | 0 | 0 | 0 | 0 | 0
2025-10-21 21:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-10-21 22:00 | 49.52 | 0 | 0 | 49.52 | 0 | 0 | 0 | 0 | 0
2025-10-21 23:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 0 | 0 | 0
2025-10-22 | 46.99 | 0 | 0 | 46.99 | 0 | 0 | 0 | 0 | 0
2025-10-22 01:00 | 45.93 | 0 | 0 | 45.93 | 0 | 0 | 0 | 0 | 0
2025-10-22 02:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 0 | 0 | 0
2025-10-22 03:00 | 44.56 | 0 | 0 | 44.56 | 0 | 0 | 0 | 0 | 0
2025-10-22 04:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 0 | 0 | 0
2025-10-22 05:00 | 45.9 | 0 | 0 | 45.9 | 0 | 0 | 0 | 0 | 0
2025-10-22 06:00 | 46.9 | 0 | 0 | 46.9 | 0 | 0 | 0 | 0 | 0
2025-10-22 07:00 | 48.81 | 20.67 | 20.67 | 28.13 | 0 | 0 | 0 | 0 | 0
2025-10-22 08:00 | 51.52 | 77.87 | 51.52 | 0 | 0 | 0 | 0 | 26.36 | 0
2025-10-22 09:00 | 52.87 | 85.15 | 52.87 | 0 | 0 | 0 | 0 | 32.28 | 0
2025-10-22 10:00 | 56.11 | 64.39 | 56.11 | 0 | 0 | 0 | 0 | 8.29 | 0
2025-10-22 11:00 | 58.19 | 55.36 | 55.36 | 2.83 | 0 | 0 | 0 | 0 | 0
2025-10-22 12:00 | 59.57 | 54.45 | 54.45 | 5.12 | 0 | 0 | 0 | 0 | 0
2025-10-22 13:00 | 60.02 | 68.98 | 60.02 | 0 | 0 | 0 | 0 | 8.96 | 0
2025-10-22 14:00 | 60.24 | 29.66 | 29.66 | 30.58 | 0 | 0 | 0 | 0 | 0
2025-10-22 15:00 | 62.15 | 13.13 | 13.13 | 49.02 | 0 | 0 | 0 | 0 | 0
2025-10-22 16:00 | 61.39 | 6.26 | 6.26 | 55.13 | 0 | 0 | 0 | 0 | 0
2025-10-22 17:00 | 60.14 | 0 | 0 | 60.14 | 0 | 0 | 0 | 0 | 0
2025-10-22 18:00 | 59.78 | 0 | 0 | 59.78 | 0 | 0 | 0 | 0 | 0
2025-10-22 19:00 | 57.04 | 0 | 0 | 57.04 | 0 | 0 | 0 | 0 | 0
2025-10-22 20:00 | 55.22 | 0 | 0 | 55.22 | 0 | 0 | 0 | 0 | 0
2025-10-22 21:00 | 53.49 | 0 | 0 | 53.49 | 0 | 0 | 0 | 0 | 0
2025-10-22 22:00 | 50.44 | 0 | 0 | 50.44 | 0 | 0 | 0 | 0 | 0
2025-10-22 23:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0 | 0 | 0
2025-10-23 | 47.48 | 0 | 0 | 47.48 | 0 | 0 | 0 | 0 | 0
2025-10-23 01:00 | 45.62 | 0 | 0 | 45.62 | 0 | 0 | 0 | 0 | 0
2025-10-23 02:00 | 45.25 | 0 | 0 | 45.25 | 0 | 0 | 0 | 0 | 0
2025-10-23 03:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0 | 0 | 0
2025-10-23 04:00 | 44.63 | 0 | 0 | 44.63 | 0 | 0 | 0 | 0 | 0
2025-10-23 05:00 | 44.35 | 0 | 0 | 44.35 | 0 | 0 | 0 | 0 | 0
2025-10-23 06:00 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 0 | 0 | 0
2025-10-23 07:00 | 49.18 | 3.71 | 3.71 | 45.47 | 0 | 0 | 0 | 0 | 0
2025-10-23 08:00 | 50.2 | 19.2 | 19.2 | 31 | 0 | 0 | 0 | 0 | 0
2025-10-23 09:00 | 53.17 | 26.12 | 26.12 | 27.05 | 0 | 0 | 0 | 0 | 0
2025-10-23 10:00 | 55.88 | 33.24 | 33.24 | 22.64 | 0 | 0 | 0 | 0 | 0
2025-10-23 11:00 | 58.68 | 43.89 | 43.89 | 14.79 | 0 | 0 | 0 | 0 | 0
2025-10-23 12:00 | 59.59 | 47 | 47 | 12.58 | 0 | 0 | 0 | 0 | 0
2025-10-23 13:00 | 61.04 | 29.48 | 29.48 | 31.56 | 0 | 0 | 0 | 0 | 0
2025-10-23 14:00 | 62.28 | 21.67 | 21.67 | 40.61 | 0 | 0 | 0 | 0 | 0
2025-10-23 15:00 | 62.8 | 7.56 | 7.56 | 55.24 | 0 | 0 | 0 | 0 | 0
2025-10-23 16:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 0 | 0 | 0
2025-10-23 17:00 | 61.89 | 0 | 0 | 61.89 | 0 | 0 | 0 | 0 | 0
2025-10-23 18:00 | 59.48 | 0 | 0 | 59.48 | 0 | 0 | 0 | 0 | 0
2025-10-23 19:00 | 58 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0
2025-10-23 20:00 | 55.94 | 0 | 0 | 55.94 | 0 | 0 | 0 | 0 | 0
2025-10-23 21:00 | 53.14 | 0 | 0 | 53.14 | 0 | 0 | 0 | 0 | 0
2025-10-23 22:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0 | 0 | 0
2025-10-23 23:00 | 48.87 | 0 | 0 | 48.87 | 0 | 0 | 0 | 0 | 0
2025-10-24 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 0 | 0 | 0
2025-10-24 01:00 | 45.48 | 0 | 0 | 45.48 | 0 | 0 | 0 | 0 | 0
2025-10-24 02:00 | 44.69 | 0 | 0 | 44.69 | 0 | 0 | 0 | 0 | 0
2025-10-24 03:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 0 | 0 | 0
2025-10-24 04:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0 | 0 | 0
2025-10-24 05:00 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 0 | 0 | 0
2025-10-24 06:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 0 | 0 | 0
2025-10-24 07:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 0 | 0 | 0
2025-10-24 08:00 | 50.92 | 10.36 | 10.36 | 40.56 | 0 | 0 | 0 | 0 | 0
2025-10-24 09:00 | 52.02 | 18.85 | 18.85 | 33.16 | 0 | 0 | 0 | 0 | 0
2025-10-24 10:00 | 55.33 | 8.08 | 8.08 | 47.25 | 0 | 0 | 0 | 0 | 0
2025-10-24 11:00 | 58.36 | 4.44 | 4.44 | 53.93 | 0 | 0 | 0 | 0 | 0
2025-10-24 12:00 | 59.79 | 11.03 | 11.03 | 48.77 | 0 | 0 | 0 | 0 | 0
2025-10-24 13:00 | 61.44 | 79.97 | 61.44 | 0 | 0 | 0 | 0 | 18.53 | 0
2025-10-24 14:00 | 60.84 | 59.12 | 59.12 | 1.73 | 0 | 0 | 0 | 0 | 0
2025-10-24 15:00 | 62.48 | 32.51 | 32.51 | 29.98 | 0 | 0 | 0 | 0 | 0
2025-10-24 16:00 | 62.52 | 32.38 | 32.38 | 30.14 | 0 | 0 | 0 | 0 | 0
2025-10-24 17:00 | 61.62 | 0 | 0 | 61.62 | 0 | 0 | 0 | 0 | 0
2025-10-24 18:00 | 60.34 | 0 | 0 | 60.34 | 0 | 0 | 0 | 0 | 0
2025-10-24 19:00 | 57.78 | 0 | 0 | 57.78 | 0 | 0 | 0 | 0 | 0
2025-10-24 20:00 | 55.53 | 0 | 0 | 55.53 | 0 | 0 | 0 | 0 | 0
2025-10-24 21:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 0 | 0 | 0
2025-10-24 22:00 | 50.73 | 0 | 0 | 50.73 | 0 | 0 | 0 | 0 | 0
2025-10-24 23:00 | 48.01 | 0 | 0 | 48.01 | 0 | 0 | 0 | 0 | 0
2025-10-25 | 45.66 | 0 | 0 | 45.66 | 0 | 0 | 0 | 0 | 0
2025-10-25 01:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0 | 0 | 0
2025-10-25 02:00 | 45.12 | 0 | 0 | 45.12 | 0 | 0 | 0 | 0 | 0
2025-10-25 03:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 0 | 0 | 0
2025-10-25 04:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 0 | 0 | 0
2025-10-25 05:00 | 44.97 | 0 | 0 | 44.97 | 0 | 0 | 0 | 0 | 0
2025-10-25 06:00 | 45.69 | 0 | 0 | 45.69 | 0 | 0 | 0 | 0 | 0
2025-10-25 07:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 0 | 0 | 0
2025-10-25 08:00 | 49.26 | 7.75 | 7.75 | 41.5 | 0 | 0 | 0 | 0 | 0
2025-10-25 09:00 | 52.18 | 41.01 | 41.01 | 11.17 | 0 | 0 | 0 | 0 | 0
2025-10-25 10:00 | 54.51 | 38.7 | 38.7 | 15.81 | 0 | 0 | 0 | 0 | 0
2025-10-25 11:00 | 56.55 | 38.68 | 38.68 | 17.87 | 0 | 0 | 0 | 0 | 0
2025-10-25 12:00 | 57.68 | 33.97 | 33.97 | 23.71 | 0 | 0 | 0 | 0 | 0
2025-10-25 13:00 | 58.34 | 33.76 | 33.76 | 24.58 | 0 | 0 | 0 | 0 | 0
2025-10-25 14:00 | 59.61 | 13.37 | 13.37 | 46.24 | 0 | 0 | 0 | 0 | 0
2025-10-25 15:00 | 59.89 | 1.43 | 1.43 | 58.46 | 0 | 0 | 0 | 0 | 0
2025-10-25 16:00 | 59.62 | 1.86 | 1.86 | 57.77 | 0 | 0 | 0 | 0 | 0
2025-10-25 17:00 | 59.74 | 0 | 0 | 59.74 | 0 | 0 | 0 | 0 | 0
2025-10-25 18:00 | 57.43 | 0 | 0 | 57.43 | 0 | 0 | 0 | 0 | 0
2025-10-25 19:00 | 56.59 | 0 | 0 | 56.59 | 0 | 0 | 0 | 0 | 0
2025-10-25 20:00 | 54.62 | 0 | 0 | 54.62 | 0 | 0 | 0 | 0 | 0
2025-10-25 21:00 | 52.94 | 0 | 0 | 52.94 | 0 | 0 | 0 | 0 | 0
2025-10-25 22:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0 | 0 | 0
2025-10-25 23:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 0 | 0 | 0
2025-10-26 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 0 | 0 | 0
2025-10-26 01:00 | 45.28 | 0 | 0 | 45.28 | 0 | 0 | 0 | 0 | 0
2025-10-26 02:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0 | 0 | 0
2025-10-26 03:00 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 0 | 0 | 0
2025-10-26 04:00 | 44.42 | 0 | 0 | 44.42 | 0 | 0 | 0 | 0 | 0
2025-10-26 05:00 | 45.28 | 0 | 0 | 45.28 | 0 | 0 | 0 | 0 | 0
2025-10-26 06:00 | 46.58 | 0 | 0 | 46.58 | 0 | 0 | 0 | 0 | 0
2025-10-26 07:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0 | 0 | 0
2025-10-26 08:00 | 50.3 | 1.08 | 1.08 | 49.22 | 0 | 0 | 0 | 0 | 0
2025-10-26 09:00 | 50.94 | 2.57 | 2.57 | 48.37 | 0 | 0 | 0 | 0 | 0
2025-10-26 10:00 | 52.81 | 82.06 | 52.81 | 0 | 0 | 0 | 0 | 29.25 | 0
2025-10-26 11:00 | 54.06 | 78.47 | 54.06 | 0 | 0 | 0 | 0 | 24.41 | 0
2025-10-26 12:00 | 55.5 | 76.59 | 55.5 | 0 | 0 | 0 | 0 | 21.09 | 0
2025-10-26 13:00 | 55.08 | 83.42 | 55.08 | 0 | 0 | 0 | 0 | 28.34 | 0
2025-10-26 14:00 | 55.25 | 91.5 | 55.25 | 0 | 0 | 0 | 0 | 36.25 | 0
2025-10-26 15:00 | 54.94 | 92.98 | 54.94 | 0 | 0 | 0 | 0 | 38.04 | 0
2025-10-26 16:00 | 56.35 | 42.52 | 42.52 | 13.83 | 0 | 0 | 0 | 0 | 0
2025-10-26 17:00 | 55.45 | 0 | 0 | 55.45 | 0 | 0 | 0 | 0 | 0
2025-10-26 18:00 | 54.87 | 0 | 0 | 54.87 | 0 | 0 | 0 | 0 | 0
2025-10-26 19:00 | 55.32 | 0 | 0 | 55.32 | 0 | 0 | 0 | 0 | 0
2025-10-26 20:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 0 | 0 | 0
2025-10-26 21:00 | 50.52 | 0 | 0 | 50.52 | 0 | 0 | 0 | 0 | 0
2025-10-26 22:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 0 | 0 | 0
2025-10-26 23:00 | 47.41 | 0 | 0 | 47.41 | 0 | 0 | 0 | 0 | 0
2025-10-27 | 46.12 | 0 | 0 | 46.12 | 0 | 0 | 0 | 0 | 0
2025-10-27 01:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 0 | 0 | 0
2025-10-27 02:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 0 | 0 | 0
2025-10-27 03:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 0 | 0 | 0
2025-10-27 04:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0 | 0 | 0
2025-10-27 05:00 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 0 | 0 | 0
2025-10-27 06:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 0 | 0 | 0
2025-10-27 07:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 0 | 0 | 0
2025-10-27 08:00 | 50.48 | 5.14 | 5.14 | 45.34 | 0 | 0 | 0 | 0 | 0
2025-10-27 09:00 | 52.69 | 2.6 | 2.6 | 50.09 | 0 | 0 | 0 | 0 | 0
2025-10-27 10:00 | 55.24 | 3.9 | 3.9 | 51.34 | 0 | 0 | 0 | 0 | 0
2025-10-27 11:00 | 57.18 | 4.67 | 4.67 | 52.51 | 0 | 0 | 0 | 0 | 0
2025-10-27 12:00 | 59.38 | 4.78 | 4.78 | 54.6 | 0 | 0 | 0 | 0 | 0
2025-10-27 13:00 | 60.91 | 68.43 | 60.91 | 0 | 0 | 0 | 0 | 7.52 | 0
2025-10-27 14:00 | 61.56 | 93.64 | 61.56 | 0 | 0 | 0 | 0 | 32.08 | 0
2025-10-27 15:00 | 61.69 | 96.07 | 61.69 | 0 | 0 | 0 | 0 | 34.38 | 0
2025-10-27 16:00 | 62.24 | 43.22 | 43.22 | 19.02 | 0 | 0 | 0 | 0 | 0
2025-10-27 17:00 | 60.3 | 0 | 0 | 60.3 | 0 | 0 | 0 | 0 | 0
2025-10-27 18:00 | 59.24 | 0 | 0 | 59.24 | 0 | 0 | 0 | 0 | 0
2025-10-27 19:00 | 57.32 | 0 | 0 | 57.32 | 0 | 0 | 0 | 0 | 0
2025-10-27 20:00 | 54.6 | 0 | 0 | 54.6 | 0 | 0 | 0 | 0 | 0
2025-10-27 21:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 0 | 0 | 0
2025-10-27 22:00 | 50.07 | 0 | 0 | 50.07 | 0 | 0 | 0 | 0 | 0
2025-10-27 23:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 0 | 0 | 0
2025-10-28 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 0 | 0 | 0
2025-10-28 01:00 | 44.51 | 0 | 0 | 44.51 | 0 | 0 | 0 | 0 | 0
2025-10-28 02:00 | 44.1 | 0 | 0 | 44.1 | 0 | 0 | 0 | 0 | 0
2025-10-28 03:00 | 44.32 | 0 | 0 | 44.32 | 0 | 0 | 0 | 0 | 0
2025-10-28 04:00 | 44.25 | 0 | 0 | 44.25 | 0 | 0 | 0 | 0 | 0
2025-10-28 05:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0 | 0 | 0
2025-10-28 06:00 | 46.58 | 0 | 0 | 46.58 | 0 | 0 | 0 | 0 | 0
2025-10-28 07:00 | 47.93 | 10.22 | 10.22 | 37.71 | 0 | 0 | 0 | 0 | 0
2025-10-28 08:00 | 50.85 | 88.4 | 50.85 | 0 | 0 | 0 | 0 | 37.54 | 0
2025-10-28 09:00 | 53.38 | 92.23 | 53.38 | 0 | 0 | 0 | 0 | 38.85 | 0
2025-10-28 10:00 | 56.23 | 83.94 | 56.23 | 0 | 0 | 0 | 0 | 27.71 | 0
2025-10-28 11:00 | 59.17 | 74.88 | 59.17 | 0 | 0 | 0 | 0 | 15.71 | 0
2025-10-28 12:00 | 61.82 | 72.43 | 61.82 | 0 | 0 | 0 | 0 | 10.62 | 0
2025-10-28 13:00 | 64.58 | 79.01 | 64.58 | 0 | 0 | 0 | 0 | 14.43 | 0
2025-10-28 14:00 | 65.24 | 86.72 | 65.24 | 0 | 0 | 0 | 0 | 21.49 | 0
2025-10-28 15:00 | 66.25 | 85.97 | 66.25 | 0 | 0 | 0 | 0 | 19.72 | 0
2025-10-28 16:00 | 65.72 | 34.71 | 34.71 | 31.01 | 0 | 0 | 0 | 0 | 0
2025-10-28 17:00 | 64.24 | 0 | 0 | 64.24 | 0 | 0 | 0 | 0 | 0
2025-10-28 18:00 | 60.94 | 0 | 0 | 60.94 | 0 | 0 | 0 | 0 | 0
2025-10-28 19:00 | 59.78 | 0 | 0 | 59.78 | 0 | 0 | 0 | 0 | 0
2025-10-28 20:00 | 56.1 | 0 | 0 | 56.1 | 0 | 0 | 0 | 0 | 0
2025-10-28 21:00 | 53.75 | 0 | 0 | 53.75 | 0 | 0 | 0 | 0 | 0
2025-10-28 22:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0 | 0 | 0
2025-10-28 23:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0 | 0 | 0
2025-10-29 | 46.88 | 0 | 0 | 46.88 | 0 | 0 | 0 | 0 | 0
2025-10-29 01:00 | 44.17 | 0 | 0 | 44.17 | 0 | 0 | 0 | 0 | 0
2025-10-29 02:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 0 | 0 | 0
2025-10-29 03:00 | 43.61 | 0 | 0 | 43.61 | 0 | 0 | 0 | 0 | 0
2025-10-29 04:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 0 | 0 | 0
2025-10-29 05:00 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 0 | 0 | 0
2025-10-29 06:00 | 45.24 | 0 | 0 | 45.24 | 0 | 0 | 0 | 0 | 0
2025-10-29 07:00 | 47.41 | 0 | 0 | 47.41 | 0 | 0 | 0 | 0 | 0
2025-10-29 08:00 | 48.54 | 2.51 | 2.51 | 46.03 | 0 | 0 | 0 | 0 | 0
2025-10-29 09:00 | 50.52 | 5.53 | 5.53 | 44.99 | 0 | 0 | 0 | 0 | 0
2025-10-29 10:00 | 52.66 | 8.27 | 8.27 | 44.39 | 0 | 0 | 0 | 0 | 0
2025-10-29 11:00 | 53.56 | 8.93 | 8.93 | 44.64 | 0 | 0 | 0 | 0 | 0
2025-10-29 12:00 | 53.65 | 10.16 | 10.16 | 43.49 | 0 | 0 | 0 | 0 | 0
2025-10-29 13:00 | 55.49 | 9.15 | 9.15 | 46.34 | 0 | 0 | 0 | 0 | 0
2025-10-29 14:00 | 55.45 | 6.65 | 6.65 | 48.8 | 0 | 0 | 0 | 0 | 0
2025-10-29 15:00 | 55.31 | 3.73 | 3.73 | 51.58 | 0 | 0 | 0 | 0 | 0
2025-10-29 16:00 | 55.83 | 0.22 | 0.22 | 55.61 | 0 | 0 | 0 | 0 | 0
2025-10-29 17:00 | 54.98 | 0 | 0 | 54.98 | 0 | 0 | 0 | 0 | 0
2025-10-29 18:00 | 53.81 | 0 | 0 | 53.81 | 0 | 0 | 0 | 0 | 0
2025-10-29 19:00 | 54.36 | 0 | 0 | 54.36 | 0 | 0 | 0 | 0 | 0
2025-10-29 20:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0 | 0 | 0
2025-10-29 21:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 0 | 0 | 0
2025-10-29 22:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 0 | 0 | 0
2025-10-29 23:00 | 48.01 | 0 | 0 | 48.01 | 0 | 0 | 0 | 0 | 0
2025-10-30 | 45.62 | 0 | 0 | 45.62 | 0 | 0 | 0 | 0 | 0
2025-10-30 01:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 0 | 0 | 0
2025-10-30 02:00 | 43.37 | 0 | 0 | 43.37 | 0 | 0 | 0 | 0 | 0
2025-10-30 03:00 | 44.09 | 0 | 0 | 44.09 | 0 | 0 | 0 | 0 | 0
2025-10-30 04:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 0 | 0 | 0
2025-10-30 05:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 0 | 0 | 0
2025-10-30 06:00 | 46.57 | 0 | 0 | 46.57 | 0 | 0 | 0 | 0 | 0
2025-10-30 07:00 | 48.07 | 9.33 | 9.33 | 38.74 | 0 | 0 | 0 | 0 | 0
2025-10-30 08:00 | 49.73 | 81.6 | 49.73 | 0 | 0 | 0 | 0 | 31.87 | 0
2025-10-30 09:00 | 52.2 | 87.08 | 52.2 | 0 | 0 | 0 | 0 | 34.88 | 0
2025-10-30 10:00 | 54.94 | 76.26 | 54.94 | 0 | 0 | 0 | 0 | 21.32 | 0
2025-10-30 11:00 | 56.77 | 69.35 | 56.77 | 0 | 0 | 0 | 0 | 12.59 | 0
2025-10-30 12:00 | 59.31 | 65.61 | 59.31 | 0 | 0 | 0 | 0 | 6.3 | 0
2025-10-30 13:00 | 61.13 | 72.31 | 61.13 | 0 | 0 | 0 | 0 | 11.18 | 0
2025-10-30 14:00 | 61.2 | 77.98 | 61.2 | 0 | 0 | 0 | 0 | 16.79 | 0
2025-10-30 15:00 | 62.32 | 74.05 | 62.32 | 0 | 0 | 0 | 0 | 11.73 | 0
2025-10-30 16:00 | 61.89 | 25.5 | 25.5 | 36.39 | 0 | 0 | 0 | 0 | 0
2025-10-30 17:00 | 61.49 | 0 | 0 | 61.49 | 0 | 0 | 0 | 0 | 0
2025-10-30 18:00 | 58.39 | 0 | 0 | 58.39 | 0 | 0 | 0 | 0 | 0
2025-10-30 19:00 | 56.99 | 0 | 0 | 56.99 | 0 | 0 | 0 | 0 | 0
2025-10-30 20:00 | 54.54 | 0 | 0 | 54.54 | 0 | 0 | 0 | 0 | 0
2025-10-30 21:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 0 | 0 | 0
2025-10-30 22:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 0 | 0 | 0
2025-10-30 23:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 0 | 0 | 0
2025-10-31 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 0 | 0 | 0
2025-10-31 01:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0 | 0 | 0
2025-10-31 02:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0 | 0 | 0
2025-10-31 03:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0 | 0 | 0
2025-10-31 04:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0
2025-10-31 05:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 0 | 0 | 0
2025-10-31 06:00 | 45.24 | 0 | 0 | 45.24 | 0 | 0 | 0 | 0 | 0
2025-10-31 07:00 | 47.53 | 7.4 | 7.4 | 40.12 | 0 | 0 | 0 | 0 | 0
2025-10-31 08:00 | 49.8 | 73.86 | 49.8 | 0 | 0 | 0 | 0 | 24.06 | 0
2025-10-31 09:00 | 50.08 | 83.02 | 50.08 | 0 | 0 | 0 | 0 | 32.94 | 0
2025-10-31 10:00 | 53.83 | 77.12 | 53.83 | 0 | 0 | 0 | 0 | 23.29 | 0
2025-10-31 11:00 | 54.87 | 69.56 | 54.87 | 0 | 0 | 0 | 0 | 14.69 | 0
2025-10-31 12:00 | 55.52 | 67.55 | 55.52 | 0 | 0 | 0 | 0 | 12.03 | 0
2025-10-31 13:00 | 56.12 | 71.26 | 56.12 | 0 | 0 | 0 | 0 | 15.14 | 0
2025-10-31 14:00 | 57.57 | 77.76 | 57.57 | 0 | 0 | 0 | 0 | 20.19 | 0
2025-10-31 15:00 | 58.57 | 71.61 | 58.57 | 0 | 0 | 0 | 0 | 13.04 | 0
2025-10-31 16:00 | 58.3 | 24.32 | 24.32 | 33.98 | 0 | 0 | 0 | 0 | 0
2025-10-31 17:00 | 57.93 | 0 | 0 | 57.93 | 0 | 0 | 0 | 0 | 0
2025-10-31 18:00 | 56.19 | 0 | 0 | 56.19 | 0 | 0 | 0 | 0 | 0
2025-10-31 19:00 | 54.39 | 0 | 0 | 54.39 | 0 | 0 | 0 | 0 | 0
2025-10-31 20:00 | 52.93 | 0 | 0 | 52.93 | 0 | 0 | 0 | 0 | 0
2025-10-31 21:00 | 51.2 | 0 | 0 | 51.2 | 0 | 0 | 0 | 0 | 0
2025-10-31 22:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 0 | 0 | 0
2025-10-31 23:00 | 46.9 | 0 | 0 | 46.9 | 0 | 0 | 0 | 0 | 0
2025-11-01 | 45.97 | 0 | 0 | 45.97 | 0 | 0 | 0 | 0 | 0
2025-11-01 01:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 0 | 0 | 0
2025-11-01 02:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 0 | 0 | 0
2025-11-01 03:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 0 | 0 | 0
2025-11-01 04:00 | 43.98 | 0 | 0 | 43.98 | 0 | 0 | 0 | 0 | 0
2025-11-01 05:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0 | 0 | 0
2025-11-01 06:00 | 45.17 | 0 | 0 | 45.17 | 0 | 0 | 0 | 0 | 0
2025-11-01 07:00 | 47.64 | 8.66 | 8.66 | 38.98 | 0 | 0 | 0 | 0 | 0
2025-11-01 08:00 | 50.17 | 78.96 | 50.17 | 0 | 0 | 0 | 0 | 28.79 | 0
2025-11-01 09:00 | 51.26 | 84.54 | 51.26 | 0 | 0 | 0 | 0 | 33.28 | 0
2025-11-01 10:00 | 53.82 | 75.31 | 53.82 | 0 | 0 | 0 | 0 | 21.48 | 0
2025-11-01 11:00 | 55.63 | 66.36 | 55.63 | 0 | 0 | 0 | 0 | 10.73 | 0
2025-11-01 12:00 | 56.44 | 64.83 | 56.44 | 0 | 0 | 0 | 0 | 8.38 | 0
2025-11-01 13:00 | 58.01 | 72.9 | 58.01 | 0 | 0 | 0 | 0 | 14.89 | 0
2025-11-01 14:00 | 58.14 | 81.99 | 58.14 | 0 | 0 | 0 | 0 | 23.85 | 0
2025-11-01 15:00 | 58.95 | 81.75 | 58.95 | 0 | 0 | 0 | 0 | 22.8 | 0
2025-11-01 16:00 | 58.47 | 25.92 | 25.92 | 32.55 | 0 | 0 | 0 | 0 | 0
2025-11-01 17:00 | 57.8 | 0 | 0 | 57.8 | 0 | 0 | 0 | 0 | 0
2025-11-01 18:00 | 56.37 | 0 | 0 | 56.37 | 0 | 0 | 0 | 0 | 0
2025-11-01 19:00 | 54.97 | 0 | 0 | 54.97 | 0 | 0 | 0 | 0 | 0
2025-11-01 20:00 | 53.47 | 0 | 0 | 53.47 | 0 | 0 | 0 | 0 | 0
2025-11-01 21:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 0 | 0 | 0
2025-11-01 22:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0 | 0 | 0
2025-11-01 23:00 | 46.8 | 0 | 0 | 46.8 | 0 | 0 | 0 | 0 | 0
2025-11-02 | 44.54 | 0 | 0 | 44.54 | 0 | 0 | 0 | 0 | 0
2025-11-02 01:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 0 | 0 | 0
2025-11-02 02:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0 | 0 | 0
2025-11-02 03:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0 | 0 | 0
2025-11-02 04:00 | 42.92 | 0 | 0 | 42.92 | 0 | 0 | 0 | 0 | 0
2025-11-02 05:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 0 | 0 | 0
2025-11-02 06:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 0 | 0 | 0
2025-11-02 07:00 | 46.25 | 13.05 | 13.05 | 33.2 | 0 | 0 | 0 | 0 | 0
2025-11-02 08:00 | 48.88 | 92.32 | 48.88 | 0 | 0 | 0 | 0 | 43.44 | 0
2025-11-02 09:00 | 50.64 | 97.09 | 50.64 | 0 | 0 | 0 | 0 | 46.45 | 0
2025-11-02 10:00 | 52.32 | 88.73 | 52.32 | 0 | 0 | 0 | 0 | 36.42 | 0
2025-11-02 11:00 | 52.95 | 77.86 | 52.95 | 0 | 0 | 0 | 0 | 24.91 | 0
2025-11-02 12:00 | 54.99 | 16.46 | 16.46 | 38.53 | 0 | 0 | 0 | 0 | 0
2025-11-02 13:00 | 54.99 | 42.96 | 42.96 | 12.03 | 0 | 0 | 0 | 0 | 0
2025-11-02 14:00 | 56.07 | 34.96 | 34.96 | 21.11 | 0 | 0 | 0 | 0 | 0
2025-11-02 15:00 | 55.65 | 1.17 | 1.17 | 54.48 | 0 | 0 | 0 | 0 | 0
2025-11-02 16:00 | 55.63 | 0 | 0 | 55.63 | 0 | 0 | 0 | 0 | 0
2025-11-02 17:00 | 54.02 | 0 | 0 | 54.02 | 0 | 0 | 0 | 0 | 0
2025-11-02 18:00 | 54.25 | 0 | 0 | 54.25 | 0 | 0 | 0 | 0 | 0
2025-11-02 19:00 | 53.3 | 0 | 0 | 53.3 | 0 | 0 | 0 | 0 | 0
2025-11-02 20:00 | 51.64 | 0 | 0 | 51.64 | 0 | 0 | 0 | 0 | 0
2025-11-02 21:00 | 51.1 | 0 | 0 | 51.1 | 0 | 0 | 0 | 0 | 0
2025-11-02 22:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 0 | 0 | 0
2025-11-02 23:00 | 46.54 | 0 | 0 | 46.54 | 0 | 0 | 0 | 0 | 0
2025-11-03 | 44.74 | 0 | 0 | 44.74 | 0 | 0 | 0 | 0 | 0
2025-11-03 01:00 | 43.68 | 0 | 0 | 43.68 | 0 | 0 | 0 | 0 | 0
2025-11-03 02:00 | 43.7 | 0 | 0 | 43.7 | 0 | 0 | 0 | 0 | 0
2025-11-03 03:00 | 43.65 | 0 | 0 | 43.65 | 0 | 0 | 0 | 0 | 0
2025-11-03 04:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 0 | 0 | 0
2025-11-03 05:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0 | 0 | 0
2025-11-03 06:00 | 44.61 | 0 | 0 | 44.61 | 0 | 0 | 0 | 0 | 0
2025-11-03 07:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0 | 0 | 0
2025-11-03 08:00 | 49.16 | 0.9 | 0.9 | 48.26 | 0 | 0 | 0 | 0 | 0
2025-11-03 09:00 | 50.47 | 2.13 | 2.13 | 48.34 | 0 | 0 | 0 | 0 | 0
2025-11-03 10:00 | 51.72 | 3.34 | 3.34 | 48.37 | 0 | 0 | 0 | 0 | 0
2025-11-03 11:00 | 53.5 | 4.62 | 4.62 | 48.88 | 0 | 0 | 0 | 0 | 0
2025-11-03 12:00 | 55.7 | 5.43 | 5.43 | 50.27 | 0 | 0 | 0 | 0 | 0
2025-11-03 13:00 | 57 | 53.1 | 53.1 | 3.9 | 0 | 0 | 0 | 0 | 0
2025-11-03 14:00 | 56.39 | 55.58 | 55.58 | 0.81 | 0 | 0 | 0 | 0 | 0
2025-11-03 15:00 | 57.5 | 52.71 | 52.71 | 4.78 | 0 | 0 | 0 | 0 | 0
2025-11-03 16:00 | 58.23 | 17.33 | 17.33 | 40.91 | 0 | 0 | 0 | 0 | 0
2025-11-03 17:00 | 56.62 | 0 | 0 | 56.62 | 0 | 0 | 0 | 0 | 0
2025-11-03 18:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 0 | 0 | 0
2025-11-03 19:00 | 54.48 | 0 | 0 | 54.48 | 0 | 0 | 0 | 0 | 0
2025-11-03 20:00 | 51.87 | 0 | 0 | 51.87 | 0 | 0 | 0 | 0 | 0
2025-11-03 21:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 0 | 0 | 0
2025-11-03 22:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 0 | 0 | 0
2025-11-03 23:00 | 46.3 | 0 | 0 | 46.3 | 0 | 0 | 0 | 0 | 0
2025-11-04 | 44.65 | 0 | 0 | 44.65 | 0 | 0 | 0 | 0 | 0
2025-11-04 01:00 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 0 | 0 | 0
2025-11-04 02:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 0 | 0 | 0
2025-11-04 03:00 | 43.33 | 0 | 0 | 43.33 | 0 | 0 | 0 | 0 | 0
2025-11-04 04:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 0 | 0 | 0
2025-11-04 05:00 | 43.83 | 0 | 0 | 43.83 | 0 | 0 | 0 | 0 | 0
2025-11-04 06:00 | 45.42 | 0 | 0 | 45.42 | 0 | 0 | 0 | 0 | 0
2025-11-04 07:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0 | 0 | 0
2025-11-04 08:00 | 49.32 | 5.42 | 5.42 | 43.89 | 0 | 0 | 0 | 0 | 0
2025-11-04 09:00 | 50.42 | 10.87 | 10.87 | 39.55 | 0 | 0 | 0 | 0 | 0
2025-11-04 10:00 | 54.2 | 16.98 | 16.98 | 37.22 | 0 | 0 | 0 | 0 | 0
2025-11-04 11:00 | 55.22 | 16.53 | 16.53 | 38.7 | 0 | 0 | 0 | 0 | 0
2025-11-04 12:00 | 58.55 | 16.47 | 16.47 | 42.08 | 0 | 0 | 0 | 0 | 0
2025-11-04 13:00 | 60.84 | 13.74 | 13.74 | 47.1 | 0 | 0 | 0 | 0 | 0
2025-11-04 14:00 | 61.85 | 12.16 | 12.16 | 49.69 | 0 | 0 | 0 | 0 | 0
2025-11-04 15:00 | 61.27 | 4.95 | 4.95 | 56.32 | 0 | 0 | 0 | 0 | 0
2025-11-04 16:00 | 60.95 | 0.5 | 0.5 | 60.45 | 0 | 0 | 0 | 0 | 0
2025-11-04 17:00 | 60.07 | 0 | 0 | 60.07 | 0 | 0 | 0 | 0 | 0
2025-11-04 18:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 0 | 0 | 0
2025-11-04 19:00 | 55.44 | 0 | 0 | 55.44 | 0 | 0 | 0 | 0 | 0
2025-11-04 20:00 | 53.98 | 0 | 0 | 53.98 | 0 | 0 | 0 | 0 | 0
2025-11-04 21:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0
2025-11-04 22:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 0 | 0 | 0
2025-11-04 23:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 0 | 0 | 0
2025-11-05 | 45.05 | 0 | 0 | 45.05 | 0 | 0 | 0 | 0 | 0
2025-11-05 01:00 | 43.42 | 0 | 0 | 43.42 | 0 | 0 | 0 | 0 | 0
2025-11-05 02:00 | 41.95 | 0 | 0 | 41.95 | 0 | 0 | 0 | 0 | 0
2025-11-05 03:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 0 | 0 | 0
2025-11-05 04:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0 | 0 | 0
2025-11-05 05:00 | 43.4 | 0 | 0 | 43.4 | 0 | 0 | 0 | 0 | 0
2025-11-05 06:00 | 45.18 | 0 | 0 | 45.18 | 0 | 0 | 0 | 0 | 0
2025-11-05 07:00 | 47.3 | 0 | 0 | 47.3 | 0 | 0 | 0 | 0 | 0
2025-11-05 08:00 | 48.54 | 1.4 | 1.4 | 47.14 | 0 | 0 | 0 | 0 | 0
2025-11-05 09:00 | 51 | 3.46 | 3.46 | 47.54 | 0 | 0 | 0 | 0 | 0
2025-11-05 10:00 | 52.22 | 5.29 | 5.29 | 46.93 | 0 | 0 | 0 | 0 | 0
2025-11-05 11:00 | 55.18 | 6.75 | 6.75 | 48.43 | 0 | 0 | 0 | 0 | 0
2025-11-05 12:00 | 56.88 | 6.83 | 6.83 | 50.05 | 0 | 0 | 0 | 0 | 0
2025-11-05 13:00 | 58.97 | 6.08 | 6.08 | 52.89 | 0 | 0 | 0 | 0 | 0
2025-11-05 14:00 | 59 | 4.48 | 4.48 | 54.52 | 0 | 0 | 0 | 0 | 0
2025-11-05 15:00 | 59.47 | 2.25 | 2.25 | 57.22 | 0 | 0 | 0 | 0 | 0
2025-11-05 16:00 | 59.81 | 0 | 0 | 59.81 | 0 | 0 | 0 | 0 | 0
2025-11-05 17:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 0 | 0 | 0
2025-11-05 18:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 0 | 0 | 0
2025-11-05 19:00 | 56.33 | 0 | 0 | 56.33 | 0 | 0 | 0 | 0 | 0
2025-11-05 20:00 | 52.4 | 0 | 0 | 52.4 | 0 | 0 | 0 | 0 | 0
2025-11-05 21:00 | 50.69 | 0 | 0 | 50.69 | 0 | 0 | 0 | 0 | 0
2025-11-05 22:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 0 | 0 | 0
2025-11-05 23:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 0 | 0 | 0
2025-11-06 | 44.76 | 0 | 0 | 44.76 | 0 | 0 | 0 | 0 | 0
2025-11-06 01:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0 | 0 | 0
2025-11-06 02:00 | 42.68 | 0 | 0 | 42.68 | 0 | 0 | 0 | 0 | 0
2025-11-06 03:00 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 0 | 0 | 0
2025-11-06 04:00 | 43.87 | 0 | 0 | 43.87 | 0 | 0 | 0 | 0 | 0
2025-11-06 05:00 | 43.46 | 0 | 0 | 43.46 | 0 | 0 | 0 | 0 | 0
2025-11-06 06:00 | 45.15 | 0 | 0 | 45.15 | 0 | 0 | 0 | 0 | 0
2025-11-06 07:00 | 46.45 | 0.26 | 0.26 | 46.19 | 0 | 0 | 0 | 0 | 0
2025-11-06 08:00 | 48.62 | 7.19 | 7.19 | 41.42 | 0 | 0 | 0 | 0 | 0
2025-11-06 09:00 | 51.06 | 11.84 | 11.84 | 39.22 | 0 | 0 | 0 | 0 | 0
2025-11-06 10:00 | 53.16 | 13.9 | 13.9 | 39.26 | 0 | 0 | 0 | 0 | 0
2025-11-06 11:00 | 56.46 | 17.53 | 17.53 | 38.93 | 0 | 0 | 0 | 0 | 0
2025-11-06 12:00 | 58.69 | 16.46 | 16.46 | 42.24 | 0 | 0 | 0 | 0 | 0
2025-11-06 13:00 | 61.36 | 16.65 | 16.65 | 44.71 | 0 | 0 | 0 | 0 | 0
2025-11-06 14:00 | 61.38 | 12.91 | 12.91 | 48.47 | 0 | 0 | 0 | 0 | 0
2025-11-06 15:00 | 62.11 | 9.48 | 9.48 | 52.63 | 0 | 0 | 0 | 0 | 0
2025-11-06 16:00 | 61.53 | 3.8 | 3.8 | 57.73 | 0 | 0 | 0 | 0 | 0
2025-11-06 17:00 | 61.49 | 0 | 0 | 61.49 | 0 | 0 | 0 | 0 | 0
2025-11-06 18:00 | 58.46 | 0 | 0 | 58.46 | 0 | 0 | 0 | 0 | 0
2025-11-06 19:00 | 56.83 | 0 | 0 | 56.83 | 0 | 0 | 0 | 0 | 0
2025-11-06 20:00 | 54.42 | 0 | 0 | 54.42 | 0 | 0 | 0 | 0 | 0
2025-11-06 21:00 | 51.21 | 0 | 0 | 51.21 | 0 | 0 | 0 | 0 | 0
2025-11-06 22:00 | 48.1 | 0 | 0 | 48.1 | 0 | 0 | 0 | 0 | 0
2025-11-06 23:00 | 45.93 | 0 | 0 | 45.93 | 0 | 0 | 0 | 0 | 0
2025-11-07 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 0 | 0 | 0
2025-11-07 01:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 0 | 0 | 0
2025-11-07 02:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 0 | 0 | 0
2025-11-07 03:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0 | 0 | 0
2025-11-07 04:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 0 | 0 | 0
2025-11-07 05:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0 | 0 | 0
2025-11-07 06:00 | 44.2 | 0 | 0 | 44.2 | 0 | 0 | 0 | 0 | 0
2025-11-07 07:00 | 45.86 | 1.77 | 1.77 | 44.09 | 0 | 0 | 0 | 0 | 0
2025-11-07 08:00 | 48.74 | 7.53 | 7.53 | 41.21 | 0 | 0 | 0 | 0 | 0
2025-11-07 09:00 | 50.37 | 58.58 | 50.37 | 0 | 0 | 0 | 0 | 8.21 | 0
2025-11-07 10:00 | 51.7 | 57.71 | 51.7 | 0 | 0 | 0 | 0 | 6.01 | 0
2025-11-07 11:00 | 55.74 | 40.3 | 40.3 | 15.44 | 0 | 0 | 0 | 0 | 0
2025-11-07 12:00 | 56.97 | 51.62 | 51.62 | 5.35 | 0 | 0 | 0 | 0 | 0
2025-11-07 13:00 | 59.36 | 58.44 | 58.44 | 0.92 | 0 | 0 | 0 | 0 | 0
2025-11-07 14:00 | 60.87 | 22.09 | 22.09 | 38.78 | 0 | 0 | 0 | 0 | 0
2025-11-07 15:00 | 60.55 | 38.12 | 38.12 | 22.42 | 0 | 0 | 0 | 0 | 0
2025-11-07 16:00 | 60.67 | 0 | 0 | 60.67 | 0 | 0 | 0 | 0 | 0
2025-11-07 17:00 | 59.2 | 0 | 0 | 59.2 | 0 | 0 | 0 | 0 | 0
2025-11-07 18:00 | 58.28 | 0 | 0 | 58.28 | 0 | 0 | 0 | 0 | 0
2025-11-07 19:00 | 54.88 | 0 | 0 | 54.88 | 0 | 0 | 0 | 0 | 0
2025-11-07 20:00 | 53.08 | 0 | 0 | 53.08 | 0 | 0 | 0 | 0 | 0
2025-11-07 21:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 0 | 0 | 0
2025-11-07 22:00 | 48.29 | 0 | 0 | 48.29 | 0 | 0 | 0 | 0 | 0
2025-11-07 23:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 0 | 0 | 0
2025-11-08 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 0 | 0 | 0
2025-11-08 01:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 0 | 0 | 0
2025-11-08 02:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0 | 0 | 0
2025-11-08 03:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 0 | 0 | 0
2025-11-08 04:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 0 | 0 | 0
2025-11-08 05:00 | 43.87 | 0 | 0 | 43.87 | 0 | 0 | 0 | 0 | 0
2025-11-08 06:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 0 | 0 | 0
2025-11-08 07:00 | 45.39 | 0.27 | 0.27 | 45.12 | 0 | 0 | 0 | 0 | 0
2025-11-08 08:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 0 | 0 | 0
2025-11-08 09:00 | 50.1 | 2.11 | 2.11 | 47.99 | 0 | 0 | 0 | 0 | 0
2025-11-08 10:00 | 51.93 | 17.94 | 17.94 | 33.99 | 0 | 0 | 0 | 0 | 0
2025-11-08 11:00 | 54.03 | 75.13 | 54.03 | 0 | 0 | 0 | 0 | 21.1 | 0
2025-11-08 12:00 | 54.56 | 19.7 | 19.7 | 34.86 | 0 | 0 | 0 | 0 | 0
2025-11-08 13:00 | 56.99 | 20.22 | 20.22 | 36.78 | 0 | 0 | 0 | 0 | 0
2025-11-08 14:00 | 57.56 | 79.27 | 57.56 | 0 | 0 | 0 | 0 | 21.71 | 0
2025-11-08 15:00 | 58.69 | 16.65 | 16.65 | 42.04 | 0 | 0 | 0 | 0 | 0
2025-11-08 16:00 | 58.44 | 15.89 | 15.89 | 42.55 | 0 | 0 | 0 | 0 | 0
2025-11-08 17:00 | 57.38 | 0 | 0 | 57.38 | 0 | 0 | 0 | 0 | 0
2025-11-08 18:00 | 55.95 | 0 | 0 | 55.95 | 0 | 0 | 0 | 0 | 0
2025-11-08 19:00 | 53.27 | 0 | 0 | 53.27 | 0 | 0 | 0 | 0 | 0
2025-11-08 20:00 | 52.34 | 0 | 0 | 52.34 | 0 | 0 | 0 | 0 | 0
2025-11-08 21:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0 | 0 | 0
2025-11-08 22:00 | 48.54 | 0 | 0 | 48.54 | 0 | 0 | 0 | 0 | 0
2025-11-08 23:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 0 | 0 | 0
2025-11-09 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 0 | 0 | 0
2025-11-09 01:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 0 | 0 | 0
2025-11-09 02:00 | 42.04 | 0 | 0 | 42.04 | 0 | 0 | 0 | 0 | 0
2025-11-09 03:00 | 42.24 | 0 | 0 | 42.24 | 0 | 0 | 0 | 0 | 0
2025-11-09 04:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 0 | 0 | 0
2025-11-09 05:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 0 | 0 | 0
2025-11-09 06:00 | 44.91 | 0 | 0 | 44.91 | 0 | 0 | 0 | 0 | 0
2025-11-09 07:00 | 45.54 | 4.72 | 4.72 | 40.82 | 0 | 0 | 0 | 0 | 0
2025-11-09 08:00 | 47.68 | 77.59 | 47.68 | 0 | 0 | 0 | 0 | 29.91 | 0
2025-11-09 09:00 | 50.09 | 91.38 | 50.09 | 0 | 0 | 0 | 0 | 41.29 | 0
2025-11-09 10:00 | 52.98 | 77.83 | 52.98 | 0 | 0 | 0 | 0 | 24.85 | 0
2025-11-09 11:00 | 55.07 | 22.06 | 22.06 | 33.01 | 0 | 0 | 0 | 0 | 0
2025-11-09 12:00 | 57.93 | 5.94 | 5.94 | 51.99 | 0 | 0 | 0 | 0 | 0
2025-11-09 13:00 | 59.68 | 3.17 | 3.17 | 56.51 | 0 | 0 | 0 | 0 | 0
2025-11-09 14:00 | 60.54 | 2.19 | 2.19 | 58.35 | 0 | 0 | 0 | 0 | 0
2025-11-09 15:00 | 61.78 | 0.88 | 0.88 | 60.9 | 0 | 0 | 0 | 0 | 0
2025-11-09 16:00 | 60.91 | 0 | 0 | 60.91 | 0 | 0 | 0 | 0 | 0
2025-11-09 17:00 | 60.3 | 0 | 0 | 60.3 | 0 | 0 | 0 | 0 | 0
2025-11-09 18:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 0 | 0 | 0
2025-11-09 19:00 | 55.67 | 0 | 0 | 55.67 | 0 | 0 | 0 | 0 | 0
2025-11-09 20:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 0 | 0 | 0
2025-11-09 21:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 0 | 0 | 0
2025-11-09 22:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 0 | 0 | 0
2025-11-09 23:00 | 45.89 | 0 | 0 | 45.89 | 0 | 0 | 0 | 0 | 0
2025-11-10 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0 | 0 | 0
2025-11-10 01:00 | 42.6 | 0 | 0 | 42.6 | 0 | 0 | 0 | 0 | 0
2025-11-10 02:00 | 42.66 | 0 | 0 | 42.66 | 0 | 0 | 0 | 0 | 0
2025-11-10 03:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0 | 0 | 0
2025-11-10 04:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0 | 0 | 0
2025-11-10 05:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 0 | 0 | 0
2025-11-10 06:00 | 44.93 | 0 | 0 | 44.93 | 0 | 0 | 0 | 0 | 0
2025-11-10 07:00 | 45.13 | 0 | 0 | 45.13 | 0 | 0 | 0 | 0 | 0
2025-11-10 08:00 | 46.8 | 0.95 | 0.95 | 45.85 | 0 | 0 | 0 | 0 | 0
2025-11-10 09:00 | 49.22 | 2.96 | 2.96 | 46.26 | 0 | 0 | 0 | 0 | 0
2025-11-10 10:00 | 50.87 | 5.26 | 5.26 | 45.61 | 0 | 0 | 0 | 0 | 0
2025-11-10 11:00 | 52.8 | 6.29 | 6.29 | 46.51 | 0 | 0 | 0 | 0 | 0
2025-11-10 12:00 | 55.48 | 6.61 | 6.61 | 48.87 | 0 | 0 | 0 | 0 | 0
2025-11-10 13:00 | 56.48 | 5.69 | 5.69 | 50.79 | 0 | 0 | 0 | 0 | 0
2025-11-10 14:00 | 57.07 | 3.91 | 3.91 | 53.16 | 0 | 0 | 0 | 0 | 0
2025-11-10 15:00 | 57.4 | 1.78 | 1.78 | 55.62 | 0 | 0 | 0 | 0 | 0
2025-11-10 16:00 | 57.01 | 0 | 0 | 57.01 | 0 | 0 | 0 | 0 | 0
2025-11-10 17:00 | 57.3 | 0 | 0 | 57.3 | 0 | 0 | 0 | 0 | 0
2025-11-10 18:00 | 54.8 | 0 | 0 | 54.8 | 0 | 0 | 0 | 0 | 0
2025-11-10 19:00 | 52.83 | 0 | 0 | 52.83 | 0 | 0 | 0 | 0 | 0
2025-11-10 20:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 0 | 0 | 0
2025-11-10 21:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0 | 0 | 0
2025-11-10 22:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 0 | 0 | 0
2025-11-10 23:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0 | 0 | 0
2025-11-11 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0 | 0 | 0
2025-11-11 01:00 | 43.42 | 0 | 0 | 43.42 | 0 | 0 | 0 | 0 | 0
2025-11-11 02:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 0 | 0 | 0
2025-11-11 03:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 0 | 0 | 0
2025-11-11 04:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0 | 0 | 0
2025-11-11 05:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 0 | 0 | 0
2025-11-11 06:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 0 | 0 | 0
2025-11-11 07:00 | 45.04 | 0 | 0 | 45.04 | 0 | 0 | 0 | 0 | 0
2025-11-11 08:00 | 46.21 | 3.7 | 3.7 | 42.51 | 0 | 0 | 0 | 0 | 0
2025-11-11 09:00 | 49.86 | 10.26 | 10.26 | 39.6 | 0 | 0 | 0 | 0 | 0
2025-11-11 10:00 | 51.58 | 3.68 | 3.68 | 47.91 | 0 | 0 | 0 | 0 | 0
2025-11-11 11:00 | 53.7 | 13.61 | 13.61 | 40.09 | 0 | 0 | 0 | 0 | 0
2025-11-11 12:00 | 54.77 | 22.77 | 22.77 | 32 | 0 | 0 | 0 | 0 | 0
2025-11-11 13:00 | 56.5 | 24.66 | 24.66 | 31.84 | 0 | 0 | 0 | 0 | 0
2025-11-11 14:00 | 57.72 | 21.18 | 21.18 | 36.54 | 0 | 0 | 0 | 0 | 0
2025-11-11 15:00 | 57.94 | 10.05 | 10.05 | 47.89 | 0 | 0 | 0 | 0 | 0
2025-11-11 16:00 | 58.02 | 0.73 | 0.73 | 57.29 | 0 | 0 | 0 | 0 | 0
2025-11-11 17:00 | 57.34 | 0 | 0 | 57.34 | 0 | 0 | 0 | 0 | 0
2025-11-11 18:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 0 | 0 | 0
2025-11-11 19:00 | 53.78 | 0 | 0 | 53.78 | 0 | 0 | 0 | 0 | 0
2025-11-11 20:00 | 52.27 | 0 | 0 | 52.27 | 0 | 0 | 0 | 0 | 0
2025-11-11 21:00 | 49.15 | 0 | 0 | 49.15 | 0 | 0 | 0 | 0 | 0
2025-11-11 22:00 | 46.64 | 0 | 0 | 46.64 | 0 | 0 | 0 | 0 | 0
2025-11-11 23:00 | 45.43 | 0 | 0 | 45.43 | 0 | 0 | 0 | 0 | 0
2025-11-12 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0 | 0 | 0
2025-11-12 01:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 0 | 0 | 0
2025-11-12 02:00 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 0 | 0 | 0
2025-11-12 03:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 0 | 0 | 0
2025-11-12 04:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 0 | 0 | 0
2025-11-12 05:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0 | 0 | 0
2025-11-12 06:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 0 | 0 | 0
2025-11-12 07:00 | 45.71 | 1.16 | 1.16 | 44.54 | 0 | 0 | 0 | 0 | 0
2025-11-12 08:00 | 46.53 | 43.76 | 43.76 | 2.77 | 0 | 0 | 0 | 0 | 0
2025-11-12 09:00 | 49.18 | 57.49 | 49.18 | 0 | 0 | 0 | 0 | 8.31 | 0
2025-11-12 10:00 | 49.98 | 45.12 | 45.12 | 4.85 | 0 | 0 | 0 | 0 | 0
2025-11-12 11:00 | 51.64 | 49.62 | 49.62 | 2.02 | 0 | 0 | 0 | 0 | 0
2025-11-12 12:00 | 53.42 | 49.28 | 49.28 | 4.14 | 0 | 0 | 0 | 0 | 0
2025-11-12 13:00 | 54.55 | 53.67 | 53.67 | 0.88 | 0 | 0 | 0 | 0 | 0
2025-11-12 14:00 | 55.27 | 69.08 | 55.27 | 0 | 0 | 0 | 0 | 13.81 | 0
2025-11-12 15:00 | 55.06 | 77.54 | 55.06 | 0 | 0 | 0 | 0 | 22.48 | 0
2025-11-12 16:00 | 55.15 | 14.43 | 14.43 | 40.72 | 0 | 0 | 0 | 0 | 0
2025-11-12 17:00 | 54.63 | 0 | 0 | 54.63 | 0 | 0 | 0 | 0 | 0
2025-11-12 18:00 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 0 | 0 | 0
2025-11-12 19:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 0 | 0 | 0
2025-11-12 20:00 | 49.62 | 0 | 0 | 49.62 | 0 | 0 | 0 | 0 | 0
2025-11-12 21:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 0 | 0 | 0
2025-11-12 22:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 0 | 0 | 0
2025-11-12 23:00 | 45.05 | 0 | 0 | 45.05 | 0 | 0 | 0 | 0 | 0
2025-11-13 | 44.34 | 0 | 0 | 44.34 | 0 | 0 | 0 | 0 | 0
2025-11-13 01:00 | 41.88 | 0 | 0 | 41.88 | 0 | 0 | 0 | 0 | 0
2025-11-13 02:00 | 42.72 | 0 | 0 | 42.72 | 0 | 0 | 0 | 0 | 0
2025-11-13 03:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 0 | 0 | 0
2025-11-13 04:00 | 42.06 | 0 | 0 | 42.06 | 0 | 0 | 0 | 0 | 0
2025-11-13 05:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 0 | 0 | 0
2025-11-13 06:00 | 42.87 | 0 | 0 | 42.87 | 0 | 0 | 0 | 0 | 0
2025-11-13 07:00 | 45.08 | 0.68 | 0.68 | 44.4 | 0 | 0 | 0 | 0 | 0
2025-11-13 08:00 | 47 | 45.31 | 45.31 | 1.69 | 0 | 0 | 0 | 0 | 0
2025-11-13 09:00 | 48.99 | 54.07 | 48.99 | 0 | 0 | 0 | 0 | 5.08 | 0
2025-11-13 10:00 | 50.37 | 61.67 | 50.37 | 0 | 0 | 0 | 0 | 11.29 | 0
2025-11-13 11:00 | 51.08 | 55 | 51.08 | 0 | 0 | 0 | 0 | 3.92 | 0
2025-11-13 12:00 | 52.87 | 48.74 | 48.74 | 4.13 | 0 | 0 | 0 | 0 | 0
2025-11-13 13:00 | 55.79 | 47.27 | 47.27 | 8.53 | 0 | 0 | 0 | 0 | 0
2025-11-13 14:00 | 54.93 | 35.88 | 35.88 | 19.05 | 0 | 0 | 0 | 0 | 0
2025-11-13 15:00 | 56.43 | 23.31 | 23.31 | 33.12 | 0 | 0 | 0 | 0 | 0
2025-11-13 16:00 | 55.01 | 3.52 | 3.52 | 51.49 | 0 | 0 | 0 | 0 | 0
2025-11-13 17:00 | 54.68 | 0 | 0 | 54.68 | 0 | 0 | 0 | 0 | 0
2025-11-13 18:00 | 53.95 | 0 | 0 | 53.95 | 0 | 0 | 0 | 0 | 0
2025-11-13 19:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 0 | 0 | 0
2025-11-13 20:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0 | 0 | 0
2025-11-13 21:00 | 48.69 | 0 | 0 | 48.69 | 0 | 0 | 0 | 0 | 0
2025-11-13 22:00 | 47.07 | 0 | 0 | 47.07 | 0 | 0 | 0 | 0 | 0
2025-11-13 23:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 0 | 0 | 0
2025-11-14 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 0 | 0 | 0
2025-11-14 01:00 | 43.24 | 0 | 0 | 43.24 | 0 | 0 | 0 | 0 | 0
2025-11-14 02:00 | 41.71 | 0 | 0 | 41.71 | 0 | 0 | 0 | 0 | 0
2025-11-14 03:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 0 | 0 | 0
2025-11-14 04:00 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 0 | 0 | 0
2025-11-14 05:00 | 42.84 | 0 | 0 | 42.84 | 0 | 0 | 0 | 0 | 0
2025-11-14 06:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 0 | 0 | 0
2025-11-14 07:00 | 44.33 | 0 | 0 | 44.33 | 0 | 0 | 0 | 0 | 0
2025-11-14 08:00 | 46.5 | 1.29 | 1.29 | 45.21 | 0 | 0 | 0 | 0 | 0
2025-11-14 09:00 | 47.97 | 6.61 | 6.61 | 41.37 | 0 | 0 | 0 | 0 | 0
2025-11-14 10:00 | 49.07 | 25.82 | 25.82 | 23.25 | 0 | 0 | 0 | 0 | 0
2025-11-14 11:00 | 51.04 | 28.6 | 28.6 | 22.44 | 0 | 0 | 0 | 0 | 0
2025-11-14 12:00 | 52.07 | 43.01 | 43.01 | 9.06 | 0 | 0 | 0 | 0 | 0
2025-11-14 13:00 | 52.8 | 42.12 | 42.12 | 10.69 | 0 | 0 | 0 | 0 | 0
2025-11-14 14:00 | 53.32 | 11.32 | 11.32 | 42 | 0 | 0 | 0 | 0 | 0
2025-11-14 15:00 | 53.49 | 4.89 | 4.89 | 48.6 | 0 | 0 | 0 | 0 | 0
2025-11-14 16:00 | 53.18 | 0.7 | 0.7 | 52.48 | 0 | 0 | 0 | 0 | 0
2025-11-14 17:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 0 | 0 | 0
2025-11-14 18:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 0 | 0 | 0
2025-11-14 19:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0 | 0 | 0
2025-11-14 20:00 | 48.79 | 0 | 0 | 48.79 | 0 | 0 | 0 | 0 | 0
2025-11-14 21:00 | 47.68 | 0 | 0 | 47.68 | 0 | 0 | 0 | 0 | 0
2025-11-14 22:00 | 46.14 | 0 | 0 | 46.14 | 0 | 0 | 0 | 0 | 0
2025-11-14 23:00 | 45.88 | 0 | 0 | 45.88 | 0 | 0 | 0 | 0 | 0
2025-11-15 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 0 | 0 | 0
2025-11-15 01:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 0 | 0 | 0
2025-11-15 02:00 | 41.78 | 0 | 0 | 41.78 | 0 | 0 | 0 | 0 | 0
2025-11-15 03:00 | 41.59 | 0 | 0 | 41.59 | 0 | 0 | 0 | 0 | 0
2025-11-15 04:00 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 0 | 0 | 0
2025-11-15 05:00 | 42.95 | 0 | 0 | 42.95 | 0 | 0 | 0 | 0 | 0
2025-11-15 06:00 | 43.23 | 0 | 0 | 43.23 | 0 | 0 | 0 | 0 | 0
2025-11-15 07:00 | 45.06 | 0.33 | 0.33 | 44.73 | 0 | 0 | 0 | 0 | 0
2025-11-15 08:00 | 45.84 | 23.22 | 23.22 | 22.62 | 0 | 0 | 0 | 0 | 0
2025-11-15 09:00 | 48.84 | 52.96 | 48.84 | 0 | 0 | 0 | 0 | 4.11 | 0
2025-11-15 10:00 | 50.5 | 62.63 | 50.5 | 0 | 0 | 0 | 0 | 12.13 | 0
2025-11-15 11:00 | 52.84 | 51.12 | 51.12 | 1.72 | 0 | 0 | 0 | 0 | 0
2025-11-15 12:00 | 53.89 | 40.63 | 40.63 | 13.26 | 0 | 0 | 0 | 0 | 0
2025-11-15 13:00 | 56.36 | 46.06 | 46.06 | 10.3 | 0 | 0 | 0 | 0 | 0
2025-11-15 14:00 | 56.21 | 66.14 | 56.21 | 0 | 0 | 0 | 0 | 9.93 | 0
2025-11-15 15:00 | 57.45 | 78.4 | 57.45 | 0 | 0 | 0 | 0 | 20.95 | 0
2025-11-15 16:00 | 56.45 | 9.74 | 9.74 | 46.71 | 0 | 0 | 0 | 0 | 0
2025-11-15 17:00 | 55.73 | 0 | 0 | 55.73 | 0 | 0 | 0 | 0 | 0
2025-11-15 18:00 | 55.31 | 0 | 0 | 55.31 | 0 | 0 | 0 | 0 | 0
2025-11-15 19:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0 | 0 | 0
2025-11-15 20:00 | 51.48 | 0 | 0 | 51.48 | 0 | 0 | 0 | 0 | 0
2025-11-15 21:00 | 49.58 | 0 | 0 | 49.58 | 0 | 0 | 0 | 0 | 0
2025-11-15 22:00 | 46.39 | 0 | 0 | 46.39 | 0 | 0 | 0 | 0 | 0
2025-11-15 23:00 | 45.71 | 0 | 0 | 45.71 | 0 | 0 | 0 | 0 | 0
2025-11-16 | 42.47 | 0 | 0 | 42.47 | 0 | 0 | 0 | 0 | 0
2025-11-16 01:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 0 | 0 | 0
2025-11-16 02:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 0 | 0 | 0
2025-11-16 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0 | 0 | 0
2025-11-16 04:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 0 | 0 | 0
2025-11-16 05:00 | 42.66 | 0 | 0 | 42.66 | 0 | 0 | 0 | 0 | 0
2025-11-16 06:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0 | 0 | 0
2025-11-16 07:00 | 44.58 | 0 | 0 | 44.58 | 0 | 0 | 0 | 0 | 0
2025-11-16 08:00 | 45.93 | 37.26 | 37.26 | 8.67 | 0 | 0 | 0 | 0 | 0
2025-11-16 09:00 | 47.54 | 22.44 | 22.44 | 25.1 | 0 | 0 | 0 | 0 | 0
2025-11-16 10:00 | 48.74 | 42.77 | 42.77 | 5.97 | 0 | 0 | 0 | 0 | 0
2025-11-16 11:00 | 50 | 46.41 | 46.41 | 3.59 | 0 | 0 | 0 | 0 | 0
2025-11-16 12:00 | 50.75 | 21.76 | 21.76 | 28.99 | 0 | 0 | 0 | 0 | 0
2025-11-16 13:00 | 51.73 | 18.69 | 18.69 | 33.03 | 0 | 0 | 0 | 0 | 0
2025-11-16 14:00 | 50.89 | 1.59 | 1.59 | 49.3 | 0 | 0 | 0 | 0 | 0
2025-11-16 15:00 | 51.77 | 2.8 | 2.8 | 48.97 | 0 | 0 | 0 | 0 | 0
2025-11-16 16:00 | 51.01 | 0.82 | 0.82 | 50.19 | 0 | 0 | 0 | 0 | 0
2025-11-16 17:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 0 | 0 | 0
2025-11-16 18:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0 | 0 | 0
2025-11-16 19:00 | 49.5 | 0 | 0 | 49.5 | 0 | 0 | 0 | 0 | 0
2025-11-16 20:00 | 48.66 | 0 | 0 | 48.66 | 0 | 0 | 0 | 0 | 0
2025-11-16 21:00 | 47.66 | 0 | 0 | 47.66 | 0 | 0 | 0 | 0 | 0
2025-11-16 22:00 | 44.83 | 0 | 0 | 44.83 | 0 | 0 | 0 | 0 | 0
2025-11-16 23:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 0 | 0 | 0
2025-11-17 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 0 | 0 | 0
2025-11-17 01:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0 | 0 | 0
2025-11-17 02:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0 | 0 | 0
2025-11-17 03:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0 | 0 | 0
2025-11-17 04:00 | 41.91 | 0 | 0 | 41.91 | 0 | 0 | 0 | 0 | 0
2025-11-17 05:00 | 42.26 | 0 | 0 | 42.26 | 0 | 0 | 0 | 0 | 0
2025-11-17 06:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0 | 0 | 0
2025-11-17 07:00 | 44.71 | 0 | 0 | 44.71 | 0 | 0 | 0 | 0 | 0
2025-11-17 08:00 | 46.61 | 8.43 | 8.43 | 38.18 | 0 | 0 | 0 | 0 | 0
2025-11-17 09:00 | 48.09 | 17.22 | 17.22 | 30.87 | 0 | 0 | 0 | 0 | 0
2025-11-17 10:00 | 50.28 | 29.37 | 29.37 | 20.92 | 0 | 0 | 0 | 0 | 0
2025-11-17 11:00 | 51.81 | 40.77 | 40.77 | 11.04 | 0 | 0 | 0 | 0 | 0
2025-11-17 12:00 | 54.43 | 18.25 | 18.25 | 36.19 | 0 | 0 | 0 | 0 | 0
2025-11-17 13:00 | 55.87 | 62.34 | 55.87 | 0 | 0 | 0 | 0 | 6.46 | 0
2025-11-17 14:00 | 56.64 | 20.53 | 20.53 | 36.11 | 0 | 0 | 0 | 0 | 0
2025-11-17 15:00 | 56.03 | 0 | 0 | 56.03 | 0 | 0 | 0 | 0 | 0
2025-11-17 16:00 | 55.47 | 0 | 0 | 55.47 | 0 | 0 | 0 | 0 | 0
2025-11-17 17:00 | 55.75 | 0 | 0 | 55.75 | 0 | 0 | 0 | 0 | 0
2025-11-17 18:00 | 54.07 | 0 | 0 | 54.07 | 0 | 0 | 0 | 0 | 0
2025-11-17 19:00 | 52.29 | 0 | 0 | 52.29 | 0 | 0 | 0 | 0 | 0
2025-11-17 20:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 0 | 0 | 0
2025-11-17 21:00 | 48.46 | 0 | 0 | 48.46 | 0 | 0 | 0 | 0 | 0
2025-11-17 22:00 | 45.79 | 0 | 0 | 45.79 | 0 | 0 | 0 | 0 | 0
2025-11-17 23:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 0 | 0 | 0
2025-11-18 | 43.65 | 0 | 0 | 43.65 | 0 | 0 | 0 | 0 | 0
2025-11-18 01:00 | 42.75 | 0 | 0 | 42.75 | 0 | 0 | 0 | 0 | 0
2025-11-18 02:00 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 0 | 0 | 0
2025-11-18 03:00 | 40.38 | 0 | 0 | 40.38 | 0 | 0 | 0 | 0 | 0
2025-11-18 04:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 0 | 0 | 0
2025-11-18 05:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 0 | 0 | 0
2025-11-18 06:00 | 42.53 | 0 | 0 | 42.53 | 0 | 0 | 0 | 0 | 0
2025-11-18 07:00 | 44.27 | 0.18 | 0.18 | 44.09 | 0 | 0 | 0 | 0 | 0
2025-11-18 08:00 | 46.54 | 53.4 | 46.54 | 0 | 0 | 0 | 0 | 6.86 | 0
2025-11-18 09:00 | 47.78 | 79.11 | 47.78 | 0 | 0 | 0 | 0 | 31.34 | 0
2025-11-18 10:00 | 50.33 | 70.82 | 50.33 | 0 | 0 | 0 | 0 | 20.5 | 0
2025-11-18 11:00 | 50.22 | 59.18 | 50.22 | 0 | 0 | 0 | 0 | 8.96 | 0
2025-11-18 12:00 | 51.36 | 57.37 | 51.36 | 0 | 0 | 0 | 0 | 6.01 | 0
2025-11-18 13:00 | 53.44 | 66.25 | 53.44 | 0 | 0 | 0 | 0 | 12.81 | 0
2025-11-18 14:00 | 52.84 | 74.62 | 52.84 | 0 | 0 | 0 | 0 | 21.78 | 0
2025-11-18 15:00 | 53.55 | 75.34 | 53.55 | 0 | 0 | 0 | 0 | 21.79 | 0
2025-11-18 16:00 | 53.4 | 3.74 | 3.74 | 49.66 | 0 | 0 | 0 | 0 | 0
2025-11-18 17:00 | 53.35 | 0 | 0 | 53.35 | 0 | 0 | 0 | 0 | 0
2025-11-18 18:00 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 0 | 0 | 0
2025-11-18 19:00 | 50.81 | 0 | 0 | 50.81 | 0 | 0 | 0 | 0 | 0
2025-11-18 20:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 0 | 0 | 0
2025-11-18 21:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0 | 0 | 0
2025-11-18 22:00 | 47.84 | 0 | 0 | 47.84 | 0 | 0 | 0 | 0 | 0
2025-11-18 23:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 0 | 0 | 0
2025-11-19 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0 | 0 | 0
2025-11-19 01:00 | 41.17 | 0 | 0 | 41.17 | 0 | 0 | 0 | 0 | 0
2025-11-19 02:00 | 40.85 | 0 | 0 | 40.85 | 0 | 0 | 0 | 0 | 0
2025-11-19 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0 | 0 | 0
2025-11-19 04:00 | 40.9 | 0 | 0 | 40.9 | 0 | 0 | 0 | 0 | 0
2025-11-19 05:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 0 | 0 | 0
2025-11-19 06:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0 | 0 | 0
2025-11-19 07:00 | 44.96 | 0 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0
2025-11-19 08:00 | 46.01 | 17.02 | 17.02 | 28.98 | 0 | 0 | 0 | 0 | 0
2025-11-19 09:00 | 47.45 | 45.98 | 45.98 | 1.47 | 0 | 0 | 0 | 0 | 0
2025-11-19 10:00 | 50.78 | 47.48 | 47.48 | 3.3 | 0 | 0 | 0 | 0 | 0
2025-11-19 11:00 | 52.09 | 54.21 | 52.09 | 0 | 0 | 0 | 0 | 2.12 | 0
2025-11-19 12:00 | 53.03 | 50.53 | 50.53 | 2.51 | 0 | 0 | 0 | 0 | 0
2025-11-19 13:00 | 55.66 | 53.35 | 53.35 | 2.31 | 0 | 0 | 0 | 0 | 0
2025-11-19 14:00 | 56.72 | 40.56 | 40.56 | 16.16 | 0 | 0 | 0 | 0 | 0
2025-11-19 15:00 | 55.3 | 6.88 | 6.88 | 48.42 | 0 | 0 | 0 | 0 | 0
2025-11-19 16:00 | 55.79 | 1 | 1 | 54.79 | 0 | 0 | 0 | 0 | 0
2025-11-19 17:00 | 55.25 | 0 | 0 | 55.25 | 0 | 0 | 0 | 0 | 0
2025-11-19 18:00 | 54.26 | 0 | 0 | 54.26 | 0 | 0 | 0 | 0 | 0
2025-11-19 19:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 0 | 0 | 0
2025-11-19 20:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 0 | 0 | 0
2025-11-19 21:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0 | 0 | 0
2025-11-19 22:00 | 45.85 | 0 | 0 | 45.85 | 0 | 0 | 0 | 0 | 0
2025-11-19 23:00 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 0 | 0 | 0
2025-11-20 | 42.17 | 0 | 0 | 42.17 | 0 | 0 | 0 | 0 | 0
2025-11-20 01:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 0 | 0 | 0
2025-11-20 02:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 0 | 0 | 0
2025-11-20 03:00 | 40.96 | 0 | 0 | 40.96 | 0 | 0 | 0 | 0 | 0
2025-11-20 04:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 0 | 0 | 0
2025-11-20 05:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0 | 0 | 0
2025-11-20 06:00 | 42.33 | 0 | 0 | 42.33 | 0 | 0 | 0 | 0 | 0
2025-11-20 07:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 0 | 0 | 0
2025-11-20 08:00 | 45.01 | 26.2 | 26.2 | 18.81 | 0 | 0 | 0 | 0 | 0
2025-11-20 09:00 | 48.23 | 59.6 | 48.23 | 0 | 0 | 0 | 0 | 11.36 | 0
2025-11-20 10:00 | 50.16 | 69.03 | 50.16 | 0 | 0 | 0 | 0 | 18.87 | 0
2025-11-20 11:00 | 51.74 | 62.24 | 51.74 | 0 | 0 | 0 | 0 | 10.5 | 0
2025-11-20 12:00 | 52.57 | 39.02 | 39.02 | 13.54 | 0 | 0 | 0 | 0 | 0
2025-11-20 13:00 | 53.75 | 52.56 | 52.56 | 1.19 | 0 | 0 | 0 | 0 | 0
2025-11-20 14:00 | 54.86 | 45.86 | 45.86 | 9 | 0 | 0 | 0 | 0 | 0
2025-11-20 15:00 | 54.59 | 48.79 | 48.79 | 5.8 | 0 | 0 | 0 | 0 | 0
2025-11-20 16:00 | 54.48 | 6.06 | 6.06 | 48.42 | 0 | 0 | 0 | 0 | 0
2025-11-20 17:00 | 54.49 | 0 | 0 | 54.49 | 0 | 0 | 0 | 0 | 0
2025-11-20 18:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 0 | 0 | 0
2025-11-20 19:00 | 50.79 | 0 | 0 | 50.79 | 0 | 0 | 0 | 0 | 0
2025-11-20 20:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 0 | 0 | 0
2025-11-20 21:00 | 47.83 | 0 | 0 | 47.83 | 0 | 0 | 0 | 0 | 0
2025-11-20 22:00 | 46.53 | 0 | 0 | 46.53 | 0 | 0 | 0 | 0 | 0
2025-11-20 23:00 | 44.4 | 0 | 0 | 44.4 | 0 | 0 | 0 | 0 | 0
2025-11-21 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0 | 0 | 0
2025-11-21 01:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 0 | 0 | 0
2025-11-21 02:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0 | 0 | 0
2025-11-21 03:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 0 | 0 | 0
2025-11-21 04:00 | 40.87 | 0 | 0 | 40.87 | 0 | 0 | 0 | 0 | 0
2025-11-21 05:00 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 0 | 0 | 0
2025-11-21 06:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0 | 0 | 0
2025-11-21 07:00 | 44.33 | 0 | 0 | 44.33 | 0 | 0 | 0 | 0 | 0
2025-11-21 08:00 | 46.24 | 17.32 | 17.32 | 28.92 | 0 | 0 | 0 | 0 | 0
2025-11-21 09:00 | 48.2 | 48.77 | 48.2 | 0 | 0 | 0 | 0 | 0.57 | 0
2025-11-21 10:00 | 50.14 | 23.17 | 23.17 | 26.97 | 0 | 0 | 0 | 0 | 0
2025-11-21 11:00 | 52.05 | 38.27 | 38.27 | 13.77 | 0 | 0 | 0 | 0 | 0
2025-11-21 12:00 | 54.94 | 42.45 | 42.45 | 12.5 | 0 | 0 | 0 | 0 | 0
2025-11-21 13:00 | 56.15 | 63.4 | 56.15 | 0 | 0 | 0 | 0 | 7.26 | 0
2025-11-21 14:00 | 56.48 | 60.74 | 56.48 | 0 | 0 | 0 | 0 | 4.26 | 0
2025-11-21 15:00 | 57.24 | 52.79 | 52.79 | 4.45 | 0 | 0 | 0 | 0 | 0
2025-11-21 16:00 | 56.12 | 3.04 | 3.04 | 53.08 | 0 | 0 | 0 | 0 | 0
2025-11-21 17:00 | 55.99 | 0 | 0 | 55.99 | 0 | 0 | 0 | 0 | 0
2025-11-21 18:00 | 54.29 | 0 | 0 | 54.29 | 0 | 0 | 0 | 0 | 0
2025-11-21 19:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 0 | 0 | 0
2025-11-21 20:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 0 | 0 | 0
2025-11-21 21:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0 | 0 | 0
2025-11-21 22:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 0 | 0 | 0
2025-11-21 23:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 0 | 0 | 0
2025-11-22 | 42.99 | 0 | 0 | 42.99 | 0 | 0 | 0 | 0 | 0
2025-11-22 01:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0 | 0 | 0
2025-11-22 02:00 | 40.25 | 0 | 0 | 40.25 | 0 | 0 | 0 | 0 | 0
2025-11-22 03:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0
2025-11-22 04:00 | 40.61 | 0 | 0 | 40.61 | 0 | 0 | 0 | 0 | 0
2025-11-22 05:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 0 | 0 | 0
2025-11-22 06:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0 | 0 | 0
2025-11-22 07:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 0 | 0 | 0
2025-11-22 08:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 0 | 0 | 0
2025-11-22 09:00 | 47.43 | 4.29 | 4.29 | 43.14 | 0 | 0 | 0 | 0 | 0
2025-11-22 10:00 | 48.41 | 21.86 | 21.86 | 26.55 | 0 | 0 | 0 | 0 | 0
2025-11-22 11:00 | 50.44 | 49.94 | 49.94 | 0.5 | 0 | 0 | 0 | 0 | 0
2025-11-22 12:00 | 52.25 | 49.09 | 49.09 | 3.17 | 0 | 0 | 0 | 0 | 0
2025-11-22 13:00 | 53.45 | 33.62 | 33.62 | 19.83 | 0 | 0 | 0 | 0 | 0
2025-11-22 14:00 | 55.24 | 57.32 | 55.24 | 0 | 0 | 0 | 0 | 2.09 | 0
2025-11-22 15:00 | 54.7 | 4.39 | 4.39 | 50.31 | 0 | 0 | 0 | 0 | 0
2025-11-22 16:00 | 53.51 | 1.74 | 1.74 | 51.78 | 0 | 0 | 0 | 0 | 0
2025-11-22 17:00 | 53.76 | 0 | 0 | 53.76 | 0 | 0 | 0 | 0 | 0
2025-11-22 18:00 | 52.61 | 0 | 0 | 52.61 | 0 | 0 | 0 | 0 | 0
2025-11-22 19:00 | 50.72 | 0 | 0 | 50.72 | 0 | 0 | 0 | 0 | 0
2025-11-22 20:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0 | 0 | 0
2025-11-22 21:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0 | 0 | 0
2025-11-22 22:00 | 44.87 | 0 | 0 | 44.87 | 0 | 0 | 0 | 0 | 0
2025-11-22 23:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 0 | 0 | 0
2025-11-23 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 0 | 0 | 0
2025-11-23 01:00 | 41.59 | 0 | 0 | 41.59 | 0 | 0 | 0 | 0 | 0
2025-11-23 02:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 0 | 0 | 0
2025-11-23 03:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 0 | 0 | 0
2025-11-23 04:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0 | 0 | 0
2025-11-23 05:00 | 41.85 | 0 | 0 | 41.85 | 0 | 0 | 0 | 0 | 0
2025-11-23 06:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 0 | 0 | 0
2025-11-23 07:00 | 43.41 | 0 | 0 | 43.41 | 0 | 0 | 0 | 0 | 0
2025-11-23 08:00 | 43.89 | 37.79 | 37.79 | 6.1 | 0 | 0 | 0 | 0 | 0
2025-11-23 09:00 | 45.21 | 67.53 | 45.21 | 0 | 0 | 0 | 0 | 22.32 | 0
2025-11-23 10:00 | 46.82 | 57.62 | 46.82 | 0 | 0 | 0 | 0 | 10.79 | 0
2025-11-23 11:00 | 47.88 | 44.27 | 44.27 | 3.61 | 0 | 0 | 0 | 0 | 0
2025-11-23 12:00 | 47.53 | 47.31 | 47.31 | 0.22 | 0 | 0 | 0 | 0 | 0
2025-11-23 13:00 | 49.11 | 61.03 | 49.11 | 0 | 0 | 0 | 0 | 11.91 | 0
2025-11-23 14:00 | 48.73 | 74.86 | 48.73 | 0 | 0 | 0 | 0 | 26.12 | 0
2025-11-23 15:00 | 49.87 | 68.79 | 49.87 | 0 | 0 | 0 | 0 | 18.91 | 0
2025-11-23 16:00 | 48.97 | 5.72 | 5.72 | 43.25 | 0 | 0 | 0 | 0 | 0
2025-11-23 17:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 0 | 0 | 0
2025-11-23 18:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0 | 0 | 0
2025-11-23 19:00 | 47.24 | 0 | 0 | 47.24 | 0 | 0 | 0 | 0 | 0
2025-11-23 20:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0 | 0 | 0
2025-11-23 21:00 | 45.72 | 0 | 0 | 45.72 | 0 | 0 | 0 | 0 | 0
2025-11-23 22:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0 | 0 | 0
2025-11-23 23:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 0 | 0 | 0
2025-11-24 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 0 | 0 | 0
2025-11-24 01:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 0 | 0 | 0
2025-11-24 02:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0 | 0 | 0
2025-11-24 03:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0 | 0 | 0
2025-11-24 04:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 0 | 0 | 0
2025-11-24 05:00 | 41.6 | 0 | 0 | 41.6 | 0 | 0 | 0 | 0 | 0
2025-11-24 06:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 0 | 0 | 0
2025-11-24 07:00 | 42.75 | 0 | 0 | 42.75 | 0 | 0 | 0 | 0 | 0
2025-11-24 08:00 | 44.51 | 3.59 | 3.59 | 40.92 | 0 | 0 | 0 | 0 | 0
2025-11-24 09:00 | 45.91 | 22.64 | 22.64 | 23.27 | 0 | 0 | 0 | 0 | 0
2025-11-24 10:00 | 48.78 | 8.72 | 8.72 | 40.06 | 0 | 0 | 0 | 0 | 0
2025-11-24 11:00 | 49.77 | 22.27 | 22.27 | 27.5 | 0 | 0 | 0 | 0 | 0
2025-11-24 12:00 | 50.33 | 27.16 | 27.16 | 23.17 | 0 | 0 | 0 | 0 | 0
2025-11-24 13:00 | 51.77 | 46.92 | 46.92 | 4.85 | 0 | 0 | 0 | 0 | 0
2025-11-24 14:00 | 51.39 | 71.88 | 51.39 | 0 | 0 | 0 | 0 | 20.49 | 0
2025-11-24 15:00 | 51.93 | 65.1 | 51.93 | 0 | 0 | 0 | 0 | 13.18 | 0
2025-11-24 16:00 | 52.12 | 1.83 | 1.83 | 50.29 | 0 | 0 | 0 | 0 | 0
2025-11-24 17:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 0 | 0 | 0
2025-11-24 18:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 0 | 0 | 0
2025-11-24 19:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 0 | 0 | 0
2025-11-24 20:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 0 | 0 | 0
2025-11-24 21:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 0 | 0 | 0
2025-11-24 22:00 | 44.67 | 0 | 0 | 44.67 | 0 | 0 | 0 | 0 | 0
2025-11-24 23:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0 | 0 | 0
2025-11-25 | 42.07 | 0 | 0 | 42.07 | 0 | 0 | 0 | 0 | 0
2025-11-25 01:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 0 | 0 | 0
2025-11-25 02:00 | 40.57 | 0 | 0 | 40.57 | 0 | 0 | 0 | 0 | 0
2025-11-25 03:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 0 | 0 | 0
2025-11-25 04:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 0 | 0 | 0
2025-11-25 05:00 | 41.25 | 0 | 0 | 41.25 | 0 | 0 | 0 | 0 | 0
2025-11-25 06:00 | 42.69 | 0 | 0 | 42.69 | 0 | 0 | 0 | 0 | 0
2025-11-25 07:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 0 | 0 | 0
2025-11-25 08:00 | 44.12 | 0.32 | 0.32 | 43.8 | 0 | 0 | 0 | 0 | 0
2025-11-25 09:00 | 45.69 | 0.96 | 0.96 | 44.73 | 0 | 0 | 0 | 0 | 0
2025-11-25 10:00 | 46.18 | 1.84 | 1.84 | 44.34 | 0 | 0 | 0 | 0 | 0
2025-11-25 11:00 | 48.42 | 7.85 | 7.85 | 40.57 | 0 | 0 | 0 | 0 | 0
2025-11-25 12:00 | 48.67 | 8.52 | 8.52 | 40.15 | 0 | 0 | 0 | 0 | 0
2025-11-25 13:00 | 48.83 | 43.67 | 43.67 | 5.15 | 0 | 0 | 0 | 0 | 0
2025-11-25 14:00 | 49.43 | 52.03 | 49.43 | 0 | 0 | 0 | 0 | 2.6 | 0
2025-11-25 15:00 | 49.37 | 37.53 | 37.53 | 11.84 | 0 | 0 | 0 | 0 | 0
2025-11-25 16:00 | 50.17 | 1.2 | 1.2 | 48.98 | 0 | 0 | 0 | 0 | 0
2025-11-25 17:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0 | 0 | 0
2025-11-25 18:00 | 48.65 | 0 | 0 | 48.65 | 0 | 0 | 0 | 0 | 0
2025-11-25 19:00 | 48.05 | 0 | 0 | 48.05 | 0 | 0 | 0 | 0 | 0
2025-11-25 20:00 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 0 | 0 | 0
2025-11-25 21:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 0 | 0 | 0
2025-11-25 22:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0 | 0 | 0
2025-11-25 23:00 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 0 | 0 | 0
2025-11-26 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 0 | 0 | 0
2025-11-26 01:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0 | 0 | 0
2025-11-26 02:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0 | 0 | 0
2025-11-26 03:00 | 40.18 | 0 | 0 | 40.18 | 0 | 0 | 0 | 0 | 0
2025-11-26 04:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0 | 0 | 0
2025-11-26 05:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 0 | 0 | 0
2025-11-26 06:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 0 | 0 | 0
2025-11-26 07:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 0 | 0 | 0
2025-11-26 08:00 | 44.68 | 29.67 | 29.67 | 15.02 | 0 | 0 | 0 | 0 | 0
2025-11-26 09:00 | 45.98 | 55.08 | 45.98 | 0 | 0 | 0 | 0 | 9.1 | 0
2025-11-26 10:00 | 47.33 | 61.87 | 47.33 | 0 | 0 | 0 | 0 | 14.54 | 0
2025-11-26 11:00 | 49.7 | 51.38 | 49.7 | 0 | 0 | 0 | 0 | 1.68 | 0
2025-11-26 12:00 | 49.67 | 46.69 | 46.69 | 2.97 | 0 | 0 | 0 | 0 | 0
2025-11-26 13:00 | 50.7 | 38.99 | 38.99 | 11.71 | 0 | 0 | 0 | 0 | 0
2025-11-26 14:00 | 50.46 | 52.3 | 50.46 | 0 | 0 | 0 | 0 | 1.83 | 0
2025-11-26 15:00 | 50.28 | 30.58 | 30.58 | 19.7 | 0 | 0 | 0 | 0 | 0
2025-11-26 16:00 | 50.46 | 1.09 | 1.09 | 49.36 | 0 | 0 | 0 | 0 | 0
2025-11-26 17:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 0 | 0 | 0
2025-11-26 18:00 | 49.56 | 0 | 0 | 49.56 | 0 | 0 | 0 | 0 | 0
2025-11-26 19:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 0 | 0 | 0
2025-11-26 20:00 | 46.99 | 0 | 0 | 46.99 | 0 | 0 | 0 | 0 | 0
2025-11-26 21:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 0 | 0 | 0
2025-11-26 22:00 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 0 | 0 | 0
2025-11-26 23:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 0 | 0 | 0
2025-11-27 | 42.23 | 0 | 0 | 42.23 | 0 | 0 | 0 | 0 | 0
2025-11-27 01:00 | 40.34 | 0 | 0 | 40.34 | 0 | 0 | 0 | 0 | 0
2025-11-27 02:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0 | 0 | 0
2025-11-27 03:00 | 39.72 | 0 | 0 | 39.72 | 0 | 0 | 0 | 0 | 0
2025-11-27 04:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 0 | 0 | 0
2025-11-27 05:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 0 | 0 | 0
2025-11-27 06:00 | 42.59 | 0 | 0 | 42.59 | 0 | 0 | 0 | 0 | 0
2025-11-27 07:00 | 42.93 | 0 | 0 | 42.93 | 0 | 0 | 0 | 0 | 0
2025-11-27 08:00 | 44.85 | 9.88 | 9.88 | 34.98 | 0 | 0 | 0 | 0 | 0
2025-11-27 09:00 | 46.92 | 22.21 | 22.21 | 24.71 | 0 | 0 | 0 | 0 | 0
2025-11-27 10:00 | 48.13 | 37.63 | 37.63 | 10.5 | 0 | 0 | 0 | 0 | 0
2025-11-27 11:00 | 50.45 | 52.6 | 50.45 | 0 | 0 | 0 | 0 | 2.16 | 0
2025-11-27 12:00 | 52.07 | 46.44 | 46.44 | 5.63 | 0 | 0 | 0 | 0 | 0
2025-11-27 13:00 | 53.31 | 48.34 | 48.34 | 4.97 | 0 | 0 | 0 | 0 | 0
2025-11-27 14:00 | 54.22 | 47.5 | 47.5 | 6.73 | 0 | 0 | 0 | 0 | 0
2025-11-27 15:00 | 55.3 | 47.59 | 47.59 | 7.72 | 0 | 0 | 0 | 0 | 0
2025-11-27 16:00 | 54.14 | 3.49 | 3.49 | 50.66 | 0 | 0 | 0 | 0 | 0
2025-11-27 17:00 | 53.85 | 0 | 0 | 53.85 | 0 | 0 | 0 | 0 | 0
2025-11-27 18:00 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 0 | 0 | 0
2025-11-27 19:00 | 49.79 | 0 | 0 | 49.79 | 0 | 0 | 0 | 0 | 0
2025-11-27 20:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0 | 0 | 0
2025-11-27 21:00 | 45.91 | 0 | 0 | 45.91 | 0 | 0 | 0 | 0 | 0
2025-11-27 22:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 0 | 0 | 0
2025-11-27 23:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 0 | 0 | 0
2025-11-28 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 0 | 0 | 0
2025-11-28 01:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 0 | 0 | 0
2025-11-28 02:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 0 | 0 | 0
2025-11-28 03:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0 | 0 | 0
2025-11-28 04:00 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 0 | 0 | 0
2025-11-28 05:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0 | 0 | 0
2025-11-28 06:00 | 41.87 | 0 | 0 | 41.87 | 0 | 0 | 0 | 0 | 0
2025-11-28 07:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 0 | 0 | 0
2025-11-28 08:00 | 43.13 | 35.85 | 35.85 | 7.28 | 0 | 0 | 0 | 0 | 0
2025-11-28 09:00 | 46.98 | 76.71 | 46.98 | 0 | 0 | 0 | 0 | 29.73 | 0
2025-11-28 10:00 | 47.9 | 64.69 | 47.9 | 0 | 0 | 0 | 0 | 16.79 | 0
2025-11-28 11:00 | 49.58 | 49.3 | 49.3 | 0.28 | 0 | 0 | 0 | 0 | 0
2025-11-28 12:00 | 50.55 | 48.13 | 48.13 | 2.42 | 0 | 0 | 0 | 0 | 0
2025-11-28 13:00 | 50.79 | 54.48 | 50.79 | 0 | 0 | 0 | 0 | 3.69 | 0
2025-11-28 14:00 | 52.75 | 37.12 | 37.12 | 15.62 | 0 | 0 | 0 | 0 | 0
2025-11-28 15:00 | 52.37 | 5.43 | 5.43 | 46.93 | 0 | 0 | 0 | 0 | 0
2025-11-28 16:00 | 52.68 | 0.21 | 0.21 | 52.47 | 0 | 0 | 0 | 0 | 0
2025-11-28 17:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 0 | 0 | 0
2025-11-28 18:00 | 50.74 | 0 | 0 | 50.74 | 0 | 0 | 0 | 0 | 0
2025-11-28 19:00 | 48.84 | 0 | 0 | 48.84 | 0 | 0 | 0 | 0 | 0
2025-11-28 20:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0 | 0 | 0
2025-11-28 21:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 0 | 0 | 0
2025-11-28 22:00 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 0 | 0 | 0
2025-11-28 23:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 0 | 0 | 0
2025-11-29 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 0 | 0 | 0
2025-11-29 01:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 0 | 0 | 0
2025-11-29 02:00 | 39.99 | 0 | 0 | 39.99 | 0 | 0 | 0 | 0 | 0
2025-11-29 03:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0 | 0 | 0
2025-11-29 04:00 | 39.98 | 0 | 0 | 39.98 | 0 | 0 | 0 | 0 | 0
2025-11-29 05:00 | 39.81 | 0 | 0 | 39.81 | 0 | 0 | 0 | 0 | 0
2025-11-29 06:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 0 | 0 | 0
2025-11-29 07:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0 | 0 | 0
2025-11-29 08:00 | 43.8 | 0.28 | 0.28 | 43.52 | 0 | 0 | 0 | 0 | 0
2025-11-29 09:00 | 44.49 | 3 | 3 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-11-29 10:00 | 46.06 | 5.74 | 5.74 | 40.32 | 0 | 0 | 0 | 0 | 0
2025-11-29 11:00 | 46.56 | 7.02 | 7.02 | 39.54 | 0 | 0 | 0 | 0 | 0
2025-11-29 12:00 | 48.88 | 7.9 | 7.9 | 40.98 | 0 | 0 | 0 | 0 | 0
2025-11-29 13:00 | 48.3 | 6.42 | 6.42 | 41.88 | 0 | 0 | 0 | 0 | 0
2025-11-29 14:00 | 49.67 | 4.51 | 4.51 | 45.16 | 0 | 0 | 0 | 0 | 0
2025-11-29 15:00 | 49.25 | 1.8 | 1.8 | 47.44 | 0 | 0 | 0 | 0 | 0
2025-11-29 16:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 0 | 0 | 0
2025-11-29 17:00 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 0 | 0 | 0
2025-11-29 18:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 0 | 0 | 0
2025-11-29 19:00 | 47.9 | 0 | 0 | 47.9 | 0 | 0 | 0 | 0 | 0
2025-11-29 20:00 | 45.72 | 0 | 0 | 45.72 | 0 | 0 | 0 | 0 | 0
2025-11-29 21:00 | 44.73 | 0 | 0 | 44.73 | 0 | 0 | 0 | 0 | 0
2025-11-29 22:00 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 0 | 0 | 0
2025-11-29 23:00 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 0 | 0 | 0
2025-11-30 | 42.21 | 0 | 0 | 42.21 | 0 | 0 | 0 | 0 | 0
2025-11-30 01:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 0 | 0 | 0
2025-11-30 02:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 0 | 0 | 0
2025-11-30 03:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 0 | 0 | 0
2025-11-30 04:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 0 | 0 | 0
2025-11-30 05:00 | 40.9 | 0 | 0 | 40.9 | 0 | 0 | 0 | 0 | 0
2025-11-30 06:00 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 0 | 0 | 0
2025-11-30 07:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 0 | 0 | 0
2025-11-30 08:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0 | 0 | 0
2025-11-30 09:00 | 44.49 | 4.08 | 4.08 | 40.41 | 0 | 0 | 0 | 0 | 0
2025-11-30 10:00 | 45.65 | 37.02 | 37.02 | 8.63 | 0 | 0 | 0 | 0 | 0
2025-11-30 11:00 | 47.06 | 24.37 | 24.37 | 22.69 | 0 | 0 | 0 | 0 | 0
2025-11-30 12:00 | 47.24 | 21.5 | 21.5 | 25.74 | 0 | 0 | 0 | 0 | 0
2025-11-30 13:00 | 48.55 | 28.78 | 28.78 | 19.76 | 0 | 0 | 0 | 0 | 0
2025-11-30 14:00 | 48.45 | 41.9 | 41.9 | 6.54 | 0 | 0 | 0 | 0 | 0
2025-11-30 15:00 | 48.87 | 45.52 | 45.52 | 3.34 | 0 | 0 | 0 | 0 | 0
2025-11-30 16:00 | 49.37 | 0.67 | 0.67 | 48.71 | 0 | 0 | 0 | 0 | 0
2025-11-30 17:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 0 | 0 | 0
2025-11-30 18:00 | 48.19 | 0 | 0 | 48.19 | 0 | 0 | 0 | 0 | 0
2025-11-30 19:00 | 46.02 | 0 | 0 | 46.02 | 0 | 0 | 0 | 0 | 0
2025-11-30 20:00 | 45.68 | 0 | 0 | 45.68 | 0 | 0 | 0 | 0 | 0
2025-11-30 21:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 0 | 0 | 0
2025-11-30 22:00 | 44.53 | 0 | 0 | 44.53 | 0 | 0 | 0 | 0 | 0
2025-11-30 23:00 | 41.4 | 0 | 0 | 41.4 | 0 | 0 | 0 | 0 | 0
2025-12-01 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 0 | 0 | 0
2025-12-01 01:00 | 41.09 | 0 | 0 | 41.09 | 0 | 0 | 0 | 0 | 0
2025-12-01 02:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0 | 0 | 0
2025-12-01 03:00 | 39.52 | 0 | 0 | 39.52 | 0 | 0 | 0 | 0 | 0
2025-12-01 04:00 | 39.98 | 0 | 0 | 39.98 | 0 | 0 | 0 | 0 | 0
2025-12-01 05:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 0 | 0 | 0
2025-12-01 06:00 | 42.02 | 0 | 0 | 42.02 | 0 | 0 | 0 | 0 | 0
2025-12-01 07:00 | 42.59 | 0 | 0 | 42.59 | 0 | 0 | 0 | 0 | 0
2025-12-01 08:00 | 44.36 | 27.53 | 27.53 | 16.82 | 0 | 0 | 0 | 0 | 0
2025-12-01 09:00 | 44.94 | 69.51 | 44.94 | 0 | 0 | 0 | 0 | 24.57 | 0
2025-12-01 10:00 | 46.17 | 65.44 | 46.17 | 0 | 0 | 0 | 0 | 19.27 | 0
2025-12-01 11:00 | 47.76 | 55.53 | 47.76 | 0 | 0 | 0 | 0 | 7.77 | 0
2025-12-01 12:00 | 48.44 | 33.58 | 33.58 | 14.85 | 0 | 0 | 0 | 0 | 0
2025-12-01 13:00 | 50.14 | 25.47 | 25.47 | 24.67 | 0 | 0 | 0 | 0 | 0
2025-12-01 14:00 | 50.26 | 1.23 | 1.23 | 49.03 | 0 | 0 | 0 | 0 | 0
2025-12-01 15:00 | 50.3 | 0 | 0 | 50.3 | 0 | 0 | 0 | 0 | 0
2025-12-01 16:00 | 50.7 | 1.95 | 1.95 | 48.75 | 0 | 0 | 0 | 0 | 0
2025-12-01 17:00 | 49.32 | 0 | 0 | 49.32 | 0 | 0 | 0 | 0 | 0
2025-12-01 18:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 0 | 0 | 0
2025-12-01 19:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 0 | 0 | 0
2025-12-01 20:00 | 47.12 | 0 | 0 | 47.12 | 0 | 0 | 0 | 0 | 0
2025-12-01 21:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 0 | 0 | 0
2025-12-01 22:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 0 | 0 | 0
2025-12-01 23:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0 | 0 | 0
2025-12-02 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 0 | 0 | 0
2025-12-02 01:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 0 | 0 | 0
2025-12-02 02:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 0 | 0 | 0
2025-12-02 03:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 0 | 0 | 0
2025-12-02 04:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0 | 0 | 0
2025-12-02 05:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0 | 0 | 0
2025-12-02 06:00 | 41.4 | 0 | 0 | 41.4 | 0 | 0 | 0 | 0 | 0
2025-12-02 07:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 0 | 0 | 0
2025-12-02 08:00 | 42.75 | 12.74 | 12.74 | 30 | 0 | 0 | 0 | 0 | 0
2025-12-02 09:00 | 44.66 | 69.63 | 44.66 | 0 | 0 | 0 | 0 | 24.97 | 0
2025-12-02 10:00 | 45.23 | 70 | 45.23 | 0 | 0 | 0 | 0 | 24.77 | 0
2025-12-02 11:00 | 46.76 | 56.85 | 46.76 | 0 | 0 | 0 | 0 | 10.09 | 0
2025-12-02 12:00 | 46.93 | 2.61 | 2.61 | 44.32 | 0 | 0 | 0 | 0 | 0
2025-12-02 13:00 | 48.05 | 14.35 | 14.35 | 33.71 | 0 | 0 | 0 | 0 | 0
2025-12-02 14:00 | 48.07 | 23.8 | 23.8 | 24.27 | 0 | 0 | 0 | 0 | 0
2025-12-02 15:00 | 48.1 | 2.32 | 2.32 | 45.79 | 0 | 0 | 0 | 0 | 0
2025-12-02 16:00 | 47.67 | 2.22 | 2.22 | 45.45 | 0 | 0 | 0 | 0 | 0
2025-12-02 17:00 | 47.66 | 0 | 0 | 47.66 | 0 | 0 | 0 | 0 | 0
2025-12-02 18:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0 | 0 | 0
2025-12-02 19:00 | 46.27 | 0 | 0 | 46.27 | 0 | 0 | 0 | 0 | 0
2025-12-02 20:00 | 45.65 | 0 | 0 | 45.65 | 0 | 0 | 0 | 0 | 0
2025-12-02 21:00 | 44.36 | 0 | 0 | 44.36 | 0 | 0 | 0 | 0 | 0
2025-12-02 22:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 0 | 0 | 0
2025-12-02 23:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0 | 0 | 0
2025-12-03 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 0 | 0 | 0
2025-12-03 01:00 | 40.17 | 0 | 0 | 40.17 | 0 | 0 | 0 | 0 | 0
2025-12-03 02:00 | 39.71 | 0 | 0 | 39.71 | 0 | 0 | 0 | 0 | 0
2025-12-03 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0 | 0 | 0
2025-12-03 04:00 | 39.52 | 0 | 0 | 39.52 | 0 | 0 | 0 | 0 | 0
2025-12-03 05:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 0 | 0 | 0
2025-12-03 06:00 | 41.38 | 0 | 0 | 41.38 | 0 | 0 | 0 | 0 | 0
2025-12-03 07:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 0 | 0 | 0
2025-12-03 08:00 | 42.64 | 1.8 | 1.8 | 40.84 | 0 | 0 | 0 | 0 | 0
2025-12-03 09:00 | 44.92 | 6.22 | 6.22 | 38.7 | 0 | 0 | 0 | 0 | 0
2025-12-03 10:00 | 45.58 | 10.59 | 10.59 | 34.99 | 0 | 0 | 0 | 0 | 0
2025-12-03 11:00 | 46.2 | 11.99 | 11.99 | 34.2 | 0 | 0 | 0 | 0 | 0
2025-12-03 12:00 | 48.25 | 14.2 | 14.2 | 34.04 | 0 | 0 | 0 | 0 | 0
2025-12-03 13:00 | 48.98 | 10.9 | 10.9 | 38.07 | 0 | 0 | 0 | 0 | 0
2025-12-03 14:00 | 48.78 | 5.48 | 5.48 | 43.3 | 0 | 0 | 0 | 0 | 0
2025-12-03 15:00 | 49.15 | 2.36 | 2.36 | 46.79 | 0 | 0 | 0 | 0 | 0
2025-12-03 16:00 | 49.04 | 0 | 0 | 49.04 | 0 | 0 | 0 | 0 | 0
2025-12-03 17:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0 | 0 | 0
2025-12-03 18:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0 | 0 | 0
2025-12-03 19:00 | 46.03 | 0 | 0 | 46.03 | 0 | 0 | 0 | 0 | 0
2025-12-03 20:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 0 | 0 | 0
2025-12-03 21:00 | 44.96 | 0 | 0 | 44.96 | 0 | 0 | 0 | 0 | 0
2025-12-03 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0 | 0 | 0
2025-12-03 23:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-12-04 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 0 | 0 | 0
2025-12-04 01:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0 | 0 | 0
2025-12-04 02:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0 | 0 | 0
2025-12-04 03:00 | 39.7 | 0 | 0 | 39.7 | 0 | 0 | 0 | 0 | 0
2025-12-04 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 0 | 0 | 0
2025-12-04 05:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 0 | 0 | 0
2025-12-04 06:00 | 41.07 | 0 | 0 | 41.07 | 0 | 0 | 0 | 0 | 0
2025-12-04 07:00 | 41.72 | 0 | 0 | 41.72 | 0 | 0 | 0 | 0 | 0
2025-12-04 08:00 | 43.38 | 15.74 | 15.74 | 27.63 | 0 | 0 | 0 | 0 | 0
2025-12-04 09:00 | 44.06 | 9.59 | 9.59 | 34.47 | 0 | 0 | 0 | 0 | 0
2025-12-04 10:00 | 46.05 | 16.52 | 16.52 | 29.53 | 0 | 0 | 0 | 0 | 0
2025-12-04 11:00 | 47.9 | 19.85 | 19.85 | 28.05 | 0 | 0 | 0 | 0 | 0
2025-12-04 12:00 | 49.03 | 53.12 | 49.03 | 0 | 0 | 0 | 0 | 4.09 | 0
2025-12-04 13:00 | 49.25 | 64.73 | 49.25 | 0 | 0 | 0 | 0 | 15.48 | 0
2025-12-04 14:00 | 49.64 | 69.63 | 49.64 | 0 | 0 | 0 | 0 | 19.99 | 0
2025-12-04 15:00 | 50.43 | 60.34 | 50.43 | 0 | 0 | 0 | 0 | 9.9 | 0
2025-12-04 16:00 | 50.51 | 0.62 | 0.62 | 49.89 | 0 | 0 | 0 | 0 | 0
2025-12-04 17:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0 | 0 | 0
2025-12-04 18:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 0 | 0 | 0
2025-12-04 19:00 | 47.69 | 0 | 0 | 47.69 | 0 | 0 | 0 | 0 | 0
2025-12-04 20:00 | 46.93 | 0 | 0 | 46.93 | 0 | 0 | 0 | 0 | 0
2025-12-04 21:00 | 44.83 | 0 | 0 | 44.83 | 0 | 0 | 0 | 0 | 0
2025-12-04 22:00 | 42.49 | 0 | 0 | 42.49 | 0 | 0 | 0 | 0 | 0
2025-12-04 23:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0 | 0 | 0
2025-12-05 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 0 | 0 | 0
2025-12-05 01:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0 | 0 | 0
2025-12-05 02:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0 | 0 | 0
2025-12-05 03:00 | 39.12 | 0 | 0 | 39.12 | 0 | 0 | 0 | 0 | 0
2025-12-05 04:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 0 | 0 | 0
2025-12-05 05:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 0 | 0 | 0
2025-12-05 06:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 0 | 0 | 0
2025-12-05 07:00 | 42 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0
2025-12-05 08:00 | 44 | 2.43 | 2.43 | 41.57 | 0 | 0 | 0 | 0 | 0
2025-12-05 09:00 | 44.89 | 13.4 | 13.4 | 31.49 | 0 | 0 | 0 | 0 | 0
2025-12-05 10:00 | 46.43 | 63.25 | 46.43 | 0 | 0 | 0 | 0 | 16.82 | 0
2025-12-05 11:00 | 47.88 | 56.42 | 47.88 | 0 | 0 | 0 | 0 | 8.53 | 0
2025-12-05 12:00 | 48.74 | 31.17 | 31.17 | 17.57 | 0 | 0 | 0 | 0 | 0
2025-12-05 13:00 | 50.92 | 17 | 17 | 33.92 | 0 | 0 | 0 | 0 | 0
2025-12-05 14:00 | 52.53 | 27.71 | 27.71 | 24.82 | 0 | 0 | 0 | 0 | 0
2025-12-05 15:00 | 51.98 | 0 | 0 | 51.98 | 0 | 0 | 0 | 0 | 0
2025-12-05 16:00 | 51.85 | 0 | 0 | 51.85 | 0 | 0 | 0 | 0 | 0
2025-12-05 17:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 0 | 0 | 0
2025-12-05 18:00 | 49.53 | 0 | 0 | 49.53 | 0 | 0 | 0 | 0 | 0
2025-12-05 19:00 | 48.71 | 0 | 0 | 48.71 | 0 | 0 | 0 | 0 | 0
2025-12-05 20:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 0 | 0 | 0
2025-12-05 21:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 0 | 0 | 0
2025-12-05 22:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 0 | 0 | 0
2025-12-05 23:00 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 0 | 0 | 0
2025-12-06 | 40.76 | 0 | 0 | 40.76 | 0 | 0 | 0 | 0 | 0
2025-12-06 01:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 0 | 0 | 0
2025-12-06 02:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 0 | 0 | 0
2025-12-06 03:00 | 38.57 | 0 | 0 | 38.57 | 0 | 0 | 0 | 0 | 0
2025-12-06 04:00 | 39.33 | 0 | 0 | 39.33 | 0 | 0 | 0 | 0 | 0
2025-12-06 05:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 0 | 0 | 0
2025-12-06 06:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0
2025-12-06 07:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0 | 0 | 0
2025-12-06 08:00 | 42.92 | 0 | 0 | 42.92 | 0 | 0 | 0 | 0 | 0
2025-12-06 09:00 | 43.94 | 1.56 | 1.56 | 42.38 | 0 | 0 | 0 | 0 | 0
2025-12-06 10:00 | 45.83 | 2.97 | 2.97 | 42.86 | 0 | 0 | 0 | 0 | 0
2025-12-06 11:00 | 47.27 | 6.58 | 6.58 | 40.7 | 0 | 0 | 0 | 0 | 0
2025-12-06 12:00 | 48.37 | 8.09 | 8.09 | 40.28 | 0 | 0 | 0 | 0 | 0
2025-12-06 13:00 | 50.11 | 45.2 | 45.2 | 4.92 | 0 | 0 | 0 | 0 | 0
2025-12-06 14:00 | 49.32 | 48.49 | 48.49 | 0.83 | 0 | 0 | 0 | 0 | 0
2025-12-06 15:00 | 49.49 | 36.19 | 36.19 | 13.29 | 0 | 0 | 0 | 0 | 0
2025-12-06 16:00 | 50.27 | 0.51 | 0.51 | 49.76 | 0 | 0 | 0 | 0 | 0
2025-12-06 17:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 0 | 0 | 0
2025-12-06 18:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 0 | 0 | 0
2025-12-06 19:00 | 47.16 | 0 | 0 | 47.16 | 0 | 0 | 0 | 0 | 0
2025-12-06 20:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 0 | 0 | 0
2025-12-06 21:00 | 44.52 | 0 | 0 | 44.52 | 0 | 0 | 0 | 0 | 0
2025-12-06 22:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 0 | 0 | 0
2025-12-06 23:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 0 | 0 | 0
2025-12-07 | 40.26 | 0 | 0 | 40.26 | 0 | 0 | 0 | 0 | 0
2025-12-07 01:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0 | 0 | 0
2025-12-07 02:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 0 | 0 | 0
2025-12-07 03:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 0 | 0 | 0
2025-12-07 04:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 0 | 0 | 0
2025-12-07 05:00 | 40.02 | 0 | 0 | 40.02 | 0 | 0 | 0 | 0 | 0
2025-12-07 06:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0 | 0 | 0
2025-12-07 07:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 0 | 0 | 0
2025-12-07 08:00 | 42.3 | 0.81 | 0.81 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-12-07 09:00 | 43.09 | 3.57 | 3.57 | 39.52 | 0 | 0 | 0 | 0 | 0
2025-12-07 10:00 | 43.45 | 7.95 | 7.95 | 35.51 | 0 | 0 | 0 | 0 | 0
2025-12-07 11:00 | 44.43 | 11.24 | 11.24 | 33.19 | 0 | 0 | 0 | 0 | 0
2025-12-07 12:00 | 45.63 | 11.75 | 11.75 | 33.88 | 0 | 0 | 0 | 0 | 0
2025-12-07 13:00 | 45.43 | 8.79 | 8.79 | 36.65 | 0 | 0 | 0 | 0 | 0
2025-12-07 14:00 | 45.09 | 6.12 | 6.12 | 38.97 | 0 | 0 | 0 | 0 | 0
2025-12-07 15:00 | 45.39 | 1.97 | 1.97 | 43.43 | 0 | 0 | 0 | 0 | 0
2025-12-07 16:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 0 | 0 | 0
2025-12-07 17:00 | 44.7 | 0 | 0 | 44.7 | 0 | 0 | 0 | 0 | 0
2025-12-07 18:00 | 45.09 | 0 | 0 | 45.09 | 0 | 0 | 0 | 0 | 0
2025-12-07 19:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 0 | 0 | 0
2025-12-07 20:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 0 | 0 | 0
2025-12-07 21:00 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 0 | 0 | 0
2025-12-07 22:00 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 0 | 0 | 0
2025-12-07 23:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 0 | 0 | 0
2025-12-08 | 41.32 | 0 | 0 | 41.32 | 0 | 0 | 0 | 0 | 0
2025-12-08 01:00 | 39.72 | 0 | 0 | 39.72 | 0 | 0 | 0 | 0 | 0
2025-12-08 02:00 | 39.24 | 0 | 0 | 39.24 | 0 | 0 | 0 | 0 | 0
2025-12-08 03:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 0 | 0 | 0
2025-12-08 04:00 | 39.58 | 0 | 0 | 39.58 | 0 | 0 | 0 | 0 | 0
2025-12-08 05:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 0 | 0 | 0
2025-12-08 06:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 0 | 0 | 0
2025-12-08 07:00 | 41.29 | 0 | 0 | 41.29 | 0 | 0 | 0 | 0 | 0
2025-12-08 08:00 | 43.17 | 5.55 | 5.55 | 37.62 | 0 | 0 | 0 | 0 | 0
2025-12-08 09:00 | 43.99 | 7.12 | 7.12 | 36.87 | 0 | 0 | 0 | 0 | 0
2025-12-08 10:00 | 45.18 | 3.51 | 3.51 | 41.67 | 0 | 0 | 0 | 0 | 0
2025-12-08 11:00 | 47.22 | 17.79 | 17.79 | 29.44 | 0 | 0 | 0 | 0 | 0
2025-12-08 12:00 | 48.39 | 20.01 | 20.01 | 28.39 | 0 | 0 | 0 | 0 | 0
2025-12-08 13:00 | 48.48 | 32.84 | 32.84 | 15.65 | 0 | 0 | 0 | 0 | 0
2025-12-08 14:00 | 49.36 | 24.34 | 24.34 | 25.03 | 0 | 0 | 0 | 0 | 0
2025-12-08 15:00 | 48.84 | 4.05 | 4.05 | 44.79 | 0 | 0 | 0 | 0 | 0
2025-12-08 16:00 | 48.81 | 0.04 | 0.04 | 48.77 | 0 | 0 | 0 | 0 | 0
2025-12-08 17:00 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 0 | 0 | 0
2025-12-08 18:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 0 | 0 | 0
2025-12-08 19:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 0 | 0 | 0
2025-12-08 20:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 0 | 0 | 0
2025-12-08 21:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0 | 0 | 0
2025-12-08 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0 | 0 | 0
2025-12-08 23:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 0 | 0 | 0
2025-12-09 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 0 | 0 | 0
2025-12-09 01:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 0 | 0 | 0
2025-12-09 02:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0
2025-12-09 03:00 | 37.95 | 0 | 0 | 37.95 | 0 | 0 | 0 | 0 | 0
2025-12-09 04:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 0 | 0 | 0
2025-12-09 05:00 | 40.33 | 0 | 0 | 40.33 | 0 | 0 | 0 | 0 | 0
2025-12-09 06:00 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 0 | 0 | 0
2025-12-09 07:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0 | 0 | 0
2025-12-09 08:00 | 42.66 | 12.51 | 12.51 | 30.15 | 0 | 0 | 0 | 0 | 0
2025-12-09 09:00 | 43.3 | 33.35 | 33.35 | 9.95 | 0 | 0 | 0 | 0 | 0
2025-12-09 10:00 | 44.49 | 8.56 | 8.56 | 35.93 | 0 | 0 | 0 | 0 | 0
2025-12-09 11:00 | 46.23 | 14.13 | 14.13 | 32.1 | 0 | 0 | 0 | 0 | 0
2025-12-09 12:00 | 47.94 | 25.88 | 25.88 | 22.07 | 0 | 0 | 0 | 0 | 0
2025-12-09 13:00 | 48.43 | 35.95 | 35.95 | 12.48 | 0 | 0 | 0 | 0 | 0
2025-12-09 14:00 | 48.27 | 66.16 | 48.27 | 0 | 0 | 0 | 0 | 17.89 | 0
2025-12-09 15:00 | 49.16 | 60.31 | 49.16 | 0 | 0 | 0 | 0 | 11.16 | 0
2025-12-09 16:00 | 47.51 | 1.87 | 1.87 | 45.64 | 0 | 0 | 0 | 0 | 0
2025-12-09 17:00 | 47.75 | 0 | 0 | 47.75 | 0 | 0 | 0 | 0 | 0
2025-12-09 18:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 0 | 0 | 0
2025-12-09 19:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 0 | 0 | 0
2025-12-09 20:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0 | 0 | 0
2025-12-09 21:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 0 | 0 | 0
2025-12-09 22:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 0 | 0 | 0
2025-12-09 23:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0 | 0 | 0
2025-12-10 | 40.47 | 0 | 0 | 40.47 | 0 | 0 | 0 | 0 | 0
2025-12-10 01:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 0 | 0 | 0
2025-12-10 02:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 0 | 0 | 0
2025-12-10 03:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0 | 0 | 0
2025-12-10 04:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0 | 0 | 0
2025-12-10 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0 | 0 | 0
2025-12-10 06:00 | 40.17 | 0 | 0 | 40.17 | 0 | 0 | 0 | 0 | 0
2025-12-10 07:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 0 | 0 | 0
2025-12-10 08:00 | 41.9 | 15.38 | 15.38 | 26.53 | 0 | 0 | 0 | 0 | 0
2025-12-10 09:00 | 44.69 | 36.51 | 36.51 | 8.19 | 0 | 0 | 0 | 0 | 0
2025-12-10 10:00 | 44.48 | 33.48 | 33.48 | 11 | 0 | 0 | 0 | 0 | 0
2025-12-10 11:00 | 46.26 | 9.01 | 9.01 | 37.26 | 0 | 0 | 0 | 0 | 0
2025-12-10 12:00 | 47.09 | 40.82 | 40.82 | 6.27 | 0 | 0 | 0 | 0 | 0
2025-12-10 13:00 | 49.53 | 18.92 | 18.92 | 30.61 | 0 | 0 | 0 | 0 | 0
2025-12-10 14:00 | 48.74 | 39.35 | 39.35 | 9.39 | 0 | 0 | 0 | 0 | 0
2025-12-10 15:00 | 48.93 | 46.36 | 46.36 | 2.57 | 0 | 0 | 0 | 0 | 0
2025-12-10 16:00 | 48.8 | 1.51 | 1.51 | 47.29 | 0 | 0 | 0 | 0 | 0
2025-12-10 17:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 0 | 0 | 0
2025-12-10 18:00 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 0 | 0 | 0
2025-12-10 19:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 0 | 0 | 0
2025-12-10 20:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 0 | 0 | 0
2025-12-10 21:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 0 | 0 | 0
2025-12-10 22:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0 | 0 | 0
2025-12-10 23:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 0 | 0 | 0
2025-12-11 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0 | 0 | 0
2025-12-11 01:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0
2025-12-11 02:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0 | 0 | 0
2025-12-11 03:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-12-11 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 0 | 0 | 0
2025-12-11 05:00 | 39.04 | 0 | 0 | 39.04 | 0 | 0 | 0 | 0 | 0
2025-12-11 06:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 0 | 0 | 0
2025-12-11 07:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0 | 0 | 0
2025-12-11 08:00 | 43.3 | 9.29 | 9.29 | 34.01 | 0 | 0 | 0 | 0 | 0
2025-12-11 09:00 | 44.24 | 53.27 | 44.24 | 0 | 0 | 0 | 0 | 9.03 | 0
2025-12-11 10:00 | 46.54 | 37.5 | 37.5 | 9.05 | 0 | 0 | 0 | 0 | 0
2025-12-11 11:00 | 47.04 | 53.11 | 47.04 | 0 | 0 | 0 | 0 | 6.08 | 0
2025-12-11 12:00 | 49.39 | 32.9 | 32.9 | 16.49 | 0 | 0 | 0 | 0 | 0
2025-12-11 13:00 | 49.69 | 36.55 | 36.55 | 13.15 | 0 | 0 | 0 | 0 | 0
2025-12-11 14:00 | 50.88 | 25.76 | 25.76 | 25.12 | 0 | 0 | 0 | 0 | 0
2025-12-11 15:00 | 51.13 | 3.38 | 3.38 | 47.75 | 0 | 0 | 0 | 0 | 0
2025-12-11 16:00 | 51.09 | 0.25 | 0.25 | 50.84 | 0 | 0 | 0 | 0 | 0
2025-12-11 17:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0 | 0 | 0
2025-12-11 18:00 | 48.49 | 0 | 0 | 48.49 | 0 | 0 | 0 | 0 | 0
2025-12-11 19:00 | 47.85 | 0 | 0 | 47.85 | 0 | 0 | 0 | 0 | 0
2025-12-11 20:00 | 46.66 | 0 | 0 | 46.66 | 0 | 0 | 0 | 0 | 0
2025-12-11 21:00 | 43.86 | 0 | 0 | 43.86 | 0 | 0 | 0 | 0 | 0
2025-12-11 22:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 0 | 0 | 0
2025-12-11 23:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0 | 0 | 0
2025-12-12 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 0 | 0 | 0
2025-12-12 01:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0 | 0 | 0
2025-12-12 02:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0
2025-12-12 03:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 0 | 0 | 0
2025-12-12 04:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0 | 0 | 0
2025-12-12 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0 | 0 | 0
2025-12-12 06:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0 | 0 | 0
2025-12-12 07:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 0 | 0 | 0
2025-12-12 08:00 | 40.98 | 11.2 | 11.2 | 29.78 | 0 | 0 | 0 | 0 | 0
2025-12-12 09:00 | 41.83 | 73.88 | 41.83 | 0 | 0 | 0 | 0 | 32.05 | 0
2025-12-12 10:00 | 43.21 | 67.45 | 43.21 | 0 | 0 | 0 | 0 | 24.24 | 0
2025-12-12 11:00 | 43.13 | 54.94 | 43.13 | 0 | 0 | 0 | 0 | 11.82 | 0
2025-12-12 12:00 | 43.31 | 50.5 | 43.31 | 0 | 0 | 0 | 0 | 7.19 | 0
2025-12-12 13:00 | 44.66 | 58.41 | 44.66 | 0 | 0 | 0 | 0 | 13.75 | 0
2025-12-12 14:00 | 44.82 | 68.25 | 44.82 | 0 | 0 | 0 | 0 | 23.43 | 0
2025-12-12 15:00 | 44.33 | 56.24 | 44.33 | 0 | 0 | 0 | 0 | 11.9 | 0
2025-12-12 16:00 | 44.62 | 0.66 | 0.66 | 43.96 | 0 | 0 | 0 | 0 | 0
2025-12-12 17:00 | 44.44 | 0 | 0 | 44.44 | 0 | 0 | 0 | 0 | 0
2025-12-12 18:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 0 | 0 | 0
2025-12-12 19:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0
2025-12-12 20:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 0 | 0 | 0
2025-12-12 21:00 | 42.31 | 0 | 0 | 42.31 | 0 | 0 | 0 | 0 | 0
2025-12-12 22:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 0 | 0 | 0
2025-12-12 23:00 | 40.52 | 0 | 0 | 40.52 | 0 | 0 | 0 | 0 | 0
2025-12-13 | 39.86 | 0 | 0 | 39.86 | 0 | 0 | 0 | 0 | 0
2025-12-13 01:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 0 | 0 | 0
2025-12-13 02:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 0 | 0 | 0
2025-12-13 03:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0 | 0 | 0
2025-12-13 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 0 | 0 | 0
2025-12-13 05:00 | 39.06 | 0 | 0 | 39.06 | 0 | 0 | 0 | 0 | 0
2025-12-13 06:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 0 | 0 | 0
2025-12-13 07:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0 | 0 | 0
2025-12-13 08:00 | 41.65 | 8.13 | 8.13 | 33.53 | 0 | 0 | 0 | 0 | 0
2025-12-13 09:00 | 42.23 | 52.39 | 42.23 | 0 | 0 | 0 | 0 | 10.16 | 0
2025-12-13 10:00 | 44.08 | 56.58 | 44.08 | 0 | 0 | 0 | 0 | 12.5 | 0
2025-12-13 11:00 | 45.01 | 48.76 | 45.01 | 0 | 0 | 0 | 0 | 3.76 | 0
2025-12-13 12:00 | 46.08 | 44.83 | 44.83 | 1.24 | 0 | 0 | 0 | 0 | 0
2025-12-13 13:00 | 47.03 | 45.63 | 45.63 | 1.4 | 0 | 0 | 0 | 0 | 0
2025-12-13 14:00 | 46.69 | 45.2 | 45.2 | 1.48 | 0 | 0 | 0 | 0 | 0
2025-12-13 15:00 | 47.96 | 36.52 | 36.52 | 11.44 | 0 | 0 | 0 | 0 | 0
2025-12-13 16:00 | 46.82 | 0.59 | 0.59 | 46.22 | 0 | 0 | 0 | 0 | 0
2025-12-13 17:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 0 | 0 | 0
2025-12-13 18:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0 | 0 | 0
2025-12-13 19:00 | 44.74 | 0 | 0 | 44.74 | 0 | 0 | 0 | 0 | 0
2025-12-13 20:00 | 44.27 | 0 | 0 | 44.27 | 0 | 0 | 0 | 0 | 0
2025-12-13 21:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0 | 0 | 0
2025-12-13 22:00 | 41.67 | 0 | 0 | 41.67 | 0 | 0 | 0 | 0 | 0
2025-12-13 23:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 0 | 0 | 0
2025-12-14 | 39.56 | 0 | 0 | 39.56 | 0 | 0 | 0 | 0 | 0
2025-12-14 01:00 | 39.44 | 0 | 0 | 39.44 | 0 | 0 | 0 | 0 | 0
2025-12-14 02:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 0 | 0 | 0
2025-12-14 03:00 | 39 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
2025-12-14 04:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 0 | 0 | 0
2025-12-14 05:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 0 | 0 | 0
2025-12-14 06:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 0 | 0 | 0
2025-12-14 07:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 0 | 0 | 0
2025-12-14 08:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 0 | 0 | 0
2025-12-14 09:00 | 43.26 | 0 | 0 | 43.26 | 0 | 0 | 0 | 0 | 0
2025-12-14 10:00 | 45.19 | 2.57 | 2.57 | 42.63 | 0 | 0 | 0 | 0 | 0
2025-12-14 11:00 | 45.56 | 10.81 | 10.81 | 34.76 | 0 | 0 | 0 | 0 | 0
2025-12-14 12:00 | 46.74 | 7.61 | 7.61 | 39.13 | 0 | 0 | 0 | 0 | 0
2025-12-14 13:00 | 47.74 | 45.81 | 45.81 | 1.93 | 0 | 0 | 0 | 0 | 0
2025-12-14 14:00 | 48.69 | 54.42 | 48.69 | 0 | 0 | 0 | 0 | 5.74 | 0
2025-12-14 15:00 | 48.35 | 37.93 | 37.93 | 10.42 | 0 | 0 | 0 | 0 | 0
2025-12-14 16:00 | 48.13 | 0.49 | 0.49 | 47.64 | 0 | 0 | 0 | 0 | 0
2025-12-14 17:00 | 47.17 | 0 | 0 | 47.17 | 0 | 0 | 0 | 0 | 0
2025-12-14 18:00 | 46.69 | 0 | 0 | 46.69 | 0 | 0 | 0 | 0 | 0
2025-12-14 19:00 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 0 | 0 | 0
2025-12-14 20:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 0 | 0 | 0
2025-12-14 21:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 0 | 0 | 0
2025-12-14 22:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 0 | 0 | 0
2025-12-14 23:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 0 | 0 | 0
2025-12-15 | 40.32 | 0 | 0 | 40.32 | 0 | 0 | 0 | 0 | 0
2025-12-15 01:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0 | 0 | 0
2025-12-15 02:00 | 38.52 | 0 | 0 | 38.52 | 0 | 0 | 0 | 0 | 0
2025-12-15 03:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0 | 0 | 0
2025-12-15 04:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0 | 0 | 0
2025-12-15 05:00 | 39.13 | 0 | 0 | 39.13 | 0 | 0 | 0 | 0 | 0
2025-12-15 06:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 0 | 0 | 0
2025-12-15 07:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0 | 0 | 0
2025-12-15 08:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 0 | 0 | 0
2025-12-15 09:00 | 42.88 | 0.95 | 0.95 | 41.93 | 0 | 0 | 0 | 0 | 0
2025-12-15 10:00 | 42.69 | 1.73 | 1.73 | 40.97 | 0 | 0 | 0 | 0 | 0
2025-12-15 11:00 | 43.85 | 2.88 | 2.88 | 40.97 | 0 | 0 | 0 | 0 | 0
2025-12-15 12:00 | 43.61 | 6.16 | 6.16 | 37.45 | 0 | 0 | 0 | 0 | 0
2025-12-15 13:00 | 44.89 | 42.42 | 42.42 | 2.47 | 0 | 0 | 0 | 0 | 0
2025-12-15 14:00 | 44.75 | 47.84 | 44.75 | 0 | 0 | 0 | 0 | 3.09 | 0
2025-12-15 15:00 | 44.97 | 40.21 | 40.21 | 4.75 | 0 | 0 | 0 | 0 | 0
2025-12-15 16:00 | 44.69 | 0.59 | 0.59 | 44.1 | 0 | 0 | 0 | 0 | 0
2025-12-15 17:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0 | 0 | 0
2025-12-15 18:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 0 | 0 | 0
2025-12-15 19:00 | 44.08 | 0 | 0 | 44.08 | 0 | 0 | 0 | 0 | 0
2025-12-15 20:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 0 | 0 | 0
2025-12-15 21:00 | 41.95 | 0 | 0 | 41.95 | 0 | 0 | 0 | 0 | 0
2025-12-15 22:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 0 | 0 | 0
2025-12-15 23:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 0 | 0 | 0
2025-12-16 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 0 | 0 | 0
2025-12-16 01:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 0 | 0 | 0
2025-12-16 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0 | 0 | 0
2025-12-16 03:00 | 37.86 | 0 | 0 | 37.86 | 0 | 0 | 0 | 0 | 0
2025-12-16 04:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 0 | 0 | 0
2025-12-16 05:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0 | 0 | 0
2025-12-16 06:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 0 | 0 | 0
2025-12-16 07:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0 | 0 | 0
2025-12-16 08:00 | 40.81 | 0.55 | 0.55 | 40.25 | 0 | 0 | 0 | 0 | 0
2025-12-16 09:00 | 42.42 | 4.72 | 4.72 | 37.7 | 0 | 0 | 0 | 0 | 0
2025-12-16 10:00 | 44.84 | 11.31 | 11.31 | 33.53 | 0 | 0 | 0 | 0 | 0
2025-12-16 11:00 | 47.3 | 12.25 | 12.25 | 35.05 | 0 | 0 | 0 | 0 | 0
2025-12-16 12:00 | 47.29 | 14.59 | 14.59 | 32.7 | 0 | 0 | 0 | 0 | 0
2025-12-16 13:00 | 49.12 | 15.33 | 15.33 | 33.79 | 0 | 0 | 0 | 0 | 0
2025-12-16 14:00 | 49.12 | 6.08 | 6.08 | 43.04 | 0 | 0 | 0 | 0 | 0
2025-12-16 15:00 | 49.62 | 2.94 | 2.94 | 46.68 | 0 | 0 | 0 | 0 | 0
2025-12-16 16:00 | 49.97 | 0 | 0 | 49.97 | 0 | 0 | 0 | 0 | 0
2025-12-16 17:00 | 48.51 | 0 | 0 | 48.51 | 0 | 0 | 0 | 0 | 0
2025-12-16 18:00 | 47.29 | 0 | 0 | 47.29 | 0 | 0 | 0 | 0 | 0
2025-12-16 19:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 0 | 0 | 0
2025-12-16 20:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 0 | 0 | 0
2025-12-16 21:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 0 | 0 | 0
2025-12-16 22:00 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 0 | 0 | 0
2025-12-16 23:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 0 | 0 | 0
2025-12-17 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 0 | 0 | 0
2025-12-17 01:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0 | 0 | 0
2025-12-17 02:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 0 | 0 | 0
2025-12-17 03:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 0 | 0 | 0
2025-12-17 04:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0 | 0 | 0
2025-12-17 05:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 0 | 0 | 0
2025-12-17 06:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 0 | 0 | 0
2025-12-17 07:00 | 40.32 | 0 | 0 | 40.32 | 0 | 0 | 0 | 0 | 0
2025-12-17 08:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0 | 0 | 0
2025-12-17 09:00 | 41.91 | 35.16 | 35.16 | 6.74 | 0 | 0 | 0 | 0 | 0
2025-12-17 10:00 | 43.11 | 1.7 | 1.7 | 41.42 | 0 | 0 | 0 | 0 | 0
2025-12-17 11:00 | 45.45 | 56.46 | 45.45 | 0 | 0 | 0 | 0 | 11.01 | 0
2025-12-17 12:00 | 45.58 | 53.24 | 45.58 | 0 | 0 | 0 | 0 | 7.66 | 0
2025-12-17 13:00 | 47.09 | 61.55 | 47.09 | 0 | 0 | 0 | 0 | 14.46 | 0
2025-12-17 14:00 | 47.51 | 71.57 | 47.51 | 0 | 0 | 0 | 0 | 24.07 | 0
2025-12-17 15:00 | 47.58 | 61.09 | 47.58 | 0 | 0 | 0 | 0 | 13.51 | 0
2025-12-17 16:00 | 47.66 | 1.39 | 1.39 | 46.27 | 0 | 0 | 0 | 0 | 0
2025-12-17 17:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 0 | 0 | 0
2025-12-17 18:00 | 44.8 | 0 | 0 | 44.8 | 0 | 0 | 0 | 0 | 0
2025-12-17 19:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0 | 0 | 0
2025-12-17 20:00 | 44.19 | 0 | 0 | 44.19 | 0 | 0 | 0 | 0 | 0
2025-12-17 21:00 | 43.57 | 0 | 0 | 43.57 | 0 | 0 | 0 | 0 | 0
2025-12-17 22:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 0 | 0 | 0
2025-12-17 23:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 0 | 0 | 0
2025-12-18 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0
2025-12-18 01:00 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 0 | 0 | 0
2025-12-18 02:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 0 | 0 | 0
2025-12-18 03:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0 | 0 | 0
2025-12-18 04:00 | 38.42 | 0 | 0 | 38.42 | 0 | 0 | 0 | 0 | 0
2025-12-18 05:00 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 0 | 0 | 0
2025-12-18 06:00 | 40.1 | 0 | 0 | 40.1 | 0 | 0 | 0 | 0 | 0
2025-12-18 07:00 | 40.97 | 0 | 0 | 40.97 | 0 | 0 | 0 | 0 | 0
2025-12-18 08:00 | 42.1 | 7.54 | 7.54 | 34.55 | 0 | 0 | 0 | 0 | 0
2025-12-18 09:00 | 43.03 | 71.08 | 43.03 | 0 | 0 | 0 | 0 | 28.05 | 0
2025-12-18 10:00 | 43.95 | 65.23 | 43.95 | 0 | 0 | 0 | 0 | 21.28 | 0
2025-12-18 11:00 | 45.78 | 52.28 | 45.78 | 0 | 0 | 0 | 0 | 6.49 | 0
2025-12-18 12:00 | 46.93 | 47.87 | 46.93 | 0 | 0 | 0 | 0 | 0.93 | 0
2025-12-18 13:00 | 47.31 | 55.93 | 47.31 | 0 | 0 | 0 | 0 | 8.62 | 0
2025-12-18 14:00 | 47.8 | 65.34 | 47.8 | 0 | 0 | 0 | 0 | 17.55 | 0
2025-12-18 15:00 | 48.73 | 54.97 | 48.73 | 0 | 0 | 0 | 0 | 6.24 | 0
2025-12-18 16:00 | 48.8 | 0.81 | 0.81 | 47.99 | 0 | 0 | 0 | 0 | 0
2025-12-18 17:00 | 47.03 | 0 | 0 | 47.03 | 0 | 0 | 0 | 0 | 0
2025-12-18 18:00 | 46.39 | 0 | 0 | 46.39 | 0 | 0 | 0 | 0 | 0
2025-12-18 19:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 0 | 0 | 0
2025-12-18 20:00 | 44.37 | 0 | 0 | 44.37 | 0 | 0 | 0 | 0 | 0
2025-12-18 21:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 0 | 0 | 0
2025-12-18 22:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0 | 0 | 0
2025-12-18 23:00 | 40.58 | 0 | 0 | 40.58 | 0 | 0 | 0 | 0 | 0
2025-12-19 | 39.53 | 0 | 0 | 39.53 | 0 | 0 | 0 | 0 | 0
2025-12-19 01:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 0 | 0 | 0
2025-12-19 02:00 | 37.95 | 0 | 0 | 37.95 | 0 | 0 | 0 | 0 | 0
2025-12-19 03:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 0 | 0 | 0
2025-12-19 04:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 0 | 0 | 0
2025-12-19 05:00 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 0 | 0 | 0
2025-12-19 06:00 | 38.52 | 0 | 0 | 38.52 | 0 | 0 | 0 | 0 | 0
2025-12-19 07:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 0 | 0 | 0
2025-12-19 08:00 | 41.31 | 7.38 | 7.38 | 33.93 | 0 | 0 | 0 | 0 | 0
2025-12-19 09:00 | 41.98 | 55.49 | 41.98 | 0 | 0 | 0 | 0 | 13.51 | 0
2025-12-19 10:00 | 43.05 | 37.82 | 37.82 | 5.23 | 0 | 0 | 0 | 0 | 0
2025-12-19 11:00 | 44.38 | 48.92 | 44.38 | 0 | 0 | 0 | 0 | 4.54 | 0
2025-12-19 12:00 | 44.17 | 15.04 | 15.04 | 29.13 | 0 | 0 | 0 | 0 | 0
2025-12-19 13:00 | 45.4 | 19.94 | 19.94 | 25.46 | 0 | 0 | 0 | 0 | 0
2025-12-19 14:00 | 46 | 10.28 | 10.28 | 35.71 | 0 | 0 | 0 | 0 | 0
2025-12-19 15:00 | 44.87 | 2.72 | 2.72 | 42.15 | 0 | 0 | 0 | 0 | 0
2025-12-19 16:00 | 45.99 | 0.47 | 0.47 | 45.52 | 0 | 0 | 0 | 0 | 0
2025-12-19 17:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0 | 0 | 0
2025-12-19 18:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0 | 0 | 0
2025-12-19 19:00 | 43.41 | 0 | 0 | 43.41 | 0 | 0 | 0 | 0 | 0
2025-12-19 20:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 0 | 0 | 0
2025-12-19 21:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 0 | 0 | 0
2025-12-19 22:00 | 40.27 | 0 | 0 | 40.27 | 0 | 0 | 0 | 0 | 0
2025-12-19 23:00 | 40.19 | 0 | 0 | 40.19 | 0 | 0 | 0 | 0 | 0
2025-12-20 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0 | 0 | 0
2025-12-20 01:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0 | 0 | 0
2025-12-20 02:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 0 | 0 | 0
2025-12-20 03:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 0 | 0 | 0
2025-12-20 04:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0 | 0 | 0
2025-12-20 05:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0 | 0 | 0
2025-12-20 06:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0 | 0 | 0
2025-12-20 07:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 0 | 0 | 0
2025-12-20 08:00 | 41.83 | 6.94 | 6.94 | 34.89 | 0 | 0 | 0 | 0 | 0
2025-12-20 09:00 | 42.45 | 57.74 | 42.45 | 0 | 0 | 0 | 0 | 15.29 | 0
2025-12-20 10:00 | 42.6 | 57.04 | 42.6 | 0 | 0 | 0 | 0 | 14.45 | 0
2025-12-20 11:00 | 45.24 | 50.14 | 45.24 | 0 | 0 | 0 | 0 | 4.9 | 0
2025-12-20 12:00 | 46.87 | 41.76 | 41.76 | 5.11 | 0 | 0 | 0 | 0 | 0
2025-12-20 13:00 | 47.6 | 50.76 | 47.6 | 0 | 0 | 0 | 0 | 3.16 | 0
2025-12-20 14:00 | 47.76 | 61.07 | 47.76 | 0 | 0 | 0 | 0 | 13.31 | 0
2025-12-20 15:00 | 47.13 | 44.41 | 44.41 | 2.72 | 0 | 0 | 0 | 0 | 0
2025-12-20 16:00 | 47.27 | 0.82 | 0.82 | 46.45 | 0 | 0 | 0 | 0 | 0
2025-12-20 17:00 | 47.96 | 0 | 0 | 47.96 | 0 | 0 | 0 | 0 | 0
2025-12-20 18:00 | 45.43 | 0 | 0 | 45.43 | 0 | 0 | 0 | 0 | 0
2025-12-20 19:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 0 | 0 | 0
2025-12-20 20:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 0 | 0 | 0
2025-12-20 21:00 | 42.31 | 0 | 0 | 42.31 | 0 | 0 | 0 | 0 | 0
2025-12-20 22:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 0 | 0 | 0
2025-12-20 23:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0 | 0 | 0
2025-12-21 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 0 | 0 | 0
2025-12-21 01:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 0 | 0 | 0
2025-12-21 02:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0 | 0 | 0
2025-12-21 03:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 0 | 0 | 0
2025-12-21 04:00 | 38.01 | 0 | 0 | 38.01 | 0 | 0 | 0 | 0 | 0
2025-12-21 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0 | 0 | 0
2025-12-21 06:00 | 39.59 | 0 | 0 | 39.59 | 0 | 0 | 0 | 0 | 0
2025-12-21 07:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0 | 0 | 0
2025-12-21 08:00 | 40.96 | 6.32 | 6.32 | 34.64 | 0 | 0 | 0 | 0 | 0
2025-12-21 09:00 | 43.22 | 51.06 | 43.22 | 0 | 0 | 0 | 0 | 7.84 | 0
2025-12-21 10:00 | 44.55 | 57.26 | 44.55 | 0 | 0 | 0 | 0 | 12.71 | 0
2025-12-21 11:00 | 44.17 | 51.15 | 44.17 | 0 | 0 | 0 | 0 | 6.99 | 0
2025-12-21 12:00 | 46.52 | 45.12 | 45.12 | 1.4 | 0 | 0 | 0 | 0 | 0
2025-12-21 13:00 | 47.08 | 46.26 | 46.26 | 0.82 | 0 | 0 | 0 | 0 | 0
2025-12-21 14:00 | 47.2 | 54.44 | 47.2 | 0 | 0 | 0 | 0 | 7.23 | 0
2025-12-21 15:00 | 48.05 | 43.47 | 43.47 | 4.57 | 0 | 0 | 0 | 0 | 0
2025-12-21 16:00 | 47.04 | 0.9 | 0.9 | 46.14 | 0 | 0 | 0 | 0 | 0
2025-12-21 17:00 | 46.91 | 0 | 0 | 46.91 | 0 | 0 | 0 | 0 | 0
2025-12-21 18:00 | 45.85 | 0 | 0 | 45.85 | 0 | 0 | 0 | 0 | 0
2025-12-21 19:00 | 44.85 | 0 | 0 | 44.85 | 0 | 0 | 0 | 0 | 0
2025-12-21 20:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0 | 0 | 0
2025-12-21 21:00 | 41.99 | 0 | 0 | 41.99 | 0 | 0 | 0 | 0 | 0
2025-12-21 22:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 0 | 0 | 0
2025-12-21 23:00 | 40.33 | 0 | 0 | 40.33 | 0 | 0 | 0 | 0 | 0
2025-12-22 | 39.93 | 0 | 0 | 39.93 | 0 | 0 | 0 | 0 | 0
2025-12-22 01:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 0 | 0 | 0
2025-12-22 02:00 | 37.68 | 0 | 0 | 37.68 | 0 | 0 | 0 | 0 | 0
2025-12-22 03:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 0 | 0 | 0
2025-12-22 04:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0 | 0 | 0
2025-12-22 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0 | 0 | 0
2025-12-22 06:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 0 | 0 | 0
2025-12-22 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0 | 0 | 0
2025-12-22 08:00 | 41.3 | 6.67 | 6.67 | 34.63 | 0 | 0 | 0 | 0 | 0
2025-12-22 09:00 | 42.35 | 68.52 | 42.35 | 0 | 0 | 0 | 0 | 26.17 | 0
2025-12-22 10:00 | 43.82 | 64.47 | 43.82 | 0 | 0 | 0 | 0 | 20.65 | 0
2025-12-22 11:00 | 44.69 | 52.58 | 44.69 | 0 | 0 | 0 | 0 | 7.88 | 0
2025-12-22 12:00 | 45.81 | 30.65 | 30.65 | 15.17 | 0 | 0 | 0 | 0 | 0
2025-12-22 13:00 | 45.82 | 38.27 | 38.27 | 7.55 | 0 | 0 | 0 | 0 | 0
2025-12-22 14:00 | 45.89 | 62.67 | 45.89 | 0 | 0 | 0 | 0 | 16.78 | 0
2025-12-22 15:00 | 47.53 | 59.37 | 47.53 | 0 | 0 | 0 | 0 | 11.84 | 0
2025-12-22 16:00 | 45.56 | 2.11 | 2.11 | 43.45 | 0 | 0 | 0 | 0 | 0
2025-12-22 17:00 | 45.16 | 0 | 0 | 45.16 | 0 | 0 | 0 | 0 | 0
2025-12-22 18:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0 | 0 | 0
2025-12-22 19:00 | 45.06 | 0 | 0 | 45.06 | 0 | 0 | 0 | 0 | 0
2025-12-22 20:00 | 43.28 | 0 | 0 | 43.28 | 0 | 0 | 0 | 0 | 0
2025-12-22 21:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 0 | 0 | 0
2025-12-22 22:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 0 | 0 | 0
2025-12-22 23:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 0 | 0 | 0
2025-12-23 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0 | 0 | 0
2025-12-23 01:00 | 38.68 | 0 | 0 | 38.68 | 0 | 0 | 0 | 0 | 0
2025-12-23 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 0 | 0 | 0
2025-12-23 03:00 | 37.1 | 0 | 0 | 37.1 | 0 | 0 | 0 | 0 | 0
2025-12-23 04:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 0 | 0 | 0
2025-12-23 05:00 | 38.83 | 0 | 0 | 38.83 | 0 | 0 | 0 | 0 | 0
2025-12-23 06:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 0 | 0 | 0
2025-12-23 07:00 | 40.1 | 0 | 0 | 40.1 | 0 | 0 | 0 | 0 | 0
2025-12-23 08:00 | 41.11 | 0 | 0 | 41.11 | 0 | 0 | 0 | 0 | 0
2025-12-23 09:00 | 41.83 | 30.36 | 30.36 | 11.48 | 0 | 0 | 0 | 0 | 0
2025-12-23 10:00 | 42.51 | 1.39 | 1.39 | 41.11 | 0 | 0 | 0 | 0 | 0
2025-12-23 11:00 | 44.39 | 39.99 | 39.99 | 4.39 | 0 | 0 | 0 | 0 | 0
2025-12-23 12:00 | 45.32 | 45.52 | 45.32 | 0 | 0 | 0 | 0 | 0.21 | 0
2025-12-23 13:00 | 46.16 | 52.62 | 46.16 | 0 | 0 | 0 | 0 | 6.46 | 0
2025-12-23 14:00 | 46.31 | 60.86 | 46.31 | 0 | 0 | 0 | 0 | 14.55 | 0
2025-12-23 15:00 | 45.73 | 52.09 | 45.73 | 0 | 0 | 0 | 0 | 6.37 | 0
2025-12-23 16:00 | 46.5 | 2.39 | 2.39 | 44.11 | 0 | 0 | 0 | 0 | 0
2025-12-23 17:00 | 45.71 | 0 | 0 | 45.71 | 0 | 0 | 0 | 0 | 0
2025-12-23 18:00 | 44.77 | 0 | 0 | 44.77 | 0 | 0 | 0 | 0 | 0
2025-12-23 19:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 0 | 0 | 0
2025-12-23 20:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0 | 0 | 0
2025-12-23 21:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 0 | 0 | 0
2025-12-23 22:00 | 40.13 | 0 | 0 | 40.13 | 0 | 0 | 0 | 0 | 0
2025-12-23 23:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 0 | 0 | 0
2025-12-24 | 38.71 | 0 | 0 | 38.71 | 0 | 0 | 0 | 0 | 0
2025-12-24 01:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 0 | 0 | 0
2025-12-24 02:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0 | 0 | 0
2025-12-24 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 0 | 0 | 0
2025-12-24 04:00 | 38.49 | 0 | 0 | 38.49 | 0 | 0 | 0 | 0 | 0
2025-12-24 05:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 0 | 0 | 0
2025-12-24 06:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 0 | 0 | 0
2025-12-24 07:00 | 38.47 | 0 | 0 | 38.47 | 0 | 0 | 0 | 0 | 0
2025-12-24 08:00 | 40.71 | 0 | 0 | 40.71 | 0 | 0 | 0 | 0 | 0
2025-12-24 09:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 0 | 0 | 0
2025-12-24 10:00 | 43.74 | 1.5 | 1.5 | 42.24 | 0 | 0 | 0 | 0 | 0
2025-12-24 11:00 | 43.56 | 2.49 | 2.49 | 41.07 | 0 | 0 | 0 | 0 | 0
2025-12-24 12:00 | 45.78 | 2.61 | 2.61 | 43.17 | 0 | 0 | 0 | 0 | 0
2025-12-24 13:00 | 44.49 | 33.87 | 33.87 | 10.62 | 0 | 0 | 0 | 0 | 0
2025-12-24 14:00 | 45.86 | 35.06 | 35.06 | 10.81 | 0 | 0 | 0 | 0 | 0
2025-12-24 15:00 | 45.99 | 27.93 | 27.93 | 18.06 | 0 | 0 | 0 | 0 | 0
2025-12-24 16:00 | 46.62 | 0.77 | 0.77 | 45.85 | 0 | 0 | 0 | 0 | 0
2025-12-24 17:00 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 0 | 0 | 0
2025-12-24 18:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 0 | 0 | 0
2025-12-24 19:00 | 43.32 | 0 | 0 | 43.32 | 0 | 0 | 0 | 0 | 0
2025-12-24 20:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 0 | 0 | 0
2025-12-24 21:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0 | 0 | 0
2025-12-24 22:00 | 39.91 | 0 | 0 | 39.91 | 0 | 0 | 0 | 0 | 0
2025-12-24 23:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 0 | 0 | 0
2025-12-25 | 39.28 | 0 | 0 | 39.28 | 0 | 0 | 0 | 0 | 0
2025-12-25 01:00 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 0 | 0 | 0
2025-12-25 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 0 | 0 | 0
2025-12-25 03:00 | 37.51 | 0 | 0 | 37.51 | 0 | 0 | 0 | 0 | 0
2025-12-25 04:00 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 0 | 0 | 0
2025-12-25 05:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 0 | 0 | 0
2025-12-25 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 0 | 0 | 0
2025-12-25 07:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0 | 0 | 0
2025-12-25 08:00 | 40.92 | 5.51 | 5.51 | 35.41 | 0 | 0 | 0 | 0 | 0
2025-12-25 09:00 | 41.15 | 30.96 | 30.96 | 10.19 | 0 | 0 | 0 | 0 | 0
2025-12-25 10:00 | 42.03 | 23.64 | 23.64 | 18.39 | 0 | 0 | 0 | 0 | 0
2025-12-25 11:00 | 43.12 | 26.11 | 26.11 | 17 | 0 | 0 | 0 | 0 | 0
2025-12-25 12:00 | 43 | 30.88 | 30.88 | 12.11 | 0 | 0 | 0 | 0 | 0
2025-12-25 13:00 | 44.18 | 49.53 | 44.18 | 0 | 0 | 0 | 0 | 5.34 | 0
2025-12-25 14:00 | 43.64 | 56.96 | 43.64 | 0 | 0 | 0 | 0 | 13.32 | 0
2025-12-25 15:00 | 44.36 | 47.82 | 44.36 | 0 | 0 | 0 | 0 | 3.46 | 0
2025-12-25 16:00 | 43.72 | 2.47 | 2.47 | 41.25 | 0 | 0 | 0 | 0 | 0
2025-12-25 17:00 | 43.46 | 0 | 0 | 43.46 | 0 | 0 | 0 | 0 | 0
2025-12-25 18:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 0 | 0 | 0
2025-12-25 19:00 | 42.97 | 0 | 0 | 42.97 | 0 | 0 | 0 | 0 | 0
2025-12-25 20:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0 | 0 | 0
2025-12-25 21:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 0 | 0 | 0
2025-12-25 22:00 | 40.12 | 0 | 0 | 40.12 | 0 | 0 | 0 | 0 | 0
2025-12-25 23:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 0 | 0 | 0
2025-12-26 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0 | 0 | 0
2025-12-26 01:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 0 | 0 | 0
2025-12-26 02:00 | 37.79 | 0 | 0 | 37.79 | 0 | 0 | 0 | 0 | 0
2025-12-26 03:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 0 | 0 | 0
2025-12-26 04:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0 | 0 | 0
2025-12-26 05:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0 | 0 | 0
2025-12-26 06:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 0 | 0 | 0
2025-12-26 07:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 0 | 0 | 0
2025-12-26 08:00 | 39.92 | 4.49 | 4.49 | 35.43 | 0 | 0 | 0 | 0 | 0
2025-12-26 09:00 | 41.84 | 50.98 | 41.84 | 0 | 0 | 0 | 0 | 9.14 | 0
2025-12-26 10:00 | 41.11 | 57.88 | 41.11 | 0 | 0 | 0 | 0 | 16.77 | 0
2025-12-26 11:00 | 43.17 | 48.67 | 43.17 | 0 | 0 | 0 | 0 | 5.5 | 0
2025-12-26 12:00 | 44.89 | 36.25 | 36.25 | 8.64 | 0 | 0 | 0 | 0 | 0
2025-12-26 13:00 | 44.78 | 28.2 | 28.2 | 16.58 | 0 | 0 | 0 | 0 | 0
2025-12-26 14:00 | 45.6 | 15.06 | 15.06 | 30.55 | 0 | 0 | 0 | 0 | 0
2025-12-26 15:00 | 44.46 | 6.19 | 6.19 | 38.27 | 0 | 0 | 0 | 0 | 0
2025-12-26 16:00 | 44.36 | 0.84 | 0.84 | 43.52 | 0 | 0 | 0 | 0 | 0
2025-12-26 17:00 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 0 | 0 | 0
2025-12-26 18:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 0 | 0 | 0
2025-12-26 19:00 | 43.44 | 0 | 0 | 43.44 | 0 | 0 | 0 | 0 | 0
2025-12-26 20:00 | 41.91 | 0 | 0 | 41.91 | 0 | 0 | 0 | 0 | 0
2025-12-26 21:00 | 41.52 | 0 | 0 | 41.52 | 0 | 0 | 0 | 0 | 0
2025-12-26 22:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0 | 0 | 0
2025-12-26 23:00 | 40.12 | 0 | 0 | 40.12 | 0 | 0 | 0 | 0 | 0
2025-12-27 | 40 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0
2025-12-27 01:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 0 | 0 | 0
2025-12-27 02:00 | 37.31 | 0 | 0 | 37.31 | 0 | 0 | 0 | 0 | 0
2025-12-27 03:00 | 36.22 | 0 | 0 | 36.22 | 0 | 0 | 0 | 0 | 0
2025-12-27 04:00 | 36.78 | 0 | 0 | 36.78 | 0 | 0 | 0 | 0 | 0
2025-12-27 05:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 0 | 0 | 0
2025-12-27 06:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-12-27 07:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 0 | 0 | 0
2025-12-27 08:00 | 40.7 | 0 | 0 | 40.7 | 0 | 0 | 0 | 0 | 0
2025-12-27 09:00 | 42.11 | 1.65 | 1.65 | 40.46 | 0 | 0 | 0 | 0 | 0
2025-12-27 10:00 | 42.25 | 4.31 | 4.31 | 37.94 | 0 | 0 | 0 | 0 | 0
2025-12-27 11:00 | 43.06 | 6 | 6 | 37.06 | 0 | 0 | 0 | 0 | 0
2025-12-27 12:00 | 44.08 | 6.12 | 6.12 | 37.96 | 0 | 0 | 0 | 0 | 0
2025-12-27 13:00 | 44.32 | 5.68 | 5.68 | 38.64 | 0 | 0 | 0 | 0 | 0
2025-12-27 14:00 | 44.72 | 4.63 | 4.63 | 40.09 | 0 | 0 | 0 | 0 | 0
2025-12-27 15:00 | 45.34 | 2.01 | 2.01 | 43.33 | 0 | 0 | 0 | 0 | 0
2025-12-27 16:00 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 0 | 0 | 0
2025-12-27 17:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 0 | 0 | 0
2025-12-27 18:00 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 0 | 0 | 0
2025-12-27 19:00 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 0 | 0 | 0
2025-12-27 20:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 0 | 0 | 0
2025-12-27 21:00 | 41.63 | 0 | 0 | 41.63 | 0 | 0 | 0 | 0 | 0
2025-12-27 22:00 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 0 | 0 | 0
2025-12-27 23:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 0 | 0 | 0
2025-12-28 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0 | 0 | 0
2025-12-28 01:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 0 | 0 | 0
2025-12-28 02:00 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 0 | 0 | 0
2025-12-28 03:00 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0 | 0 | 0
2025-12-28 04:00 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 0 | 0 | 0
2025-12-28 05:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0 | 0 | 0
2025-12-28 06:00 | 39.47 | 0 | 0 | 39.47 | 0 | 0 | 0 | 0 | 0
2025-12-28 07:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 0 | 0 | 0
2025-12-28 08:00 | 41.07 | 1.27 | 1.27 | 39.8 | 0 | 0 | 0 | 0 | 0
2025-12-28 09:00 | 40.96 | 7.21 | 7.21 | 33.75 | 0 | 0 | 0 | 0 | 0
2025-12-28 10:00 | 42.26 | 24.56 | 24.56 | 17.7 | 0 | 0 | 0 | 0 | 0
2025-12-28 11:00 | 43.85 | 35.14 | 35.14 | 8.71 | 0 | 0 | 0 | 0 | 0
2025-12-28 12:00 | 45.08 | 24.58 | 24.58 | 20.5 | 0 | 0 | 0 | 0 | 0
2025-12-28 13:00 | 44.58 | 23.44 | 23.44 | 21.14 | 0 | 0 | 0 | 0 | 0
2025-12-28 14:00 | 45.34 | 13.97 | 13.97 | 31.37 | 0 | 0 | 0 | 0 | 0
2025-12-28 15:00 | 45.79 | 0 | 0 | 45.79 | 0 | 0 | 0 | 0 | 0
2025-12-28 16:00 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 0 | 0 | 0
2025-12-28 17:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 0 | 0 | 0
2025-12-28 18:00 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 0 | 0 | 0
2025-12-28 19:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0 | 0 | 0
2025-12-28 20:00 | 42.17 | 0 | 0 | 42.17 | 0 | 0 | 0 | 0 | 0
2025-12-28 21:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 0 | 0 | 0
2025-12-28 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 0 | 0 | 0
2025-12-28 23:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 0 | 0 | 0
2025-12-29 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 0 | 0 | 0
2025-12-29 01:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0 | 0 | 0
2025-12-29 02:00 | 37.28 | 0 | 0 | 37.28 | 0 | 0 | 0 | 0 | 0
2025-12-29 03:00 | 38.37 | 0 | 0 | 38.37 | 0 | 0 | 0 | 0 | 0
2025-12-29 04:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 0 | 0 | 0
2025-12-29 05:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 0 | 0 | 0
2025-12-29 06:00 | 38.85 | 0 | 0 | 38.85 | 0 | 0 | 0 | 0 | 0
2025-12-29 07:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0 | 0 | 0
2025-12-29 08:00 | 41.06 | 1.44 | 1.44 | 39.62 | 0 | 0 | 0 | 0 | 0
2025-12-29 09:00 | 41.78 | 42.2 | 41.78 | 0 | 0 | 0 | 0 | 0.42 | 0
2025-12-29 10:00 | 43.29 | 52.54 | 43.29 | 0 | 0 | 0 | 0 | 9.25 | 0
2025-12-29 11:00 | 43.59 | 30.65 | 30.65 | 12.94 | 0 | 0 | 0 | 0 | 0
2025-12-29 12:00 | 45.41 | 26.19 | 26.19 | 19.22 | 0 | 0 | 0 | 0 | 0
2025-12-29 13:00 | 46.21 | 21.87 | 21.87 | 24.34 | 0 | 0 | 0 | 0 | 0
2025-12-29 14:00 | 47.04 | 7.55 | 7.55 | 39.49 | 0 | 0 | 0 | 0 | 0
2025-12-29 15:00 | 45.62 | 1.11 | 1.11 | 44.51 | 0 | 0 | 0 | 0 | 0
2025-12-29 16:00 | 45.82 | 0.49 | 0.49 | 45.33 | 0 | 0 | 0 | 0 | 0
2025-12-29 17:00 | 46.17 | 0 | 0 | 46.17 | 0 | 0 | 0 | 0 | 0
2025-12-29 18:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 0 | 0 | 0
2025-12-29 19:00 | 44.17 | 0 | 0 | 44.17 | 0 | 0 | 0 | 0 | 0
2025-12-29 20:00 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 0 | 0 | 0
2025-12-29 21:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 0 | 0 | 0
2025-12-29 22:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 0 | 0 | 0
2025-12-29 23:00 | 38.85 | 0 | 0 | 38.85 | 0 | 0 | 0 | 0 | 0
2025-12-30 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0 | 0 | 0
2025-12-30 01:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0 | 0 | 0
2025-12-30 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 0 | 0 | 0
2025-12-30 03:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 0 | 0 | 0
2025-12-30 04:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0 | 0 | 0
2025-12-30 05:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0 | 0 | 0
2025-12-30 06:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0 | 0 | 0
2025-12-30 07:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 0 | 0 | 0
2025-12-30 08:00 | 40.12 | 0.6 | 0.6 | 39.52 | 0 | 0 | 0 | 0 | 0
2025-12-30 09:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 0 | 0 | 0
2025-12-30 10:00 | 41.25 | 14.1 | 14.1 | 27.15 | 0 | 0 | 0 | 0 | 0
2025-12-30 11:00 | 41.37 | 25.69 | 25.69 | 15.68 | 0 | 0 | 0 | 0 | 0
2025-12-30 12:00 | 41.98 | 28.94 | 28.94 | 13.04 | 0 | 0 | 0 | 0 | 0
2025-12-30 13:00 | 42.56 | 25.88 | 25.88 | 16.68 | 0 | 0 | 0 | 0 | 0
2025-12-30 14:00 | 43.5 | 41.17 | 41.17 | 2.33 | 0 | 0 | 0 | 0 | 0
2025-12-30 15:00 | 44.03 | 44.8 | 44.03 | 0 | 0 | 0 | 0 | 0.78 | 0
2025-12-30 16:00 | 42.52 | 4.24 | 4.24 | 38.27 | 0 | 0 | 0 | 0 | 0
2025-12-30 17:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 0 | 0 | 0
2025-12-30 18:00 | 42.08 | 0 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0
2025-12-30 19:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0 | 0 | 0
2025-12-30 20:00 | 42.08 | 0 | 0 | 42.08 | 0 | 0 | 0 | 0 | 0
2025-12-30 21:00 | 40.55 | 0 | 0 | 40.55 | 0 | 0 | 0 | 0 | 0
2025-12-30 22:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 0 | 0 | 0
2025-12-30 23:00 | 39.86 | 0 | 0 | 39.86 | 0 | 0 | 0 | 0 | 0
2025-12-31 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 0 | 0 | 0
2025-12-31 01:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 0 | 0 | 0
2025-12-31 02:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 0 | 0 | 0
2025-12-31 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 0 | 0 | 0
2025-12-31 04:00 | 37.61 | 0 | 0 | 37.61 | 0 | 0 | 0 | 0 | 0
2025-12-31 05:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 0 | 0 | 0
2025-12-31 06:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0 | 0 | 0
2025-12-31 07:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0 | 0 | 0
2025-12-31 08:00 | 39.98 | 3.92 | 3.92 | 36.06 | 0 | 0 | 0 | 0 | 0
2025-12-31 09:00 | 41.27 | 39.39 | 39.39 | 1.88 | 0 | 0 | 0 | 0 | 0
2025-12-31 10:00 | 42.37 | 44.25 | 42.37 | 0 | 0 | 0 | 0 | 1.88 | 0
2025-12-31 11:00 | 43.07 | 48.76 | 43.07 | 0 | 0 | 0 | 0 | 5.69 | 0
2025-12-31 12:00 | 43.43 | 42.22 | 42.22 | 1.22 | 0 | 0 | 0 | 0 | 0
2025-12-31 13:00 | 44.63 | 57.55 | 44.63 | 0 | 0 | 0 | 0 | 12.93 | 0
2025-12-31 14:00 | 44.08 | 69.02 | 44.08 | 0 | 0 | 0 | 0 | 24.94 | 0
2025-12-31 15:00 | 43.98 | 68.72 | 43.98 | 0 | 0 | 0 | 0 | 24.74 | 0
2025-12-31 16:00 | 42.92 | 6.19 | 6.19 | 36.73 | 0 | 0 | 0 | 0 | 0
2025-12-31 17:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 0 | 0 | 0
2025-12-31 18:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0 | 0 | 0
2025-12-31 19:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0 | 0 | 0
2025-12-31 20:00 | 40.97 | 0 | 0 | 40.97 | 0 | 0 | 0 | 0 | 0
2025-12-31 21:00 | 40.68 | 0 | 0 | 40.68 | 0 | 0 | 0 | 0 | 0
2025-12-31 22:00 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 0 | 0 | 0
2025-12-31 23:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 0 | 0 | 0

## Sim_SSR40pct
Timestamp | Load (MW) | PV available (MW) | PV used on-site (MW) | Grid import (MW) | BESS charge (MW) | BESS discharge (MW) | BESS state of charge (MWh) | PV curtailed (MW) | Unmet load (MW)
2025-01-01 | 39.07 | 0 | 0 | 36.48 | 0 | 2.58 | 0.68 | 0 | 0
2025-01-01 01:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 03:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 04:00 | 37.77 | 0 | 0 | 37.77 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 05:00 | 37.73 | 0 | 0 | 37.73 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 06:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 07:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 08:00 | 40.47 | 0.35 | 0.35 | 40.12 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 09:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 10:00 | 43.25 | 39.6 | 39.6 | 3.65 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 11:00 | 42.95 | 51.11 | 46.35 | 0 | 3.4 | 0 | 3.91 | 4.76 | 0
2025-01-01 12:00 | 42.89 | 47.41 | 45.22 | 0 | 2.33 | 0 | 6.12 | 2.19 | 0
2025-01-01 13:00 | 45.35 | 15.24 | 15.24 | 26.71 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-01 14:00 | 44.73 | 17.49 | 17.49 | 25.47 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-01 15:00 | 45.16 | 7.79 | 7.79 | 37.36 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 16:00 | 45.62 | 0.73 | 0.73 | 44.89 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 17:00 | 43.75 | 0 | 0 | 43.75 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 18:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 19:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 20:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 21:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 22:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 0.68 | 0 | 0
2025-01-01 23:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 01:00 | 36.51 | 0 | 0 | 36.51 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 02:00 | 37.33 | 0 | 0 | 37.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 04:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 05:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 06:00 | 38.3 | 0 | 0 | 38.3 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 07:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 08:00 | 39.84 | 3.35 | 3.35 | 36.49 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 09:00 | 40.79 | 0.73 | 0.73 | 40.07 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 10:00 | 40.93 | 11.93 | 11.93 | 29 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 11:00 | 41.86 | 40.23 | 40.23 | 1.63 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 12:00 | 42.58 | 49.61 | 45.98 | 0 | 3.4 | 0 | 3.91 | 3.63 | 0
2025-01-02 13:00 | 43.28 | 52.12 | 45.61 | 0 | 2.33 | 0 | 6.12 | 6.51 | 0
2025-01-02 14:00 | 42.91 | 35.75 | 35.75 | 3.77 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-02 15:00 | 43.45 | 53.79 | 46.85 | 0 | 3.4 | 0 | 5.77 | 6.94 | 0
2025-01-02 16:00 | 42.98 | 6.95 | 6.95 | 32.62 | 0 | 3.4 | 2.19 | 0 | 0
2025-01-02 17:00 | 42.81 | 0 | 0 | 41.38 | 0 | 1.44 | 0.68 | 0 | 0
2025-01-02 18:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 19:00 | 40.95 | 0 | 0 | 40.95 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 20:00 | 40.64 | 0 | 0 | 40.64 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 21:00 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 22:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 0.68 | 0 | 0
2025-01-02 23:00 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 01:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 02:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 03:00 | 37.67 | 0 | 0 | 37.67 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 04:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 05:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 06:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 07:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 08:00 | 39.56 | 5.56 | 5.56 | 34 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 09:00 | 40.75 | 58.94 | 44.15 | 0 | 3.4 | 0 | 3.91 | 14.79 | 0
2025-01-03 10:00 | 41.4 | 61.46 | 43.72 | 0 | 2.33 | 0 | 6.12 | 17.74 | 0
2025-01-03 11:00 | 42.74 | 45.74 | 42.74 | 0 | 0 | 0 | 6.12 | 3 | 0
2025-01-03 12:00 | 43.93 | 43.72 | 43.72 | 0 | 0 | 0.22 | 5.89 | 0 | 0
2025-01-03 13:00 | 45.24 | 53.25 | 45.47 | 0 | 0.24 | 0 | 6.12 | 7.78 | 0
2025-01-03 14:00 | 46.16 | 56.05 | 46.16 | 0 | 0 | 0 | 6.12 | 9.89 | 0
2025-01-03 15:00 | 44.76 | 59.27 | 44.76 | 0 | 0 | 0 | 6.12 | 14.51 | 0
2025-01-03 16:00 | 45.49 | 2.76 | 2.76 | 39.33 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-03 17:00 | 44.31 | 0 | 0 | 42.55 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-03 18:00 | 44.35 | 0 | 0 | 44.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 19:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 20:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 21:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 22:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 0.68 | 0 | 0
2025-01-03 23:00 | 38.76 | 0 | 0 | 38.76 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 | 37.64 | 0 | 0 | 37.64 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 01:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 02:00 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 03:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 04:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 05:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 06:00 | 38.84 | 0 | 0 | 38.84 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 07:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 08:00 | 39.21 | 5.61 | 5.61 | 33.61 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 09:00 | 41.56 | 63.95 | 44.96 | 0 | 3.4 | 0 | 3.91 | 18.98 | 0
2025-01-04 10:00 | 41.98 | 65.08 | 44.31 | 0 | 2.33 | 0 | 6.12 | 20.77 | 0
2025-01-04 11:00 | 43.79 | 50.17 | 43.79 | 0 | 0 | 0 | 6.12 | 6.38 | 0
2025-01-04 12:00 | 44.38 | 45.3 | 44.38 | 0 | 0 | 0 | 6.12 | 0.92 | 0
2025-01-04 13:00 | 44.88 | 44.2 | 44.2 | 0 | 0 | 0.68 | 5.4 | 0 | 0
2025-01-04 14:00 | 45.6 | 40.92 | 40.92 | 1.28 | 0 | 3.4 | 1.82 | 0 | 0
2025-01-04 15:00 | 46.56 | 17.8 | 17.8 | 27.68 | 0 | 1.09 | 0.68 | 0 | 0
2025-01-04 16:00 | 46.46 | 2.17 | 2.17 | 44.29 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 17:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 18:00 | 44.27 | 0 | 0 | 44.27 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 19:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 20:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 21:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 22:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-04 23:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 01:00 | 36.72 | 0 | 0 | 36.72 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 02:00 | 36.13 | 0 | 0 | 36.13 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 03:00 | 36.48 | 0 | 0 | 36.48 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 04:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 05:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 06:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 07:00 | 39.24 | 0 | 0 | 39.24 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 08:00 | 38.89 | 5.6 | 5.6 | 33.29 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 09:00 | 40.19 | 69.74 | 43.59 | 0 | 3.4 | 0 | 3.91 | 26.15 | 0
2025-01-05 10:00 | 40.38 | 56.56 | 42.7 | 0 | 2.33 | 0 | 6.12 | 13.86 | 0
2025-01-05 11:00 | 40.89 | 41.29 | 40.89 | 0 | 0 | 0 | 6.12 | 0.4 | 0
2025-01-05 12:00 | 41.45 | 37.95 | 37.95 | 0.1 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-05 13:00 | 41.88 | 35.68 | 35.68 | 4.43 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-05 14:00 | 41.52 | 22.65 | 22.65 | 18.87 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 15:00 | 42.25 | 33.53 | 33.53 | 8.72 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 16:00 | 41.11 | 5.31 | 5.31 | 35.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 17:00 | 41.57 | 0 | 0 | 41.57 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 18:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 19:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 20:00 | 41.3 | 0 | 0 | 41.3 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 21:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 22:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-05 23:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 01:00 | 37.09 | 0 | 0 | 37.09 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 02:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 03:00 | 36.58 | 0 | 0 | 36.58 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 04:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 05:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 06:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 07:00 | 38.54 | 0 | 0 | 38.54 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 08:00 | 39.65 | 1.65 | 1.65 | 38 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 09:00 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 10:00 | 41.31 | 31.52 | 31.52 | 9.79 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 11:00 | 40.51 | 40.66 | 40.66 | 0 | 0.15 | 0 | 0.82 | 0 | 0
2025-01-06 12:00 | 41.72 | 35.39 | 35.39 | 6.2 | 0 | 0.13 | 0.68 | 0 | 0
2025-01-06 13:00 | 41.22 | 32.44 | 32.44 | 8.78 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 14:00 | 41.67 | 25.68 | 25.68 | 15.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 15:00 | 43.16 | 4.26 | 4.26 | 38.91 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 16:00 | 42.86 | 1.43 | 1.43 | 41.44 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 17:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 18:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 19:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 20:00 | 40.57 | 0 | 0 | 40.57 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 21:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 22:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 0.68 | 0 | 0
2025-01-06 23:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 01:00 | 36.66 | 0 | 0 | 36.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 03:00 | 37.02 | 0 | 0 | 37.02 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 04:00 | 37.04 | 0 | 0 | 37.04 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 05:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 06:00 | 38.18 | 0 | 0 | 38.18 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 07:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 08:00 | 39.28 | 0 | 0 | 39.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 09:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 10:00 | 42.32 | 2.3 | 2.3 | 40.01 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 11:00 | 41.9 | 6.14 | 6.14 | 35.76 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 12:00 | 42.7 | 5.59 | 5.59 | 37.12 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 13:00 | 44.4 | 41.59 | 41.59 | 2.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 14:00 | 44.01 | 44.55 | 44.55 | 0 | 0.54 | 0 | 1.2 | 0 | 0
2025-01-07 15:00 | 44.93 | 49.89 | 48.33 | 0 | 3.4 | 0 | 4.43 | 1.56 | 0
2025-01-07 16:00 | 43.88 | 3.06 | 3.06 | 37.42 | 0 | 3.4 | 0.85 | 0 | 0
2025-01-07 17:00 | 44.46 | 0 | 0 | 44.3 | 0 | 0.16 | 0.68 | 0 | 0
2025-01-07 18:00 | 43.21 | 0 | 0 | 43.21 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 19:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 20:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 21:00 | 40.38 | 0 | 0 | 40.38 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 22:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0.68 | 0 | 0
2025-01-07 23:00 | 38.53 | 0 | 0 | 38.53 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 | 38.18 | 0 | 0 | 38.18 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 01:00 | 36.62 | 0 | 0 | 36.62 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 02:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 03:00 | 36.66 | 0 | 0 | 36.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 04:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 05:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 06:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 07:00 | 37.83 | 0 | 0 | 37.83 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 08:00 | 39.08 | 2.87 | 2.87 | 36.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 09:00 | 40.48 | 54.59 | 43.88 | 0 | 3.4 | 0 | 3.91 | 10.7 | 0
2025-01-08 10:00 | 41.12 | 46.52 | 43.45 | 0 | 2.33 | 0 | 6.12 | 3.07 | 0
2025-01-08 11:00 | 41.87 | 40.62 | 40.62 | 0 | 0 | 1.24 | 4.81 | 0 | 0
2025-01-08 12:00 | 42.58 | 30.81 | 30.81 | 8.37 | 0 | 3.4 | 1.23 | 0 | 0
2025-01-08 13:00 | 43.26 | 30.82 | 30.82 | 11.92 | 0 | 0.52 | 0.68 | 0 | 0
2025-01-08 14:00 | 42.97 | 21.02 | 21.02 | 21.95 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 15:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 16:00 | 43.81 | 0.49 | 0.49 | 43.31 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 17:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 18:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 19:00 | 42.14 | 0 | 0 | 42.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 20:00 | 42.23 | 0 | 0 | 42.23 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 21:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 22:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0.68 | 0 | 0
2025-01-08 23:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 | 37.41 | 0 | 0 | 37.41 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 01:00 | 36.75 | 0 | 0 | 36.75 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 02:00 | 36.57 | 0 | 0 | 36.57 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 04:00 | 37.19 | 0 | 0 | 37.19 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 05:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 06:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 07:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 08:00 | 39.86 | 4.53 | 4.53 | 35.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 09:00 | 40.32 | 54.25 | 43.72 | 0 | 3.4 | 0 | 3.91 | 10.54 | 0
2025-01-09 10:00 | 40.97 | 63.39 | 43.3 | 0 | 2.33 | 0 | 6.12 | 20.09 | 0
2025-01-09 11:00 | 42.41 | 53.19 | 42.41 | 0 | 0 | 0 | 6.12 | 10.78 | 0
2025-01-09 12:00 | 42.95 | 50.69 | 42.95 | 0 | 0 | 0 | 6.12 | 7.74 | 0
2025-01-09 13:00 | 42.69 | 61.34 | 42.69 | 0 | 0 | 0 | 6.12 | 18.65 | 0
2025-01-09 14:00 | 43.73 | 72.15 | 43.73 | 0 | 0 | 0 | 6.12 | 28.42 | 0
2025-01-09 15:00 | 44.01 | 74.05 | 44.01 | 0 | 0 | 0 | 6.12 | 30.03 | 0
2025-01-09 16:00 | 43.31 | 11.39 | 11.39 | 28.52 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-09 17:00 | 43.51 | 0 | 0 | 41.74 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-09 18:00 | 42.13 | 0 | 0 | 42.13 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 19:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 20:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 21:00 | 40.27 | 0 | 0 | 40.27 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 22:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0.68 | 0 | 0
2025-01-09 23:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 | 37.29 | 0 | 0 | 37.29 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 01:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 02:00 | 36.45 | 0 | 0 | 36.45 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 03:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 04:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 05:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 06:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 07:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 08:00 | 40.11 | 1.65 | 1.65 | 38.46 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 09:00 | 39.47 | 23.38 | 23.38 | 16.09 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 10:00 | 40.95 | 35.23 | 35.23 | 5.72 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 11:00 | 42.4 | 16.56 | 16.56 | 25.83 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 12:00 | 41.2 | 23.28 | 23.28 | 17.92 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 13:00 | 41.79 | 36.62 | 36.62 | 5.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 14:00 | 42.46 | 10.28 | 10.28 | 32.18 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 15:00 | 42.5 | 0.06 | 0.06 | 42.44 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 16:00 | 43.08 | 0.33 | 0.33 | 42.75 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 17:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 18:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 19:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 20:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 21:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 22:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-10 23:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 01:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 02:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 03:00 | 36 | 0 | 0 | 36 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 04:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 05:00 | 36.79 | 0 | 0 | 36.79 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 07:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 08:00 | 39.78 | 5.3 | 5.3 | 34.47 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 09:00 | 40.17 | 72.35 | 43.57 | 0 | 3.4 | 0 | 3.91 | 28.78 | 0
2025-01-11 10:00 | 40.98 | 70.19 | 43.31 | 0 | 2.33 | 0 | 6.12 | 26.88 | 0
2025-01-11 11:00 | 43 | 58.87 | 43 | 0 | 0 | 0 | 6.12 | 15.87 | 0
2025-01-11 12:00 | 43.66 | 51.69 | 43.66 | 0 | 0 | 0 | 6.12 | 8.03 | 0
2025-01-11 13:00 | 43.94 | 56.66 | 43.94 | 0 | 0 | 0 | 6.12 | 12.72 | 0
2025-01-11 14:00 | 45.42 | 67.69 | 45.42 | 0 | 0 | 0 | 6.12 | 22.26 | 0
2025-01-11 15:00 | 44.63 | 69.51 | 44.63 | 0 | 0 | 0 | 6.12 | 24.88 | 0
2025-01-11 16:00 | 44.71 | 6.98 | 6.98 | 34.33 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-11 17:00 | 44.38 | 0 | 0 | 42.61 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-11 18:00 | 43.23 | 0 | 0 | 43.23 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 19:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 20:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 21:00 | 40.37 | 0 | 0 | 40.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 0.68 | 0 | 0
2025-01-11 23:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 | 36.64 | 0 | 0 | 36.64 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 01:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 02:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 03:00 | 36.61 | 0 | 0 | 36.61 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 04:00 | 35.96 | 0 | 0 | 35.96 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 06:00 | 37.7 | 0 | 0 | 37.7 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 07:00 | 38.5 | 0 | 0 | 38.5 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 08:00 | 38.94 | 5.94 | 5.94 | 32.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 09:00 | 40.78 | 56.69 | 44.18 | 0 | 3.4 | 0 | 3.91 | 12.51 | 0
2025-01-12 10:00 | 41.79 | 54.06 | 44.11 | 0 | 2.33 | 0 | 6.12 | 9.95 | 0
2025-01-12 11:00 | 41.77 | 52.16 | 41.77 | 0 | 0 | 0 | 6.12 | 10.39 | 0
2025-01-12 12:00 | 43.74 | 56.79 | 43.74 | 0 | 0 | 0 | 6.12 | 13.05 | 0
2025-01-12 13:00 | 45.1 | 63.13 | 45.1 | 0 | 0 | 0 | 6.12 | 18.04 | 0
2025-01-12 14:00 | 44.59 | 74.02 | 44.59 | 0 | 0 | 0 | 6.12 | 29.43 | 0
2025-01-12 15:00 | 44.49 | 76.46 | 44.49 | 0 | 0 | 0 | 6.12 | 31.98 | 0
2025-01-12 16:00 | 44.43 | 14.19 | 14.19 | 26.84 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-12 17:00 | 44.38 | 0 | 0 | 42.61 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-12 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 19:00 | 42.6 | 0 | 0 | 42.6 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 21:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 22:00 | 39.41 | 0 | 0 | 39.41 | 0 | 0 | 0.68 | 0 | 0
2025-01-12 23:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 | 37.24 | 0 | 0 | 37.24 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 01:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 02:00 | 37.07 | 0 | 0 | 37.07 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 03:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 04:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 05:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 06:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 07:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 08:00 | 39.33 | 3.52 | 3.52 | 35.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 09:00 | 39.78 | 36.98 | 36.98 | 2.8 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 10:00 | 40.96 | 30.12 | 30.12 | 10.84 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 11:00 | 41.93 | 21.09 | 21.09 | 20.84 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 12:00 | 41.84 | 13.28 | 13.28 | 28.56 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 13:00 | 42.44 | 38.06 | 38.06 | 4.38 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 14:00 | 43.83 | 61.2 | 47.23 | 0 | 3.4 | 0 | 3.91 | 13.97 | 0
2025-01-13 15:00 | 43.45 | 70.5 | 45.78 | 0 | 2.33 | 0 | 6.12 | 24.73 | 0
2025-01-13 16:00 | 42.31 | 15.81 | 15.81 | 23.1 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-13 17:00 | 43.64 | 0 | 0 | 41.87 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-13 18:00 | 42.82 | 0 | 0 | 42.82 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 19:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 20:00 | 40.47 | 0 | 0 | 40.47 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 21:00 | 40.65 | 0 | 0 | 40.65 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 22:00 | 39.51 | 0 | 0 | 39.51 | 0 | 0 | 0.68 | 0 | 0
2025-01-13 23:00 | 39.7 | 0 | 0 | 39.7 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 | 38 | 0 | 0 | 38 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 01:00 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 02:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 03:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 04:00 | 37.2 | 0 | 0 | 37.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 05:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 06:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 07:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 08:00 | 39.24 | 2.1 | 2.1 | 37.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 09:00 | 40.91 | 0 | 0 | 40.91 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 10:00 | 42.35 | 23.81 | 23.81 | 18.54 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 11:00 | 42.42 | 7.58 | 7.58 | 34.84 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 12:00 | 43.38 | 17.48 | 17.48 | 25.9 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 13:00 | 44.48 | 31.4 | 31.4 | 13.08 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 14:00 | 44.67 | 56.66 | 48.07 | 0 | 3.4 | 0 | 3.91 | 8.59 | 0
2025-01-14 15:00 | 45.44 | 67.78 | 47.76 | 0 | 2.33 | 0 | 6.12 | 20.02 | 0
2025-01-14 16:00 | 43.67 | 15.89 | 15.89 | 24.38 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-14 17:00 | 43.91 | 0 | 0 | 42.14 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-14 18:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 19:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 20:00 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 21:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 22:00 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 0.68 | 0 | 0
2025-01-14 23:00 | 39.11 | 0 | 0 | 39.11 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 01:00 | 36.69 | 0 | 0 | 36.69 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 02:00 | 36.83 | 0 | 0 | 36.83 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 03:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 04:00 | 36.37 | 0 | 0 | 36.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 05:00 | 36.75 | 0 | 0 | 36.75 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 06:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 07:00 | 38.37 | 0 | 0 | 38.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 08:00 | 39.66 | 5.23 | 5.23 | 34.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 09:00 | 40.27 | 59.3 | 43.67 | 0 | 3.4 | 0 | 3.91 | 15.63 | 0
2025-01-15 10:00 | 41.59 | 59.44 | 43.92 | 0 | 2.33 | 0 | 6.12 | 15.52 | 0
2025-01-15 11:00 | 41.64 | 52.05 | 41.64 | 0 | 0 | 0 | 6.12 | 10.41 | 0
2025-01-15 12:00 | 42.95 | 44.11 | 42.95 | 0 | 0 | 0 | 6.12 | 1.16 | 0
2025-01-15 13:00 | 43.47 | 52.23 | 43.47 | 0 | 0 | 0 | 6.12 | 8.77 | 0
2025-01-15 14:00 | 43.36 | 36.92 | 36.92 | 3.04 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-15 15:00 | 43.32 | 50.39 | 46.72 | 0 | 3.4 | 0 | 5.77 | 3.67 | 0
2025-01-15 16:00 | 44.31 | 9.01 | 9.01 | 31.9 | 0 | 3.4 | 2.19 | 0 | 0
2025-01-15 17:00 | 43.4 | 0 | 0 | 41.96 | 0 | 1.44 | 0.68 | 0 | 0
2025-01-15 18:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 19:00 | 42.11 | 0 | 0 | 42.11 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 20:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 21:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 22:00 | 38.59 | 0 | 0 | 38.59 | 0 | 0 | 0.68 | 0 | 0
2025-01-15 23:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 01:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 02:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 03:00 | 36.16 | 0 | 0 | 36.16 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 04:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 05:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 06:00 | 37.72 | 0 | 0 | 37.72 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 07:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 08:00 | 39 | 0 | 0 | 39 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 09:00 | 39.98 | 0.01 | 0.01 | 39.97 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 10:00 | 40.65 | 5.61 | 5.61 | 35.04 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 11:00 | 41.6 | 8.51 | 8.51 | 33.09 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 12:00 | 42.14 | 9.57 | 9.57 | 32.57 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 13:00 | 41.31 | 42.62 | 42.62 | 0 | 1.31 | 0 | 1.92 | 0 | 0
2025-01-16 14:00 | 41.24 | 53.03 | 44.64 | 0 | 3.4 | 0 | 5.15 | 8.39 | 0
2025-01-16 15:00 | 42.94 | 35.77 | 35.77 | 3.78 | 0 | 3.4 | 1.57 | 0 | 0
2025-01-16 16:00 | 42.96 | 10.06 | 10.06 | 32.04 | 0 | 0.85 | 0.68 | 0 | 0
2025-01-16 17:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 18:00 | 40.8 | 0 | 0 | 40.8 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 19:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 20:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 21:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 22:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-16 23:00 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 01:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 02:00 | 36.68 | 0 | 0 | 36.68 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 03:00 | 36.21 | 0 | 0 | 36.21 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 04:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 05:00 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 06:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 07:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 08:00 | 39.7 | 0.79 | 0.79 | 38.91 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 09:00 | 40.51 | 0.09 | 0.09 | 40.42 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 10:00 | 41.35 | 9.46 | 9.46 | 31.89 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 11:00 | 42.64 | 23.66 | 23.66 | 18.98 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 12:00 | 43.1 | 26.35 | 26.35 | 16.76 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 13:00 | 43.76 | 25.24 | 25.24 | 18.52 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 14:00 | 44.08 | 26.75 | 26.75 | 17.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 15:00 | 44.06 | 15.7 | 15.7 | 28.36 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 16:00 | 42.87 | 3.54 | 3.54 | 39.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 17:00 | 43.43 | 0 | 0 | 43.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 18:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 19:00 | 41.38 | 0 | 0 | 41.38 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 20:00 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 21:00 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 22:00 | 39.95 | 0 | 0 | 39.95 | 0 | 0 | 0.68 | 0 | 0
2025-01-17 23:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 01:00 | 37.15 | 0 | 0 | 37.15 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 02:00 | 36.92 | 0 | 0 | 36.92 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 03:00 | 36.15 | 0 | 0 | 36.15 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 04:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 05:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 06:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 07:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 08:00 | 38.99 | 0.3 | 0.3 | 38.69 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 09:00 | 40.67 | 3.59 | 3.59 | 37.08 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 10:00 | 40.92 | 7.21 | 7.21 | 33.7 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 11:00 | 41.09 | 8.96 | 8.96 | 32.13 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 12:00 | 41.71 | 10.82 | 10.82 | 30.9 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 13:00 | 41.98 | 11.55 | 11.55 | 30.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 14:00 | 42.08 | 8.37 | 8.37 | 33.71 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 15:00 | 41.72 | 4.23 | 4.23 | 37.48 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 16:00 | 42.11 | 0.33 | 0.33 | 41.78 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 17:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 18:00 | 40.96 | 0 | 0 | 40.96 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 19:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 20:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 21:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 22:00 | 38.97 | 0 | 0 | 38.97 | 0 | 0 | 0.68 | 0 | 0
2025-01-18 23:00 | 38.8 | 0 | 0 | 38.8 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 01:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 02:00 | 36.82 | 0 | 0 | 36.82 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 03:00 | 36.27 | 0 | 0 | 36.27 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 04:00 | 36.26 | 0 | 0 | 36.26 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 05:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 06:00 | 37.88 | 0 | 0 | 37.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 07:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 08:00 | 39.87 | 0 | 0 | 39.87 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 09:00 | 40.24 | 2.24 | 2.24 | 38 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 10:00 | 40.7 | 4.22 | 4.22 | 36.49 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 11:00 | 42.15 | 5.37 | 5.37 | 36.78 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 12:00 | 43.29 | 6.56 | 6.56 | 36.73 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 13:00 | 43.76 | 6.23 | 6.23 | 37.53 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 14:00 | 44.01 | 5.3 | 5.3 | 38.71 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 15:00 | 44.57 | 2.67 | 2.67 | 41.9 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 16:00 | 44.05 | 0.15 | 0.15 | 43.9 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 17:00 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 18:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 19:00 | 42.11 | 0 | 0 | 42.11 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 20:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 21:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 22:00 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 0.68 | 0 | 0
2025-01-19 23:00 | 38.19 | 0 | 0 | 38.19 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 01:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 02:00 | 35.74 | 0 | 0 | 35.74 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 03:00 | 35.75 | 0 | 0 | 35.75 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 04:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 05:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 06:00 | 37.6 | 0 | 0 | 37.6 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 07:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 08:00 | 37.81 | 9.17 | 9.17 | 28.65 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 09:00 | 40.21 | 69.34 | 43.61 | 0 | 3.4 | 0 | 3.91 | 25.74 | 0
2025-01-20 10:00 | 41.65 | 61.8 | 43.97 | 0 | 2.33 | 0 | 6.12 | 17.83 | 0
2025-01-20 11:00 | 41.1 | 52.27 | 41.1 | 0 | 0 | 0 | 6.12 | 11.17 | 0
2025-01-20 12:00 | 42.15 | 46.79 | 42.15 | 0 | 0 | 0 | 6.12 | 4.64 | 0
2025-01-20 13:00 | 42.49 | 53.41 | 42.49 | 0 | 0 | 0 | 6.12 | 10.92 | 0
2025-01-20 14:00 | 42.75 | 67.67 | 42.75 | 0 | 0 | 0 | 6.12 | 24.93 | 0
2025-01-20 15:00 | 43.14 | 74.01 | 43.14 | 0 | 0 | 0 | 6.12 | 30.87 | 0
2025-01-20 16:00 | 43.91 | 27.56 | 27.56 | 12.95 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-20 17:00 | 43.78 | 0 | 0 | 42.02 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-20 18:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 19:00 | 42.61 | 0 | 0 | 42.61 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 20:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 21:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 22:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 0.68 | 0 | 0
2025-01-20 23:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 | 37.83 | 0 | 0 | 37.83 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 01:00 | 38.71 | 0 | 0 | 38.71 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 02:00 | 37.21 | 0 | 0 | 37.21 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 03:00 | 36.32 | 0 | 0 | 36.32 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 04:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 05:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 06:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 07:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 08:00 | 39.13 | 9.68 | 9.68 | 29.45 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 09:00 | 40.1 | 58.65 | 43.5 | 0 | 3.4 | 0 | 3.91 | 15.15 | 0
2025-01-21 10:00 | 40.79 | 67.45 | 43.12 | 0 | 2.33 | 0 | 6.12 | 24.33 | 0
2025-01-21 11:00 | 41.72 | 56.06 | 41.72 | 0 | 0 | 0 | 6.12 | 14.34 | 0
2025-01-21 12:00 | 42.42 | 49.51 | 42.42 | 0 | 0 | 0 | 6.12 | 7.09 | 0
2025-01-21 13:00 | 41.74 | 57.79 | 41.74 | 0 | 0 | 0 | 6.12 | 16.04 | 0
2025-01-21 14:00 | 43.36 | 65.14 | 43.36 | 0 | 0 | 0 | 6.12 | 21.78 | 0
2025-01-21 15:00 | 42.64 | 69.7 | 42.64 | 0 | 0 | 0 | 6.12 | 27.07 | 0
2025-01-21 16:00 | 42.3 | 24.93 | 24.93 | 13.97 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-21 17:00 | 42.68 | 0 | 0 | 40.91 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-21 18:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 19:00 | 41.21 | 0 | 0 | 41.21 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 20:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 21:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 22:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 0.68 | 0 | 0
2025-01-21 23:00 | 38.04 | 0 | 0 | 38.04 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 | 37.6 | 0 | 0 | 37.6 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 01:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 02:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 03:00 | 37.03 | 0 | 0 | 37.03 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 04:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 05:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 06:00 | 36.65 | 0 | 0 | 36.65 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 07:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 08:00 | 38.92 | 10.55 | 10.55 | 28.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 09:00 | 39.75 | 52.26 | 43.15 | 0 | 3.4 | 0 | 3.91 | 9.11 | 0
2025-01-22 10:00 | 40.53 | 40.74 | 40.74 | 0 | 0.21 | 0 | 4.11 | 0 | 0
2025-01-22 11:00 | 41.32 | 32.04 | 32.04 | 6.02 | 0 | 3.26 | 0.68 | 0 | 0
2025-01-22 12:00 | 42.24 | 52.65 | 45.64 | 0 | 3.4 | 0 | 3.91 | 7.01 | 0
2025-01-22 13:00 | 41.62 | 55.13 | 43.95 | 0 | 2.33 | 0 | 6.12 | 11.18 | 0
2025-01-22 14:00 | 41.85 | 40.08 | 40.08 | 0 | 0 | 1.77 | 4.26 | 0 | 0
2025-01-22 15:00 | 41.97 | 53.58 | 43.94 | 0 | 1.96 | 0 | 6.12 | 9.64 | 0
2025-01-22 16:00 | 42.58 | 0 | 0 | 39.18 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-22 17:00 | 42.8 | 0 | 0 | 41.04 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-22 18:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 19:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 20:00 | 39.69 | 0 | 0 | 39.69 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 21:00 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 22:00 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 0.68 | 0 | 0
2025-01-22 23:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 01:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 02:00 | 37.31 | 0 | 0 | 37.31 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 03:00 | 36.33 | 0 | 0 | 36.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 04:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 05:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 06:00 | 36.91 | 0 | 0 | 36.91 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 07:00 | 38.62 | 0 | 0 | 38.62 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 08:00 | 39.39 | 9.01 | 9.01 | 30.38 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 09:00 | 40.29 | 23.77 | 23.77 | 16.52 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 10:00 | 42.24 | 43 | 43 | 0 | 0.77 | 0 | 1.41 | 0 | 0
2025-01-23 11:00 | 42.18 | 57.82 | 45.58 | 0 | 3.4 | 0 | 4.64 | 12.24 | 0
2025-01-23 12:00 | 44.46 | 53.02 | 46.02 | 0 | 1.56 | 0 | 6.12 | 7 | 0
2025-01-23 13:00 | 44.05 | 61.04 | 44.05 | 0 | 0 | 0 | 6.12 | 16.99 | 0
2025-01-23 14:00 | 44 | 36.19 | 36.19 | 4.41 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-23 15:00 | 44.84 | 35.58 | 35.58 | 7.49 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-23 16:00 | 44.1 | 0 | 0 | 44.1 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 17:00 | 43.79 | 0 | 0 | 43.79 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 18:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 19:00 | 42.77 | 0 | 0 | 42.77 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 20:00 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 21:00 | 40.86 | 0 | 0 | 40.86 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 22:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 0.68 | 0 | 0
2025-01-23 23:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 | 37.9 | 0 | 0 | 37.9 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 01:00 | 37.79 | 0 | 0 | 37.79 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 02:00 | 35.84 | 0 | 0 | 35.84 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 03:00 | 36.51 | 0 | 0 | 36.51 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 04:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 05:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 06:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 07:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 08:00 | 40.05 | 1.02 | 1.02 | 39.03 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 09:00 | 39.87 | 5.67 | 5.67 | 34.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 10:00 | 41 | 22.28 | 22.28 | 18.72 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 11:00 | 41.45 | 36.59 | 36.59 | 4.85 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 12:00 | 42.26 | 30.02 | 30.02 | 12.24 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 13:00 | 42.73 | 17.07 | 17.07 | 25.66 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 14:00 | 43.26 | 16.56 | 16.56 | 26.7 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 15:00 | 43.73 | 0.72 | 0.72 | 43.01 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 16:00 | 43.86 | 2 | 2 | 41.87 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 17:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 19:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 20:00 | 40.75 | 0 | 0 | 40.75 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 21:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 22:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 0.68 | 0 | 0
2025-01-24 23:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 01:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 02:00 | 37.38 | 0 | 0 | 37.38 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 03:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 04:00 | 36.61 | 0 | 0 | 36.61 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 05:00 | 37.28 | 0 | 0 | 37.28 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 06:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 07:00 | 38.5 | 0 | 0 | 38.5 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 08:00 | 37.25 | 5.03 | 5.03 | 32.21 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 09:00 | 39.01 | 57.95 | 42.41 | 0 | 3.4 | 0 | 3.91 | 15.54 | 0
2025-01-25 10:00 | 40.89 | 49.89 | 43.22 | 0 | 2.33 | 0 | 6.12 | 6.67 | 0
2025-01-25 11:00 | 41.62 | 38.85 | 38.85 | 0 | 0 | 2.77 | 3.2 | 0 | 0
2025-01-25 12:00 | 41.41 | 42.63 | 42.63 | 0 | 1.23 | 0 | 4.37 | 0 | 0
2025-01-25 13:00 | 42.09 | 57.38 | 43.94 | 0 | 1.85 | 0 | 6.12 | 13.44 | 0
2025-01-25 14:00 | 43.41 | 37.26 | 37.26 | 2.75 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-25 15:00 | 42.58 | 5.07 | 5.07 | 35.74 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-25 16:00 | 43.85 | 0 | 0 | 43.85 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 17:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 18:00 | 42.19 | 0 | 0 | 42.19 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 19:00 | 42.19 | 0 | 0 | 42.19 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 20:00 | 40.73 | 0 | 0 | 40.73 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 21:00 | 39.37 | 0 | 0 | 39.37 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 22:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0.68 | 0 | 0
2025-01-25 23:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 01:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 02:00 | 36.42 | 0 | 0 | 36.42 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 03:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 04:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 05:00 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 06:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 07:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 08:00 | 39.4 | 3.54 | 3.54 | 35.85 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 09:00 | 39.41 | 11.53 | 11.53 | 27.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 10:00 | 40.19 | 12.3 | 12.3 | 27.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 11:00 | 42 | 25.7 | 25.7 | 16.29 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 12:00 | 41.86 | 34.22 | 34.22 | 7.64 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 13:00 | 41.83 | 44.39 | 44.39 | 0 | 2.56 | 0 | 3.11 | 0 | 0
2025-01-26 14:00 | 43.05 | 69.02 | 46.21 | 0 | 3.16 | 0 | 6.12 | 22.81 | 0
2025-01-26 15:00 | 43.16 | 72.81 | 43.16 | 0 | 0 | 0 | 6.12 | 29.65 | 0
2025-01-26 16:00 | 42.06 | 33.43 | 33.43 | 5.24 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-26 17:00 | 42.65 | 0 | 0 | 40.88 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-26 18:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 19:00 | 41.63 | 0 | 0 | 41.63 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 20:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 21:00 | 39.2 | 0 | 0 | 39.2 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 22:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 0.68 | 0 | 0
2025-01-26 23:00 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 | 37.43 | 0 | 0 | 37.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 01:00 | 37.57 | 0 | 0 | 37.57 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 02:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 03:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 04:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 05:00 | 37.08 | 0 | 0 | 37.08 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 06:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 07:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 08:00 | 39.31 | 2.52 | 2.52 | 36.79 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 09:00 | 40.25 | 36.71 | 36.71 | 3.54 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 10:00 | 41.55 | 71.4 | 44.95 | 0 | 3.4 | 0 | 3.91 | 26.45 | 0
2025-01-27 11:00 | 42.03 | 48.64 | 44.35 | 0 | 2.33 | 0 | 6.12 | 4.29 | 0
2025-01-27 12:00 | 42.49 | 31.4 | 31.4 | 7.69 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-27 13:00 | 43.27 | 14.53 | 14.53 | 26.97 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-27 14:00 | 44.19 | 8.6 | 8.6 | 35.59 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 15:00 | 44.01 | 6.22 | 6.22 | 37.79 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 16:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 17:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 18:00 | 42.67 | 0 | 0 | 42.67 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 19:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 22:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 0.68 | 0 | 0
2025-01-27 23:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 | 36.85 | 0 | 0 | 36.85 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 01:00 | 36.62 | 0 | 0 | 36.62 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 02:00 | 36.29 | 0 | 0 | 36.29 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 03:00 | 36.71 | 0 | 0 | 36.71 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 04:00 | 36.67 | 0 | 0 | 36.67 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 05:00 | 36.97 | 0 | 0 | 36.97 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 07:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 08:00 | 39.39 | 24.32 | 24.32 | 15.07 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 09:00 | 40.35 | 69.08 | 43.75 | 0 | 3.4 | 0 | 3.91 | 25.32 | 0
2025-01-28 10:00 | 41.39 | 33.94 | 33.94 | 4.38 | 0 | 3.07 | 0.68 | 0 | 0
2025-01-28 11:00 | 40.91 | 24.24 | 24.24 | 16.67 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 12:00 | 42.55 | 28.78 | 28.78 | 13.77 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 13:00 | 42.23 | 21.07 | 21.07 | 21.16 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 14:00 | 43.72 | 25.41 | 25.41 | 18.31 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 15:00 | 43.83 | 45.56 | 45.56 | 0 | 1.74 | 0 | 2.33 | 0 | 0
2025-01-28 16:00 | 44.22 | 14.25 | 14.25 | 28.4 | 0 | 1.57 | 0.68 | 0 | 0
2025-01-28 17:00 | 43.92 | 0 | 0 | 43.92 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 18:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 19:00 | 41.71 | 0 | 0 | 41.71 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 20:00 | 41.32 | 0 | 0 | 41.32 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 21:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 22:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0.68 | 0 | 0
2025-01-28 23:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 01:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 02:00 | 37.15 | 0 | 0 | 37.15 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 03:00 | 36.22 | 0 | 0 | 36.22 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 04:00 | 37.3 | 0 | 0 | 37.3 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 05:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 06:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 07:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 08:00 | 38.83 | 21.81 | 21.81 | 17.02 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 09:00 | 39.91 | 72.61 | 43.31 | 0 | 3.4 | 0 | 3.91 | 29.3 | 0
2025-01-29 10:00 | 41.4 | 61.64 | 43.72 | 0 | 2.33 | 0 | 6.12 | 17.91 | 0
2025-01-29 11:00 | 41.54 | 59.08 | 41.54 | 0 | 0 | 0 | 6.12 | 17.54 | 0
2025-01-29 12:00 | 43.01 | 52.21 | 43.01 | 0 | 0 | 0 | 6.12 | 9.2 | 0
2025-01-29 13:00 | 42.78 | 57.38 | 42.78 | 0 | 0 | 0 | 6.12 | 14.6 | 0
2025-01-29 14:00 | 43.68 | 41.32 | 41.32 | 0 | 0 | 2.36 | 3.64 | 0 | 0
2025-01-29 15:00 | 43.97 | 40.72 | 40.72 | 0.44 | 0 | 2.81 | 0.68 | 0 | 0
2025-01-29 16:00 | 45.01 | 12.53 | 12.53 | 32.47 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 17:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 18:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 19:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 21:00 | 40.24 | 0 | 0 | 40.24 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 22:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 0.68 | 0 | 0
2025-01-29 23:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 01:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 02:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 03:00 | 36.39 | 0 | 0 | 36.39 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 04:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 05:00 | 36.63 | 0 | 0 | 36.63 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 06:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 07:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 08:00 | 39.24 | 14.56 | 14.56 | 24.69 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 09:00 | 40.11 | 25.94 | 25.94 | 14.17 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 10:00 | 40.6 | 49.76 | 44 | 0 | 3.4 | 0 | 3.91 | 5.75 | 0
2025-01-30 11:00 | 41.94 | 49.77 | 44.27 | 0 | 2.33 | 0 | 6.12 | 5.5 | 0
2025-01-30 12:00 | 42.05 | 44.9 | 42.05 | 0 | 0 | 0 | 6.12 | 2.85 | 0
2025-01-30 13:00 | 43 | 53.23 | 43 | 0 | 0 | 0 | 6.12 | 10.24 | 0
2025-01-30 14:00 | 43.95 | 53.8 | 43.95 | 0 | 0 | 0 | 6.12 | 9.85 | 0
2025-01-30 15:00 | 44.63 | 65.15 | 44.63 | 0 | 0 | 0 | 6.12 | 20.52 | 0
2025-01-30 16:00 | 45.24 | 36.99 | 36.99 | 4.86 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-30 17:00 | 43.16 | 0 | 0 | 41.39 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-30 18:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 19:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 20:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 21:00 | 40.43 | 0 | 0 | 40.43 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 22:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 0.68 | 0 | 0
2025-01-30 23:00 | 38.48 | 0 | 0 | 38.48 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 | 37.57 | 0 | 0 | 37.57 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 01:00 | 36.49 | 0 | 0 | 36.49 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 02:00 | 36.07 | 0 | 0 | 36.07 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 03:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 04:00 | 36.71 | 0 | 0 | 36.71 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 05:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 06:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 07:00 | 38.98 | 0 | 0 | 38.98 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 08:00 | 39.68 | 27.73 | 27.73 | 11.95 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 09:00 | 40.43 | 79.33 | 43.83 | 0 | 3.4 | 0 | 3.91 | 35.5 | 0
2025-01-31 10:00 | 42.63 | 77.95 | 44.95 | 0 | 2.33 | 0 | 6.12 | 32.99 | 0
2025-01-31 11:00 | 44.05 | 68.62 | 44.05 | 0 | 0 | 0 | 6.12 | 24.57 | 0
2025-01-31 12:00 | 44.64 | 61.77 | 44.64 | 0 | 0 | 0 | 6.12 | 17.13 | 0
2025-01-31 13:00 | 45.79 | 57.65 | 45.79 | 0 | 0 | 0 | 6.12 | 11.87 | 0
2025-01-31 14:00 | 46.51 | 41.5 | 41.5 | 1.61 | 0 | 3.4 | 2.54 | 0 | 0
2025-01-31 15:00 | 46.66 | 17.34 | 17.34 | 27.55 | 0 | 1.77 | 0.68 | 0 | 0
2025-01-31 16:00 | 46.2 | 19.84 | 19.84 | 26.35 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 17:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 18:00 | 44.65 | 0 | 0 | 44.65 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 19:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 20:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 21:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 22:00 | 39.19 | 0 | 0 | 39.19 | 0 | 0 | 0.68 | 0 | 0
2025-01-31 23:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 01:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 02:00 | 36.73 | 0 | 0 | 36.73 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 03:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 04:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 05:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 06:00 | 37.77 | 0 | 0 | 37.77 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 07:00 | 38.98 | 0 | 0 | 38.98 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 08:00 | 39.01 | 23.06 | 23.06 | 15.96 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 09:00 | 40.19 | 68.7 | 43.59 | 0 | 3.4 | 0 | 3.91 | 25.11 | 0
2025-02-01 10:00 | 40.33 | 69.47 | 42.65 | 0 | 2.33 | 0 | 6.12 | 26.82 | 0
2025-02-01 11:00 | 41.78 | 48.34 | 41.78 | 0 | 0 | 0 | 6.12 | 6.56 | 0
2025-02-01 12:00 | 42.18 | 44.42 | 42.18 | 0 | 0 | 0 | 6.12 | 2.25 | 0
2025-02-01 13:00 | 42.27 | 53.73 | 42.27 | 0 | 0 | 0 | 6.12 | 11.46 | 0
2025-02-01 14:00 | 42.82 | 62.52 | 42.82 | 0 | 0 | 0 | 6.12 | 19.7 | 0
2025-02-01 15:00 | 42.94 | 74.18 | 42.94 | 0 | 0 | 0 | 6.12 | 31.23 | 0
2025-02-01 16:00 | 42.8 | 40.83 | 40.83 | 0 | 0 | 1.97 | 4.05 | 0 | 0
2025-02-01 17:00 | 43.53 | 0 | 0 | 40.33 | 0 | 3.2 | 0.68 | 0 | 0
2025-02-01 18:00 | 42.12 | 0 | 0 | 42.12 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 19:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 20:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 22:00 | 39.06 | 0 | 0 | 39.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-01 23:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 01:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 02:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 03:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 04:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 05:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 06:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 08:00 | 38.04 | 36.21 | 36.21 | 1.83 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 09:00 | 39.01 | 85.37 | 42.41 | 0 | 3.4 | 0 | 3.91 | 42.96 | 0
2025-02-02 10:00 | 40.53 | 79.06 | 42.86 | 0 | 2.33 | 0 | 6.12 | 36.2 | 0
2025-02-02 11:00 | 41.53 | 15.34 | 15.34 | 22.79 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-02 12:00 | 42.47 | 38.81 | 38.81 | 1.89 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-02 13:00 | 42.81 | 62.9 | 46.21 | 0 | 3.4 | 0 | 3.91 | 16.69 | 0
2025-02-02 14:00 | 42.66 | 72.15 | 44.99 | 0 | 2.33 | 0 | 6.12 | 27.16 | 0
2025-02-02 15:00 | 43.46 | 56.47 | 43.46 | 0 | 0 | 0 | 6.12 | 13.01 | 0
2025-02-02 16:00 | 43.37 | 45.51 | 43.37 | 0 | 0 | 0 | 6.12 | 2.14 | 0
2025-02-02 17:00 | 42.67 | 0 | 0 | 39.27 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-02 18:00 | 42.6 | 0 | 0 | 40.84 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-02 19:00 | 41.66 | 0 | 0 | 41.66 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 20:00 | 40.52 | 0 | 0 | 40.52 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 21:00 | 40.36 | 0 | 0 | 40.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 22:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 0.68 | 0 | 0
2025-02-02 23:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 01:00 | 36.02 | 0 | 0 | 36.02 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 02:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 03:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 04:00 | 36.72 | 0 | 0 | 36.72 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 06:00 | 37.02 | 0 | 0 | 37.02 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 07:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 08:00 | 38.76 | 1.4 | 1.4 | 37.35 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 09:00 | 41.19 | 8.34 | 8.34 | 32.85 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 10:00 | 41.6 | 11.46 | 11.46 | 30.14 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 11:00 | 41.15 | 28.92 | 28.92 | 12.23 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 12:00 | 41.72 | 31.18 | 31.18 | 10.54 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 13:00 | 41.73 | 38.39 | 38.39 | 3.34 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 14:00 | 41.59 | 28.73 | 28.73 | 12.86 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 15:00 | 42.57 | 22.59 | 22.59 | 19.98 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 16:00 | 42.05 | 44.68 | 44.68 | 0 | 2.63 | 0 | 3.18 | 0 | 0
2025-02-03 17:00 | 42.26 | 0.56 | 0.56 | 39.33 | 0 | 2.37 | 0.68 | 0 | 0
2025-02-03 18:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 19:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 20:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 21:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 22:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 0.68 | 0 | 0
2025-02-03 23:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 01:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 02:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 03:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 04:00 | 36.24 | 0 | 0 | 36.24 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 06:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 07:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 08:00 | 39.4 | 4.79 | 4.79 | 34.61 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 09:00 | 41.21 | 25.48 | 25.48 | 15.73 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 10:00 | 41.95 | 40.94 | 40.94 | 1.01 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 11:00 | 42.27 | 15.3 | 15.3 | 26.98 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 12:00 | 43.61 | 27.48 | 27.48 | 16.14 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 13:00 | 44.86 | 20.15 | 20.15 | 24.71 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 14:00 | 45.29 | 22.48 | 22.48 | 22.81 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 15:00 | 43.84 | 12.55 | 12.55 | 31.29 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 16:00 | 43.85 | 9.39 | 9.39 | 34.46 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 17:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 18:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 19:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 20:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 21:00 | 40.65 | 0 | 0 | 40.65 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 22:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0.68 | 0 | 0
2025-02-04 23:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 | 37.55 | 0 | 0 | 37.55 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 01:00 | 36.95 | 0 | 0 | 36.95 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 02:00 | 36.52 | 0 | 0 | 36.52 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 03:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 04:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 05:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 06:00 | 37.64 | 0 | 0 | 37.64 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 07:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 08:00 | 39.24 | 12.08 | 12.08 | 27.16 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 09:00 | 39.32 | 13.84 | 13.84 | 25.48 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 10:00 | 41.06 | 36.55 | 36.55 | 4.51 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 11:00 | 41.91 | 36.66 | 36.66 | 5.25 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 12:00 | 42.64 | 43.01 | 43.01 | 0 | 0.37 | 0 | 1.03 | 0 | 0
2025-02-05 13:00 | 43.92 | 42.44 | 42.44 | 1.14 | 0 | 0.33 | 0.68 | 0 | 0
2025-02-05 14:00 | 45.66 | 37.58 | 37.58 | 8.08 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 15:00 | 45.14 | 29.01 | 29.01 | 16.13 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 16:00 | 45.64 | 40.98 | 40.98 | 4.67 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 17:00 | 44.72 | 1.01 | 1.01 | 43.71 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 18:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 19:00 | 42.37 | 0 | 0 | 42.37 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 20:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 21:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 22:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 0.68 | 0 | 0
2025-02-05 23:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 01:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 02:00 | 36.43 | 0 | 0 | 36.43 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 03:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 04:00 | 37.03 | 0 | 0 | 37.03 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 05:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 06:00 | 37.49 | 0 | 0 | 37.49 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 07:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 08:00 | 39.71 | 41.09 | 41.09 | 0 | 1.38 | 0 | 1.99 | 0 | 0
2025-02-06 09:00 | 40.62 | 89.38 | 44.02 | 0 | 3.4 | 0 | 5.22 | 45.36 | 0
2025-02-06 10:00 | 41.97 | 84.52 | 42.92 | 0 | 0.95 | 0 | 6.12 | 41.6 | 0
2025-02-06 11:00 | 42.64 | 75.48 | 42.64 | 0 | 0 | 0 | 6.12 | 32.84 | 0
2025-02-06 12:00 | 42.2 | 67.93 | 42.2 | 0 | 0 | 0 | 6.12 | 25.73 | 0
2025-02-06 13:00 | 44.08 | 72.02 | 44.08 | 0 | 0 | 0 | 6.12 | 27.94 | 0
2025-02-06 14:00 | 43.3 | 81.8 | 43.3 | 0 | 0 | 0 | 6.12 | 38.49 | 0
2025-02-06 15:00 | 44.21 | 88.01 | 44.21 | 0 | 0 | 0 | 6.12 | 43.81 | 0
2025-02-06 16:00 | 43.6 | 62.85 | 43.6 | 0 | 0 | 0 | 6.12 | 19.25 | 0
2025-02-06 17:00 | 43.03 | 0.62 | 0.62 | 39.01 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-06 18:00 | 41.8 | 0 | 0 | 40.03 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-06 19:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 20:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 21:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 22:00 | 40.19 | 0 | 0 | 40.19 | 0 | 0 | 0.68 | 0 | 0
2025-02-06 23:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 | 38.05 | 0 | 0 | 38.05 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 01:00 | 37 | 0 | 0 | 37 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 02:00 | 36.7 | 0 | 0 | 36.7 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 03:00 | 37.29 | 0 | 0 | 37.29 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 04:00 | 37 | 0 | 0 | 37 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 05:00 | 38.23 | 0 | 0 | 38.23 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 06:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 07:00 | 39.08 | 0 | 0 | 39.08 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 08:00 | 39.4 | 40.97 | 40.97 | 0 | 1.58 | 0 | 2.18 | 0 | 0
2025-02-07 09:00 | 40.53 | 68.45 | 43.93 | 0 | 3.4 | 0 | 5.41 | 24.51 | 0
2025-02-07 10:00 | 40.66 | 15.93 | 15.93 | 21.33 | 0 | 3.4 | 1.83 | 0 | 0
2025-02-07 11:00 | 41.53 | 48.48 | 44.93 | 0 | 3.4 | 0 | 5.06 | 3.55 | 0
2025-02-07 12:00 | 42.05 | 63 | 43.16 | 0 | 1.12 | 0 | 6.12 | 19.84 | 0
2025-02-07 13:00 | 42.09 | 79.24 | 42.09 | 0 | 0 | 0 | 6.12 | 37.14 | 0
2025-02-07 14:00 | 43.09 | 78.03 | 43.09 | 0 | 0 | 0 | 6.12 | 34.94 | 0
2025-02-07 15:00 | 43.17 | 55.39 | 43.17 | 0 | 0 | 0 | 6.12 | 12.22 | 0
2025-02-07 16:00 | 43.06 | 0.15 | 0.15 | 39.51 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-07 17:00 | 43.28 | 0 | 0 | 41.51 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-07 18:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 19:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 20:00 | 41.07 | 0 | 0 | 41.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 21:00 | 39.82 | 0 | 0 | 39.82 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 22:00 | 39.36 | 0 | 0 | 39.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-07 23:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 01:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 03:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 04:00 | 35.97 | 0 | 0 | 35.97 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 05:00 | 36.39 | 0 | 0 | 36.39 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 06:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 07:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 08:00 | 39.53 | 26.24 | 26.24 | 13.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 09:00 | 39.53 | 62.76 | 42.93 | 0 | 3.4 | 0 | 3.91 | 19.83 | 0
2025-02-08 10:00 | 40.94 | 69.38 | 43.27 | 0 | 2.33 | 0 | 6.12 | 26.12 | 0
2025-02-08 11:00 | 42.63 | 64.2 | 42.63 | 0 | 0 | 0 | 6.12 | 21.57 | 0
2025-02-08 12:00 | 42.6 | 58.78 | 42.6 | 0 | 0 | 0 | 6.12 | 16.18 | 0
2025-02-08 13:00 | 42.68 | 68.03 | 42.68 | 0 | 0 | 0 | 6.12 | 25.35 | 0
2025-02-08 14:00 | 42.63 | 68.69 | 42.63 | 0 | 0 | 0 | 6.12 | 26.06 | 0
2025-02-08 15:00 | 42.74 | 76.88 | 42.74 | 0 | 0 | 0 | 6.12 | 34.14 | 0
2025-02-08 16:00 | 41.79 | 59.93 | 41.79 | 0 | 0 | 0 | 6.12 | 18.14 | 0
2025-02-08 17:00 | 42.73 | 0.95 | 0.95 | 38.37 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-08 18:00 | 42.61 | 0 | 0 | 40.84 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-08 19:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 20:00 | 40.62 | 0 | 0 | 40.62 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 21:00 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 22:00 | 38.92 | 0 | 0 | 38.92 | 0 | 0 | 0.68 | 0 | 0
2025-02-08 23:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 01:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 02:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 03:00 | 36.84 | 0 | 0 | 36.84 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 04:00 | 35.85 | 0 | 0 | 35.85 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 05:00 | 36.95 | 0 | 0 | 36.95 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 06:00 | 38.64 | 0 | 0 | 38.64 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 07:00 | 37.41 | 0 | 0 | 37.41 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 08:00 | 39.54 | 5.15 | 5.15 | 34.38 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 09:00 | 40.14 | 46.9 | 43.54 | 0 | 3.4 | 0 | 3.91 | 3.36 | 0
2025-02-09 10:00 | 42.17 | 63.94 | 44.49 | 0 | 2.33 | 0 | 6.12 | 19.45 | 0
2025-02-09 11:00 | 42.42 | 80.13 | 42.42 | 0 | 0 | 0 | 6.12 | 37.71 | 0
2025-02-09 12:00 | 43.84 | 68.89 | 43.84 | 0 | 0 | 0 | 6.12 | 25.05 | 0
2025-02-09 13:00 | 44.6 | 37.37 | 37.37 | 3.83 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-09 14:00 | 45.67 | 11.68 | 11.68 | 32.22 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-09 15:00 | 44.8 | 13.07 | 13.07 | 31.73 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 16:00 | 44.94 | 0.1 | 0.1 | 44.83 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 17:00 | 43.57 | 0.4 | 0.4 | 43.17 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 18:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 19:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 20:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 21:00 | 40.71 | 0 | 0 | 40.71 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 22:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0.68 | 0 | 0
2025-02-09 23:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 01:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 02:00 | 36.33 | 0 | 0 | 36.33 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 04:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 05:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 06:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 08:00 | 39.92 | 46.69 | 43.32 | 0 | 3.4 | 0 | 3.91 | 3.37 | 0
2025-02-10 09:00 | 41.03 | 87.4 | 43.35 | 0 | 2.33 | 0 | 6.12 | 44.05 | 0
2025-02-10 10:00 | 42.82 | 83.84 | 42.82 | 0 | 0 | 0 | 6.12 | 41.02 | 0
2025-02-10 11:00 | 43.14 | 73.06 | 43.14 | 0 | 0 | 0 | 6.12 | 29.91 | 0
2025-02-10 12:00 | 44.14 | 67.79 | 44.14 | 0 | 0 | 0 | 6.12 | 23.65 | 0
2025-02-10 13:00 | 45.87 | 71.3 | 45.87 | 0 | 0 | 0 | 6.12 | 25.43 | 0
2025-02-10 14:00 | 44.86 | 79.67 | 44.86 | 0 | 0 | 0 | 6.12 | 34.82 | 0
2025-02-10 15:00 | 44.72 | 84.97 | 44.72 | 0 | 0 | 0 | 6.12 | 40.25 | 0
2025-02-10 16:00 | 45.18 | 63.83 | 45.18 | 0 | 0 | 0 | 6.12 | 18.65 | 0
2025-02-10 17:00 | 44.73 | 1.37 | 1.37 | 39.96 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-10 18:00 | 43.54 | 0 | 0 | 41.78 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-10 19:00 | 42.39 | 0 | 0 | 42.39 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 20:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 21:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 22:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0.68 | 0 | 0
2025-02-10 23:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 01:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 02:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 03:00 | 36.4 | 0 | 0 | 36.4 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 04:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 05:00 | 38.49 | 0 | 0 | 38.49 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 06:00 | 38.35 | 0 | 0 | 38.35 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 07:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 08:00 | 39.56 | 27.92 | 27.92 | 11.64 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 09:00 | 40.62 | 20.51 | 20.51 | 20.11 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 10:00 | 41.74 | 38.6 | 38.6 | 3.14 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 11:00 | 42.66 | 44.1 | 44.1 | 0 | 1.44 | 0 | 2.05 | 0 | 0
2025-02-11 12:00 | 44.17 | 33.39 | 33.39 | 9.48 | 0 | 1.3 | 0.68 | 0 | 0
2025-02-11 13:00 | 43.52 | 54.17 | 46.92 | 0 | 3.4 | 0 | 3.91 | 7.25 | 0
2025-02-11 14:00 | 45.24 | 73.51 | 47.57 | 0 | 2.33 | 0 | 6.12 | 25.94 | 0
2025-02-11 15:00 | 44.77 | 96.26 | 44.77 | 0 | 0 | 0 | 6.12 | 51.49 | 0
2025-02-11 16:00 | 45 | 71.46 | 45 | 0 | 0 | 0 | 6.12 | 26.46 | 0
2025-02-11 17:00 | 43.82 | 4.65 | 4.65 | 35.77 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-11 18:00 | 44.38 | 0 | 0 | 42.61 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-11 19:00 | 43.47 | 0 | 0 | 43.47 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 20:00 | 42.34 | 0 | 0 | 42.34 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 21:00 | 40.07 | 0 | 0 | 40.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 0.68 | 0 | 0
2025-02-11 23:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 | 37.33 | 0 | 0 | 37.33 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 01:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 02:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 03:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 04:00 | 37.3 | 0 | 0 | 37.3 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 05:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 06:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 07:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 08:00 | 38.23 | 20.27 | 20.27 | 17.96 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 09:00 | 40.34 | 44.77 | 43.74 | 0 | 3.4 | 0 | 3.91 | 1.03 | 0
2025-02-12 10:00 | 41.23 | 20.02 | 20.02 | 18.14 | 0 | 3.07 | 0.68 | 0 | 0
2025-02-12 11:00 | 41.17 | 29.6 | 29.6 | 11.58 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 12:00 | 42.7 | 16.46 | 16.46 | 26.24 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 13:00 | 43.74 | 49.2 | 47.14 | 0 | 3.4 | 0 | 3.91 | 2.07 | 0
2025-02-12 14:00 | 42.85 | 92.14 | 45.17 | 0 | 2.33 | 0 | 6.12 | 46.96 | 0
2025-02-12 15:00 | 43.65 | 100.86 | 43.65 | 0 | 0 | 0 | 6.12 | 57.21 | 0
2025-02-12 16:00 | 42.93 | 83.76 | 42.93 | 0 | 0 | 0 | 6.12 | 40.83 | 0
2025-02-12 17:00 | 42.78 | 5.42 | 5.42 | 33.96 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-12 18:00 | 43.4 | 0 | 0 | 41.63 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-12 19:00 | 41.78 | 0 | 0 | 41.78 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 20:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 22:00 | 40.59 | 0 | 0 | 40.59 | 0 | 0 | 0.68 | 0 | 0
2025-02-12 23:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 01:00 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 02:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 03:00 | 37.72 | 0 | 0 | 37.72 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 04:00 | 37.09 | 0 | 0 | 37.09 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 05:00 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 06:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 07:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 08:00 | 40.24 | 8.21 | 8.21 | 32.02 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 09:00 | 41 | 16.36 | 16.36 | 24.64 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 10:00 | 42.19 | 6.13 | 6.13 | 36.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 11:00 | 42.8 | 51.45 | 46.2 | 0 | 3.4 | 0 | 3.91 | 5.25 | 0
2025-02-13 12:00 | 43.87 | 68.26 | 46.2 | 0 | 2.33 | 0 | 6.12 | 22.07 | 0
2025-02-13 13:00 | 44.03 | 64.78 | 44.03 | 0 | 0 | 0 | 6.12 | 20.75 | 0
2025-02-13 14:00 | 45.75 | 59.18 | 45.75 | 0 | 0 | 0 | 6.12 | 13.43 | 0
2025-02-13 15:00 | 43.99 | 25.63 | 25.63 | 14.96 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-13 16:00 | 45.26 | 54.09 | 48.66 | 0 | 3.4 | 0 | 5.77 | 5.42 | 0
2025-02-13 17:00 | 44.92 | 1.17 | 1.17 | 40.36 | 0 | 3.4 | 2.19 | 0 | 0
2025-02-13 18:00 | 43.19 | 0 | 0 | 41.75 | 0 | 1.44 | 0.68 | 0 | 0
2025-02-13 19:00 | 43.92 | 0 | 0 | 43.92 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 20:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 21:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 22:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 0.68 | 0 | 0
2025-02-13 23:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 01:00 | 37.87 | 0 | 0 | 37.87 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 02:00 | 38 | 0 | 0 | 38 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 03:00 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 04:00 | 36.84 | 0 | 0 | 36.84 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 05:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 06:00 | 38.72 | 0 | 0 | 38.72 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 07:00 | 39.36 | 0 | 0 | 39.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 08:00 | 40.31 | 13.51 | 13.51 | 26.8 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 09:00 | 40.78 | 1.76 | 1.76 | 39.02 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 10:00 | 41.43 | 45.83 | 44.83 | 0 | 3.4 | 0 | 3.91 | 1.01 | 0
2025-02-14 11:00 | 42.38 | 31.82 | 31.82 | 7.49 | 0 | 3.07 | 0.68 | 0 | 0
2025-02-14 12:00 | 42.79 | 34.43 | 34.43 | 8.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 13:00 | 44.33 | 34.05 | 34.05 | 10.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 14:00 | 44.56 | 22.54 | 22.54 | 22.02 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 15:00 | 44.51 | 53.08 | 47.91 | 0 | 3.4 | 0 | 3.91 | 5.17 | 0
2025-02-14 16:00 | 43.12 | 59.61 | 45.45 | 0 | 2.33 | 0 | 6.12 | 14.16 | 0
2025-02-14 17:00 | 43.59 | 0.97 | 0.97 | 39.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-14 18:00 | 44.16 | 0 | 0 | 42.4 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-14 19:00 | 42.48 | 0 | 0 | 42.48 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 20:00 | 42.07 | 0 | 0 | 42.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 21:00 | 40.22 | 0 | 0 | 40.22 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 22:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 0.68 | 0 | 0
2025-02-14 23:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 | 38.47 | 0 | 0 | 38.47 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 01:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 02:00 | 38.11 | 0 | 0 | 38.11 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 03:00 | 37.07 | 0 | 0 | 37.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 04:00 | 37.05 | 0 | 0 | 37.05 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 05:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 06:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 07:00 | 39.06 | 0.02 | 0.02 | 39.03 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 08:00 | 39.83 | 23.32 | 23.32 | 16.51 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 09:00 | 41.76 | 68.23 | 45.16 | 0 | 3.4 | 0 | 3.91 | 23.06 | 0
2025-02-15 10:00 | 41.98 | 71.9 | 44.31 | 0 | 2.33 | 0 | 6.12 | 27.59 | 0
2025-02-15 11:00 | 44.14 | 53.27 | 44.14 | 0 | 0 | 0 | 6.12 | 9.13 | 0
2025-02-15 12:00 | 43.86 | 54.72 | 43.86 | 0 | 0 | 0 | 6.12 | 10.86 | 0
2025-02-15 13:00 | 45.34 | 31.92 | 31.92 | 10.02 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-15 14:00 | 45.03 | 49 | 48.43 | 0 | 3.4 | 0 | 5.77 | 0.57 | 0
2025-02-15 15:00 | 45.47 | 73.4 | 45.83 | 0 | 0.37 | 0 | 6.12 | 27.57 | 0
2025-02-15 16:00 | 44.49 | 61.85 | 44.49 | 0 | 0 | 0 | 6.12 | 17.36 | 0
2025-02-15 17:00 | 44.02 | 0.75 | 0.75 | 39.87 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-15 18:00 | 44.04 | 0 | 0 | 42.27 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-15 19:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 20:00 | 42.06 | 0 | 0 | 42.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 21:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 22:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 0.68 | 0 | 0
2025-02-15 23:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 01:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 02:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 03:00 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 04:00 | 36.27 | 0 | 0 | 36.27 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 05:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 06:00 | 38.32 | 0 | 0 | 38.32 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 07:00 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 08:00 | 39.5 | 1.21 | 1.21 | 38.3 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 09:00 | 41.14 | 2.78 | 2.78 | 38.37 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 10:00 | 43.34 | 6.08 | 6.08 | 37.26 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 11:00 | 43.82 | 5.75 | 5.75 | 38.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 12:00 | 44.85 | 9.5 | 9.5 | 35.35 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 13:00 | 45.4 | 51.23 | 48.79 | 0 | 3.4 | 0 | 3.91 | 2.43 | 0
2025-02-16 14:00 | 45.99 | 45.33 | 45.33 | 0 | 0 | 0.66 | 3.21 | 0 | 0
2025-02-16 15:00 | 46.38 | 36.31 | 36.31 | 7.67 | 0 | 2.41 | 0.68 | 0 | 0
2025-02-16 16:00 | 45.42 | 29.12 | 29.12 | 16.3 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 17:00 | 45.78 | 2.11 | 2.11 | 43.66 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 18:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 19:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 20:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 21:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 22:00 | 40.22 | 0 | 0 | 40.22 | 0 | 0 | 0.68 | 0 | 0
2025-02-16 23:00 | 38.92 | 0 | 0 | 38.92 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 01:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 02:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 03:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 04:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 05:00 | 38.19 | 0 | 0 | 38.19 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 06:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 07:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 08:00 | 39.88 | 0.09 | 0.09 | 39.79 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 09:00 | 41.87 | 1.72 | 1.72 | 40.15 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 10:00 | 42.4 | 3.04 | 3.04 | 39.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 11:00 | 43.1 | 4.06 | 4.06 | 39.04 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 12:00 | 44.3 | 4.48 | 4.48 | 39.82 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 13:00 | 43.64 | 47.2 | 47.04 | 0 | 3.4 | 0 | 3.91 | 0.16 | 0
2025-02-17 14:00 | 45.08 | 46.46 | 46.46 | 0 | 1.37 | 0 | 5.21 | 0 | 0
2025-02-17 15:00 | 46.24 | 35.17 | 35.17 | 7.68 | 0 | 3.4 | 1.64 | 0 | 0
2025-02-17 16:00 | 45.17 | 34.89 | 34.89 | 9.37 | 0 | 0.91 | 0.68 | 0 | 0
2025-02-17 17:00 | 44.73 | 1.98 | 1.98 | 42.75 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 18:00 | 44.32 | 0 | 0 | 44.32 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 19:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 20:00 | 41.24 | 0 | 0 | 41.24 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 21:00 | 40.37 | 0 | 0 | 40.37 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 22:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 0.68 | 0 | 0
2025-02-17 23:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 01:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 02:00 | 36.54 | 0 | 0 | 36.54 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 03:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 04:00 | 36.13 | 0 | 0 | 36.13 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 05:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 06:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 07:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 08:00 | 40.9 | 5.26 | 5.26 | 35.64 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 09:00 | 42.06 | 7.33 | 7.33 | 34.73 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 10:00 | 42.51 | 17.9 | 17.9 | 24.61 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 11:00 | 42.61 | 28.85 | 28.85 | 13.75 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 12:00 | 44.94 | 23.36 | 23.36 | 21.58 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 13:00 | 45.65 | 18.86 | 18.86 | 26.8 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 14:00 | 46 | 14.62 | 14.62 | 31.38 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 15:00 | 46.5 | 9.8 | 9.8 | 36.7 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 16:00 | 45.27 | 2.02 | 2.02 | 43.25 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 17:00 | 46.38 | 0.05 | 0.05 | 46.33 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 18:00 | 44.15 | 0 | 0 | 44.15 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 19:00 | 44.05 | 0 | 0 | 44.05 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 20:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 21:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 22:00 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 0.68 | 0 | 0
2025-02-18 23:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 01:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 02:00 | 37.51 | 0 | 0 | 37.51 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 03:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 04:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 05:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 06:00 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 07:00 | 39.66 | 0.6 | 0.6 | 39.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 08:00 | 40.53 | 25.45 | 25.45 | 15.08 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 09:00 | 40.56 | 65.5 | 43.96 | 0 | 3.4 | 0 | 3.91 | 21.54 | 0
2025-02-19 10:00 | 42 | 71 | 44.33 | 0 | 2.33 | 0 | 6.12 | 26.67 | 0
2025-02-19 11:00 | 43.03 | 73.02 | 43.03 | 0 | 0 | 0 | 6.12 | 29.99 | 0
2025-02-19 12:00 | 43.96 | 68.64 | 43.96 | 0 | 0 | 0 | 6.12 | 24.68 | 0
2025-02-19 13:00 | 44.08 | 71.86 | 44.08 | 0 | 0 | 0 | 6.12 | 27.78 | 0
2025-02-19 14:00 | 44.85 | 68.45 | 44.85 | 0 | 0 | 0 | 6.12 | 23.6 | 0
2025-02-19 15:00 | 44.94 | 65.61 | 44.94 | 0 | 0 | 0 | 6.12 | 20.67 | 0
2025-02-19 16:00 | 45.55 | 32.82 | 32.82 | 9.34 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-19 17:00 | 45.17 | 4.9 | 4.9 | 38.51 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-19 18:00 | 44.07 | 0 | 0 | 44.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 19:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 20:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 21:00 | 40.94 | 0 | 0 | 40.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 22:00 | 39.75 | 0 | 0 | 39.75 | 0 | 0 | 0.68 | 0 | 0
2025-02-19 23:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 01:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 02:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 03:00 | 37.86 | 0 | 0 | 37.86 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 04:00 | 36.83 | 0 | 0 | 36.83 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 05:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 06:00 | 38.54 | 0 | 0 | 38.54 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 07:00 | 39.65 | 1.23 | 1.23 | 38.43 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 08:00 | 40.45 | 58.24 | 43.85 | 0 | 3.4 | 0 | 3.91 | 14.39 | 0
2025-02-20 09:00 | 40.8 | 77.64 | 43.12 | 0 | 2.33 | 0 | 6.12 | 34.52 | 0
2025-02-20 10:00 | 41.97 | 80 | 41.97 | 0 | 0 | 0 | 6.12 | 38.03 | 0
2025-02-20 11:00 | 43.63 | 70.88 | 43.63 | 0 | 0 | 0 | 6.12 | 27.25 | 0
2025-02-20 12:00 | 45.01 | 66.4 | 45.01 | 0 | 0 | 0 | 6.12 | 21.39 | 0
2025-02-20 13:00 | 44.07 | 70.19 | 44.07 | 0 | 0 | 0 | 6.12 | 26.12 | 0
2025-02-20 14:00 | 45.78 | 79.21 | 45.78 | 0 | 0 | 0 | 6.12 | 33.42 | 0
2025-02-20 15:00 | 46.35 | 70.73 | 46.35 | 0 | 0 | 0 | 6.12 | 24.38 | 0
2025-02-20 16:00 | 45.53 | 57.18 | 45.53 | 0 | 0 | 0 | 6.12 | 11.65 | 0
2025-02-20 17:00 | 45.45 | 7.96 | 7.96 | 34.09 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-20 18:00 | 44.14 | 0 | 0 | 42.38 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-20 19:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 20:00 | 41.79 | 0 | 0 | 41.79 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 21:00 | 40.35 | 0 | 0 | 40.35 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 22:00 | 40.93 | 0 | 0 | 40.93 | 0 | 0 | 0.68 | 0 | 0
2025-02-20 23:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 01:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 02:00 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 03:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 04:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 06:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 07:00 | 39.75 | 0.33 | 0.33 | 39.43 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 08:00 | 40.74 | 19.2 | 19.2 | 21.53 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 09:00 | 42.54 | 49.15 | 45.94 | 0 | 3.4 | 0 | 3.91 | 3.21 | 0
2025-02-21 10:00 | 42.38 | 72.83 | 44.7 | 0 | 2.33 | 0 | 6.12 | 28.13 | 0
2025-02-21 11:00 | 43.99 | 83.86 | 43.99 | 0 | 0 | 0 | 6.12 | 39.87 | 0
2025-02-21 12:00 | 45.56 | 40.3 | 40.3 | 1.86 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-21 13:00 | 46.38 | 23.61 | 23.61 | 21 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-21 14:00 | 45.52 | 6.16 | 6.16 | 39.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 15:00 | 46.24 | 4.11 | 4.11 | 42.13 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 16:00 | 46.91 | 1.23 | 1.23 | 45.68 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 17:00 | 46 | 0.54 | 0.54 | 45.46 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 18:00 | 45.09 | 0 | 0 | 45.09 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 19:00 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 20:00 | 42.72 | 0 | 0 | 42.72 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 21:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 22:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0.68 | 0 | 0
2025-02-21 23:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 01:00 | 37.8 | 0 | 0 | 37.8 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 02:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 04:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 05:00 | 38.3 | 0 | 0 | 38.3 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 06:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 07:00 | 39.78 | 1.94 | 1.94 | 37.84 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 08:00 | 40.32 | 62.8 | 43.72 | 0 | 3.4 | 0 | 3.91 | 19.08 | 0
2025-02-22 09:00 | 41.48 | 81.93 | 43.81 | 0 | 2.33 | 0 | 6.12 | 38.12 | 0
2025-02-22 10:00 | 42.42 | 64.32 | 42.42 | 0 | 0 | 0 | 6.12 | 21.9 | 0
2025-02-22 11:00 | 42.55 | 75.36 | 42.55 | 0 | 0 | 0 | 6.12 | 32.81 | 0
2025-02-22 12:00 | 43.5 | 78.18 | 43.5 | 0 | 0 | 0 | 6.12 | 34.68 | 0
2025-02-22 13:00 | 42.1 | 54.19 | 42.1 | 0 | 0 | 0 | 6.12 | 12.09 | 0
2025-02-22 14:00 | 44.27 | 41.51 | 41.51 | 0 | 0 | 2.76 | 3.22 | 0 | 0
2025-02-22 15:00 | 43.73 | 26.19 | 26.19 | 15.13 | 0 | 2.41 | 0.68 | 0 | 0
2025-02-22 16:00 | 44.01 | 5.74 | 5.74 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 17:00 | 42.66 | 0.95 | 0.95 | 41.72 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 19:00 | 42.53 | 0 | 0 | 42.53 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 20:00 | 41.83 | 0 | 0 | 41.83 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 21:00 | 41.24 | 0 | 0 | 41.24 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 22:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0.68 | 0 | 0
2025-02-22 23:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 01:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 02:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 04:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 05:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 06:00 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 07:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 08:00 | 40.65 | 9 | 9 | 31.65 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 09:00 | 41.56 | 9.29 | 9.29 | 32.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 10:00 | 43.19 | 3.13 | 3.13 | 40.07 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 11:00 | 43.42 | 85.53 | 46.82 | 0 | 3.4 | 0 | 3.91 | 38.71 | 0
2025-02-23 12:00 | 43.92 | 65.48 | 46.25 | 0 | 2.33 | 0 | 6.12 | 19.23 | 0
2025-02-23 13:00 | 44.6 | 44.84 | 44.6 | 0 | 0 | 0 | 6.12 | 0.24 | 0
2025-02-23 14:00 | 45.85 | 42.71 | 42.71 | 0 | 0 | 3.14 | 2.81 | 0 | 0
2025-02-23 15:00 | 45.6 | 89.97 | 49 | 0 | 3.4 | 0 | 6.04 | 40.97 | 0
2025-02-23 16:00 | 45.02 | 81.84 | 45.1 | 0 | 0.08 | 0 | 6.12 | 36.74 | 0
2025-02-23 17:00 | 44.73 | 16.11 | 16.11 | 25.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-23 18:00 | 43.49 | 0 | 0 | 41.72 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-23 19:00 | 43.7 | 0 | 0 | 43.7 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 20:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 21:00 | 42 | 0 | 0 | 42 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 22:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 0.68 | 0 | 0
2025-02-23 23:00 | 40.87 | 0 | 0 | 40.87 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 01:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 02:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 03:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 04:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 05:00 | 38.4 | 0 | 0 | 38.4 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 06:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 07:00 | 39.9 | 6.12 | 6.12 | 33.78 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 08:00 | 40.34 | 77.32 | 43.74 | 0 | 3.4 | 0 | 3.91 | 33.58 | 0
2025-02-24 09:00 | 41.63 | 75.75 | 43.96 | 0 | 2.33 | 0 | 6.12 | 31.79 | 0
2025-02-24 10:00 | 41.84 | 85.13 | 41.84 | 0 | 0 | 0 | 6.12 | 43.29 | 0
2025-02-24 11:00 | 43.58 | 91.48 | 43.58 | 0 | 0 | 0 | 6.12 | 47.89 | 0
2025-02-24 12:00 | 44.48 | 85.72 | 44.48 | 0 | 0 | 0 | 6.12 | 41.24 | 0
2025-02-24 13:00 | 44.69 | 61.01 | 44.69 | 0 | 0 | 0 | 6.12 | 16.32 | 0
2025-02-24 14:00 | 44.34 | 59.19 | 44.34 | 0 | 0 | 0 | 6.12 | 14.85 | 0
2025-02-24 15:00 | 45.76 | 9.79 | 9.79 | 32.57 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-24 16:00 | 45.33 | 1.1 | 1.1 | 42.46 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-24 17:00 | 44.44 | 0 | 0 | 44.44 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 18:00 | 44.11 | 0 | 0 | 44.11 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 19:00 | 42.77 | 0 | 0 | 42.77 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 20:00 | 42.13 | 0 | 0 | 42.13 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 21:00 | 41.41 | 0 | 0 | 41.41 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 22:00 | 41.31 | 0 | 0 | 41.31 | 0 | 0 | 0.68 | 0 | 0
2025-02-24 23:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 | 39.33 | 0 | 0 | 39.33 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 01:00 | 38.09 | 0 | 0 | 38.09 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 02:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 03:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 04:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 05:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 06:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 07:00 | 39.14 | 2.1 | 2.1 | 37.04 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 08:00 | 40.5 | 58.95 | 43.9 | 0 | 3.4 | 0 | 3.91 | 15.05 | 0
2025-02-25 09:00 | 41.11 | 79 | 43.43 | 0 | 2.33 | 0 | 6.12 | 35.57 | 0
2025-02-25 10:00 | 42.87 | 82.37 | 42.87 | 0 | 0 | 0 | 6.12 | 39.5 | 0
2025-02-25 11:00 | 43.28 | 72.09 | 43.28 | 0 | 0 | 0 | 6.12 | 28.82 | 0
2025-02-25 12:00 | 45.4 | 71.06 | 45.4 | 0 | 0 | 0 | 6.12 | 25.66 | 0
2025-02-25 13:00 | 43.87 | 77.21 | 43.87 | 0 | 0 | 0 | 6.12 | 33.34 | 0
2025-02-25 14:00 | 45.16 | 76.33 | 45.16 | 0 | 0 | 0 | 6.12 | 31.16 | 0
2025-02-25 15:00 | 44.61 | 64.23 | 44.61 | 0 | 0 | 0 | 6.12 | 19.62 | 0
2025-02-25 16:00 | 44.82 | 65.45 | 44.82 | 0 | 0 | 0 | 6.12 | 20.64 | 0
2025-02-25 17:00 | 44.81 | 11.01 | 11.01 | 30.4 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-25 18:00 | 43.05 | 0 | 0 | 41.28 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-25 19:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 20:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 21:00 | 41.5 | 0 | 0 | 41.5 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 22:00 | 40.89 | 0 | 0 | 40.89 | 0 | 0 | 0.68 | 0 | 0
2025-02-25 23:00 | 40.34 | 0 | 0 | 40.34 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 01:00 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 02:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 03:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 04:00 | 37.97 | 0 | 0 | 37.97 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 05:00 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 06:00 | 39.17 | 0 | 0 | 39.17 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 07:00 | 39.67 | 2.84 | 2.84 | 36.82 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 08:00 | 40.68 | 24.75 | 24.75 | 15.92 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 09:00 | 42.29 | 78.92 | 45.69 | 0 | 3.4 | 0 | 3.91 | 33.24 | 0
2025-02-26 10:00 | 42.34 | 87.6 | 44.67 | 0 | 2.33 | 0 | 6.12 | 42.93 | 0
2025-02-26 11:00 | 44.48 | 78.02 | 44.48 | 0 | 0 | 0 | 6.12 | 33.54 | 0
2025-02-26 12:00 | 44.06 | 78.32 | 44.06 | 0 | 0 | 0 | 6.12 | 34.25 | 0
2025-02-26 13:00 | 45.04 | 63.27 | 45.04 | 0 | 0 | 0 | 6.12 | 18.23 | 0
2025-02-26 14:00 | 46.71 | 39.39 | 39.39 | 3.92 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-26 15:00 | 46.44 | 19.29 | 19.29 | 25.39 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-26 16:00 | 45.8 | 4.99 | 4.99 | 40.81 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 17:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 18:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 19:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 20:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 21:00 | 41.94 | 0 | 0 | 41.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 22:00 | 40.93 | 0 | 0 | 40.93 | 0 | 0 | 0.68 | 0 | 0
2025-02-26 23:00 | 39.85 | 0 | 0 | 39.85 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 | 38.53 | 0 | 0 | 38.53 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 01:00 | 38.27 | 0 | 0 | 38.27 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 02:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 03:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 04:00 | 38 | 0 | 0 | 38 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 05:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 06:00 | 39.3 | 0 | 0 | 39.3 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 07:00 | 40.03 | 4.97 | 4.97 | 35.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 08:00 | 42.16 | 77.21 | 45.56 | 0 | 3.4 | 0 | 3.91 | 31.65 | 0
2025-02-27 09:00 | 43.04 | 91.12 | 45.36 | 0 | 2.33 | 0 | 6.12 | 45.76 | 0
2025-02-27 10:00 | 43.57 | 89.2 | 43.57 | 0 | 0 | 0 | 6.12 | 45.63 | 0
2025-02-27 11:00 | 45.97 | 83.43 | 45.97 | 0 | 0 | 0 | 6.12 | 37.46 | 0
2025-02-27 12:00 | 46.51 | 76.75 | 46.51 | 0 | 0 | 0 | 6.12 | 30.24 | 0
2025-02-27 13:00 | 47.61 | 80.25 | 47.61 | 0 | 0 | 0 | 6.12 | 32.64 | 0
2025-02-27 14:00 | 48.7 | 87.23 | 48.7 | 0 | 0 | 0 | 6.12 | 38.53 | 0
2025-02-27 15:00 | 48.52 | 94.02 | 48.52 | 0 | 0 | 0 | 6.12 | 45.5 | 0
2025-02-27 16:00 | 48.99 | 85.24 | 48.99 | 0 | 0 | 0 | 6.12 | 36.25 | 0
2025-02-27 17:00 | 47.51 | 20.07 | 20.07 | 24.04 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-27 18:00 | 46.59 | 0 | 0 | 44.82 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-27 19:00 | 45.3 | 0 | 0 | 45.3 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 20:00 | 43.94 | 0 | 0 | 43.94 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 21:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 22:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0.68 | 0 | 0
2025-02-27 23:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 01:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 02:00 | 38.21 | 0 | 0 | 38.21 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 03:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 04:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 06:00 | 38.73 | 0 | 0 | 38.73 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 07:00 | 39.57 | 5.75 | 5.75 | 33.83 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 08:00 | 40.96 | 86.96 | 44.36 | 0 | 3.4 | 0 | 3.91 | 42.6 | 0
2025-02-28 09:00 | 41.39 | 98.33 | 43.72 | 0 | 2.33 | 0 | 6.12 | 54.61 | 0
2025-02-28 10:00 | 43.34 | 94.42 | 43.34 | 0 | 0 | 0 | 6.12 | 51.08 | 0
2025-02-28 11:00 | 43.28 | 86.89 | 43.28 | 0 | 0 | 0 | 6.12 | 43.62 | 0
2025-02-28 12:00 | 45.81 | 81.98 | 45.81 | 0 | 0 | 0 | 6.12 | 36.17 | 0
2025-02-28 13:00 | 44.68 | 84.82 | 44.68 | 0 | 0 | 0 | 6.12 | 40.15 | 0
2025-02-28 14:00 | 45.24 | 91.46 | 45.24 | 0 | 0 | 0 | 6.12 | 46.22 | 0
2025-02-28 15:00 | 44.66 | 97.1 | 44.66 | 0 | 0 | 0 | 6.12 | 52.44 | 0
2025-02-28 16:00 | 46.06 | 91.6 | 46.06 | 0 | 0 | 0 | 6.12 | 45.55 | 0
2025-02-28 17:00 | 45.46 | 25.19 | 25.19 | 16.88 | 0 | 3.4 | 2.54 | 0 | 0
2025-02-28 18:00 | 44.56 | 0 | 0 | 42.79 | 0 | 1.77 | 0.68 | 0 | 0
2025-02-28 19:00 | 43.06 | 0 | 0 | 43.06 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 20:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 21:00 | 41.44 | 0 | 0 | 41.44 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 22:00 | 41.77 | 0 | 0 | 41.77 | 0 | 0 | 0.68 | 0 | 0
2025-02-28 23:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 01:00 | 37.47 | 0 | 0 | 37.47 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 03:00 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 04:00 | 38.86 | 0 | 0 | 38.86 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 05:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 06:00 | 38.62 | 0 | 0 | 38.62 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 07:00 | 40.53 | 4.6 | 4.6 | 35.93 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 08:00 | 42.05 | 60.17 | 45.45 | 0 | 3.4 | 0 | 3.91 | 14.72 | 0
2025-03-01 09:00 | 42.02 | 45.65 | 44.34 | 0 | 2.33 | 0 | 6.12 | 1.31 | 0
2025-03-01 10:00 | 44.2 | 70.62 | 44.2 | 0 | 0 | 0 | 6.12 | 26.42 | 0
2025-03-01 11:00 | 45.64 | 60.91 | 45.64 | 0 | 0 | 0 | 6.12 | 15.27 | 0
2025-03-01 12:00 | 46.51 | 69.53 | 46.51 | 0 | 0 | 0 | 6.12 | 23.02 | 0
2025-03-01 13:00 | 46.65 | 68.62 | 46.65 | 0 | 0 | 0 | 6.12 | 21.97 | 0
2025-03-01 14:00 | 47.99 | 71.77 | 47.99 | 0 | 0 | 0 | 6.12 | 23.78 | 0
2025-03-01 15:00 | 48.19 | 74.43 | 48.19 | 0 | 0 | 0 | 6.12 | 26.24 | 0
2025-03-01 16:00 | 48.08 | 78.28 | 48.08 | 0 | 0 | 0 | 6.12 | 30.19 | 0
2025-03-01 17:00 | 47.29 | 21.25 | 21.25 | 22.64 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-01 18:00 | 46.44 | 0 | 0 | 44.68 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-01 19:00 | 45.49 | 0 | 0 | 45.49 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 20:00 | 44.42 | 0 | 0 | 44.42 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 21:00 | 42.7 | 0 | 0 | 42.7 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 22:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 0.68 | 0 | 0
2025-03-01 23:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 | 38.45 | 0 | 0 | 38.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 01:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 02:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 03:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 04:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 05:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 06:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 07:00 | 40.36 | 8.56 | 8.56 | 31.8 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 08:00 | 41.08 | 81.17 | 44.48 | 0 | 3.4 | 0 | 3.91 | 36.68 | 0
2025-03-02 09:00 | 42.01 | 96.6 | 44.34 | 0 | 2.33 | 0 | 6.12 | 52.26 | 0
2025-03-02 10:00 | 42.45 | 93.91 | 42.45 | 0 | 0 | 0 | 6.12 | 51.46 | 0
2025-03-02 11:00 | 43.64 | 86.93 | 43.64 | 0 | 0 | 0 | 6.12 | 43.3 | 0
2025-03-02 12:00 | 44.24 | 82.38 | 44.24 | 0 | 0 | 0 | 6.12 | 38.14 | 0
2025-03-02 13:00 | 44.34 | 86.12 | 44.34 | 0 | 0 | 0 | 6.12 | 41.78 | 0
2025-03-02 14:00 | 44.15 | 92.51 | 44.15 | 0 | 0 | 0 | 6.12 | 48.35 | 0
2025-03-02 15:00 | 43.29 | 95.99 | 43.29 | 0 | 0 | 0 | 6.12 | 52.7 | 0
2025-03-02 16:00 | 44.67 | 85.82 | 44.67 | 0 | 0 | 0 | 6.12 | 41.16 | 0
2025-03-02 17:00 | 44.71 | 25.89 | 25.89 | 15.42 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-02 18:00 | 44.1 | 0 | 0 | 42.33 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-02 19:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 20:00 | 43.02 | 0 | 0 | 43.02 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 21:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 22:00 | 41.87 | 0 | 0 | 41.87 | 0 | 0 | 0.68 | 0 | 0
2025-03-02 23:00 | 39.78 | 0 | 0 | 39.78 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 | 39.44 | 0 | 0 | 39.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 01:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 02:00 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 03:00 | 37.7 | 0 | 0 | 37.7 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 04:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 06:00 | 39.6 | 0 | 0 | 39.6 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 07:00 | 40.57 | 0.13 | 0.13 | 40.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 08:00 | 41.37 | 19.83 | 19.83 | 21.55 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 09:00 | 43.34 | 2.59 | 2.59 | 40.74 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 10:00 | 43.23 | 33.59 | 33.59 | 9.64 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 11:00 | 44.38 | 62.55 | 47.78 | 0 | 3.4 | 0 | 3.91 | 14.77 | 0
2025-03-03 12:00 | 45.51 | 44.69 | 44.69 | 0 | 0 | 0.83 | 3.04 | 0 | 0
2025-03-03 13:00 | 46.58 | 25.12 | 25.12 | 19.23 | 0 | 2.24 | 0.68 | 0 | 0
2025-03-03 14:00 | 45.79 | 37.92 | 37.92 | 7.87 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 15:00 | 46.02 | 24.56 | 24.56 | 21.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 16:00 | 45.52 | 54.9 | 48.92 | 0 | 3.4 | 0 | 3.91 | 5.98 | 0
2025-03-03 17:00 | 46.16 | 15.77 | 15.77 | 27.32 | 0 | 3.07 | 0.68 | 0 | 0
2025-03-03 18:00 | 44.95 | 0 | 0 | 44.95 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 19:00 | 44.48 | 0 | 0 | 44.48 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 20:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 21:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 22:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 0.68 | 0 | 0
2025-03-03 23:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 01:00 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 02:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 03:00 | 38.25 | 0 | 0 | 38.25 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 04:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 06:00 | 38.97 | 0 | 0 | 38.97 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 07:00 | 40.95 | 7.99 | 7.99 | 32.96 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 08:00 | 41.19 | 39.13 | 39.13 | 2.07 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 09:00 | 43.65 | 85.24 | 47.05 | 0 | 3.4 | 0 | 3.91 | 38.19 | 0
2025-03-04 10:00 | 44.66 | 40.85 | 40.85 | 0.75 | 0 | 3.07 | 0.68 | 0 | 0
2025-03-04 11:00 | 45.44 | 50.67 | 48.84 | 0 | 3.4 | 0 | 3.91 | 1.84 | 0
2025-03-04 12:00 | 46.35 | 53.82 | 48.68 | 0 | 2.33 | 0 | 6.12 | 5.14 | 0
2025-03-04 13:00 | 46.93 | 61.45 | 46.93 | 0 | 0 | 0 | 6.12 | 14.52 | 0
2025-03-04 14:00 | 47.85 | 97.16 | 47.85 | 0 | 0 | 0 | 6.12 | 49.3 | 0
2025-03-04 15:00 | 47.49 | 76.36 | 47.49 | 0 | 0 | 0 | 6.12 | 28.87 | 0
2025-03-04 16:00 | 47.63 | 47.32 | 47.32 | 0 | 0 | 0.31 | 5.79 | 0 | 0
2025-03-04 17:00 | 47.47 | 10.34 | 10.34 | 33.73 | 0 | 3.4 | 2.21 | 0 | 0
2025-03-04 18:00 | 45.99 | 0 | 0 | 44.54 | 0 | 1.46 | 0.68 | 0 | 0
2025-03-04 19:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 20:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 21:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 22:00 | 40.82 | 0 | 0 | 40.82 | 0 | 0 | 0.68 | 0 | 0
2025-03-04 23:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 01:00 | 39.75 | 0 | 0 | 39.75 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 03:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 04:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 05:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 06:00 | 39.84 | 0 | 0 | 39.84 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 07:00 | 39.77 | 9.62 | 9.62 | 30.16 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 08:00 | 42.09 | 97.11 | 45.49 | 0 | 3.4 | 0 | 3.91 | 51.62 | 0
2025-03-05 09:00 | 42.72 | 100.21 | 45.05 | 0 | 2.33 | 0 | 6.12 | 55.16 | 0
2025-03-05 10:00 | 44.69 | 87.68 | 44.69 | 0 | 0 | 0 | 6.12 | 42.99 | 0
2025-03-05 11:00 | 45.08 | 71.89 | 45.08 | 0 | 0 | 0 | 6.12 | 26.81 | 0
2025-03-05 12:00 | 47.24 | 54.23 | 47.24 | 0 | 0 | 0 | 6.12 | 6.99 | 0
2025-03-05 13:00 | 48.35 | 45.76 | 45.76 | 0 | 0 | 2.59 | 3.4 | 0 | 0
2025-03-05 14:00 | 48 | 42.47 | 42.47 | 2.95 | 0 | 2.58 | 0.68 | 0 | 0
2025-03-05 15:00 | 48.01 | 38.32 | 38.32 | 9.69 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 16:00 | 47.31 | 25.29 | 25.29 | 22.03 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 17:00 | 47.71 | 3.62 | 3.62 | 44.09 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 18:00 | 46.68 | 0 | 0 | 46.68 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 19:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 20:00 | 44.82 | 0 | 0 | 44.82 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 21:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 22:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0.68 | 0 | 0
2025-03-05 23:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 | 40.43 | 0 | 0 | 40.43 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 01:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 02:00 | 38.59 | 0 | 0 | 38.59 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 03:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 04:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 06:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 07:00 | 40.67 | 12.98 | 12.98 | 27.69 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 08:00 | 42.33 | 74.38 | 45.73 | 0 | 3.4 | 0 | 3.91 | 28.64 | 0
2025-03-06 09:00 | 43.07 | 88.67 | 45.39 | 0 | 2.33 | 0 | 6.12 | 43.28 | 0
2025-03-06 10:00 | 45.09 | 86.36 | 45.09 | 0 | 0 | 0 | 6.12 | 41.27 | 0
2025-03-06 11:00 | 46.43 | 84.74 | 46.43 | 0 | 0 | 0 | 6.12 | 38.3 | 0
2025-03-06 12:00 | 45.86 | 81.76 | 45.86 | 0 | 0 | 0 | 6.12 | 35.9 | 0
2025-03-06 13:00 | 48.82 | 86.9 | 48.82 | 0 | 0 | 0 | 6.12 | 38.08 | 0
2025-03-06 14:00 | 47.29 | 95.31 | 47.29 | 0 | 0 | 0 | 6.12 | 48.02 | 0
2025-03-06 15:00 | 48.7 | 94.48 | 48.7 | 0 | 0 | 0 | 6.12 | 45.78 | 0
2025-03-06 16:00 | 49.32 | 83.23 | 49.32 | 0 | 0 | 0 | 6.12 | 33.91 | 0
2025-03-06 17:00 | 48.07 | 31.2 | 31.2 | 13.47 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-06 18:00 | 46.59 | 0 | 0 | 44.82 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-06 19:00 | 45.61 | 0 | 0 | 45.61 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 20:00 | 45.35 | 0 | 0 | 45.35 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 21:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 22:00 | 42.68 | 0 | 0 | 42.68 | 0 | 0 | 0.68 | 0 | 0
2025-03-06 23:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 01:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 02:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 03:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 04:00 | 39.11 | 0 | 0 | 39.11 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 05:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 06:00 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 07:00 | 40.6 | 19.12 | 19.12 | 21.48 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 08:00 | 42.92 | 85.22 | 46.32 | 0 | 3.4 | 0 | 3.91 | 38.91 | 0
2025-03-07 09:00 | 42.97 | 92.76 | 45.29 | 0 | 2.33 | 0 | 6.12 | 47.47 | 0
2025-03-07 10:00 | 45.86 | 92.32 | 45.86 | 0 | 0 | 0 | 6.12 | 46.46 | 0
2025-03-07 11:00 | 46.41 | 85.91 | 46.41 | 0 | 0 | 0 | 6.12 | 39.51 | 0
2025-03-07 12:00 | 47.04 | 77.75 | 47.04 | 0 | 0 | 0 | 6.12 | 30.71 | 0
2025-03-07 13:00 | 48.23 | 79.15 | 48.23 | 0 | 0 | 0 | 6.12 | 30.92 | 0
2025-03-07 14:00 | 48.77 | 80 | 48.77 | 0 | 0 | 0 | 6.12 | 31.23 | 0
2025-03-07 15:00 | 48.74 | 80.55 | 48.74 | 0 | 0 | 0 | 6.12 | 31.82 | 0
2025-03-07 16:00 | 49.21 | 82.72 | 49.21 | 0 | 0 | 0 | 6.12 | 33.51 | 0
2025-03-07 17:00 | 47.95 | 32.93 | 32.93 | 11.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-07 18:00 | 46.53 | 0 | 0 | 44.77 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-07 19:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 20:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 21:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 22:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 0.68 | 0 | 0
2025-03-07 23:00 | 40.59 | 0 | 0 | 40.59 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 01:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 02:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 03:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 04:00 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 05:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 06:00 | 39.55 | 0 | 0 | 39.55 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 07:00 | 41.48 | 20.12 | 20.12 | 21.36 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 08:00 | 41.53 | 75.45 | 44.93 | 0 | 3.4 | 0 | 3.91 | 30.52 | 0
2025-03-08 09:00 | 43.16 | 89.27 | 45.49 | 0 | 2.33 | 0 | 6.12 | 43.78 | 0
2025-03-08 10:00 | 44.16 | 87.98 | 44.16 | 0 | 0 | 0 | 6.12 | 43.82 | 0
2025-03-08 11:00 | 45.59 | 83.92 | 45.59 | 0 | 0 | 0 | 6.12 | 38.33 | 0
2025-03-08 12:00 | 46.08 | 82.02 | 46.08 | 0 | 0 | 0 | 6.12 | 35.94 | 0
2025-03-08 13:00 | 46.94 | 83.58 | 46.94 | 0 | 0 | 0 | 6.12 | 36.64 | 0
2025-03-08 14:00 | 47.38 | 84.11 | 47.38 | 0 | 0 | 0 | 6.12 | 36.74 | 0
2025-03-08 15:00 | 47.27 | 89.17 | 47.27 | 0 | 0 | 0 | 6.12 | 41.9 | 0
2025-03-08 16:00 | 47.74 | 86.84 | 47.74 | 0 | 0 | 0 | 6.12 | 39.1 | 0
2025-03-08 17:00 | 47.19 | 34.87 | 34.87 | 8.93 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-08 18:00 | 46.36 | 0 | 0 | 44.59 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-08 19:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 20:00 | 44.85 | 0 | 0 | 44.85 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 21:00 | 43.19 | 0 | 0 | 43.19 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 22:00 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-08 23:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 01:00 | 38.74 | 0 | 0 | 38.74 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 02:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 03:00 | 37.82 | 0 | 0 | 37.82 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 04:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 05:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 06:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 07:00 | 41.22 | 22.18 | 22.18 | 19.03 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 08:00 | 41.96 | 80.47 | 45.36 | 0 | 3.4 | 0 | 3.91 | 35.11 | 0
2025-03-09 09:00 | 43.42 | 94.87 | 45.75 | 0 | 2.33 | 0 | 6.12 | 49.13 | 0
2025-03-09 10:00 | 44.42 | 91.81 | 44.42 | 0 | 0 | 0 | 6.12 | 47.39 | 0
2025-03-09 11:00 | 45.18 | 86.48 | 45.18 | 0 | 0 | 0 | 6.12 | 41.29 | 0
2025-03-09 12:00 | 46.3 | 83.19 | 46.3 | 0 | 0 | 0 | 6.12 | 36.89 | 0
2025-03-09 13:00 | 47.2 | 84.31 | 47.2 | 0 | 0 | 0 | 6.12 | 37.1 | 0
2025-03-09 14:00 | 47.13 | 85.11 | 47.13 | 0 | 0 | 0 | 6.12 | 37.98 | 0
2025-03-09 15:00 | 47.24 | 86.96 | 47.24 | 0 | 0 | 0 | 6.12 | 39.72 | 0
2025-03-09 16:00 | 46.83 | 72.75 | 46.83 | 0 | 0 | 0 | 6.12 | 25.92 | 0
2025-03-09 17:00 | 47.3 | 34.04 | 34.04 | 9.85 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-09 18:00 | 46.72 | 0 | 0 | 44.95 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-09 19:00 | 45.69 | 0 | 0 | 45.69 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 20:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 21:00 | 43.45 | 0 | 0 | 43.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 22:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-09 23:00 | 41.29 | 0 | 0 | 41.29 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 01:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 02:00 | 40.13 | 0 | 0 | 40.13 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 03:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 04:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 05:00 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 06:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 07:00 | 40.7 | 23.9 | 23.9 | 16.8 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 08:00 | 43.26 | 75.89 | 46.66 | 0 | 3.4 | 0 | 3.91 | 29.23 | 0
2025-03-10 09:00 | 44.1 | 81.14 | 46.42 | 0 | 2.33 | 0 | 6.12 | 34.72 | 0
2025-03-10 10:00 | 45.08 | 96.37 | 45.08 | 0 | 0 | 0 | 6.12 | 51.29 | 0
2025-03-10 11:00 | 47.67 | 86.26 | 47.67 | 0 | 0 | 0 | 6.12 | 38.59 | 0
2025-03-10 12:00 | 48.66 | 76.34 | 48.66 | 0 | 0 | 0 | 6.12 | 27.68 | 0
2025-03-10 13:00 | 48.71 | 79.31 | 48.71 | 0 | 0 | 0 | 6.12 | 30.61 | 0
2025-03-10 14:00 | 50.86 | 77.72 | 50.86 | 0 | 0 | 0 | 6.12 | 26.85 | 0
2025-03-10 15:00 | 50.52 | 63.51 | 50.52 | 0 | 0 | 0 | 6.12 | 12.99 | 0
2025-03-10 16:00 | 49.97 | 33.47 | 33.47 | 13.1 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-10 17:00 | 50.13 | 5.56 | 5.56 | 42.81 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-10 18:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 19:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 20:00 | 45.31 | 0 | 0 | 45.31 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 21:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0.68 | 0 | 0
2025-03-10 23:00 | 41.41 | 0 | 0 | 41.41 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 | 40 | 0 | 0 | 40 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 01:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 02:00 | 39.08 | 0 | 0 | 39.08 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 03:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 04:00 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 05:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 06:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 07:00 | 41.51 | 8.45 | 8.45 | 33.07 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 08:00 | 42.35 | 16.52 | 16.52 | 25.83 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 09:00 | 44.49 | 46.23 | 46.23 | 0 | 1.74 | 0 | 2.33 | 0 | 0
2025-03-11 10:00 | 44.83 | 70.45 | 48.23 | 0 | 3.4 | 0 | 5.56 | 22.22 | 0
2025-03-11 11:00 | 46.55 | 69.4 | 47.13 | 0 | 0.59 | 0 | 6.12 | 22.27 | 0
2025-03-11 12:00 | 46.99 | 79.68 | 46.99 | 0 | 0 | 0 | 6.12 | 32.69 | 0
2025-03-11 13:00 | 47.99 | 83.11 | 47.99 | 0 | 0 | 0 | 6.12 | 35.12 | 0
2025-03-11 14:00 | 48.77 | 87.94 | 48.77 | 0 | 0 | 0 | 6.12 | 39.18 | 0
2025-03-11 15:00 | 48.33 | 78.28 | 48.33 | 0 | 0 | 0 | 6.12 | 29.95 | 0
2025-03-11 16:00 | 48.9 | 63.85 | 48.9 | 0 | 0 | 0 | 6.12 | 14.95 | 0
2025-03-11 17:00 | 47.44 | 34.13 | 34.13 | 9.91 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-11 18:00 | 47.34 | 0 | 0 | 45.57 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-11 19:00 | 46.68 | 0 | 0 | 46.68 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 20:00 | 45.4 | 0 | 0 | 45.4 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 21:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 22:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 0.68 | 0 | 0
2025-03-11 23:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 01:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 02:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 03:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 04:00 | 38.65 | 0 | 0 | 38.65 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 05:00 | 40.09 | 0 | 0 | 40.09 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 06:00 | 39.85 | 0 | 0 | 39.85 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 07:00 | 42 | 18.83 | 18.83 | 23.16 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 08:00 | 43.89 | 65.3 | 47.29 | 0 | 3.4 | 0 | 3.91 | 18.01 | 0
2025-03-12 09:00 | 43.69 | 85.82 | 46.01 | 0 | 2.33 | 0 | 6.12 | 39.81 | 0
2025-03-12 10:00 | 44.76 | 59.03 | 44.76 | 0 | 0 | 0 | 6.12 | 14.26 | 0
2025-03-12 11:00 | 45.06 | 70 | 45.06 | 0 | 0 | 0 | 6.12 | 24.94 | 0
2025-03-12 12:00 | 45.06 | 60.39 | 45.06 | 0 | 0 | 0 | 6.12 | 15.33 | 0
2025-03-12 13:00 | 46.13 | 74.88 | 46.13 | 0 | 0 | 0 | 6.12 | 28.75 | 0
2025-03-12 14:00 | 46.17 | 68.25 | 46.17 | 0 | 0 | 0 | 6.12 | 22.08 | 0
2025-03-12 15:00 | 46.09 | 61.31 | 46.09 | 0 | 0 | 0 | 6.12 | 15.23 | 0
2025-03-12 16:00 | 47.58 | 66.9 | 47.58 | 0 | 0 | 0 | 6.12 | 19.32 | 0
2025-03-12 17:00 | 46.57 | 36.2 | 36.2 | 6.98 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-12 18:00 | 46.15 | 0 | 0 | 44.38 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-12 19:00 | 45.15 | 0 | 0 | 45.15 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 20:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 21:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 22:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-12 23:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 01:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 02:00 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 03:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 04:00 | 39.17 | 0 | 0 | 39.17 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 05:00 | 39.84 | 0 | 0 | 39.84 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 06:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 07:00 | 41.54 | 1.76 | 1.76 | 39.78 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 08:00 | 42.66 | 11.73 | 11.73 | 30.94 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 09:00 | 42.65 | 17.85 | 17.85 | 24.8 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 10:00 | 44.29 | 33.1 | 33.1 | 11.19 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 11:00 | 45.83 | 46.65 | 46.65 | 0 | 0.82 | 0 | 1.46 | 0 | 0
2025-03-13 12:00 | 46.54 | 62.44 | 49.94 | 0 | 3.4 | 0 | 4.69 | 12.51 | 0
2025-03-13 13:00 | 46.28 | 70.32 | 47.79 | 0 | 1.51 | 0 | 6.12 | 22.53 | 0
2025-03-13 14:00 | 47.25 | 69.23 | 47.25 | 0 | 0 | 0 | 6.12 | 21.98 | 0
2025-03-13 15:00 | 47.78 | 86.84 | 47.78 | 0 | 0 | 0 | 6.12 | 39.06 | 0
2025-03-13 16:00 | 47.56 | 103.26 | 47.56 | 0 | 0 | 0 | 6.12 | 55.7 | 0
2025-03-13 17:00 | 46.81 | 38.09 | 38.09 | 5.32 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-13 18:00 | 46.11 | 0 | 0 | 44.34 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-13 19:00 | 45.32 | 0 | 0 | 45.32 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 20:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 21:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 22:00 | 42.95 | 0 | 0 | 42.95 | 0 | 0 | 0.68 | 0 | 0
2025-03-13 23:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 01:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 02:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 03:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 04:00 | 39 | 0 | 0 | 39 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 05:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 06:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 07:00 | 41.84 | 44.95 | 44.95 | 0 | 3.1 | 0 | 3.63 | 0 | 0
2025-03-14 08:00 | 41.98 | 103.66 | 44.6 | 0 | 2.62 | 0 | 6.12 | 59.06 | 0
2025-03-14 09:00 | 43.63 | 75.11 | 43.63 | 0 | 0 | 0 | 6.12 | 31.49 | 0
2025-03-14 10:00 | 45.46 | 59.69 | 45.46 | 0 | 0 | 0 | 6.12 | 14.23 | 0
2025-03-14 11:00 | 45.9 | 78.51 | 45.9 | 0 | 0 | 0 | 6.12 | 32.61 | 0
2025-03-14 12:00 | 46.57 | 102.98 | 46.57 | 0 | 0 | 0 | 6.12 | 56.4 | 0
2025-03-14 13:00 | 48.11 | 92.12 | 48.11 | 0 | 0 | 0 | 6.12 | 44.01 | 0
2025-03-14 14:00 | 47.24 | 48.56 | 47.24 | 0 | 0 | 0 | 6.12 | 1.32 | 0
2025-03-14 15:00 | 47.48 | 3.65 | 3.65 | 40.43 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-14 16:00 | 47.87 | 20.84 | 20.84 | 25.26 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-14 17:00 | 47.6 | 2.91 | 2.91 | 44.69 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 18:00 | 47.08 | 0 | 0 | 47.08 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 19:00 | 46.5 | 0 | 0 | 46.5 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 20:00 | 45.17 | 0 | 0 | 45.17 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 21:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 22:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0.68 | 0 | 0
2025-03-14 23:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 | 40.94 | 0 | 0 | 40.94 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 01:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 02:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 03:00 | 39.6 | 0 | 0 | 39.6 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 04:00 | 39.53 | 0 | 0 | 39.53 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 05:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 06:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 07:00 | 42 | 3.34 | 3.34 | 38.65 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 08:00 | 43.45 | 8.38 | 8.38 | 35.06 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 09:00 | 45.92 | 12.94 | 12.94 | 32.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 10:00 | 46.05 | 12.96 | 12.96 | 33.1 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 11:00 | 47.95 | 6.48 | 6.48 | 41.47 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 12:00 | 49.52 | 24.1 | 24.1 | 25.42 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 13:00 | 50 | 32.89 | 32.89 | 17.11 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 14:00 | 51.73 | 42.88 | 42.88 | 8.86 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 15:00 | 50.59 | 38.92 | 38.92 | 11.66 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 16:00 | 50.73 | 56.03 | 54.13 | 0 | 3.4 | 0 | 3.91 | 1.91 | 0
2025-03-15 17:00 | 49.55 | 35.18 | 35.18 | 11.31 | 0 | 3.07 | 0.68 | 0 | 0
2025-03-15 18:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 19:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 20:00 | 46.74 | 0 | 0 | 46.74 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 21:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 22:00 | 43.98 | 0 | 0 | 43.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-15 23:00 | 41.96 | 0 | 0 | 41.96 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 | 40.83 | 0 | 0 | 40.83 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 01:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 02:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 04:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 05:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 06:00 | 41.46 | 0 | 0 | 41.46 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 07:00 | 41.92 | 14.95 | 14.95 | 26.97 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 08:00 | 43.48 | 21.45 | 21.45 | 22.03 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 09:00 | 44.79 | 32.26 | 32.26 | 12.53 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 10:00 | 46.6 | 31.93 | 31.93 | 14.67 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 11:00 | 47.14 | 38.63 | 38.63 | 8.52 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 12:00 | 48.18 | 31.11 | 31.11 | 17.07 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 13:00 | 49.71 | 19.71 | 19.71 | 30.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 14:00 | 50.46 | 13.27 | 13.27 | 37.19 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 15:00 | 50.52 | 15.26 | 15.26 | 35.26 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 16:00 | 49.76 | 10.85 | 10.85 | 38.9 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 17:00 | 49.94 | 4.07 | 4.07 | 45.87 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 18:00 | 48.35 | 0 | 0 | 48.35 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 19:00 | 47.31 | 0 | 0 | 47.31 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 20:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 21:00 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 22:00 | 43.73 | 0 | 0 | 43.73 | 0 | 0 | 0.68 | 0 | 0
2025-03-16 23:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 | 41.76 | 0 | 0 | 41.76 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 01:00 | 41.66 | 0 | 0 | 41.66 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 02:00 | 38.86 | 0 | 0 | 38.86 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 03:00 | 39.16 | 0 | 0 | 39.16 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 04:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 05:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 06:00 | 40.6 | 0 | 0 | 40.6 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 07:00 | 42.16 | 0 | 0 | 42.16 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 08:00 | 43.1 | 2.45 | 2.45 | 40.65 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 09:00 | 45.43 | 4.31 | 4.31 | 41.12 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 10:00 | 46.88 | 5.16 | 5.16 | 41.72 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 11:00 | 48.62 | 7.18 | 7.18 | 41.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 12:00 | 49.97 | 7.39 | 7.39 | 42.59 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 13:00 | 51.07 | 62.54 | 54.47 | 0 | 3.4 | 0 | 3.91 | 8.07 | 0
2025-03-17 14:00 | 51.25 | 57.12 | 53.58 | 0 | 2.33 | 0 | 6.12 | 3.55 | 0
2025-03-17 15:00 | 52.73 | 51.99 | 51.99 | 0 | 0 | 0.74 | 5.34 | 0 | 0
2025-03-17 16:00 | 51.55 | 40.06 | 40.06 | 8.09 | 0 | 3.4 | 1.76 | 0 | 0
2025-03-17 17:00 | 49.84 | 19.98 | 19.98 | 28.83 | 0 | 1.03 | 0.68 | 0 | 0
2025-03-17 18:00 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 19:00 | 47.51 | 0 | 0 | 47.51 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 20:00 | 46.86 | 0 | 0 | 46.86 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 21:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 22:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0.68 | 0 | 0
2025-03-17 23:00 | 43.32 | 0 | 0 | 43.32 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 01:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 02:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 03:00 | 39.13 | 0 | 0 | 39.13 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 04:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 05:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 06:00 | 40.29 | 0.04 | 0.04 | 40.24 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 07:00 | 42.22 | 0.01 | 0.01 | 42.22 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 08:00 | 43.58 | 41.14 | 41.14 | 2.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 09:00 | 44.78 | 104.28 | 48.18 | 0 | 3.4 | 0 | 3.91 | 56.1 | 0
2025-03-18 10:00 | 45.78 | 109.1 | 48.1 | 0 | 2.33 | 0 | 6.12 | 61 | 0
2025-03-18 11:00 | 47.09 | 99.65 | 47.09 | 0 | 0 | 0 | 6.12 | 52.56 | 0
2025-03-18 12:00 | 48.27 | 100.48 | 48.27 | 0 | 0 | 0 | 6.12 | 52.21 | 0
2025-03-18 13:00 | 49.15 | 61.6 | 49.15 | 0 | 0 | 0 | 6.12 | 12.44 | 0
2025-03-18 14:00 | 49.88 | 25.46 | 25.46 | 21.01 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-18 15:00 | 50.27 | 3.68 | 3.68 | 44.83 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-18 16:00 | 49.43 | 1.98 | 1.98 | 47.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 17:00 | 48.88 | 25.22 | 25.22 | 23.66 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 18:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 19:00 | 47.67 | 0 | 0 | 47.67 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 20:00 | 45.97 | 0 | 0 | 45.97 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 21:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 22:00 | 44.06 | 0 | 0 | 44.06 | 0 | 0 | 0.68 | 0 | 0
2025-03-18 23:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 01:00 | 40.04 | 0 | 0 | 40.04 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 02:00 | 39.93 | 0 | 0 | 39.93 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 03:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 04:00 | 39.87 | 0 | 0 | 39.87 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 05:00 | 40.15 | 0 | 0 | 40.15 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 06:00 | 40.62 | 0 | 0 | 40.62 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 07:00 | 42.57 | 15.79 | 15.79 | 26.78 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 08:00 | 43.5 | 40 | 40 | 3.5 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 09:00 | 45.4 | 48.8 | 48.8 | 0 | 3.39 | 0 | 3.9 | 0 | 0
2025-03-19 10:00 | 46.44 | 80.53 | 48.78 | 0 | 2.33 | 0 | 6.12 | 31.75 | 0
2025-03-19 11:00 | 47.68 | 71.06 | 47.68 | 0 | 0 | 0 | 6.12 | 23.38 | 0
2025-03-19 12:00 | 49.55 | 66.07 | 49.55 | 0 | 0 | 0 | 6.12 | 16.52 | 0
2025-03-19 13:00 | 50.43 | 90.94 | 50.43 | 0 | 0 | 0 | 6.12 | 40.5 | 0
2025-03-19 14:00 | 51.23 | 94.6 | 51.23 | 0 | 0 | 0 | 6.12 | 43.36 | 0
2025-03-19 15:00 | 52.24 | 70.83 | 52.24 | 0 | 0 | 0 | 6.12 | 18.6 | 0
2025-03-19 16:00 | 51.08 | 65.82 | 51.08 | 0 | 0 | 0 | 6.12 | 14.74 | 0
2025-03-19 17:00 | 50.6 | 27.73 | 27.73 | 19.48 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-19 18:00 | 48.89 | 0.33 | 0.33 | 46.8 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-19 19:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 20:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 21:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 22:00 | 43.36 | 0 | 0 | 43.36 | 0 | 0 | 0.68 | 0 | 0
2025-03-19 23:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 01:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 02:00 | 39.88 | 0 | 0 | 39.88 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 03:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 04:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 05:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 06:00 | 41.98 | 0.01 | 0.01 | 41.97 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 07:00 | 42.97 | 21.23 | 21.23 | 21.75 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 08:00 | 43.87 | 44.86 | 44.86 | 0 | 0.99 | 0 | 1.62 | 0 | 0
2025-03-20 09:00 | 44.99 | 70.98 | 48.39 | 0 | 3.4 | 0 | 4.85 | 22.6 | 0
2025-03-20 10:00 | 47.04 | 67.15 | 48.38 | 0 | 1.34 | 0 | 6.12 | 18.77 | 0
2025-03-20 11:00 | 48.96 | 70.78 | 48.96 | 0 | 0 | 0 | 6.12 | 21.82 | 0
2025-03-20 12:00 | 50.94 | 79.82 | 50.94 | 0 | 0 | 0 | 6.12 | 28.88 | 0
2025-03-20 13:00 | 50.91 | 84.15 | 50.91 | 0 | 0 | 0 | 6.12 | 33.24 | 0
2025-03-20 14:00 | 52.07 | 85.22 | 52.07 | 0 | 0 | 0 | 6.12 | 33.15 | 0
2025-03-20 15:00 | 52.69 | 79.71 | 52.69 | 0 | 0 | 0 | 6.12 | 27.02 | 0
2025-03-20 16:00 | 50.92 | 97.17 | 50.92 | 0 | 0 | 0 | 6.12 | 46.25 | 0
2025-03-20 17:00 | 51.95 | 71.64 | 51.95 | 0 | 0 | 0 | 6.12 | 19.69 | 0
2025-03-20 18:00 | 49.77 | 1.24 | 1.24 | 45.13 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-20 19:00 | 49.15 | 0 | 0 | 47.38 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-20 20:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 21:00 | 46.32 | 0 | 0 | 46.32 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 22:00 | 44.45 | 0 | 0 | 44.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-20 23:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 | 41.21 | 0 | 0 | 41.21 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 01:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 02:00 | 40.04 | 0 | 0 | 40.04 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 03:00 | 40.18 | 0 | 0 | 40.18 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 04:00 | 40.53 | 0 | 0 | 40.53 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 05:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 06:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 07:00 | 41.83 | 6.39 | 6.39 | 35.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 08:00 | 43.85 | 17.78 | 17.78 | 26.07 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 09:00 | 45.69 | 39.53 | 39.53 | 6.17 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 10:00 | 46.32 | 39.7 | 39.7 | 6.62 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 11:00 | 48.45 | 50.93 | 50.93 | 0 | 2.48 | 0 | 3.03 | 0 | 0
2025-03-21 12:00 | 49.66 | 49.98 | 49.98 | 0 | 0.32 | 0 | 3.34 | 0 | 0
2025-03-21 13:00 | 50.09 | 34.83 | 34.83 | 12.73 | 0 | 2.53 | 0.68 | 0 | 0
2025-03-21 14:00 | 49 | 23.98 | 23.98 | 25.02 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 15:00 | 50.07 | 12.79 | 12.79 | 37.28 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 16:00 | 51.48 | 9.36 | 9.36 | 42.12 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 17:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 18:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 19:00 | 48.75 | 0 | 0 | 48.75 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 20:00 | 46.87 | 0 | 0 | 46.87 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 21:00 | 46.04 | 0 | 0 | 46.04 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 22:00 | 44.22 | 0 | 0 | 44.22 | 0 | 0 | 0.68 | 0 | 0
2025-03-21 23:00 | 42.98 | 0 | 0 | 42.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 | 41.94 | 0 | 0 | 41.94 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 01:00 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 02:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 03:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 04:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 05:00 | 41.05 | 0 | 0 | 41.05 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 06:00 | 42.33 | 0.13 | 0.13 | 42.2 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 07:00 | 43.6 | 4.36 | 4.36 | 39.24 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 08:00 | 44.25 | 41.83 | 41.83 | 2.41 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 09:00 | 46.65 | 61.56 | 50.05 | 0 | 3.4 | 0 | 3.91 | 11.51 | 0
2025-03-22 10:00 | 48.16 | 56.68 | 50.49 | 0 | 2.33 | 0 | 6.12 | 6.19 | 0
2025-03-22 11:00 | 50.54 | 55.04 | 50.54 | 0 | 0 | 0 | 6.12 | 4.5 | 0
2025-03-22 12:00 | 50.23 | 70.72 | 50.23 | 0 | 0 | 0 | 6.12 | 20.49 | 0
2025-03-22 13:00 | 51.4 | 52.75 | 51.4 | 0 | 0 | 0 | 6.12 | 1.34 | 0
2025-03-22 14:00 | 52.17 | 69.78 | 52.17 | 0 | 0 | 0 | 6.12 | 17.61 | 0
2025-03-22 15:00 | 52.31 | 110.66 | 52.31 | 0 | 0 | 0 | 6.12 | 58.35 | 0
2025-03-22 16:00 | 51.88 | 75.8 | 51.88 | 0 | 0 | 0 | 6.12 | 23.92 | 0
2025-03-22 17:00 | 50.28 | 53.58 | 50.28 | 0 | 0 | 0 | 6.12 | 3.3 | 0
2025-03-22 18:00 | 50.39 | 0.52 | 0.52 | 46.47 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-22 19:00 | 49.44 | 0 | 0 | 47.67 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-22 20:00 | 47.45 | 0 | 0 | 47.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 21:00 | 47.03 | 0 | 0 | 47.03 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 22:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 0.68 | 0 | 0
2025-03-22 23:00 | 43.64 | 0 | 0 | 43.64 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 01:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 02:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 04:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 05:00 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 06:00 | 42.03 | 0.62 | 0.62 | 41.4 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 07:00 | 42.86 | 47.26 | 46.26 | 0 | 3.4 | 0 | 3.91 | 1 | 0
2025-03-23 08:00 | 44.51 | 88.35 | 46.84 | 0 | 2.33 | 0 | 6.12 | 41.51 | 0
2025-03-23 09:00 | 46.78 | 101.35 | 46.78 | 0 | 0 | 0 | 6.12 | 54.56 | 0
2025-03-23 10:00 | 46.84 | 96.08 | 46.84 | 0 | 0 | 0 | 6.12 | 49.24 | 0
2025-03-23 11:00 | 48.37 | 91.41 | 48.37 | 0 | 0 | 0 | 6.12 | 43.04 | 0
2025-03-23 12:00 | 49.77 | 90.52 | 49.77 | 0 | 0 | 0 | 6.12 | 40.76 | 0
2025-03-23 13:00 | 50.44 | 91.85 | 50.44 | 0 | 0 | 0 | 6.12 | 41.41 | 0
2025-03-23 14:00 | 50.33 | 97.14 | 50.33 | 0 | 0 | 0 | 6.12 | 46.81 | 0
2025-03-23 15:00 | 49.28 | 96.71 | 49.28 | 0 | 0 | 0 | 6.12 | 47.43 | 0
2025-03-23 16:00 | 50.58 | 79.24 | 50.58 | 0 | 0 | 0 | 6.12 | 28.66 | 0
2025-03-23 17:00 | 48.76 | 44.7 | 44.7 | 0.66 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-23 18:00 | 49.87 | 0.91 | 0.91 | 47.2 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-23 19:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 20:00 | 47.48 | 0 | 0 | 47.48 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 21:00 | 45.21 | 0 | 0 | 45.21 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 22:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0.68 | 0 | 0
2025-03-23 23:00 | 43.13 | 0 | 0 | 43.13 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 01:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 02:00 | 40.51 | 0 | 0 | 40.51 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 03:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 04:00 | 40.89 | 0 | 0 | 40.89 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 05:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 06:00 | 42.41 | 0.89 | 0.89 | 41.52 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 07:00 | 43.93 | 70.1 | 47.33 | 0 | 3.4 | 0 | 3.91 | 22.77 | 0
2025-03-24 08:00 | 44.47 | 96.17 | 46.79 | 0 | 2.33 | 0 | 6.12 | 49.38 | 0
2025-03-24 09:00 | 44.98 | 6.15 | 6.15 | 35.43 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-24 10:00 | 47.34 | 29.44 | 29.44 | 16.13 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-24 11:00 | 49.14 | 22.52 | 22.52 | 26.62 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 12:00 | 49.35 | 53.96 | 52.75 | 0 | 3.4 | 0 | 3.91 | 1.21 | 0
2025-03-24 13:00 | 50.58 | 107.36 | 52.91 | 0 | 2.33 | 0 | 6.12 | 54.46 | 0
2025-03-24 14:00 | 50.84 | 112.43 | 50.84 | 0 | 0 | 0 | 6.12 | 61.59 | 0
2025-03-24 15:00 | 52.11 | 116.21 | 52.11 | 0 | 0 | 0 | 6.12 | 64.1 | 0
2025-03-24 16:00 | 51.56 | 112.42 | 51.56 | 0 | 0 | 0 | 6.12 | 60.86 | 0
2025-03-24 17:00 | 50.99 | 75.48 | 50.99 | 0 | 0 | 0 | 6.12 | 24.49 | 0
2025-03-24 18:00 | 50.15 | 2.42 | 2.42 | 44.32 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-24 19:00 | 48.72 | 0 | 0 | 46.95 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-24 20:00 | 47.53 | 0 | 0 | 47.53 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 21:00 | 45.42 | 0 | 0 | 45.42 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 22:00 | 43.47 | 0 | 0 | 43.47 | 0 | 0 | 0.68 | 0 | 0
2025-03-24 23:00 | 43.26 | 0 | 0 | 43.26 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 | 42.29 | 0 | 0 | 42.29 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 01:00 | 41.79 | 0 | 0 | 41.79 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 02:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 03:00 | 41.16 | 0 | 0 | 41.16 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 04:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 05:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 06:00 | 42.36 | 0.89 | 0.89 | 41.47 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 07:00 | 44.6 | 56.07 | 48 | 0 | 3.4 | 0 | 3.91 | 8.07 | 0
2025-03-25 08:00 | 45.46 | 81.64 | 47.79 | 0 | 2.33 | 0 | 6.12 | 33.85 | 0
2025-03-25 09:00 | 46.75 | 100.18 | 46.75 | 0 | 0 | 0 | 6.12 | 53.43 | 0
2025-03-25 10:00 | 47.43 | 95.28 | 47.43 | 0 | 0 | 0 | 6.12 | 47.85 | 0
2025-03-25 11:00 | 48.5 | 91.9 | 48.5 | 0 | 0 | 0 | 6.12 | 43.41 | 0
2025-03-25 12:00 | 50.44 | 93.31 | 50.44 | 0 | 0 | 0 | 6.12 | 42.87 | 0
2025-03-25 13:00 | 50.33 | 70.1 | 50.33 | 0 | 0 | 0 | 6.12 | 19.77 | 0
2025-03-25 14:00 | 51.29 | 75.5 | 51.29 | 0 | 0 | 0 | 6.12 | 24.22 | 0
2025-03-25 15:00 | 51.52 | 68.59 | 51.52 | 0 | 0 | 0 | 6.12 | 17.06 | 0
2025-03-25 16:00 | 52.2 | 49.36 | 49.36 | 0 | 0 | 2.84 | 3.13 | 0 | 0
2025-03-25 17:00 | 50.71 | 23.19 | 23.19 | 25.19 | 0 | 2.33 | 0.68 | 0 | 0
2025-03-25 18:00 | 48.83 | 1.04 | 1.04 | 47.78 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 19:00 | 49.19 | 0 | 0 | 49.19 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 20:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 21:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 22:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0.68 | 0 | 0
2025-03-25 23:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 01:00 | 40.53 | 0 | 0 | 40.53 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 02:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 03:00 | 40.83 | 0 | 0 | 40.83 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 04:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 05:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 06:00 | 42.56 | 1.32 | 1.32 | 41.23 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 07:00 | 43.94 | 56.25 | 47.34 | 0 | 3.4 | 0 | 3.91 | 8.92 | 0
2025-03-26 08:00 | 44.63 | 89.86 | 46.95 | 0 | 2.33 | 0 | 6.12 | 42.9 | 0
2025-03-26 09:00 | 44.95 | 100.72 | 44.95 | 0 | 0 | 0 | 6.12 | 55.77 | 0
2025-03-26 10:00 | 47.48 | 99.55 | 47.48 | 0 | 0 | 0 | 6.12 | 52.07 | 0
2025-03-26 11:00 | 47.33 | 95.17 | 47.33 | 0 | 0 | 0 | 6.12 | 47.84 | 0
2025-03-26 12:00 | 49.14 | 91.87 | 49.14 | 0 | 0 | 0 | 6.12 | 42.73 | 0
2025-03-26 13:00 | 49.14 | 95.36 | 49.14 | 0 | 0 | 0 | 6.12 | 46.22 | 0
2025-03-26 14:00 | 49.36 | 97.22 | 49.36 | 0 | 0 | 0 | 6.12 | 47.86 | 0
2025-03-26 15:00 | 49.84 | 100.8 | 49.84 | 0 | 0 | 0 | 6.12 | 50.96 | 0
2025-03-26 16:00 | 49.85 | 90.11 | 49.85 | 0 | 0 | 0 | 6.12 | 40.26 | 0
2025-03-26 17:00 | 49.26 | 59.1 | 49.26 | 0 | 0 | 0 | 6.12 | 9.84 | 0
2025-03-26 18:00 | 49.28 | 1.43 | 1.43 | 44.45 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-26 19:00 | 47.94 | 0 | 0 | 46.17 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-26 20:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 21:00 | 46.07 | 0 | 0 | 46.07 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 22:00 | 44.3 | 0 | 0 | 44.3 | 0 | 0 | 0.68 | 0 | 0
2025-03-26 23:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 01:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 02:00 | 40.64 | 0 | 0 | 40.64 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 03:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 04:00 | 40.55 | 0 | 0 | 40.55 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 05:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 06:00 | 43.22 | 1.32 | 1.32 | 41.91 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 07:00 | 42.91 | 55.68 | 46.31 | 0 | 3.4 | 0 | 3.91 | 9.37 | 0
2025-03-27 08:00 | 44.61 | 93.66 | 46.94 | 0 | 2.33 | 0 | 6.12 | 46.72 | 0
2025-03-27 09:00 | 47.61 | 106.18 | 47.61 | 0 | 0 | 0 | 6.12 | 58.58 | 0
2025-03-27 10:00 | 49.49 | 107.81 | 49.49 | 0 | 0 | 0 | 6.12 | 58.32 | 0
2025-03-27 11:00 | 50.11 | 87.49 | 50.11 | 0 | 0 | 0 | 6.12 | 37.38 | 0
2025-03-27 12:00 | 51.62 | 76.58 | 51.62 | 0 | 0 | 0 | 6.12 | 24.96 | 0
2025-03-27 13:00 | 53.38 | 80.81 | 53.38 | 0 | 0 | 0 | 6.12 | 27.42 | 0
2025-03-27 14:00 | 52.63 | 93.62 | 52.63 | 0 | 0 | 0 | 6.12 | 40.98 | 0
2025-03-27 15:00 | 53.11 | 75.08 | 53.11 | 0 | 0 | 0 | 6.12 | 21.97 | 0
2025-03-27 16:00 | 53.65 | 37.82 | 37.82 | 12.44 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-27 17:00 | 53.85 | 25.65 | 25.65 | 26.43 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-27 18:00 | 51.72 | 1.4 | 1.4 | 50.32 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 19:00 | 50.53 | 0 | 0 | 50.53 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 20:00 | 49.38 | 0 | 0 | 49.38 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 21:00 | 48.11 | 0 | 0 | 48.11 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 22:00 | 45.04 | 0 | 0 | 45.04 | 0 | 0 | 0.68 | 0 | 0
2025-03-27 23:00 | 43.75 | 0 | 0 | 43.75 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 | 43.44 | 0 | 0 | 43.44 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 01:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 02:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 03:00 | 40.21 | 0 | 0 | 40.21 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 04:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 05:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 06:00 | 42.05 | 2.6 | 2.6 | 39.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 07:00 | 43.29 | 79.14 | 46.69 | 0 | 3.4 | 0 | 3.91 | 32.45 | 0
2025-03-28 08:00 | 45.35 | 111.12 | 47.68 | 0 | 2.33 | 0 | 6.12 | 63.44 | 0
2025-03-28 09:00 | 47.21 | 114.7 | 47.21 | 0 | 0 | 0 | 6.12 | 67.49 | 0
2025-03-28 10:00 | 48.12 | 111.79 | 48.12 | 0 | 0 | 0 | 6.12 | 63.67 | 0
2025-03-28 11:00 | 49.55 | 106.32 | 49.55 | 0 | 0 | 0 | 6.12 | 56.77 | 0
2025-03-28 12:00 | 50.92 | 102.67 | 50.92 | 0 | 0 | 0 | 6.12 | 51.75 | 0
2025-03-28 13:00 | 50.99 | 105.08 | 50.99 | 0 | 0 | 0 | 6.12 | 54.08 | 0
2025-03-28 14:00 | 52.37 | 109.65 | 52.37 | 0 | 0 | 0 | 6.12 | 57.28 | 0
2025-03-28 15:00 | 52.59 | 111.58 | 52.59 | 0 | 0 | 0 | 6.12 | 58.99 | 0
2025-03-28 16:00 | 53.3 | 106.52 | 53.3 | 0 | 0 | 0 | 6.12 | 53.22 | 0
2025-03-28 17:00 | 51.29 | 73.15 | 51.29 | 0 | 0 | 0 | 6.12 | 21.86 | 0
2025-03-28 18:00 | 50.4 | 2.01 | 2.01 | 44.99 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-28 19:00 | 49.9 | 0 | 0 | 48.13 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-28 20:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 21:00 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 22:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 0.68 | 0 | 0
2025-03-28 23:00 | 44.05 | 0 | 0 | 44.05 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 01:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 02:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 03:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 04:00 | 40.75 | 0 | 0 | 40.75 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 05:00 | 40.76 | 0 | 0 | 40.76 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 06:00 | 41.73 | 3.26 | 3.26 | 38.47 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 07:00 | 43.38 | 85.91 | 46.78 | 0 | 3.4 | 0 | 3.91 | 39.13 | 0
2025-03-29 08:00 | 44.88 | 114.49 | 47.21 | 0 | 2.33 | 0 | 6.12 | 67.29 | 0
2025-03-29 09:00 | 47.11 | 117.2 | 47.11 | 0 | 0 | 0 | 6.12 | 70.09 | 0
2025-03-29 10:00 | 48.24 | 112.6 | 48.24 | 0 | 0 | 0 | 6.12 | 64.37 | 0
2025-03-29 11:00 | 50.01 | 106.35 | 50.01 | 0 | 0 | 0 | 6.12 | 56.34 | 0
2025-03-29 12:00 | 51.3 | 103.21 | 51.3 | 0 | 0 | 0 | 6.12 | 51.91 | 0
2025-03-29 13:00 | 52.47 | 105.29 | 52.47 | 0 | 0 | 0 | 6.12 | 52.82 | 0
2025-03-29 14:00 | 53.99 | 109.28 | 53.99 | 0 | 0 | 0 | 6.12 | 55.29 | 0
2025-03-29 15:00 | 53.88 | 111.62 | 53.88 | 0 | 0 | 0 | 6.12 | 57.74 | 0
2025-03-29 16:00 | 53.34 | 108.92 | 53.34 | 0 | 0 | 0 | 6.12 | 55.58 | 0
2025-03-29 17:00 | 52.46 | 80.28 | 52.46 | 0 | 0 | 0 | 6.12 | 27.82 | 0
2025-03-29 18:00 | 51.47 | 2.78 | 2.78 | 45.28 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-29 19:00 | 50.53 | 0 | 0 | 48.76 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-29 20:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 21:00 | 46.73 | 0 | 0 | 46.73 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 22:00 | 45.56 | 0 | 0 | 45.56 | 0 | 0 | 0.68 | 0 | 0
2025-03-29 23:00 | 42.99 | 0 | 0 | 42.99 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 01:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 02:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 03:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 04:00 | 40.73 | 0 | 0 | 40.73 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 05:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 06:00 | 42.84 | 4.6 | 4.6 | 38.23 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 07:00 | 44.18 | 85.45 | 47.58 | 0 | 3.4 | 0 | 3.91 | 37.87 | 0
2025-03-30 08:00 | 45.81 | 112.38 | 48.14 | 0 | 2.33 | 0 | 6.12 | 64.24 | 0
2025-03-30 09:00 | 47.71 | 114.91 | 47.71 | 0 | 0 | 0 | 6.12 | 67.2 | 0
2025-03-30 10:00 | 49.91 | 111.14 | 49.91 | 0 | 0 | 0 | 6.12 | 61.24 | 0
2025-03-30 11:00 | 51.9 | 105.13 | 51.9 | 0 | 0 | 0 | 6.12 | 53.22 | 0
2025-03-30 12:00 | 52.73 | 102.74 | 52.73 | 0 | 0 | 0 | 6.12 | 50.01 | 0
2025-03-30 13:00 | 54.32 | 103.79 | 54.32 | 0 | 0 | 0 | 6.12 | 49.47 | 0
2025-03-30 14:00 | 54.31 | 107.48 | 54.31 | 0 | 0 | 0 | 6.12 | 53.17 | 0
2025-03-30 15:00 | 55.3 | 110.5 | 55.3 | 0 | 0 | 0 | 6.12 | 55.2 | 0
2025-03-30 16:00 | 54.28 | 104.55 | 54.28 | 0 | 0 | 0 | 6.12 | 50.27 | 0
2025-03-30 17:00 | 54.46 | 75.48 | 54.46 | 0 | 0 | 0 | 6.12 | 21.02 | 0
2025-03-30 18:00 | 53.84 | 3.03 | 3.03 | 47.41 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-30 19:00 | 51.16 | 0 | 0 | 49.39 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-30 20:00 | 48.38 | 0 | 0 | 48.38 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 21:00 | 47.38 | 0 | 0 | 47.38 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 22:00 | 46.48 | 0 | 0 | 46.48 | 0 | 0 | 0.68 | 0 | 0
2025-03-30 23:00 | 44.51 | 0 | 0 | 44.51 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 01:00 | 42.45 | 0 | 0 | 42.45 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 02:00 | 41.53 | 0 | 0 | 41.53 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 03:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 04:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 05:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 06:00 | 43.18 | 4.54 | 4.54 | 38.63 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 07:00 | 44.84 | 88.76 | 48.24 | 0 | 3.4 | 0 | 3.91 | 40.52 | 0
2025-03-31 08:00 | 45.88 | 113.26 | 48.21 | 0 | 2.33 | 0 | 6.12 | 65.06 | 0
2025-03-31 09:00 | 47.54 | 115.56 | 47.54 | 0 | 0 | 0 | 6.12 | 68.02 | 0
2025-03-31 10:00 | 50.53 | 112.89 | 50.53 | 0 | 0 | 0 | 6.12 | 62.36 | 0
2025-03-31 11:00 | 51.53 | 107.98 | 51.53 | 0 | 0 | 0 | 6.12 | 56.45 | 0
2025-03-31 12:00 | 53.35 | 104.82 | 53.35 | 0 | 0 | 0 | 6.12 | 51.47 | 0
2025-03-31 13:00 | 54.19 | 106.99 | 54.19 | 0 | 0 | 0 | 6.12 | 52.8 | 0
2025-03-31 14:00 | 54.59 | 111.66 | 54.59 | 0 | 0 | 0 | 6.12 | 57.07 | 0
2025-03-31 15:00 | 55.14 | 114.66 | 55.14 | 0 | 0 | 0 | 6.12 | 59.52 | 0
2025-03-31 16:00 | 55.6 | 112.13 | 55.6 | 0 | 0 | 0 | 6.12 | 56.54 | 0
2025-03-31 17:00 | 54.41 | 85.18 | 54.41 | 0 | 0 | 0 | 6.12 | 30.77 | 0
2025-03-31 18:00 | 52.09 | 4.07 | 4.07 | 44.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-03-31 19:00 | 51.32 | 0 | 0 | 49.55 | 0 | 1.77 | 0.68 | 0 | 0
2025-03-31 20:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 21:00 | 47.73 | 0 | 0 | 47.73 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 22:00 | 45.14 | 0 | 0 | 45.14 | 0 | 0 | 0.68 | 0 | 0
2025-03-31 23:00 | 45.34 | 0 | 0 | 45.34 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 | 43.49 | 0 | 0 | 43.49 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 01:00 | 42.04 | 0 | 0 | 42.04 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 02:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 03:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 04:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 05:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 06:00 | 43.42 | 3.11 | 3.11 | 40.31 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 07:00 | 44.7 | 12.61 | 12.61 | 32.09 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 08:00 | 46.36 | 49.59 | 49.59 | 0 | 3.23 | 0 | 3.74 | 0 | 0
2025-04-01 09:00 | 48.09 | 55.41 | 50.59 | 0 | 2.5 | 0 | 6.12 | 4.82 | 0
2025-04-01 10:00 | 50.64 | 52.99 | 50.64 | 0 | 0 | 0 | 6.12 | 2.35 | 0
2025-04-01 11:00 | 51.54 | 70.33 | 51.54 | 0 | 0 | 0 | 6.12 | 18.79 | 0
2025-04-01 12:00 | 52.79 | 34.85 | 34.85 | 14.54 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-01 13:00 | 55.18 | 68.41 | 58.58 | 0 | 3.4 | 0 | 5.77 | 9.83 | 0
2025-04-01 14:00 | 56 | 34.98 | 34.98 | 17.61 | 0 | 3.4 | 2.19 | 0 | 0
2025-04-01 15:00 | 56.2 | 49.87 | 49.87 | 4.9 | 0 | 1.44 | 0.68 | 0 | 0
2025-04-01 16:00 | 55.88 | 19.1 | 19.1 | 36.78 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 17:00 | 54.71 | 4.46 | 4.46 | 50.25 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 18:00 | 53.99 | 0 | 0 | 53.99 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 19:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 20:00 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 21:00 | 48.02 | 0 | 0 | 48.02 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 22:00 | 47.3 | 0 | 0 | 47.3 | 0 | 0 | 0.68 | 0 | 0
2025-04-01 23:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 | 43.51 | 0 | 0 | 43.51 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 01:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 02:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 03:00 | 41.09 | 0 | 0 | 41.09 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 04:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 05:00 | 42.39 | 0 | 0 | 42.39 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 06:00 | 43.07 | 0.52 | 0.52 | 42.55 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 07:00 | 43.58 | 4.07 | 4.07 | 39.51 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 08:00 | 46.64 | 9.3 | 9.3 | 37.34 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 09:00 | 48.64 | 14.88 | 14.88 | 33.76 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 10:00 | 50.37 | 23.3 | 23.3 | 27.06 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 11:00 | 51.37 | 26.41 | 26.41 | 24.96 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 12:00 | 52.56 | 25.56 | 25.56 | 27 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 13:00 | 54.23 | 21.26 | 21.26 | 32.97 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 14:00 | 55.05 | 19.85 | 19.85 | 35.2 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 15:00 | 55 | 17.83 | 17.83 | 37.17 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 16:00 | 53.74 | 11.22 | 11.22 | 42.53 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 17:00 | 53.67 | 5.12 | 5.12 | 48.55 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 18:00 | 52.76 | 0.27 | 0.27 | 52.49 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 19:00 | 50.29 | 0 | 0 | 50.29 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 20:00 | 49.86 | 0 | 0 | 49.86 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 21:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 22:00 | 46.54 | 0 | 0 | 46.54 | 0 | 0 | 0.68 | 0 | 0
2025-04-02 23:00 | 45.37 | 0 | 0 | 45.37 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 01:00 | 42.29 | 0 | 0 | 42.29 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 02:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 03:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 04:00 | 41.17 | 0 | 0 | 41.17 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 05:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 06:00 | 44.07 | 1.17 | 1.17 | 42.9 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 07:00 | 44.25 | 6.13 | 6.13 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 08:00 | 46.78 | 16.34 | 16.34 | 30.44 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 09:00 | 47.89 | 19.67 | 19.67 | 28.22 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 10:00 | 49.71 | 26.73 | 26.73 | 22.97 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 11:00 | 51.23 | 21.46 | 21.46 | 29.77 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 12:00 | 52.72 | 28.87 | 28.87 | 23.85 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 13:00 | 53.2 | 32.61 | 32.61 | 20.59 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 14:00 | 54.44 | 28.94 | 28.94 | 25.5 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 15:00 | 54.09 | 25.94 | 25.94 | 28.14 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 16:00 | 54.05 | 14.72 | 14.72 | 39.33 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 17:00 | 52.74 | 4.65 | 4.65 | 48.09 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 18:00 | 53.31 | 0.27 | 0.27 | 53.04 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 19:00 | 51.23 | 0 | 0 | 51.23 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 20:00 | 49.89 | 0 | 0 | 49.89 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 21:00 | 47.13 | 0 | 0 | 47.13 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 22:00 | 45.89 | 0 | 0 | 45.89 | 0 | 0 | 0.68 | 0 | 0
2025-04-03 23:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 01:00 | 41.5 | 0 | 0 | 41.5 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 02:00 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 03:00 | 41.27 | 0 | 0 | 41.27 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 04:00 | 42.48 | 0 | 0 | 42.48 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 05:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 06:00 | 43.65 | 9.78 | 9.78 | 33.87 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 07:00 | 45.55 | 102.33 | 48.95 | 0 | 3.4 | 0 | 3.91 | 53.38 | 0
2025-04-04 08:00 | 46.15 | 124.05 | 48.48 | 0 | 2.33 | 0 | 6.12 | 75.57 | 0
2025-04-04 09:00 | 47.86 | 121.2 | 47.86 | 0 | 0 | 0 | 6.12 | 73.34 | 0
2025-04-04 10:00 | 50 | 123.82 | 50 | 0 | 0 | 0 | 6.12 | 73.83 | 0
2025-04-04 11:00 | 52.13 | 88.13 | 52.13 | 0 | 0 | 0 | 6.12 | 36 | 0
2025-04-04 12:00 | 52.44 | 52.44 | 52.44 | 0 | 0 | 0 | 6.12 | 0 | 0
2025-04-04 13:00 | 53.33 | 22.17 | 22.17 | 27.76 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-04 14:00 | 55.24 | 36.57 | 36.57 | 16.91 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-04 15:00 | 54.76 | 28.49 | 28.49 | 26.27 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 16:00 | 54.64 | 30.1 | 30.1 | 24.54 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 17:00 | 53.24 | 12.32 | 12.32 | 40.92 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 18:00 | 52.77 | 5.39 | 5.39 | 47.38 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 19:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 20:00 | 50.56 | 0 | 0 | 50.56 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 21:00 | 47.97 | 0 | 0 | 47.97 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 22:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0.68 | 0 | 0
2025-04-04 23:00 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 01:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 02:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 03:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 04:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 05:00 | 43.25 | 0 | 0 | 43.25 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 06:00 | 44.34 | 3.66 | 3.66 | 40.68 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 07:00 | 44.47 | 69.96 | 47.87 | 0 | 3.4 | 0 | 3.91 | 22.1 | 0
2025-04-05 08:00 | 46.21 | 93.95 | 48.54 | 0 | 2.33 | 0 | 6.12 | 45.41 | 0
2025-04-05 09:00 | 47.6 | 49.3 | 47.6 | 0 | 0 | 0 | 6.12 | 1.7 | 0
2025-04-05 10:00 | 48.24 | 73.96 | 48.24 | 0 | 0 | 0 | 6.12 | 25.72 | 0
2025-04-05 11:00 | 49.68 | 87.07 | 49.68 | 0 | 0 | 0 | 6.12 | 37.39 | 0
2025-04-05 12:00 | 50.45 | 56.86 | 50.45 | 0 | 0 | 0 | 6.12 | 6.41 | 0
2025-04-05 13:00 | 51.52 | 49.81 | 49.81 | 0 | 0 | 1.71 | 4.32 | 0 | 0
2025-04-05 14:00 | 51.84 | 18.98 | 18.98 | 29.46 | 0 | 3.4 | 0.74 | 0 | 0
2025-04-05 15:00 | 51.17 | 53.64 | 53.64 | 0 | 2.47 | 0 | 3.08 | 0 | 0
2025-04-05 16:00 | 51.13 | 82.27 | 54.33 | 0 | 3.2 | 0 | 6.12 | 27.94 | 0
2025-04-05 17:00 | 51.28 | 61.51 | 51.28 | 0 | 0 | 0 | 6.12 | 10.22 | 0
2025-04-05 18:00 | 50.15 | 4.54 | 4.54 | 42.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-05 19:00 | 50 | 0 | 0 | 48.24 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-05 20:00 | 48.69 | 0 | 0 | 48.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 21:00 | 47.07 | 0 | 0 | 47.07 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 22:00 | 45.75 | 0 | 0 | 45.75 | 0 | 0 | 0.68 | 0 | 0
2025-04-05 23:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 01:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 02:00 | 41.77 | 0 | 0 | 41.77 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 03:00 | 41.93 | 0 | 0 | 41.93 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 04:00 | 43.22 | 0 | 0 | 43.22 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 05:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 06:00 | 42.82 | 4.61 | 4.61 | 38.21 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 07:00 | 45.72 | 20.71 | 20.71 | 25.01 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 08:00 | 46.08 | 50.81 | 49.48 | 0 | 3.4 | 0 | 3.91 | 1.33 | 0
2025-04-06 09:00 | 47.89 | 57.76 | 50.22 | 0 | 2.33 | 0 | 6.12 | 7.54 | 0
2025-04-06 10:00 | 48.9 | 64.28 | 48.9 | 0 | 0 | 0 | 6.12 | 15.38 | 0
2025-04-06 11:00 | 50.41 | 67.98 | 50.41 | 0 | 0 | 0 | 6.12 | 17.57 | 0
2025-04-06 12:00 | 50.65 | 49.64 | 49.64 | 0 | 0 | 1.01 | 5.06 | 0 | 0
2025-04-06 13:00 | 51.63 | 48.22 | 48.22 | 0.02 | 0 | 3.4 | 1.48 | 0 | 0
2025-04-06 14:00 | 52.3 | 47.36 | 47.36 | 4.17 | 0 | 0.76 | 0.68 | 0 | 0
2025-04-06 15:00 | 51.68 | 100.98 | 55.08 | 0 | 3.4 | 0 | 3.91 | 45.9 | 0
2025-04-06 16:00 | 51.72 | 78.76 | 54.05 | 0 | 2.33 | 0 | 6.12 | 24.72 | 0
2025-04-06 17:00 | 51.55 | 79.15 | 51.55 | 0 | 0 | 0 | 6.12 | 27.6 | 0
2025-04-06 18:00 | 50.41 | 11.1 | 11.1 | 35.91 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-06 19:00 | 50.06 | 0 | 0 | 48.3 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-06 20:00 | 49.25 | 0 | 0 | 49.25 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 21:00 | 47.7 | 0 | 0 | 47.7 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 22:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 0.68 | 0 | 0
2025-04-06 23:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 01:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 02:00 | 42.87 | 0 | 0 | 42.87 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 03:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 04:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 05:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 06:00 | 44.11 | 3.28 | 3.28 | 40.82 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 07:00 | 46.04 | 17.34 | 17.34 | 28.7 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 08:00 | 46.98 | 39.72 | 39.72 | 7.26 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 09:00 | 47.3 | 13.38 | 13.38 | 33.91 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 10:00 | 49.76 | 14.62 | 14.62 | 35.14 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 11:00 | 51.3 | 44.81 | 44.81 | 6.49 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 12:00 | 51.48 | 56.77 | 54.88 | 0 | 3.4 | 0 | 3.91 | 1.88 | 0
2025-04-07 13:00 | 52.74 | 99.85 | 55.07 | 0 | 2.33 | 0 | 6.12 | 44.78 | 0
2025-04-07 14:00 | 52.29 | 114.26 | 52.29 | 0 | 0 | 0 | 6.12 | 61.97 | 0
2025-04-07 15:00 | 52.02 | 52.45 | 52.02 | 0 | 0 | 0 | 6.12 | 0.44 | 0
2025-04-07 16:00 | 52.7 | 103.3 | 52.7 | 0 | 0 | 0 | 6.12 | 50.6 | 0
2025-04-07 17:00 | 51.37 | 76.92 | 51.37 | 0 | 0 | 0 | 6.12 | 25.55 | 0
2025-04-07 18:00 | 51.48 | 6.85 | 6.85 | 41.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-07 19:00 | 51.33 | 0 | 0 | 49.56 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-07 20:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 21:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 22:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 0.68 | 0 | 0
2025-04-07 23:00 | 45.23 | 0 | 0 | 45.23 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 01:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 02:00 | 42.76 | 0 | 0 | 42.76 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 03:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 04:00 | 42.35 | 0 | 0 | 42.35 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 05:00 | 43.18 | 0 | 0 | 43.18 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 06:00 | 43.66 | 14.91 | 14.91 | 28.74 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 07:00 | 45.91 | 74.11 | 49.31 | 0 | 3.4 | 0 | 3.91 | 24.8 | 0
2025-04-08 08:00 | 46.47 | 96.98 | 48.79 | 0 | 2.33 | 0 | 6.12 | 48.18 | 0
2025-04-08 09:00 | 49.01 | 105.24 | 49.01 | 0 | 0 | 0 | 6.12 | 56.23 | 0
2025-04-08 10:00 | 50.68 | 101.39 | 50.68 | 0 | 0 | 0 | 6.12 | 50.72 | 0
2025-04-08 11:00 | 51.5 | 102.42 | 51.5 | 0 | 0 | 0 | 6.12 | 50.92 | 0
2025-04-08 12:00 | 52.37 | 102.53 | 52.37 | 0 | 0 | 0 | 6.12 | 50.16 | 0
2025-04-08 13:00 | 53.43 | 98.12 | 53.43 | 0 | 0 | 0 | 6.12 | 44.68 | 0
2025-04-08 14:00 | 52.28 | 96.16 | 52.28 | 0 | 0 | 0 | 6.12 | 43.88 | 0
2025-04-08 15:00 | 54.02 | 101.12 | 54.02 | 0 | 0 | 0 | 6.12 | 47.11 | 0
2025-04-08 16:00 | 53.65 | 92.8 | 53.65 | 0 | 0 | 0 | 6.12 | 39.15 | 0
2025-04-08 17:00 | 53.21 | 64.85 | 53.21 | 0 | 0 | 0 | 6.12 | 11.64 | 0
2025-04-08 18:00 | 52.81 | 10.05 | 10.05 | 39.36 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-08 19:00 | 51.36 | 0 | 0 | 49.59 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-08 20:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 21:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 22:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 0.68 | 0 | 0
2025-04-08 23:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 | 44.4 | 0 | 0 | 44.4 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 01:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 02:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 03:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 04:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 05:00 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 06:00 | 44.41 | 18.68 | 18.68 | 25.73 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 07:00 | 45.58 | 81.76 | 48.98 | 0 | 3.4 | 0 | 3.91 | 32.78 | 0
2025-04-09 08:00 | 47.53 | 92.74 | 49.85 | 0 | 2.33 | 0 | 6.12 | 42.89 | 0
2025-04-09 09:00 | 49.27 | 100.13 | 49.27 | 0 | 0 | 0 | 6.12 | 50.86 | 0
2025-04-09 10:00 | 51.68 | 98.85 | 51.68 | 0 | 0 | 0 | 6.12 | 47.17 | 0
2025-04-09 11:00 | 54.62 | 97.36 | 54.62 | 0 | 0 | 0 | 6.12 | 42.75 | 0
2025-04-09 12:00 | 54.75 | 98.62 | 54.75 | 0 | 0 | 0 | 6.12 | 43.87 | 0
2025-04-09 13:00 | 56.11 | 98.85 | 56.11 | 0 | 0 | 0 | 6.12 | 42.74 | 0
2025-04-09 14:00 | 56.87 | 103.87 | 56.87 | 0 | 0 | 0 | 6.12 | 47 | 0
2025-04-09 15:00 | 58.67 | 103.3 | 58.67 | 0 | 0 | 0 | 6.12 | 44.63 | 0
2025-04-09 16:00 | 57.29 | 95.73 | 57.29 | 0 | 0 | 0 | 6.12 | 38.44 | 0
2025-04-09 17:00 | 56.68 | 78.52 | 56.68 | 0 | 0 | 0 | 6.12 | 21.84 | 0
2025-04-09 18:00 | 55.18 | 11.82 | 11.82 | 39.96 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-09 19:00 | 53.23 | 0 | 0 | 51.46 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-09 20:00 | 51.64 | 0 | 0 | 51.64 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 21:00 | 50.95 | 0 | 0 | 50.95 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 22:00 | 48.41 | 0 | 0 | 48.41 | 0 | 0 | 0.68 | 0 | 0
2025-04-09 23:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 | 44.72 | 0 | 0 | 44.72 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 01:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 02:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 03:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 04:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 05:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 06:00 | 44.16 | 4.4 | 4.4 | 39.76 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 07:00 | 45.74 | 1.1 | 1.1 | 44.64 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 08:00 | 47.8 | 3.89 | 3.89 | 43.92 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 09:00 | 49.27 | 25.95 | 25.95 | 23.31 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 10:00 | 50.43 | 110.24 | 53.83 | 0 | 3.4 | 0 | 3.91 | 56.41 | 0
2025-04-10 11:00 | 51.2 | 115.78 | 53.53 | 0 | 2.33 | 0 | 6.12 | 62.25 | 0
2025-04-10 12:00 | 53.2 | 112.86 | 53.2 | 0 | 0 | 0 | 6.12 | 59.66 | 0
2025-04-10 13:00 | 54.51 | 72.39 | 54.51 | 0 | 0 | 0 | 6.12 | 17.88 | 0
2025-04-10 14:00 | 53.88 | 56.82 | 53.88 | 0 | 0 | 0 | 6.12 | 2.94 | 0
2025-04-10 15:00 | 54.97 | 117.8 | 54.97 | 0 | 0 | 0 | 6.12 | 62.82 | 0
2025-04-10 16:00 | 54.65 | 84.24 | 54.65 | 0 | 0 | 0 | 6.12 | 29.59 | 0
2025-04-10 17:00 | 54.35 | 88.71 | 54.35 | 0 | 0 | 0 | 6.12 | 34.36 | 0
2025-04-10 18:00 | 53.58 | 16.08 | 16.08 | 34.1 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-10 19:00 | 51.66 | 0 | 0 | 49.9 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-10 20:00 | 49.82 | 0 | 0 | 49.82 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 21:00 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 22:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0.68 | 0 | 0
2025-04-10 23:00 | 45.56 | 0 | 0 | 45.56 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 01:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 02:00 | 43.54 | 0 | 0 | 43.54 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 03:00 | 42.82 | 0 | 0 | 42.82 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 04:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 05:00 | 43.89 | 0 | 0 | 43.89 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 06:00 | 44.86 | 24.54 | 24.54 | 20.33 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 07:00 | 45.96 | 79.42 | 49.36 | 0 | 3.4 | 0 | 3.91 | 30.06 | 0
2025-04-11 08:00 | 47.73 | 105.97 | 50.06 | 0 | 2.33 | 0 | 6.12 | 55.91 | 0
2025-04-11 09:00 | 49.42 | 115.39 | 49.42 | 0 | 0 | 0 | 6.12 | 65.97 | 0
2025-04-11 10:00 | 52.74 | 101.85 | 52.74 | 0 | 0 | 0 | 6.12 | 49.11 | 0
2025-04-11 11:00 | 53.33 | 77.36 | 53.33 | 0 | 0 | 0 | 6.12 | 24.03 | 0
2025-04-11 12:00 | 54.2 | 82.59 | 54.2 | 0 | 0 | 0 | 6.12 | 28.39 | 0
2025-04-11 13:00 | 55.71 | 97.07 | 55.71 | 0 | 0 | 0 | 6.12 | 41.36 | 0
2025-04-11 14:00 | 55.62 | 80.71 | 55.62 | 0 | 0 | 0 | 6.12 | 25.08 | 0
2025-04-11 15:00 | 57.1 | 75.14 | 57.1 | 0 | 0 | 0 | 6.12 | 18.04 | 0
2025-04-11 16:00 | 55.8 | 56.58 | 55.8 | 0 | 0 | 0 | 6.12 | 0.79 | 0
2025-04-11 17:00 | 55.73 | 59.13 | 55.73 | 0 | 0 | 0 | 6.12 | 3.4 | 0
2025-04-11 18:00 | 54.97 | 11.73 | 11.73 | 39.84 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-11 19:00 | 53.25 | 0 | 0 | 51.48 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-11 20:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 21:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 22:00 | 47.78 | 0 | 0 | 47.78 | 0 | 0 | 0.68 | 0 | 0
2025-04-11 23:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 01:00 | 44.3 | 0 | 0 | 44.3 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 02:00 | 42.74 | 0 | 0 | 42.74 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 03:00 | 42.14 | 0 | 0 | 42.14 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 04:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 05:00 | 44.11 | 0 | 0 | 44.11 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 06:00 | 45.16 | 20.01 | 20.01 | 25.16 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 07:00 | 46.82 | 75.02 | 50.22 | 0 | 3.4 | 0 | 3.91 | 24.8 | 0
2025-04-12 08:00 | 48.5 | 119.78 | 50.83 | 0 | 2.33 | 0 | 6.12 | 68.95 | 0
2025-04-12 09:00 | 51.28 | 124.64 | 51.28 | 0 | 0 | 0 | 6.12 | 73.36 | 0
2025-04-12 10:00 | 53.14 | 122.32 | 53.14 | 0 | 0 | 0 | 6.12 | 69.17 | 0
2025-04-12 11:00 | 55.75 | 118.16 | 55.75 | 0 | 0 | 0 | 6.12 | 62.4 | 0
2025-04-12 12:00 | 58.52 | 115.65 | 58.52 | 0 | 0 | 0 | 6.12 | 57.13 | 0
2025-04-12 13:00 | 60.18 | 7.21 | 7.21 | 49.57 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-12 14:00 | 60.35 | 53.97 | 53.97 | 4.6 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-12 15:00 | 60.79 | 98.2 | 64.19 | 0 | 3.4 | 0 | 3.91 | 34.01 | 0
2025-04-12 16:00 | 60.89 | 118.28 | 63.22 | 0 | 2.33 | 0 | 6.12 | 55.06 | 0
2025-04-12 17:00 | 60.61 | 99.43 | 60.61 | 0 | 0 | 0 | 6.12 | 38.83 | 0
2025-04-12 18:00 | 57.08 | 20.2 | 20.2 | 33.48 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-12 19:00 | 56.02 | 0 | 0 | 54.25 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-12 20:00 | 52.78 | 0 | 0 | 52.78 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 21:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 22:00 | 48.45 | 0 | 0 | 48.45 | 0 | 0 | 0.68 | 0 | 0
2025-04-12 23:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 01:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 02:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 03:00 | 41.93 | 0 | 0 | 41.93 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 04:00 | 43.31 | 0 | 0 | 43.31 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 05:00 | 44.06 | 0 | 0 | 44.06 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 06:00 | 45.3 | 30.47 | 30.47 | 14.84 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 07:00 | 45.66 | 91.46 | 49.06 | 0 | 3.4 | 0 | 3.91 | 42.4 | 0
2025-04-13 08:00 | 48.35 | 108.65 | 50.68 | 0 | 2.33 | 0 | 6.12 | 57.97 | 0
2025-04-13 09:00 | 50.41 | 111.39 | 50.41 | 0 | 0 | 0 | 6.12 | 60.98 | 0
2025-04-13 10:00 | 51.4 | 108.26 | 51.4 | 0 | 0 | 0 | 6.12 | 56.86 | 0
2025-04-13 11:00 | 53.6 | 104.16 | 53.6 | 0 | 0 | 0 | 6.12 | 50.56 | 0
2025-04-13 12:00 | 54.97 | 104.1 | 54.97 | 0 | 0 | 0 | 6.12 | 49.13 | 0
2025-04-13 13:00 | 57.02 | 109 | 57.02 | 0 | 0 | 0 | 6.12 | 51.98 | 0
2025-04-13 14:00 | 57.73 | 112.54 | 57.73 | 0 | 0 | 0 | 6.12 | 54.8 | 0
2025-04-13 15:00 | 56.17 | 112.52 | 56.17 | 0 | 0 | 0 | 6.12 | 56.35 | 0
2025-04-13 16:00 | 58.02 | 109.05 | 58.02 | 0 | 0 | 0 | 6.12 | 51.03 | 0
2025-04-13 17:00 | 55.64 | 91.81 | 55.64 | 0 | 0 | 0 | 6.12 | 36.16 | 0
2025-04-13 18:00 | 55.51 | 18.04 | 18.04 | 34.07 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-13 19:00 | 54.09 | 0 | 0 | 52.32 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-13 20:00 | 51.42 | 0 | 0 | 51.42 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 21:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 22:00 | 48.15 | 0 | 0 | 48.15 | 0 | 0 | 0.68 | 0 | 0
2025-04-13 23:00 | 46.71 | 0 | 0 | 46.71 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 | 45.22 | 0 | 0 | 45.22 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 01:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 02:00 | 43.09 | 0 | 0 | 43.09 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 03:00 | 42.7 | 0 | 0 | 42.7 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 04:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 05:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 06:00 | 45.47 | 16.71 | 16.71 | 28.75 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 07:00 | 46.46 | 66.96 | 49.86 | 0 | 3.4 | 0 | 3.91 | 17.1 | 0
2025-04-14 08:00 | 48.29 | 82.55 | 50.62 | 0 | 2.33 | 0 | 6.12 | 31.93 | 0
2025-04-14 09:00 | 50.77 | 98.27 | 50.77 | 0 | 0 | 0 | 6.12 | 47.5 | 0
2025-04-14 10:00 | 53.05 | 105.36 | 53.05 | 0 | 0 | 0 | 6.12 | 52.31 | 0
2025-04-14 11:00 | 55.97 | 99.99 | 55.97 | 0 | 0 | 0 | 6.12 | 44.02 | 0
2025-04-14 12:00 | 58.01 | 96.77 | 58.01 | 0 | 0 | 0 | 6.12 | 38.76 | 0
2025-04-14 13:00 | 58.97 | 96.48 | 58.97 | 0 | 0 | 0 | 6.12 | 37.51 | 0
2025-04-14 14:00 | 60.73 | 80.36 | 60.73 | 0 | 0 | 0 | 6.12 | 19.63 | 0
2025-04-14 15:00 | 61.04 | 88.06 | 61.04 | 0 | 0 | 0 | 6.12 | 27.02 | 0
2025-04-14 16:00 | 60.14 | 63.55 | 60.14 | 0 | 0 | 0 | 6.12 | 3.41 | 0
2025-04-14 17:00 | 58.64 | 74.27 | 58.64 | 0 | 0 | 0 | 6.12 | 15.64 | 0
2025-04-14 18:00 | 58.31 | 17.53 | 17.53 | 37.38 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-14 19:00 | 55.54 | 0 | 0 | 53.78 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-14 20:00 | 53.42 | 0 | 0 | 53.42 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 21:00 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 22:00 | 48.37 | 0 | 0 | 48.37 | 0 | 0 | 0.68 | 0 | 0
2025-04-14 23:00 | 46.06 | 0 | 0 | 46.06 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 01:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 02:00 | 44.71 | 0 | 0 | 44.71 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 03:00 | 42.37 | 0 | 0 | 42.37 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 04:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 05:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 06:00 | 45.92 | 32.3 | 32.3 | 13.62 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 07:00 | 46.7 | 82.6 | 50.1 | 0 | 3.4 | 0 | 3.91 | 32.49 | 0
2025-04-15 08:00 | 48.65 | 97.7 | 50.98 | 0 | 2.33 | 0 | 6.12 | 46.72 | 0
2025-04-15 09:00 | 49.18 | 104.08 | 49.18 | 0 | 0 | 0 | 6.12 | 54.9 | 0
2025-04-15 10:00 | 51.41 | 101.77 | 51.41 | 0 | 0 | 0 | 6.12 | 50.36 | 0
2025-04-15 11:00 | 52.66 | 99.76 | 52.66 | 0 | 0 | 0 | 6.12 | 47.1 | 0
2025-04-15 12:00 | 53.44 | 100.93 | 53.44 | 0 | 0 | 0 | 6.12 | 47.49 | 0
2025-04-15 13:00 | 55.32 | 104.05 | 55.32 | 0 | 0 | 0 | 6.12 | 48.73 | 0
2025-04-15 14:00 | 54.67 | 106.25 | 54.67 | 0 | 0 | 0 | 6.12 | 51.59 | 0
2025-04-15 15:00 | 55.31 | 104.12 | 55.31 | 0 | 0 | 0 | 6.12 | 48.81 | 0
2025-04-15 16:00 | 55.52 | 100.34 | 55.52 | 0 | 0 | 0 | 6.12 | 44.81 | 0
2025-04-15 17:00 | 54.84 | 85.95 | 54.84 | 0 | 0 | 0 | 6.12 | 31.11 | 0
2025-04-15 18:00 | 54.58 | 19.53 | 19.53 | 31.65 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-15 19:00 | 53.35 | 0 | 0 | 51.58 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-15 20:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 21:00 | 50.48 | 0 | 0 | 50.48 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 22:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0.68 | 0 | 0
2025-04-15 23:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 01:00 | 44.36 | 0 | 0 | 44.36 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 02:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 03:00 | 42.84 | 0 | 0 | 42.84 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 04:00 | 43.14 | 0 | 0 | 43.14 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 05:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 06:00 | 45.56 | 9.12 | 9.12 | 36.44 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 07:00 | 46.93 | 19.7 | 19.7 | 27.22 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 08:00 | 48.51 | 30.65 | 30.65 | 17.86 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 09:00 | 50.5 | 53.51 | 53.51 | 0 | 3.01 | 0 | 3.54 | 0 | 0
2025-04-16 10:00 | 52.2 | 58.5 | 54.91 | 0 | 2.71 | 0 | 6.12 | 3.59 | 0
2025-04-16 11:00 | 55.11 | 54.2 | 54.2 | 0 | 0 | 0.91 | 5.17 | 0 | 0
2025-04-16 12:00 | 56.2 | 42.96 | 42.96 | 9.84 | 0 | 3.4 | 1.59 | 0 | 0
2025-04-16 13:00 | 56.91 | 48.5 | 48.5 | 7.55 | 0 | 0.86 | 0.68 | 0 | 0
2025-04-16 14:00 | 58.48 | 46.21 | 46.21 | 12.27 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 15:00 | 58.05 | 32.68 | 32.68 | 25.37 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 16:00 | 57.38 | 17.82 | 17.82 | 39.55 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 17:00 | 57.85 | 7.45 | 7.45 | 50.4 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 18:00 | 55.9 | 0 | 0 | 55.9 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 19:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 20:00 | 52.82 | 0 | 0 | 52.82 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 21:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 22:00 | 48.85 | 0 | 0 | 48.85 | 0 | 0 | 0.68 | 0 | 0
2025-04-16 23:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 | 45.73 | 0 | 0 | 45.73 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 01:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 02:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 03:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 04:00 | 42.32 | 0 | 0 | 42.32 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 05:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 06:00 | 46.43 | 45.29 | 45.29 | 1.15 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 07:00 | 47.8 | 109.23 | 51.2 | 0 | 3.4 | 0 | 3.91 | 58.03 | 0
2025-04-17 08:00 | 49.66 | 121.48 | 51.98 | 0 | 2.33 | 0 | 6.12 | 69.5 | 0
2025-04-17 09:00 | 50 | 122.78 | 50 | 0 | 0 | 0 | 6.12 | 72.77 | 0
2025-04-17 10:00 | 52.64 | 120.02 | 52.64 | 0 | 0 | 0 | 6.12 | 67.37 | 0
2025-04-17 11:00 | 53.31 | 115.97 | 53.31 | 0 | 0 | 0 | 6.12 | 62.66 | 0
2025-04-17 12:00 | 54.99 | 113.86 | 54.99 | 0 | 0 | 0 | 6.12 | 58.87 | 0
2025-04-17 13:00 | 55.12 | 116.57 | 55.12 | 0 | 0 | 0 | 6.12 | 61.45 | 0
2025-04-17 14:00 | 55.98 | 119.92 | 55.98 | 0 | 0 | 0 | 6.12 | 63.94 | 0
2025-04-17 15:00 | 56.14 | 122.41 | 56.14 | 0 | 0 | 0 | 6.12 | 66.26 | 0
2025-04-17 16:00 | 56.75 | 119.24 | 56.75 | 0 | 0 | 0 | 6.12 | 62.49 | 0
2025-04-17 17:00 | 56.16 | 104.54 | 56.16 | 0 | 0 | 0 | 6.12 | 48.38 | 0
2025-04-17 18:00 | 55.01 | 28.57 | 28.57 | 23.04 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-17 19:00 | 52.99 | 0 | 0 | 51.23 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-17 20:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 21:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 22:00 | 49.18 | 0 | 0 | 49.18 | 0 | 0 | 0.68 | 0 | 0
2025-04-17 23:00 | 47.6 | 0 | 0 | 47.6 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 01:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 02:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 03:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 04:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 05:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 06:00 | 45.28 | 43.09 | 43.09 | 2.19 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 07:00 | 48.12 | 100.64 | 51.52 | 0 | 3.4 | 0 | 3.91 | 49.12 | 0
2025-04-18 08:00 | 49.81 | 114.46 | 52.14 | 0 | 2.33 | 0 | 6.12 | 62.33 | 0
2025-04-18 09:00 | 51.18 | 116.71 | 51.18 | 0 | 0 | 0 | 6.12 | 65.52 | 0
2025-04-18 10:00 | 52.98 | 114.77 | 52.98 | 0 | 0 | 0 | 6.12 | 61.79 | 0
2025-04-18 11:00 | 54.86 | 111.24 | 54.86 | 0 | 0 | 0 | 6.12 | 56.38 | 0
2025-04-18 12:00 | 56.55 | 107.8 | 56.55 | 0 | 0 | 0 | 6.12 | 51.24 | 0
2025-04-18 13:00 | 58.39 | 109.37 | 58.39 | 0 | 0 | 0 | 6.12 | 50.98 | 0
2025-04-18 14:00 | 58.52 | 112.67 | 58.52 | 0 | 0 | 0 | 6.12 | 54.16 | 0
2025-04-18 15:00 | 58.91 | 114.32 | 58.91 | 0 | 0 | 0 | 6.12 | 55.4 | 0
2025-04-18 16:00 | 58.89 | 107.97 | 58.89 | 0 | 0 | 0 | 6.12 | 49.08 | 0
2025-04-18 17:00 | 57 | 90.16 | 57 | 0 | 0 | 0 | 6.12 | 33.15 | 0
2025-04-18 18:00 | 56.82 | 25.3 | 25.3 | 28.12 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-18 19:00 | 54.78 | 0 | 0 | 53.01 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-18 20:00 | 51.87 | 0 | 0 | 51.87 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 21:00 | 50.11 | 0 | 0 | 50.11 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 22:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 0.68 | 0 | 0
2025-04-18 23:00 | 47.56 | 0 | 0 | 47.56 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 | 45.94 | 0 | 0 | 45.94 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 01:00 | 44.63 | 0 | 0 | 44.63 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 02:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 03:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 04:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 05:00 | 44.69 | 0 | 0 | 44.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 06:00 | 45.52 | 16.34 | 16.34 | 29.17 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 07:00 | 47.7 | 37.04 | 37.04 | 10.66 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 08:00 | 49.06 | 49.3 | 49.3 | 0 | 0.24 | 0 | 0.91 | 0 | 0
2025-04-19 09:00 | 52.97 | 56.09 | 56.09 | 0 | 3.12 | 0 | 3.87 | 0 | 0
2025-04-19 10:00 | 54.41 | 86.83 | 56.78 | 0 | 2.37 | 0 | 6.12 | 30.05 | 0
2025-04-19 11:00 | 58.16 | 78.73 | 58.16 | 0 | 0 | 0 | 6.12 | 20.57 | 0
2025-04-19 12:00 | 59.24 | 88.4 | 59.24 | 0 | 0 | 0 | 6.12 | 29.16 | 0
2025-04-19 13:00 | 61.43 | 104.92 | 61.43 | 0 | 0 | 0 | 6.12 | 43.49 | 0
2025-04-19 14:00 | 61.95 | 108.09 | 61.95 | 0 | 0 | 0 | 6.12 | 46.14 | 0
2025-04-19 15:00 | 62.33 | 108.74 | 62.33 | 0 | 0 | 0 | 6.12 | 46.42 | 0
2025-04-19 16:00 | 61.68 | 125.09 | 61.68 | 0 | 0 | 0 | 6.12 | 63.41 | 0
2025-04-19 17:00 | 60.98 | 114.33 | 60.98 | 0 | 0 | 0 | 6.12 | 53.35 | 0
2025-04-19 18:00 | 59.42 | 37.37 | 37.37 | 18.65 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-19 19:00 | 56.75 | 0 | 0 | 54.99 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-19 20:00 | 54.69 | 0 | 0 | 54.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 21:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 22:00 | 51 | 0 | 0 | 51 | 0 | 0 | 0.68 | 0 | 0
2025-04-19 23:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 | 46.65 | 0 | 0 | 46.65 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 01:00 | 44.55 | 0 | 0 | 44.55 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 02:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 03:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 04:00 | 43.61 | 0 | 0 | 43.61 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 05:00 | 44.75 | 0.3 | 0.3 | 44.45 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 06:00 | 46.67 | 4.54 | 4.54 | 42.12 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 07:00 | 47.5 | 74.82 | 50.9 | 0 | 3.4 | 0 | 3.91 | 23.93 | 0
2025-04-20 08:00 | 49.69 | 123.97 | 52.02 | 0 | 2.33 | 0 | 6.12 | 71.95 | 0
2025-04-20 09:00 | 50.89 | 108.04 | 50.89 | 0 | 0 | 0 | 6.12 | 57.15 | 0
2025-04-20 10:00 | 52.78 | 104.14 | 52.78 | 0 | 0 | 0 | 6.12 | 51.37 | 0
2025-04-20 11:00 | 53.08 | 38.85 | 38.85 | 10.83 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-20 12:00 | 55.17 | 74.9 | 58.57 | 0 | 3.4 | 0 | 5.77 | 16.34 | 0
2025-04-20 13:00 | 54.32 | 130.93 | 54.68 | 0 | 0.37 | 0 | 6.12 | 76.24 | 0
2025-04-20 14:00 | 54.51 | 45.84 | 45.84 | 5.27 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-20 15:00 | 54.4 | 5.91 | 5.91 | 46.72 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-20 16:00 | 56.06 | 3.85 | 3.85 | 52.21 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 17:00 | 54.97 | 1.73 | 1.73 | 53.24 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 18:00 | 53.8 | 0 | 0 | 53.8 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 19:00 | 53.73 | 0 | 0 | 53.73 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 20:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 21:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 22:00 | 48.23 | 0 | 0 | 48.23 | 0 | 0 | 0.68 | 0 | 0
2025-04-20 23:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 | 45.94 | 0 | 0 | 45.94 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 01:00 | 43.83 | 0 | 0 | 43.83 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 02:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 03:00 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 04:00 | 44.34 | 0 | 0 | 44.34 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 05:00 | 45.99 | 0.12 | 0.12 | 45.88 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 06:00 | 46 | 47.49 | 47.49 | 0 | 1.49 | 0 | 2.1 | 0 | 0
2025-04-21 07:00 | 47.76 | 100.95 | 51.15 | 0 | 3.4 | 0 | 5.33 | 49.8 | 0
2025-04-21 08:00 | 50.15 | 113.68 | 50.98 | 0 | 0.83 | 0 | 6.12 | 62.7 | 0
2025-04-21 09:00 | 52.91 | 118.91 | 52.91 | 0 | 0 | 0 | 6.12 | 66 | 0
2025-04-21 10:00 | 54.5 | 114.88 | 54.5 | 0 | 0 | 0 | 6.12 | 60.38 | 0
2025-04-21 11:00 | 56.71 | 111.38 | 56.71 | 0 | 0 | 0 | 6.12 | 54.67 | 0
2025-04-21 12:00 | 59.51 | 109.34 | 59.51 | 0 | 0 | 0 | 6.12 | 49.83 | 0
2025-04-21 13:00 | 60.69 | 110.78 | 60.69 | 0 | 0 | 0 | 6.12 | 50.09 | 0
2025-04-21 14:00 | 60.45 | 113.69 | 60.45 | 0 | 0 | 0 | 6.12 | 53.25 | 0
2025-04-21 15:00 | 61.18 | 116.1 | 61.18 | 0 | 0 | 0 | 6.12 | 54.92 | 0
2025-04-21 16:00 | 62.22 | 110.88 | 62.22 | 0 | 0 | 0 | 6.12 | 48.66 | 0
2025-04-21 17:00 | 60.7 | 95.24 | 60.7 | 0 | 0 | 0 | 6.12 | 34.54 | 0
2025-04-21 18:00 | 58.6 | 31.33 | 31.33 | 23.87 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-21 19:00 | 56.94 | 0 | 0 | 55.17 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-21 20:00 | 54.78 | 0 | 0 | 54.78 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 21:00 | 52.78 | 0 | 0 | 52.78 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 22:00 | 49.41 | 0 | 0 | 49.41 | 0 | 0 | 0.68 | 0 | 0
2025-04-21 23:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 01:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 02:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 03:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 04:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 05:00 | 45.5 | 0.22 | 0.22 | 45.28 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 06:00 | 46.56 | 45.42 | 45.42 | 1.14 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 07:00 | 48.17 | 91.78 | 51.57 | 0 | 3.4 | 0 | 3.91 | 40.2 | 0
2025-04-22 08:00 | 50.16 | 106.11 | 52.49 | 0 | 2.33 | 0 | 6.12 | 53.62 | 0
2025-04-22 09:00 | 52.07 | 112.73 | 52.07 | 0 | 0 | 0 | 6.12 | 60.66 | 0
2025-04-22 10:00 | 54.76 | 111.17 | 54.76 | 0 | 0 | 0 | 6.12 | 56.42 | 0
2025-04-22 11:00 | 57.59 | 102.94 | 57.59 | 0 | 0 | 0 | 6.12 | 45.35 | 0
2025-04-22 12:00 | 58.78 | 101.28 | 58.78 | 0 | 0 | 0 | 6.12 | 42.5 | 0
2025-04-22 13:00 | 59.85 | 97.88 | 59.85 | 0 | 0 | 0 | 6.12 | 38.03 | 0
2025-04-22 14:00 | 60.97 | 100.24 | 60.97 | 0 | 0 | 0 | 6.12 | 39.28 | 0
2025-04-22 15:00 | 61.63 | 96.38 | 61.63 | 0 | 0 | 0 | 6.12 | 34.76 | 0
2025-04-22 16:00 | 61.03 | 87.69 | 61.03 | 0 | 0 | 0 | 6.12 | 26.66 | 0
2025-04-22 17:00 | 60.54 | 70.73 | 60.54 | 0 | 0 | 0 | 6.12 | 10.19 | 0
2025-04-22 18:00 | 59.1 | 26.9 | 26.9 | 28.8 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-22 19:00 | 57.41 | 0 | 0 | 55.64 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-22 20:00 | 55.5 | 0 | 0 | 55.5 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 21:00 | 52.99 | 0 | 0 | 52.99 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 22:00 | 49.74 | 0 | 0 | 49.74 | 0 | 0 | 0.68 | 0 | 0
2025-04-22 23:00 | 47.65 | 0 | 0 | 47.65 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 01:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 02:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 03:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 04:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 05:00 | 44.75 | 0.55 | 0.55 | 44.2 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 06:00 | 46.26 | 49.69 | 49.66 | 0 | 3.4 | 0 | 3.91 | 0.03 | 0
2025-04-23 07:00 | 48.71 | 79.56 | 51.03 | 0 | 2.33 | 0 | 6.12 | 28.53 | 0
2025-04-23 08:00 | 50.15 | 92.56 | 50.15 | 0 | 0 | 0 | 6.12 | 42.4 | 0
2025-04-23 09:00 | 53.3 | 75.06 | 53.3 | 0 | 0 | 0 | 6.12 | 21.76 | 0
2025-04-23 10:00 | 54.11 | 85.03 | 54.11 | 0 | 0 | 0 | 6.12 | 30.92 | 0
2025-04-23 11:00 | 55.64 | 98.81 | 55.64 | 0 | 0 | 0 | 6.12 | 43.17 | 0
2025-04-23 12:00 | 57.26 | 96.7 | 57.26 | 0 | 0 | 0 | 6.12 | 39.43 | 0
2025-04-23 13:00 | 58.49 | 99.07 | 58.49 | 0 | 0 | 0 | 6.12 | 40.57 | 0
2025-04-23 14:00 | 59.26 | 108.41 | 59.26 | 0 | 0 | 0 | 6.12 | 49.15 | 0
2025-04-23 15:00 | 60.32 | 110.96 | 60.32 | 0 | 0 | 0 | 6.12 | 50.64 | 0
2025-04-23 16:00 | 58.62 | 111.21 | 58.62 | 0 | 0 | 0 | 6.12 | 52.58 | 0
2025-04-23 17:00 | 58.79 | 81.47 | 58.79 | 0 | 0 | 0 | 6.12 | 22.68 | 0
2025-04-23 18:00 | 57.36 | 21.24 | 21.24 | 32.73 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-23 19:00 | 55 | 0 | 0 | 53.23 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-23 20:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 21:00 | 52.7 | 0 | 0 | 52.7 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 22:00 | 49.62 | 0 | 0 | 49.62 | 0 | 0 | 0.68 | 0 | 0
2025-04-23 23:00 | 48.12 | 0 | 0 | 48.12 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 | 45.65 | 0 | 0 | 45.65 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 01:00 | 44.58 | 0 | 0 | 44.58 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 02:00 | 44.89 | 0 | 0 | 44.89 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 03:00 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 04:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 05:00 | 45.33 | 0 | 0 | 45.33 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 06:00 | 46.25 | 13.97 | 13.97 | 32.29 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 07:00 | 47.89 | 74.62 | 51.29 | 0 | 3.4 | 0 | 3.91 | 23.32 | 0
2025-04-24 08:00 | 50.25 | 77.86 | 52.58 | 0 | 2.33 | 0 | 6.12 | 25.28 | 0
2025-04-24 09:00 | 51.04 | 48.69 | 48.69 | 0 | 0 | 2.34 | 3.65 | 0 | 0
2025-04-24 10:00 | 52.75 | 53.23 | 53.23 | 0 | 0.48 | 0 | 4.11 | 0 | 0
2025-04-24 11:00 | 54.62 | 34.9 | 34.9 | 16.46 | 0 | 3.26 | 0.68 | 0 | 0
2025-04-24 12:00 | 56.08 | 33.08 | 33.08 | 23 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 13:00 | 56.95 | 21.18 | 21.18 | 35.77 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 14:00 | 56.44 | 43.72 | 43.72 | 12.71 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 15:00 | 57.38 | 36.54 | 36.54 | 20.84 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 16:00 | 56.38 | 27.1 | 27.1 | 29.27 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 17:00 | 57.25 | 5.02 | 5.02 | 52.23 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 18:00 | 55.03 | 0 | 0 | 55.03 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 19:00 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 20:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 21:00 | 52.63 | 0 | 0 | 52.63 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 22:00 | 50.18 | 0 | 0 | 50.18 | 0 | 0 | 0.68 | 0 | 0
2025-04-24 23:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 | 46.51 | 0 | 0 | 46.51 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 01:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 02:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 03:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 04:00 | 44.52 | 0 | 0 | 44.52 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 05:00 | 45.75 | 0.08 | 0.08 | 45.67 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 06:00 | 46.84 | 8.5 | 8.5 | 38.34 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 07:00 | 47.95 | 52.54 | 51.35 | 0 | 3.4 | 0 | 3.91 | 1.18 | 0
2025-04-25 08:00 | 50.33 | 51.1 | 51.1 | 0 | 0.77 | 0 | 4.64 | 0 | 0
2025-04-25 09:00 | 53.15 | 29.38 | 29.38 | 20.37 | 0 | 3.4 | 1.06 | 0 | 0
2025-04-25 10:00 | 55.94 | 40.62 | 40.62 | 14.96 | 0 | 0.36 | 0.68 | 0 | 0
2025-04-25 11:00 | 58.29 | 91.98 | 61.69 | 0 | 3.4 | 0 | 3.91 | 30.29 | 0
2025-04-25 12:00 | 59.73 | 95.89 | 62.06 | 0 | 2.33 | 0 | 6.12 | 33.83 | 0
2025-04-25 13:00 | 60.91 | 122.74 | 60.91 | 0 | 0 | 0 | 6.12 | 61.83 | 0
2025-04-25 14:00 | 62.04 | 125.1 | 62.04 | 0 | 0 | 0 | 6.12 | 63.06 | 0
2025-04-25 15:00 | 61.64 | 125.04 | 61.64 | 0 | 0 | 0 | 6.12 | 63.4 | 0
2025-04-25 16:00 | 61.59 | 99.31 | 61.59 | 0 | 0 | 0 | 6.12 | 37.72 | 0
2025-04-25 17:00 | 60.36 | 101.78 | 60.36 | 0 | 0 | 0 | 6.12 | 41.42 | 0
2025-04-25 18:00 | 58.72 | 37.49 | 37.49 | 17.83 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-25 19:00 | 57.65 | 0 | 0 | 55.89 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-25 20:00 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 21:00 | 53.37 | 0 | 0 | 53.37 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 22:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 0.68 | 0 | 0
2025-04-25 23:00 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 | 47.17 | 0 | 0 | 47.17 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 01:00 | 45.49 | 0 | 0 | 45.49 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 02:00 | 44.84 | 0 | 0 | 44.84 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 03:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 04:00 | 44.81 | 0 | 0 | 44.81 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 05:00 | 45.84 | 0.78 | 0.78 | 45.06 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 06:00 | 46.55 | 8.81 | 8.81 | 37.74 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 07:00 | 48.68 | 11.62 | 11.62 | 37.06 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 08:00 | 50.36 | 38.69 | 38.69 | 11.67 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 09:00 | 52.51 | 47.36 | 47.36 | 5.15 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 10:00 | 54.26 | 68.33 | 57.66 | 0 | 3.4 | 0 | 3.91 | 10.67 | 0
2025-04-26 11:00 | 57.31 | 101.8 | 59.64 | 0 | 2.33 | 0 | 6.12 | 42.17 | 0
2025-04-26 12:00 | 58.77 | 101 | 58.77 | 0 | 0 | 0 | 6.12 | 42.23 | 0
2025-04-26 13:00 | 59.67 | 84.31 | 59.67 | 0 | 0 | 0 | 6.12 | 24.64 | 0
2025-04-26 14:00 | 61.11 | 94.76 | 61.11 | 0 | 0 | 0 | 6.12 | 33.64 | 0
2025-04-26 15:00 | 60.28 | 86.27 | 60.28 | 0 | 0 | 0 | 6.12 | 25.99 | 0
2025-04-26 16:00 | 61.64 | 57.22 | 57.22 | 1.03 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-26 17:00 | 59.29 | 20.34 | 20.34 | 37.18 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-26 18:00 | 58.36 | 4.79 | 4.79 | 53.57 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 19:00 | 56.48 | 0 | 0 | 56.48 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 20:00 | 55.01 | 0 | 0 | 55.01 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 21:00 | 53.19 | 0 | 0 | 53.19 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 22:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 0.68 | 0 | 0
2025-04-26 23:00 | 49.54 | 0 | 0 | 49.54 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 01:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 02:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 03:00 | 44.67 | 0 | 0 | 44.67 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 04:00 | 44.7 | 0 | 0 | 44.7 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 05:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 06:00 | 46.71 | 0.14 | 0.14 | 46.57 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 07:00 | 50.32 | 25.36 | 25.36 | 24.96 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 08:00 | 51.07 | 44.59 | 44.59 | 6.48 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 09:00 | 52.88 | 98.32 | 56.28 | 0 | 3.4 | 0 | 3.91 | 42.05 | 0
2025-04-27 10:00 | 55.68 | 65.37 | 58.01 | 0 | 2.33 | 0 | 6.12 | 7.36 | 0
2025-04-27 11:00 | 58.29 | 82.57 | 58.29 | 0 | 0 | 0 | 6.12 | 24.27 | 0
2025-04-27 12:00 | 60.57 | 59.87 | 59.87 | 0 | 0 | 0.7 | 5.38 | 0 | 0
2025-04-27 13:00 | 62.11 | 52.63 | 52.63 | 6.08 | 0 | 3.4 | 1.8 | 0 | 0
2025-04-27 14:00 | 63.14 | 38.83 | 38.83 | 23.23 | 0 | 1.07 | 0.68 | 0 | 0
2025-04-27 15:00 | 62.8 | 55.97 | 55.97 | 6.83 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 16:00 | 62.97 | 57.33 | 57.33 | 5.63 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 17:00 | 61.39 | 86.82 | 64.79 | 0 | 3.4 | 0 | 3.91 | 22.03 | 0
2025-04-27 18:00 | 59.99 | 34.56 | 34.56 | 22.36 | 0 | 3.07 | 0.68 | 0 | 0
2025-04-27 19:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 20:00 | 55.44 | 0 | 0 | 55.44 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 21:00 | 54.14 | 0 | 0 | 54.14 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 22:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 0.68 | 0 | 0
2025-04-27 23:00 | 49.47 | 0 | 0 | 49.47 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 | 47.26 | 0 | 0 | 47.26 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 01:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 02:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 03:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 04:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 05:00 | 46.11 | 0.67 | 0.67 | 45.44 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 06:00 | 47.43 | 17.9 | 17.9 | 29.53 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 07:00 | 48.62 | 37.07 | 37.07 | 11.55 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 08:00 | 50.56 | 59.88 | 53.96 | 0 | 3.4 | 0 | 3.91 | 5.92 | 0
2025-04-28 09:00 | 53.3 | 100.35 | 55.63 | 0 | 2.33 | 0 | 6.12 | 44.72 | 0
2025-04-28 10:00 | 56.29 | 115.48 | 56.29 | 0 | 0 | 0 | 6.12 | 59.19 | 0
2025-04-28 11:00 | 58.55 | 98.48 | 58.55 | 0 | 0 | 0 | 6.12 | 39.93 | 0
2025-04-28 12:00 | 59.41 | 64.34 | 59.41 | 0 | 0 | 0 | 6.12 | 4.93 | 0
2025-04-28 13:00 | 61.05 | 60.28 | 60.28 | 0 | 0 | 0.77 | 5.31 | 0 | 0
2025-04-28 14:00 | 62.09 | 61.82 | 61.82 | 0 | 0 | 0.27 | 5.03 | 0 | 0
2025-04-28 15:00 | 62.58 | 33.16 | 33.16 | 26.03 | 0 | 3.4 | 1.45 | 0 | 0
2025-04-28 16:00 | 61.77 | 21.09 | 21.09 | 39.95 | 0 | 0.73 | 0.68 | 0 | 0
2025-04-28 17:00 | 60.83 | 1.11 | 1.11 | 59.72 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 18:00 | 59.68 | 0 | 0 | 59.68 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 19:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 20:00 | 55.42 | 0 | 0 | 55.42 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 21:00 | 53.6 | 0 | 0 | 53.6 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 22:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 0.68 | 0 | 0
2025-04-28 23:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 01:00 | 46.48 | 0 | 0 | 46.48 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 02:00 | 44.82 | 0 | 0 | 44.82 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 03:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 04:00 | 45.61 | 0 | 0 | 45.61 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 05:00 | 45.81 | 1.33 | 1.33 | 44.48 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 06:00 | 48.06 | 28.37 | 28.37 | 19.69 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 07:00 | 49.83 | 84.62 | 53.23 | 0 | 3.4 | 0 | 3.91 | 31.39 | 0
2025-04-29 08:00 | 52.05 | 46.47 | 46.47 | 2.51 | 0 | 3.07 | 0.68 | 0 | 0
2025-04-29 09:00 | 55.42 | 65.39 | 58.82 | 0 | 3.4 | 0 | 3.91 | 6.58 | 0
2025-04-29 10:00 | 58.48 | 107.99 | 60.8 | 0 | 2.33 | 0 | 6.12 | 47.19 | 0
2025-04-29 11:00 | 61.91 | 71.76 | 61.91 | 0 | 0 | 0 | 6.12 | 9.85 | 0
2025-04-29 12:00 | 63.9 | 96.4 | 63.9 | 0 | 0 | 0 | 6.12 | 32.51 | 0
2025-04-29 13:00 | 66.39 | 107.24 | 66.39 | 0 | 0 | 0 | 6.12 | 40.84 | 0
2025-04-29 14:00 | 67.76 | 122.04 | 67.76 | 0 | 0 | 0 | 6.12 | 54.28 | 0
2025-04-29 15:00 | 68.63 | 121.78 | 68.63 | 0 | 0 | 0 | 6.12 | 53.15 | 0
2025-04-29 16:00 | 67.28 | 118.85 | 67.28 | 0 | 0 | 0 | 6.12 | 51.57 | 0
2025-04-29 17:00 | 66.88 | 100.12 | 66.88 | 0 | 0 | 0 | 6.12 | 33.24 | 0
2025-04-29 18:00 | 64.4 | 40.38 | 40.38 | 20.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-29 19:00 | 60.74 | 0 | 0 | 58.97 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-29 20:00 | 58.92 | 0 | 0 | 58.92 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 21:00 | 56.3 | 0 | 0 | 56.3 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 22:00 | 52.72 | 0 | 0 | 52.72 | 0 | 0 | 0.68 | 0 | 0
2025-04-29 23:00 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 | 47.58 | 0 | 0 | 47.58 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 01:00 | 45.25 | 0 | 0 | 45.25 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 02:00 | 44.24 | 0 | 0 | 44.24 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 03:00 | 44.97 | 0 | 0 | 44.97 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 04:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 05:00 | 45.62 | 1.38 | 1.38 | 44.24 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 06:00 | 47.5 | 30.1 | 30.1 | 17.4 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 07:00 | 49.72 | 59.36 | 53.12 | 0 | 3.4 | 0 | 3.91 | 6.24 | 0
2025-04-30 08:00 | 50.86 | 94.24 | 53.18 | 0 | 2.33 | 0 | 6.12 | 41.06 | 0
2025-04-30 09:00 | 53.66 | 96.66 | 53.66 | 0 | 0 | 0 | 6.12 | 43 | 0
2025-04-30 10:00 | 56.91 | 98.46 | 56.91 | 0 | 0 | 0 | 6.12 | 41.55 | 0
2025-04-30 11:00 | 57.72 | 99.82 | 57.72 | 0 | 0 | 0 | 6.12 | 42.1 | 0
2025-04-30 12:00 | 60.47 | 101.89 | 60.47 | 0 | 0 | 0 | 6.12 | 41.42 | 0
2025-04-30 13:00 | 61.15 | 104.15 | 61.15 | 0 | 0 | 0 | 6.12 | 43 | 0
2025-04-30 14:00 | 62.51 | 97.84 | 62.51 | 0 | 0 | 0 | 6.12 | 35.34 | 0
2025-04-30 15:00 | 63.07 | 91.86 | 63.07 | 0 | 0 | 0 | 6.12 | 28.79 | 0
2025-04-30 16:00 | 62.61 | 62.54 | 62.54 | 0 | 0 | 0.07 | 6.04 | 0 | 0
2025-04-30 17:00 | 61.84 | 64.11 | 61.92 | 0 | 0.08 | 0 | 6.12 | 2.18 | 0
2025-04-30 18:00 | 59.46 | 35.69 | 35.69 | 20.37 | 0 | 3.4 | 2.54 | 0 | 0
2025-04-30 19:00 | 58.81 | 0 | 0 | 57.04 | 0 | 1.77 | 0.68 | 0 | 0
2025-04-30 20:00 | 55.73 | 0 | 0 | 55.73 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 21:00 | 54.01 | 0 | 0 | 54.01 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 22:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0.68 | 0 | 0
2025-04-30 23:00 | 49.66 | 0 | 0 | 49.66 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 | 47.8 | 0 | 0 | 47.8 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 01:00 | 45.78 | 0 | 0 | 45.78 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 02:00 | 44.61 | 0 | 0 | 44.61 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 03:00 | 45.41 | 0 | 0 | 45.41 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 04:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 05:00 | 46.78 | 0 | 0 | 46.78 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 06:00 | 47.61 | 4.29 | 4.29 | 43.32 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 07:00 | 48.72 | 5.86 | 5.86 | 42.86 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 08:00 | 51.9 | 7.5 | 7.5 | 44.4 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 09:00 | 53.26 | 16.01 | 16.01 | 37.25 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 10:00 | 55.53 | 17.46 | 17.46 | 38.07 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 11:00 | 56.71 | 22.8 | 22.8 | 33.91 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 12:00 | 59.22 | 30.33 | 30.33 | 28.89 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 13:00 | 58.95 | 39.8 | 39.8 | 19.16 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 14:00 | 59.83 | 43.18 | 43.18 | 16.65 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 15:00 | 60.25 | 59.31 | 59.31 | 0.95 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 16:00 | 59.45 | 32.24 | 32.24 | 27.21 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 17:00 | 59.56 | 33.98 | 33.98 | 25.58 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 18:00 | 59.2 | 35.76 | 35.76 | 23.45 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 19:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 20:00 | 55.55 | 0 | 0 | 55.55 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 21:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 22:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-05-01 23:00 | 49.27 | 0 | 0 | 49.27 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 | 47.46 | 0 | 0 | 47.46 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 01:00 | 46.91 | 0 | 0 | 46.91 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 02:00 | 45.26 | 0 | 0 | 45.26 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 03:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 04:00 | 45.23 | 0 | 0 | 45.23 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 05:00 | 45.41 | 0.56 | 0.56 | 44.84 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 06:00 | 47.31 | 14.56 | 14.56 | 32.75 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 07:00 | 50.33 | 14.81 | 14.81 | 35.52 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 08:00 | 51.11 | 18.51 | 18.51 | 32.61 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 09:00 | 54.29 | 6.41 | 6.41 | 47.89 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 10:00 | 57 | 26.03 | 26.03 | 30.98 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 11:00 | 60.45 | 57 | 57 | 3.45 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 12:00 | 62.02 | 69.07 | 65.42 | 0 | 3.4 | 0 | 3.91 | 3.66 | 0
2025-05-02 13:00 | 62.94 | 73.25 | 65.26 | 0 | 2.33 | 0 | 6.12 | 7.99 | 0
2025-05-02 14:00 | 64.87 | 52.82 | 52.82 | 8.65 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-02 15:00 | 64.19 | 69.83 | 67.59 | 0 | 3.4 | 0 | 5.77 | 2.24 | 0
2025-05-02 16:00 | 64.72 | 43.46 | 43.46 | 17.86 | 0 | 3.4 | 2.19 | 0 | 0
2025-05-02 17:00 | 62.54 | 21.72 | 21.72 | 39.38 | 0 | 1.44 | 0.68 | 0 | 0
2025-05-02 18:00 | 62.17 | 2.69 | 2.69 | 59.47 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 19:00 | 59.38 | 0 | 0 | 59.38 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 20:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 21:00 | 54.57 | 0 | 0 | 54.57 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 22:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0.68 | 0 | 0
2025-05-02 23:00 | 49.6 | 0 | 0 | 49.6 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 | 48.31 | 0 | 0 | 48.31 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 01:00 | 46.22 | 0 | 0 | 46.22 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 02:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 03:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 04:00 | 45.52 | 0 | 0 | 45.52 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 05:00 | 46.29 | 2.88 | 2.88 | 43.41 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 06:00 | 48.11 | 59.25 | 51.51 | 0 | 3.4 | 0 | 3.91 | 7.74 | 0
2025-05-03 07:00 | 50.31 | 113.74 | 52.64 | 0 | 2.33 | 0 | 6.12 | 61.11 | 0
2025-05-03 08:00 | 53.42 | 119.36 | 53.42 | 0 | 0 | 0 | 6.12 | 65.94 | 0
2025-05-03 09:00 | 55.4 | 121.35 | 55.4 | 0 | 0 | 0 | 6.12 | 65.95 | 0
2025-05-03 10:00 | 57.99 | 121.72 | 57.99 | 0 | 0 | 0 | 6.12 | 63.72 | 0
2025-05-03 11:00 | 61.47 | 51.45 | 51.45 | 6.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-03 12:00 | 62.28 | 46.45 | 46.45 | 14.06 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-03 13:00 | 63.89 | 49.85 | 49.85 | 14.04 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 14:00 | 65.02 | 52.21 | 52.21 | 12.8 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 15:00 | 64.51 | 59.55 | 59.55 | 4.96 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 16:00 | 64.44 | 50.54 | 50.54 | 13.91 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 17:00 | 63.39 | 27.13 | 27.13 | 36.26 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 18:00 | 62.35 | 10.43 | 10.43 | 51.92 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 19:00 | 59.84 | 0 | 0 | 59.84 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 20:00 | 57.58 | 0 | 0 | 57.58 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 21:00 | 55.48 | 0 | 0 | 55.48 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 22:00 | 52.82 | 0 | 0 | 52.82 | 0 | 0 | 0.68 | 0 | 0
2025-05-03 23:00 | 49.95 | 0 | 0 | 49.95 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 01:00 | 47.23 | 0 | 0 | 47.23 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 02:00 | 46.07 | 0 | 0 | 46.07 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 03:00 | 44.55 | 0 | 0 | 44.55 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 04:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 05:00 | 46.75 | 3.76 | 3.76 | 42.99 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 06:00 | 48.66 | 65.58 | 52.06 | 0 | 3.4 | 0 | 3.91 | 13.52 | 0
2025-05-04 07:00 | 50.91 | 83.25 | 53.24 | 0 | 2.33 | 0 | 6.12 | 30.01 | 0
2025-05-04 08:00 | 53.27 | 88.89 | 53.27 | 0 | 0 | 0 | 6.12 | 35.62 | 0
2025-05-04 09:00 | 56.43 | 99.04 | 56.43 | 0 | 0 | 0 | 6.12 | 42.61 | 0
2025-05-04 10:00 | 59.35 | 108.22 | 59.35 | 0 | 0 | 0 | 6.12 | 48.87 | 0
2025-05-04 11:00 | 62.08 | 106.64 | 62.08 | 0 | 0 | 0 | 6.12 | 44.57 | 0
2025-05-04 12:00 | 65.05 | 103.03 | 65.05 | 0 | 0 | 0 | 6.12 | 37.97 | 0
2025-05-04 13:00 | 67.39 | 103.76 | 67.39 | 0 | 0 | 0 | 6.12 | 36.37 | 0
2025-05-04 14:00 | 68.77 | 103.5 | 68.77 | 0 | 0 | 0 | 6.12 | 34.73 | 0
2025-05-04 15:00 | 68.33 | 105.2 | 68.33 | 0 | 0 | 0 | 6.12 | 36.87 | 0
2025-05-04 16:00 | 68.59 | 104.09 | 68.59 | 0 | 0 | 0 | 6.12 | 35.5 | 0
2025-05-04 17:00 | 67.41 | 67.57 | 67.41 | 0 | 0 | 0 | 6.12 | 0.17 | 0
2025-05-04 18:00 | 65.04 | 27.76 | 27.76 | 33.88 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-04 19:00 | 62.29 | 0.08 | 0.08 | 60.44 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-04 20:00 | 59.56 | 0 | 0 | 59.56 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 21:00 | 55.6 | 0 | 0 | 55.6 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 22:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0.68 | 0 | 0
2025-05-04 23:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 01:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 02:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 03:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 04:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 05:00 | 46.92 | 8.83 | 8.83 | 38.09 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 06:00 | 48.48 | 86.85 | 51.88 | 0 | 3.4 | 0 | 3.91 | 34.97 | 0
2025-05-05 07:00 | 50.79 | 124.72 | 53.11 | 0 | 2.33 | 0 | 6.12 | 71.61 | 0
2025-05-05 08:00 | 52.62 | 134.3 | 52.62 | 0 | 0 | 0 | 6.12 | 81.69 | 0
2025-05-05 09:00 | 55.95 | 135.94 | 55.95 | 0 | 0 | 0 | 6.12 | 80 | 0
2025-05-05 10:00 | 59.06 | 132.78 | 59.06 | 0 | 0 | 0 | 6.12 | 73.72 | 0
2025-05-05 11:00 | 62.09 | 77.95 | 62.09 | 0 | 0 | 0 | 6.12 | 15.86 | 0
2025-05-05 12:00 | 63.77 | 68.64 | 63.77 | 0 | 0 | 0 | 6.12 | 4.87 | 0
2025-05-05 13:00 | 65.95 | 46.54 | 46.54 | 16.01 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-05 14:00 | 66.02 | 42.22 | 42.22 | 22.03 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-05 15:00 | 67.49 | 46.39 | 46.39 | 21.1 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 16:00 | 67.11 | 36.35 | 36.35 | 30.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 17:00 | 65.61 | 21.21 | 21.21 | 44.4 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 18:00 | 64.25 | 0.11 | 0.11 | 64.14 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 19:00 | 61.65 | 0 | 0 | 61.65 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 20:00 | 57.72 | 0 | 0 | 57.72 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 21:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 22:00 | 52.61 | 0 | 0 | 52.61 | 0 | 0 | 0.68 | 0 | 0
2025-05-05 23:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 01:00 | 46.94 | 0 | 0 | 46.94 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 02:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 03:00 | 45.76 | 0 | 0 | 45.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 04:00 | 46.01 | 0 | 0 | 46.01 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 05:00 | 46.8 | 4.93 | 4.93 | 41.87 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 06:00 | 47.74 | 65.33 | 51.14 | 0 | 3.4 | 0 | 3.91 | 14.19 | 0
2025-05-06 07:00 | 49.85 | 99.88 | 52.17 | 0 | 2.33 | 0 | 6.12 | 47.7 | 0
2025-05-06 08:00 | 52.75 | 112.09 | 52.75 | 0 | 0 | 0 | 6.12 | 59.34 | 0
2025-05-06 09:00 | 55.71 | 113.12 | 55.71 | 0 | 0 | 0 | 6.12 | 57.41 | 0
2025-05-06 10:00 | 58.13 | 112.01 | 58.13 | 0 | 0 | 0 | 6.12 | 53.87 | 0
2025-05-06 11:00 | 61.32 | 109.31 | 61.32 | 0 | 0 | 0 | 6.12 | 47.99 | 0
2025-05-06 12:00 | 63.1 | 108.34 | 63.1 | 0 | 0 | 0 | 6.12 | 45.24 | 0
2025-05-06 13:00 | 64.5 | 107.74 | 64.5 | 0 | 0 | 0 | 6.12 | 43.24 | 0
2025-05-06 14:00 | 65.94 | 108.46 | 65.94 | 0 | 0 | 0 | 6.12 | 42.52 | 0
2025-05-06 15:00 | 66.57 | 103.78 | 66.57 | 0 | 0 | 0 | 6.12 | 37.22 | 0
2025-05-06 16:00 | 66.24 | 93.92 | 66.24 | 0 | 0 | 0 | 6.12 | 27.68 | 0
2025-05-06 17:00 | 65.92 | 76.57 | 65.92 | 0 | 0 | 0 | 6.12 | 10.66 | 0
2025-05-06 18:00 | 62.91 | 35.38 | 35.38 | 24.13 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-06 19:00 | 60.97 | 0.3 | 0.3 | 58.91 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-06 20:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 21:00 | 55.71 | 0 | 0 | 55.71 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 22:00 | 52.79 | 0 | 0 | 52.79 | 0 | 0 | 0.68 | 0 | 0
2025-05-06 23:00 | 49.81 | 0 | 0 | 49.81 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 | 48.49 | 0 | 0 | 48.49 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 01:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 02:00 | 45.21 | 0 | 0 | 45.21 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 03:00 | 45.34 | 0 | 0 | 45.34 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 04:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 05:00 | 47.38 | 0.49 | 0.49 | 46.89 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 06:00 | 49.04 | 12.37 | 12.37 | 36.67 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 07:00 | 50.55 | 31.61 | 31.61 | 18.94 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 08:00 | 53.65 | 50.42 | 50.42 | 3.22 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 09:00 | 55.99 | 54.23 | 54.23 | 1.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 10:00 | 59.99 | 44.31 | 44.31 | 15.68 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 11:00 | 63.69 | 29.25 | 29.25 | 34.44 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 12:00 | 66.82 | 33.43 | 33.43 | 33.38 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 13:00 | 68.36 | 28.17 | 28.17 | 40.19 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 14:00 | 70.72 | 12.91 | 12.91 | 57.82 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 15:00 | 69.95 | 11.82 | 11.82 | 58.14 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 16:00 | 69.57 | 16.55 | 16.55 | 53.03 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 17:00 | 69.07 | 8.19 | 8.19 | 60.88 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 18:00 | 67.24 | 2.2 | 2.2 | 65.04 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 19:00 | 63.74 | 0 | 0 | 63.74 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 20:00 | 60.22 | 0 | 0 | 60.22 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 21:00 | 55.82 | 0 | 0 | 55.82 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 22:00 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 0.68 | 0 | 0
2025-05-07 23:00 | 51.07 | 0 | 0 | 51.07 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 | 48.51 | 0 | 0 | 48.51 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 01:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 02:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 03:00 | 45.92 | 0 | 0 | 45.92 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 04:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 05:00 | 47.25 | 0.17 | 0.17 | 47.08 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 06:00 | 49.31 | 3.97 | 3.97 | 45.34 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 07:00 | 50.59 | 11.5 | 11.5 | 39.09 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 08:00 | 52.61 | 17.42 | 17.42 | 35.19 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 09:00 | 55.3 | 18.51 | 18.51 | 36.79 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 10:00 | 56.24 | 36.22 | 36.22 | 20.02 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 11:00 | 59.83 | 26.55 | 26.55 | 33.28 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 12:00 | 59.97 | 29.16 | 29.16 | 30.81 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 13:00 | 60.95 | 23.11 | 23.11 | 37.84 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 14:00 | 61.61 | 43.06 | 43.06 | 18.55 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 15:00 | 62.48 | 43.45 | 43.45 | 19.04 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 16:00 | 61.74 | 42.22 | 42.22 | 19.53 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 17:00 | 59.96 | 24.57 | 24.57 | 35.39 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 18:00 | 60.48 | 5.43 | 5.43 | 55.05 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 19:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 20:00 | 56.78 | 0 | 0 | 56.78 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 21:00 | 54.13 | 0 | 0 | 54.13 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 22:00 | 52.93 | 0 | 0 | 52.93 | 0 | 0 | 0.68 | 0 | 0
2025-05-08 23:00 | 50.26 | 0 | 0 | 50.26 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 01:00 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 02:00 | 47.29 | 0 | 0 | 47.29 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 03:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 04:00 | 46.35 | 0 | 0 | 46.35 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 05:00 | 47.36 | 0.46 | 0.46 | 46.9 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 06:00 | 48.7 | 1.71 | 1.71 | 46.99 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 07:00 | 51.43 | 7.43 | 7.43 | 44 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 08:00 | 52.97 | 31.22 | 31.22 | 21.74 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 09:00 | 55.26 | 44.82 | 44.82 | 10.44 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 10:00 | 58.23 | 52.75 | 52.75 | 5.48 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 11:00 | 59.51 | 62.79 | 62.79 | 0 | 3.27 | 0 | 3.79 | 0 | 0
2025-05-09 12:00 | 61.46 | 47.49 | 47.49 | 11.02 | 0 | 2.95 | 0.68 | 0 | 0
2025-05-09 13:00 | 61.96 | 41.94 | 41.94 | 20.03 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 14:00 | 63.89 | 30.57 | 30.57 | 33.32 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 15:00 | 64.77 | 21.13 | 21.13 | 43.64 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 16:00 | 63.9 | 3.18 | 3.18 | 60.72 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 17:00 | 63.48 | 4.8 | 4.8 | 58.69 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 18:00 | 61.06 | 2.81 | 2.81 | 58.25 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 19:00 | 59.9 | 0 | 0 | 59.9 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 20:00 | 57.27 | 0 | 0 | 57.27 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 21:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 22:00 | 53.52 | 0 | 0 | 53.52 | 0 | 0 | 0.68 | 0 | 0
2025-05-09 23:00 | 50.93 | 0 | 0 | 50.93 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 | 48.31 | 0 | 0 | 48.31 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 01:00 | 46.8 | 0 | 0 | 46.8 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 02:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 03:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 04:00 | 47.49 | 0 | 0 | 47.49 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 05:00 | 48.14 | 2.42 | 2.42 | 45.72 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 06:00 | 48.07 | 68.65 | 51.47 | 0 | 3.4 | 0 | 3.91 | 17.19 | 0
2025-05-10 07:00 | 51.69 | 101.92 | 54.02 | 0 | 2.33 | 0 | 6.12 | 47.91 | 0
2025-05-10 08:00 | 53.64 | 104.06 | 53.64 | 0 | 0 | 0 | 6.12 | 50.41 | 0
2025-05-10 09:00 | 54.65 | 112.35 | 54.65 | 0 | 0 | 0 | 6.12 | 57.7 | 0
2025-05-10 10:00 | 57.4 | 121.88 | 57.4 | 0 | 0 | 0 | 6.12 | 64.47 | 0
2025-05-10 11:00 | 59.99 | 90.73 | 59.99 | 0 | 0 | 0 | 6.12 | 30.74 | 0
2025-05-10 12:00 | 61.26 | 91.74 | 61.26 | 0 | 0 | 0 | 6.12 | 30.48 | 0
2025-05-10 13:00 | 61.46 | 45.75 | 45.75 | 12.31 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-10 14:00 | 63.11 | 28.27 | 28.27 | 33.07 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-10 15:00 | 61.97 | 5.1 | 5.1 | 56.87 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 16:00 | 62.69 | 21.06 | 21.06 | 41.63 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 17:00 | 62.68 | 12.62 | 12.62 | 50.06 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 18:00 | 60.99 | 6.42 | 6.42 | 54.57 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 19:00 | 59.19 | 0 | 0 | 59.19 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 20:00 | 58 | 0 | 0 | 58 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 21:00 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 22:00 | 53.83 | 0 | 0 | 53.83 | 0 | 0 | 0.68 | 0 | 0
2025-05-10 23:00 | 51.42 | 0 | 0 | 51.42 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 01:00 | 47.97 | 0 | 0 | 47.97 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 02:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 03:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 04:00 | 46.47 | 0 | 0 | 46.47 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 05:00 | 47 | 4.27 | 4.27 | 42.73 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 06:00 | 48.73 | 50.51 | 50.51 | 0 | 1.78 | 0 | 2.37 | 0 | 0
2025-05-11 07:00 | 51.13 | 49.13 | 49.13 | 0.39 | 0 | 1.61 | 0.68 | 0 | 0
2025-05-11 08:00 | 53.75 | 63.3 | 57.15 | 0 | 3.4 | 0 | 3.91 | 6.14 | 0
2025-05-11 09:00 | 56.84 | 96.07 | 59.17 | 0 | 2.33 | 0 | 6.12 | 36.9 | 0
2025-05-11 10:00 | 58.54 | 91.37 | 58.54 | 0 | 0 | 0 | 6.12 | 32.83 | 0
2025-05-11 11:00 | 61.3 | 95.43 | 61.3 | 0 | 0 | 0 | 6.12 | 34.13 | 0
2025-05-11 12:00 | 63.22 | 86.43 | 63.22 | 0 | 0 | 0 | 6.12 | 23.21 | 0
2025-05-11 13:00 | 63.99 | 73.42 | 63.99 | 0 | 0 | 0 | 6.12 | 9.43 | 0
2025-05-11 14:00 | 65.29 | 99.07 | 65.29 | 0 | 0 | 0 | 6.12 | 33.78 | 0
2025-05-11 15:00 | 65.17 | 110.83 | 65.17 | 0 | 0 | 0 | 6.12 | 45.66 | 0
2025-05-11 16:00 | 65.65 | 105.94 | 65.65 | 0 | 0 | 0 | 6.12 | 40.29 | 0
2025-05-11 17:00 | 64.42 | 100.78 | 64.42 | 0 | 0 | 0 | 6.12 | 36.36 | 0
2025-05-11 18:00 | 62.08 | 58.68 | 58.68 | 0 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-11 19:00 | 60.88 | 1.62 | 1.62 | 57.49 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-11 20:00 | 59.39 | 0 | 0 | 59.39 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 21:00 | 56.03 | 0 | 0 | 56.03 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 22:00 | 53.86 | 0 | 0 | 53.86 | 0 | 0 | 0.68 | 0 | 0
2025-05-11 23:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 | 48.76 | 0 | 0 | 48.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 01:00 | 47.98 | 0 | 0 | 47.98 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 02:00 | 46.02 | 0 | 0 | 46.02 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 03:00 | 46.05 | 0 | 0 | 46.05 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 04:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 05:00 | 47.9 | 10.28 | 10.28 | 37.62 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 06:00 | 49.13 | 78.62 | 52.53 | 0 | 3.4 | 0 | 3.91 | 26.1 | 0
2025-05-12 07:00 | 51.43 | 102.71 | 53.76 | 0 | 2.33 | 0 | 6.12 | 48.95 | 0
2025-05-12 08:00 | 53.29 | 116.09 | 53.29 | 0 | 0 | 0 | 6.12 | 62.8 | 0
2025-05-12 09:00 | 55.42 | 120.08 | 55.42 | 0 | 0 | 0 | 6.12 | 64.65 | 0
2025-05-12 10:00 | 57.67 | 117.34 | 57.67 | 0 | 0 | 0 | 6.12 | 59.67 | 0
2025-05-12 11:00 | 58.62 | 115.37 | 58.62 | 0 | 0 | 0 | 6.12 | 56.75 | 0
2025-05-12 12:00 | 60.29 | 113.03 | 60.29 | 0 | 0 | 0 | 6.12 | 52.74 | 0
2025-05-12 13:00 | 61.03 | 114.58 | 61.03 | 0 | 0 | 0 | 6.12 | 53.55 | 0
2025-05-12 14:00 | 60.94 | 115.3 | 60.94 | 0 | 0 | 0 | 6.12 | 54.36 | 0
2025-05-12 15:00 | 61.45 | 111.32 | 61.45 | 0 | 0 | 0 | 6.12 | 49.87 | 0
2025-05-12 16:00 | 62.51 | 105.9 | 62.51 | 0 | 0 | 0 | 6.12 | 43.39 | 0
2025-05-12 17:00 | 61.38 | 91.54 | 61.38 | 0 | 0 | 0 | 6.12 | 30.16 | 0
2025-05-12 18:00 | 59.61 | 48.47 | 48.47 | 7.74 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-12 19:00 | 58.21 | 1.11 | 1.11 | 55.33 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-12 20:00 | 57.29 | 0 | 0 | 57.29 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 21:00 | 56.2 | 0 | 0 | 56.2 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 22:00 | 53.22 | 0 | 0 | 53.22 | 0 | 0 | 0.68 | 0 | 0
2025-05-12 23:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 | 49.76 | 0 | 0 | 49.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 01:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 02:00 | 46.17 | 0 | 0 | 46.17 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 03:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 04:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 05:00 | 48.32 | 10.33 | 10.33 | 38 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 06:00 | 49.18 | 67.57 | 52.58 | 0 | 3.4 | 0 | 3.91 | 14.99 | 0
2025-05-13 07:00 | 51.93 | 94.3 | 54.26 | 0 | 2.33 | 0 | 6.12 | 40.04 | 0
2025-05-13 08:00 | 54.71 | 109.3 | 54.71 | 0 | 0 | 0 | 6.12 | 54.58 | 0
2025-05-13 09:00 | 57.43 | 114.62 | 57.43 | 0 | 0 | 0 | 6.12 | 57.19 | 0
2025-05-13 10:00 | 60.75 | 113.63 | 60.75 | 0 | 0 | 0 | 6.12 | 52.88 | 0
2025-05-13 11:00 | 63.33 | 110.24 | 63.33 | 0 | 0 | 0 | 6.12 | 46.91 | 0
2025-05-13 12:00 | 65.69 | 108.44 | 65.69 | 0 | 0 | 0 | 6.12 | 42.74 | 0
2025-05-13 13:00 | 68.81 | 108.74 | 68.81 | 0 | 0 | 0 | 6.12 | 39.92 | 0
2025-05-13 14:00 | 69.8 | 110.24 | 69.8 | 0 | 0 | 0 | 6.12 | 40.43 | 0
2025-05-13 15:00 | 69.34 | 107.89 | 69.34 | 0 | 0 | 0 | 6.12 | 38.55 | 0
2025-05-13 16:00 | 69.56 | 93.92 | 69.56 | 0 | 0 | 0 | 6.12 | 24.35 | 0
2025-05-13 17:00 | 67.64 | 76.83 | 67.64 | 0 | 0 | 0 | 6.12 | 9.19 | 0
2025-05-13 18:00 | 65.42 | 43.16 | 43.16 | 18.86 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-13 19:00 | 63.98 | 1.18 | 1.18 | 61.03 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-13 20:00 | 59.7 | 0 | 0 | 59.7 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 21:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 22:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 0.68 | 0 | 0
2025-05-13 23:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 01:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 02:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 03:00 | 46.97 | 0 | 0 | 46.97 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 04:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 05:00 | 47.38 | 12.95 | 12.95 | 34.43 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 06:00 | 49.58 | 78.6 | 52.98 | 0 | 3.4 | 0 | 3.91 | 25.62 | 0
2025-05-14 07:00 | 52.5 | 99.04 | 54.83 | 0 | 2.33 | 0 | 6.12 | 44.21 | 0
2025-05-14 08:00 | 55.12 | 9.92 | 9.92 | 41.8 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-14 09:00 | 57.27 | 29.56 | 29.56 | 25.94 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-14 10:00 | 58.91 | 91.47 | 62.31 | 0 | 3.4 | 0 | 3.91 | 29.16 | 0
2025-05-14 11:00 | 62.15 | 117.51 | 64.47 | 0 | 2.33 | 0 | 6.12 | 53.04 | 0
2025-05-14 12:00 | 64.36 | 122.97 | 64.36 | 0 | 0 | 0 | 6.12 | 58.6 | 0
2025-05-14 13:00 | 65.85 | 100.71 | 65.85 | 0 | 0 | 0 | 6.12 | 34.86 | 0
2025-05-14 14:00 | 66.85 | 84.33 | 66.85 | 0 | 0 | 0 | 6.12 | 17.48 | 0
2025-05-14 15:00 | 66.97 | 96.84 | 66.97 | 0 | 0 | 0 | 6.12 | 29.87 | 0
2025-05-14 16:00 | 66.42 | 40.14 | 40.14 | 22.88 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-14 17:00 | 65.19 | 11.13 | 11.13 | 52.29 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-14 18:00 | 62.99 | 0 | 0 | 62.99 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 19:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 20:00 | 59.6 | 0 | 0 | 59.6 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 21:00 | 57.19 | 0 | 0 | 57.19 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 22:00 | 53.61 | 0 | 0 | 53.61 | 0 | 0 | 0.68 | 0 | 0
2025-05-14 23:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 | 50.74 | 0 | 0 | 50.74 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 01:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 02:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 03:00 | 46.88 | 0 | 0 | 46.88 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 04:00 | 48.1 | 0 | 0 | 48.1 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 05:00 | 47.61 | 11.78 | 11.78 | 35.83 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 06:00 | 49.81 | 67.46 | 53.21 | 0 | 3.4 | 0 | 3.91 | 14.25 | 0
2025-05-15 07:00 | 51.28 | 93.85 | 53.6 | 0 | 2.33 | 0 | 6.12 | 40.24 | 0
2025-05-15 08:00 | 53.54 | 109.56 | 53.54 | 0 | 0 | 0 | 6.12 | 56.02 | 0
2025-05-15 09:00 | 55.9 | 113.37 | 55.9 | 0 | 0 | 0 | 6.12 | 57.47 | 0
2025-05-15 10:00 | 58.52 | 114.44 | 58.52 | 0 | 0 | 0 | 6.12 | 55.91 | 0
2025-05-15 11:00 | 60.37 | 113.44 | 60.37 | 0 | 0 | 0 | 6.12 | 53.07 | 0
2025-05-15 12:00 | 60.96 | 112.81 | 60.96 | 0 | 0 | 0 | 6.12 | 51.85 | 0
2025-05-15 13:00 | 61.43 | 112.11 | 61.43 | 0 | 0 | 0 | 6.12 | 50.68 | 0
2025-05-15 14:00 | 63.39 | 109.64 | 63.39 | 0 | 0 | 0 | 6.12 | 46.24 | 0
2025-05-15 15:00 | 62.1 | 105.09 | 62.1 | 0 | 0 | 0 | 6.12 | 42.99 | 0
2025-05-15 16:00 | 61.86 | 92.54 | 61.86 | 0 | 0 | 0 | 6.12 | 30.68 | 0
2025-05-15 17:00 | 60.74 | 80.82 | 60.74 | 0 | 0 | 0 | 6.12 | 20.08 | 0
2025-05-15 18:00 | 61.43 | 44.28 | 44.28 | 13.76 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-15 19:00 | 59.96 | 1.72 | 1.72 | 56.46 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-15 20:00 | 59.06 | 0 | 0 | 59.06 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 21:00 | 55.23 | 0 | 0 | 55.23 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 22:00 | 54.54 | 0 | 0 | 54.54 | 0 | 0 | 0.68 | 0 | 0
2025-05-15 23:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 | 50.3 | 0 | 0 | 50.3 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 01:00 | 47.44 | 0 | 0 | 47.44 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 02:00 | 47.95 | 0 | 0 | 47.95 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 03:00 | 47.24 | 0 | 0 | 47.24 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 04:00 | 47.19 | 0 | 0 | 47.19 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 05:00 | 48.59 | 13.94 | 13.94 | 34.65 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 06:00 | 49.51 | 73.42 | 52.91 | 0 | 3.4 | 0 | 3.91 | 20.51 | 0
2025-05-16 07:00 | 51.66 | 101.1 | 53.99 | 0 | 2.33 | 0 | 6.12 | 47.11 | 0
2025-05-16 08:00 | 54 | 98.29 | 54 | 0 | 0 | 0 | 6.12 | 44.28 | 0
2025-05-16 09:00 | 55.63 | 113.55 | 55.63 | 0 | 0 | 0 | 6.12 | 57.92 | 0
2025-05-16 10:00 | 59.19 | 109.66 | 59.19 | 0 | 0 | 0 | 6.12 | 50.47 | 0
2025-05-16 11:00 | 61.28 | 107.52 | 61.28 | 0 | 0 | 0 | 6.12 | 46.24 | 0
2025-05-16 12:00 | 61.9 | 106.83 | 61.9 | 0 | 0 | 0 | 6.12 | 44.93 | 0
2025-05-16 13:00 | 63.57 | 106.46 | 63.57 | 0 | 0 | 0 | 6.12 | 42.89 | 0
2025-05-16 14:00 | 63.95 | 105.6 | 63.95 | 0 | 0 | 0 | 6.12 | 41.65 | 0
2025-05-16 15:00 | 64.48 | 96.4 | 64.48 | 0 | 0 | 0 | 6.12 | 31.92 | 0
2025-05-16 16:00 | 63.77 | 80.12 | 63.77 | 0 | 0 | 0 | 6.12 | 16.34 | 0
2025-05-16 17:00 | 62.95 | 49.74 | 49.74 | 9.81 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-16 18:00 | 62.77 | 28.88 | 28.88 | 32.13 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-16 19:00 | 60.65 | 1.47 | 1.47 | 59.19 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 20:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 21:00 | 56.58 | 0 | 0 | 56.58 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 22:00 | 53.77 | 0 | 0 | 53.77 | 0 | 0 | 0.68 | 0 | 0
2025-05-16 23:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 | 50.47 | 0 | 0 | 50.47 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 01:00 | 48.78 | 0 | 0 | 48.78 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 02:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 03:00 | 46.64 | 0 | 0 | 46.64 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 04:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 05:00 | 48.33 | 12.21 | 12.21 | 36.12 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 06:00 | 49.51 | 52.04 | 52.04 | 0 | 2.53 | 0 | 3.09 | 0 | 0
2025-05-17 07:00 | 52.3 | 77.34 | 55.49 | 0 | 3.19 | 0 | 6.12 | 21.85 | 0
2025-05-17 08:00 | 55.79 | 89.68 | 55.79 | 0 | 0 | 0 | 6.12 | 33.89 | 0
2025-05-17 09:00 | 58.17 | 87.16 | 58.17 | 0 | 0 | 0 | 6.12 | 28.99 | 0
2025-05-17 10:00 | 60.34 | 89.8 | 60.34 | 0 | 0 | 0 | 6.12 | 29.46 | 0
2025-05-17 11:00 | 63.04 | 95 | 63.04 | 0 | 0 | 0 | 6.12 | 31.96 | 0
2025-05-17 12:00 | 67.08 | 103.07 | 67.08 | 0 | 0 | 0 | 6.12 | 35.98 | 0
2025-05-17 13:00 | 68.09 | 112.3 | 68.09 | 0 | 0 | 0 | 6.12 | 44.21 | 0
2025-05-17 14:00 | 69 | 113.89 | 69 | 0 | 0 | 0 | 6.12 | 44.89 | 0
2025-05-17 15:00 | 69.6 | 120.85 | 69.6 | 0 | 0 | 0 | 6.12 | 51.25 | 0
2025-05-17 16:00 | 68.59 | 112.29 | 68.59 | 0 | 0 | 0 | 6.12 | 43.7 | 0
2025-05-17 17:00 | 68.84 | 99.52 | 68.84 | 0 | 0 | 0 | 6.12 | 30.67 | 0
2025-05-17 18:00 | 66.05 | 61.6 | 61.6 | 1.05 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-17 19:00 | 64.5 | 2.74 | 2.74 | 59.99 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-17 20:00 | 61.04 | 0 | 0 | 61.04 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 21:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 22:00 | 55.25 | 0 | 0 | 55.25 | 0 | 0 | 0.68 | 0 | 0
2025-05-17 23:00 | 52.86 | 0 | 0 | 52.86 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 01:00 | 48.87 | 0 | 0 | 48.87 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 02:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 03:00 | 46.97 | 0 | 0 | 46.97 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 04:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 05:00 | 48.1 | 17.08 | 17.08 | 31.02 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 06:00 | 50.34 | 88.99 | 53.74 | 0 | 3.4 | 0 | 3.91 | 35.25 | 0
2025-05-18 07:00 | 52.73 | 115.02 | 55.06 | 0 | 2.33 | 0 | 6.12 | 59.96 | 0
2025-05-18 08:00 | 55.79 | 123.53 | 55.79 | 0 | 0 | 0 | 6.12 | 67.74 | 0
2025-05-18 09:00 | 58.55 | 125.64 | 58.55 | 0 | 0 | 0 | 6.12 | 67.09 | 0
2025-05-18 10:00 | 62.22 | 124.88 | 62.22 | 0 | 0 | 0 | 6.12 | 62.66 | 0
2025-05-18 11:00 | 65.14 | 123.2 | 65.14 | 0 | 0 | 0 | 6.12 | 58.06 | 0
2025-05-18 12:00 | 67.22 | 121.93 | 67.22 | 0 | 0 | 0 | 6.12 | 54.71 | 0
2025-05-18 13:00 | 70.21 | 123.68 | 70.21 | 0 | 0 | 0 | 6.12 | 53.47 | 0
2025-05-18 14:00 | 71.06 | 125.51 | 71.06 | 0 | 0 | 0 | 6.12 | 54.46 | 0
2025-05-18 15:00 | 71.22 | 124.72 | 71.22 | 0 | 0 | 0 | 6.12 | 53.5 | 0
2025-05-18 16:00 | 71.67 | 120.58 | 71.67 | 0 | 0 | 0 | 6.12 | 48.91 | 0
2025-05-18 17:00 | 70.45 | 106.53 | 70.45 | 0 | 0 | 0 | 6.12 | 36.08 | 0
2025-05-18 18:00 | 68.28 | 68.43 | 68.28 | 0 | 0 | 0 | 6.12 | 0.15 | 0
2025-05-18 19:00 | 65.51 | 2.63 | 2.63 | 59.47 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-18 20:00 | 61.09 | 0 | 0 | 59.32 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-18 21:00 | 58.09 | 0 | 0 | 58.09 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 22:00 | 56.58 | 0 | 0 | 56.58 | 0 | 0 | 0.68 | 0 | 0
2025-05-18 23:00 | 52.2 | 0 | 0 | 52.2 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 01:00 | 48.37 | 0 | 0 | 48.37 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 02:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 03:00 | 46.89 | 0 | 0 | 46.89 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 04:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 05:00 | 48.78 | 16.09 | 16.09 | 32.69 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 06:00 | 50.36 | 71.2 | 53.76 | 0 | 3.4 | 0 | 3.91 | 17.45 | 0
2025-05-19 07:00 | 52.65 | 91.5 | 54.97 | 0 | 2.33 | 0 | 6.12 | 36.53 | 0
2025-05-19 08:00 | 56.54 | 102.38 | 56.54 | 0 | 0 | 0 | 6.12 | 45.84 | 0
2025-05-19 09:00 | 59.51 | 111.27 | 59.51 | 0 | 0 | 0 | 6.12 | 51.76 | 0
2025-05-19 10:00 | 64.32 | 113.55 | 64.32 | 0 | 0 | 0 | 6.12 | 49.23 | 0
2025-05-19 11:00 | 69.37 | 110.24 | 69.37 | 0 | 0 | 0 | 6.12 | 40.87 | 0
2025-05-19 12:00 | 72.3 | 101.37 | 72.3 | 0 | 0 | 0 | 6.12 | 29.07 | 0
2025-05-19 13:00 | 74.84 | 101.02 | 74.84 | 0 | 0 | 0 | 6.12 | 26.18 | 0
2025-05-19 14:00 | 76.29 | 101.36 | 76.29 | 0 | 0 | 0 | 6.12 | 25.08 | 0
2025-05-19 15:00 | 76 | 98.12 | 76 | 0 | 0 | 0 | 6.12 | 22.12 | 0
2025-05-19 16:00 | 75.67 | 77.74 | 75.67 | 0 | 0 | 0 | 6.12 | 2.08 | 0
2025-05-19 17:00 | 75.12 | 63.85 | 63.85 | 7.88 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-19 18:00 | 71.23 | 23.14 | 23.14 | 46.32 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-19 19:00 | 67.7 | 1.84 | 1.84 | 65.86 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 20:00 | 64.02 | 0 | 0 | 64.02 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 21:00 | 59.59 | 0 | 0 | 59.59 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 22:00 | 55.79 | 0 | 0 | 55.79 | 0 | 0 | 0.68 | 0 | 0
2025-05-19 23:00 | 53.15 | 0 | 0 | 53.15 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 | 50.36 | 0 | 0 | 50.36 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 01:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 02:00 | 47.31 | 0 | 0 | 47.31 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 03:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 04:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 05:00 | 48.77 | 20.83 | 20.83 | 27.93 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 06:00 | 51.1 | 68.71 | 54.5 | 0 | 3.4 | 0 | 3.91 | 14.2 | 0
2025-05-20 07:00 | 53.49 | 103.75 | 55.82 | 0 | 2.33 | 0 | 6.12 | 47.93 | 0
2025-05-20 08:00 | 56.95 | 133.3 | 56.95 | 0 | 0 | 0 | 6.12 | 76.35 | 0
2025-05-20 09:00 | 61.48 | 92.86 | 61.48 | 0 | 0 | 0 | 6.12 | 31.37 | 0
2025-05-20 10:00 | 66.13 | 8.78 | 8.78 | 53.95 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-20 11:00 | 70.31 | 20.68 | 20.68 | 47.86 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-20 12:00 | 74.63 | 9.5 | 9.5 | 65.12 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 13:00 | 77.59 | 22.58 | 22.58 | 55.01 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 14:00 | 79.76 | 8.1 | 8.1 | 71.66 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 15:00 | 81.34 | 87.11 | 84.74 | 0 | 3.4 | 0 | 3.91 | 2.37 | 0
2025-05-20 16:00 | 80.41 | 115.03 | 82.74 | 0 | 2.33 | 0 | 6.12 | 32.29 | 0
2025-05-20 17:00 | 78.21 | 29.54 | 29.54 | 45.27 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-20 18:00 | 74.73 | 39.15 | 39.15 | 33.81 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-20 19:00 | 70.4 | 0.71 | 0.71 | 69.69 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 20:00 | 66.14 | 0 | 0 | 66.14 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 21:00 | 61.72 | 0 | 0 | 61.72 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 22:00 | 57.55 | 0 | 0 | 57.55 | 0 | 0 | 0.68 | 0 | 0
2025-05-20 23:00 | 53.51 | 0 | 0 | 53.51 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 | 51.43 | 0 | 0 | 51.43 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 01:00 | 49.05 | 0 | 0 | 49.05 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 02:00 | 48.14 | 0 | 0 | 48.14 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 03:00 | 47.58 | 0 | 0 | 47.58 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 04:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 05:00 | 48.57 | 7.9 | 7.9 | 40.67 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 06:00 | 51.08 | 43.37 | 43.37 | 7.72 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 07:00 | 54.53 | 106.15 | 57.93 | 0 | 3.4 | 0 | 3.91 | 48.22 | 0
2025-05-21 08:00 | 55.72 | 100.1 | 58.05 | 0 | 2.33 | 0 | 6.12 | 42.05 | 0
2025-05-21 09:00 | 59.01 | 117.61 | 59.01 | 0 | 0 | 0 | 6.12 | 58.6 | 0
2025-05-21 10:00 | 61.87 | 104.91 | 61.87 | 0 | 0 | 0 | 6.12 | 43.04 | 0
2025-05-21 11:00 | 64.8 | 92.48 | 64.8 | 0 | 0 | 0 | 6.12 | 27.68 | 0
2025-05-21 12:00 | 68.4 | 76.43 | 68.4 | 0 | 0 | 0 | 6.12 | 8.04 | 0
2025-05-21 13:00 | 69.29 | 69.8 | 69.29 | 0 | 0 | 0 | 6.12 | 0.51 | 0
2025-05-21 14:00 | 70.66 | 64.83 | 64.83 | 2.42 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-21 15:00 | 70.54 | 92.07 | 73.94 | 0 | 3.4 | 0 | 5.77 | 18.13 | 0
2025-05-21 16:00 | 70.52 | 100.47 | 70.88 | 0 | 0.37 | 0 | 6.12 | 29.59 | 0
2025-05-21 17:00 | 68.77 | 109.57 | 68.77 | 0 | 0 | 0 | 6.12 | 40.8 | 0
2025-05-21 18:00 | 67.94 | 70.44 | 67.94 | 0 | 0 | 0 | 6.12 | 2.5 | 0
2025-05-21 19:00 | 66.45 | 2.83 | 2.83 | 60.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-21 20:00 | 61.91 | 0 | 0 | 60.14 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-21 21:00 | 58.14 | 0 | 0 | 58.14 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 22:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 0.68 | 0 | 0
2025-05-21 23:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 01:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 02:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 03:00 | 47.47 | 0 | 0 | 47.47 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 04:00 | 48.32 | 0 | 0 | 48.32 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 05:00 | 48.93 | 9.76 | 9.76 | 39.17 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 06:00 | 50.5 | 56.87 | 53.9 | 0 | 3.4 | 0 | 3.91 | 2.96 | 0
2025-05-22 07:00 | 52.81 | 19.86 | 19.86 | 29.88 | 0 | 3.07 | 0.68 | 0 | 0
2025-05-22 08:00 | 54.67 | 54.59 | 54.59 | 0.08 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 09:00 | 57.96 | 51.47 | 51.47 | 6.49 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 10:00 | 59.18 | 105.04 | 62.58 | 0 | 3.4 | 0 | 3.91 | 42.46 | 0
2025-05-22 11:00 | 61.89 | 77.21 | 64.22 | 0 | 2.33 | 0 | 6.12 | 13 | 0
2025-05-22 12:00 | 64.15 | 67.51 | 64.15 | 0 | 0 | 0 | 6.12 | 3.36 | 0
2025-05-22 13:00 | 65.13 | 85.86 | 65.13 | 0 | 0 | 0 | 6.12 | 20.73 | 0
2025-05-22 14:00 | 66.01 | 91.88 | 66.01 | 0 | 0 | 0 | 6.12 | 25.87 | 0
2025-05-22 15:00 | 65.93 | 106.27 | 65.93 | 0 | 0 | 0 | 6.12 | 40.33 | 0
2025-05-22 16:00 | 66.3 | 124.45 | 66.3 | 0 | 0 | 0 | 6.12 | 58.14 | 0
2025-05-22 17:00 | 65.44 | 115.69 | 65.44 | 0 | 0 | 0 | 6.12 | 50.24 | 0
2025-05-22 18:00 | 63.99 | 82.69 | 63.99 | 0 | 0 | 0 | 6.12 | 18.7 | 0
2025-05-22 19:00 | 62.58 | 7.67 | 7.67 | 51.51 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-22 20:00 | 60.45 | 0 | 0 | 58.68 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-22 21:00 | 57.54 | 0 | 0 | 57.54 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 22:00 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 0.68 | 0 | 0
2025-05-22 23:00 | 53.12 | 0 | 0 | 53.12 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 01:00 | 49.69 | 0 | 0 | 49.69 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 02:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 03:00 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 04:00 | 48.28 | 0 | 0 | 48.28 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 05:00 | 49.11 | 17.61 | 17.61 | 31.49 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 06:00 | 49.85 | 72.37 | 53.25 | 0 | 3.4 | 0 | 3.91 | 19.13 | 0
2025-05-23 07:00 | 52.96 | 101.99 | 55.29 | 0 | 2.33 | 0 | 6.12 | 46.71 | 0
2025-05-23 08:00 | 53.92 | 110.66 | 53.92 | 0 | 0 | 0 | 6.12 | 56.74 | 0
2025-05-23 09:00 | 56.32 | 114.9 | 56.32 | 0 | 0 | 0 | 6.12 | 58.58 | 0
2025-05-23 10:00 | 59.12 | 111.7 | 59.12 | 0 | 0 | 0 | 6.12 | 52.58 | 0
2025-05-23 11:00 | 60.64 | 109.87 | 60.64 | 0 | 0 | 0 | 6.12 | 49.23 | 0
2025-05-23 12:00 | 60.01 | 110.26 | 60.01 | 0 | 0 | 0 | 6.12 | 50.25 | 0
2025-05-23 13:00 | 61.02 | 110.96 | 61.02 | 0 | 0 | 0 | 6.12 | 49.93 | 0
2025-05-23 14:00 | 61.5 | 110.74 | 61.5 | 0 | 0 | 0 | 6.12 | 49.23 | 0
2025-05-23 15:00 | 62.47 | 105.77 | 62.47 | 0 | 0 | 0 | 6.12 | 43.31 | 0
2025-05-23 16:00 | 61.24 | 100.43 | 61.24 | 0 | 0 | 0 | 6.12 | 39.19 | 0
2025-05-23 17:00 | 60.95 | 80.51 | 60.95 | 0 | 0 | 0 | 6.12 | 19.56 | 0
2025-05-23 18:00 | 61.4 | 53.14 | 53.14 | 4.86 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-23 19:00 | 59.54 | 4.35 | 4.35 | 53.42 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-23 20:00 | 58.8 | 0 | 0 | 58.8 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 21:00 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 22:00 | 54.76 | 0 | 0 | 54.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-23 23:00 | 51.94 | 0 | 0 | 51.94 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 01:00 | 49.73 | 0 | 0 | 49.73 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 02:00 | 48.15 | 0 | 0 | 48.15 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 03:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 04:00 | 47.8 | 0 | 0 | 47.8 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 05:00 | 49.2 | 15.06 | 15.06 | 34.14 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 06:00 | 51.29 | 39.98 | 39.98 | 11.31 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 07:00 | 54.03 | 72.18 | 57.43 | 0 | 3.4 | 0 | 3.91 | 14.76 | 0
2025-05-24 08:00 | 55.05 | 93.46 | 57.37 | 0 | 2.33 | 0 | 6.12 | 36.09 | 0
2025-05-24 09:00 | 59.01 | 98.08 | 59.01 | 0 | 0 | 0 | 6.12 | 39.07 | 0
2025-05-24 10:00 | 62.6 | 110.62 | 62.6 | 0 | 0 | 0 | 6.12 | 48.02 | 0
2025-05-24 11:00 | 65.4 | 102.63 | 65.4 | 0 | 0 | 0 | 6.12 | 37.23 | 0
2025-05-24 12:00 | 68.18 | 106.46 | 68.18 | 0 | 0 | 0 | 6.12 | 38.28 | 0
2025-05-24 13:00 | 70.08 | 106.29 | 70.08 | 0 | 0 | 0 | 6.12 | 36.21 | 0
2025-05-24 14:00 | 71.03 | 111.18 | 71.03 | 0 | 0 | 0 | 6.12 | 40.15 | 0
2025-05-24 15:00 | 71.34 | 110.24 | 71.34 | 0 | 0 | 0 | 6.12 | 38.9 | 0
2025-05-24 16:00 | 71.06 | 94.32 | 71.06 | 0 | 0 | 0 | 6.12 | 23.26 | 0
2025-05-24 17:00 | 70.52 | 79.48 | 70.52 | 0 | 0 | 0 | 6.12 | 8.96 | 0
2025-05-24 18:00 | 67.62 | 48.39 | 48.39 | 15.82 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-24 19:00 | 65.42 | 4.42 | 4.42 | 59.23 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-24 20:00 | 62.62 | 0 | 0 | 62.62 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 21:00 | 60.2 | 0 | 0 | 60.2 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 22:00 | 56.21 | 0 | 0 | 56.21 | 0 | 0 | 0.68 | 0 | 0
2025-05-24 23:00 | 54.02 | 0 | 0 | 54.02 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 | 51.79 | 0 | 0 | 51.79 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 01:00 | 49.38 | 0 | 0 | 49.38 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 02:00 | 48.18 | 0 | 0 | 48.18 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 03:00 | 47.73 | 0 | 0 | 47.73 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 04:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 05:00 | 49.84 | 1.55 | 1.55 | 48.29 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 06:00 | 51.29 | 9.06 | 9.06 | 42.23 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 07:00 | 53.53 | 19.33 | 19.33 | 34.2 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 08:00 | 55.36 | 34 | 34 | 21.36 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 09:00 | 58.02 | 42.1 | 42.1 | 15.93 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 10:00 | 62.05 | 52.29 | 52.29 | 9.76 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 11:00 | 63.09 | 56.05 | 56.05 | 7.04 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 12:00 | 64.61 | 49.25 | 49.25 | 15.36 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 13:00 | 67.05 | 55.92 | 55.92 | 11.13 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 14:00 | 67.3 | 49.55 | 49.55 | 17.75 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 15:00 | 67.73 | 27.4 | 27.4 | 40.32 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 16:00 | 67.09 | 17.77 | 17.77 | 49.33 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 17:00 | 66.18 | 9.87 | 9.87 | 56.31 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 18:00 | 64.91 | 0 | 0 | 64.91 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 19:00 | 62.49 | 0 | 0 | 62.49 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 20:00 | 60.93 | 0 | 0 | 60.93 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 21:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 22:00 | 56.85 | 0 | 0 | 56.85 | 0 | 0 | 0.68 | 0 | 0
2025-05-25 23:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 | 50.18 | 0 | 0 | 50.18 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 01:00 | 49.5 | 0 | 0 | 49.5 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 02:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 03:00 | 48.44 | 0 | 0 | 48.44 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 04:00 | 48 | 0 | 0 | 48 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 05:00 | 49.84 | 20.12 | 20.12 | 29.72 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 06:00 | 50.98 | 55.47 | 54.38 | 0 | 3.4 | 0 | 3.91 | 1.09 | 0
2025-05-26 07:00 | 52.99 | 109.28 | 55.31 | 0 | 2.33 | 0 | 6.12 | 53.97 | 0
2025-05-26 08:00 | 56.14 | 123.77 | 56.14 | 0 | 0 | 0 | 6.12 | 67.63 | 0
2025-05-26 09:00 | 59.15 | 121.63 | 59.15 | 0 | 0 | 0 | 6.12 | 62.48 | 0
2025-05-26 10:00 | 60.9 | 56.11 | 56.11 | 1.39 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-26 11:00 | 63.75 | 76.42 | 67.15 | 0 | 3.4 | 0 | 5.77 | 9.27 | 0
2025-05-26 12:00 | 66.43 | 101.34 | 66.8 | 0 | 0.37 | 0 | 6.12 | 34.54 | 0
2025-05-26 13:00 | 67.81 | 125.96 | 67.81 | 0 | 0 | 0 | 6.12 | 58.14 | 0
2025-05-26 14:00 | 69.2 | 102.72 | 69.2 | 0 | 0 | 0 | 6.12 | 33.52 | 0
2025-05-26 15:00 | 68.73 | 125.3 | 68.73 | 0 | 0 | 0 | 6.12 | 56.57 | 0
2025-05-26 16:00 | 69.36 | 119.71 | 69.36 | 0 | 0 | 0 | 6.12 | 50.35 | 0
2025-05-26 17:00 | 67.42 | 104.21 | 67.42 | 0 | 0 | 0 | 6.12 | 36.79 | 0
2025-05-26 18:00 | 67.25 | 70.25 | 67.25 | 0 | 0 | 0 | 6.12 | 3 | 0
2025-05-26 19:00 | 63.47 | 7.79 | 7.79 | 52.28 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-26 20:00 | 61.29 | 0 | 0 | 59.52 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-26 21:00 | 59.31 | 0 | 0 | 59.31 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 22:00 | 57.15 | 0 | 0 | 57.15 | 0 | 0 | 0.68 | 0 | 0
2025-05-26 23:00 | 53.82 | 0 | 0 | 53.82 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 01:00 | 49.67 | 0 | 0 | 49.67 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 02:00 | 48 | 0 | 0 | 48 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 03:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 04:00 | 47.91 | 0 | 0 | 47.91 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 05:00 | 49.02 | 22.89 | 22.89 | 26.13 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 06:00 | 51.66 | 87.41 | 55.06 | 0 | 3.4 | 0 | 3.91 | 32.35 | 0
2025-05-27 07:00 | 53.2 | 104.75 | 55.53 | 0 | 2.33 | 0 | 6.12 | 49.23 | 0
2025-05-27 08:00 | 56.53 | 116.91 | 56.53 | 0 | 0 | 0 | 6.12 | 60.38 | 0
2025-05-27 09:00 | 58.43 | 110.39 | 58.43 | 0 | 0 | 0 | 6.12 | 51.96 | 0
2025-05-27 10:00 | 61.86 | 108.58 | 61.86 | 0 | 0 | 0 | 6.12 | 46.71 | 0
2025-05-27 11:00 | 63.84 | 97.62 | 63.84 | 0 | 0 | 0 | 6.12 | 33.78 | 0
2025-05-27 12:00 | 66.77 | 79.32 | 66.77 | 0 | 0 | 0 | 6.12 | 12.55 | 0
2025-05-27 13:00 | 67.71 | 103.04 | 67.71 | 0 | 0 | 0 | 6.12 | 35.33 | 0
2025-05-27 14:00 | 69.08 | 89.07 | 69.08 | 0 | 0 | 0 | 6.12 | 19.99 | 0
2025-05-27 15:00 | 68.4 | 60.62 | 60.62 | 4.37 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-27 16:00 | 68.49 | 56.28 | 56.28 | 10.44 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-27 17:00 | 67.06 | 32.8 | 32.8 | 34.25 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 18:00 | 65.86 | 19.16 | 19.16 | 46.7 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 19:00 | 63.96 | 1.93 | 1.93 | 62.03 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 20:00 | 61.35 | 0 | 0 | 61.35 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 21:00 | 58.48 | 0 | 0 | 58.48 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 22:00 | 55.66 | 0 | 0 | 55.66 | 0 | 0 | 0.68 | 0 | 0
2025-05-27 23:00 | 52.59 | 0 | 0 | 52.59 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 | 51.11 | 0 | 0 | 51.11 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 01:00 | 50.1 | 0 | 0 | 50.1 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 02:00 | 47.83 | 0 | 0 | 47.83 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 03:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 04:00 | 49.52 | 0 | 0 | 49.52 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 05:00 | 49.47 | 0.66 | 0.66 | 48.82 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 06:00 | 51.8 | 32.98 | 32.98 | 18.82 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 07:00 | 54.36 | 28.37 | 28.37 | 25.99 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 08:00 | 57.14 | 37.02 | 37.02 | 20.12 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 09:00 | 59 | 83.94 | 62.4 | 0 | 3.4 | 0 | 3.91 | 21.54 | 0
2025-05-28 10:00 | 62.59 | 89.2 | 64.91 | 0 | 2.33 | 0 | 6.12 | 24.28 | 0
2025-05-28 11:00 | 64.61 | 106.7 | 64.61 | 0 | 0 | 0 | 6.12 | 42.09 | 0
2025-05-28 12:00 | 68.97 | 97.14 | 68.97 | 0 | 0 | 0 | 6.12 | 28.17 | 0
2025-05-28 13:00 | 68.72 | 116.42 | 68.72 | 0 | 0 | 0 | 6.12 | 47.7 | 0
2025-05-28 14:00 | 70.1 | 61.31 | 61.31 | 5.4 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-28 15:00 | 70.48 | 64.78 | 64.78 | 3.94 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-28 16:00 | 69.88 | 64.64 | 64.64 | 5.24 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 17:00 | 70.19 | 63.42 | 63.42 | 6.77 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 18:00 | 68.95 | 52.32 | 52.32 | 16.63 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 19:00 | 65.18 | 2.46 | 2.46 | 62.73 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 20:00 | 62.04 | 0 | 0 | 62.04 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 21:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 22:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 0.68 | 0 | 0
2025-05-28 23:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 01:00 | 50.04 | 0 | 0 | 50.04 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 02:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 03:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 04:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 05:00 | 49.38 | 17.48 | 17.48 | 31.9 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 06:00 | 52.21 | 69.15 | 55.61 | 0 | 3.4 | 0 | 3.91 | 13.54 | 0
2025-05-29 07:00 | 54.51 | 96.07 | 56.83 | 0 | 2.33 | 0 | 6.12 | 39.24 | 0
2025-05-29 08:00 | 58.12 | 108.84 | 58.12 | 0 | 0 | 0 | 6.12 | 50.72 | 0
2025-05-29 09:00 | 61.62 | 110.7 | 61.62 | 0 | 0 | 0 | 6.12 | 49.08 | 0
2025-05-29 10:00 | 64.22 | 112.65 | 64.22 | 0 | 0 | 0 | 6.12 | 48.43 | 0
2025-05-29 11:00 | 67.8 | 108.46 | 67.8 | 0 | 0 | 0 | 6.12 | 40.66 | 0
2025-05-29 12:00 | 71.33 | 102.98 | 71.33 | 0 | 0 | 0 | 6.12 | 31.65 | 0
2025-05-29 13:00 | 73.69 | 103.99 | 73.69 | 0 | 0 | 0 | 6.12 | 30.31 | 0
2025-05-29 14:00 | 76.2 | 98.78 | 76.2 | 0 | 0 | 0 | 6.12 | 22.58 | 0
2025-05-29 15:00 | 76.55 | 100.74 | 76.55 | 0 | 0 | 0 | 6.12 | 24.19 | 0
2025-05-29 16:00 | 76.37 | 72.29 | 72.29 | 0.68 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-29 17:00 | 74.41 | 46.93 | 46.93 | 25.72 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-29 18:00 | 71.81 | 24.65 | 24.65 | 47.15 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 19:00 | 69.12 | 4.33 | 4.33 | 64.79 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 20:00 | 65.17 | 0 | 0 | 65.17 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 21:00 | 61.26 | 0 | 0 | 61.26 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 22:00 | 58.41 | 0 | 0 | 58.41 | 0 | 0 | 0.68 | 0 | 0
2025-05-29 23:00 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 01:00 | 49.61 | 0 | 0 | 49.61 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 02:00 | 49.2 | 0 | 0 | 49.2 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 03:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 04:00 | 48.82 | 0 | 0 | 48.82 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 05:00 | 50.69 | 22.44 | 22.44 | 28.25 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 06:00 | 50.94 | 75.76 | 54.34 | 0 | 3.4 | 0 | 3.91 | 21.42 | 0
2025-05-30 07:00 | 54.38 | 98.35 | 56.7 | 0 | 2.33 | 0 | 6.12 | 41.64 | 0
2025-05-30 08:00 | 57.29 | 111.32 | 57.29 | 0 | 0 | 0 | 6.12 | 54.03 | 0
2025-05-30 09:00 | 60.09 | 110.94 | 60.09 | 0 | 0 | 0 | 6.12 | 50.85 | 0
2025-05-30 10:00 | 64.8 | 112.08 | 64.8 | 0 | 0 | 0 | 6.12 | 47.28 | 0
2025-05-30 11:00 | 66.54 | 110.41 | 66.54 | 0 | 0 | 0 | 6.12 | 43.86 | 0
2025-05-30 12:00 | 68.94 | 110.79 | 68.94 | 0 | 0 | 0 | 6.12 | 41.85 | 0
2025-05-30 13:00 | 71.13 | 109.49 | 71.13 | 0 | 0 | 0 | 6.12 | 38.36 | 0
2025-05-30 14:00 | 71.36 | 110.84 | 71.36 | 0 | 0 | 0 | 6.12 | 39.47 | 0
2025-05-30 15:00 | 72.41 | 107.76 | 72.41 | 0 | 0 | 0 | 6.12 | 35.35 | 0
2025-05-30 16:00 | 72.86 | 104.57 | 72.86 | 0 | 0 | 0 | 6.12 | 31.72 | 0
2025-05-30 17:00 | 70.8 | 93.81 | 70.8 | 0 | 0 | 0 | 6.12 | 23.01 | 0
2025-05-30 18:00 | 68.73 | 68.75 | 68.73 | 0 | 0 | 0 | 6.12 | 0.03 | 0
2025-05-30 19:00 | 67.23 | 8.97 | 8.97 | 54.87 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-30 20:00 | 64.28 | 0 | 0 | 62.51 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-30 21:00 | 60.71 | 0 | 0 | 60.71 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 22:00 | 57.08 | 0 | 0 | 57.08 | 0 | 0 | 0.68 | 0 | 0
2025-05-30 23:00 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 01:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 02:00 | 48.43 | 0 | 0 | 48.43 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 03:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 04:00 | 48.44 | 0 | 0 | 48.44 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 05:00 | 49.36 | 29.23 | 29.23 | 20.13 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 06:00 | 52.13 | 92.67 | 55.53 | 0 | 3.4 | 0 | 3.91 | 37.14 | 0
2025-05-31 07:00 | 54.58 | 113.34 | 56.91 | 0 | 2.33 | 0 | 6.12 | 56.43 | 0
2025-05-31 08:00 | 58.14 | 121.03 | 58.14 | 0 | 0 | 0 | 6.12 | 62.89 | 0
2025-05-31 09:00 | 59.96 | 122.72 | 59.96 | 0 | 0 | 0 | 6.12 | 62.76 | 0
2025-05-31 10:00 | 63.43 | 121.34 | 63.43 | 0 | 0 | 0 | 6.12 | 57.92 | 0
2025-05-31 11:00 | 66.19 | 119.25 | 66.19 | 0 | 0 | 0 | 6.12 | 53.06 | 0
2025-05-31 12:00 | 68.27 | 117.5 | 68.27 | 0 | 0 | 0 | 6.12 | 49.24 | 0
2025-05-31 13:00 | 70.56 | 119.28 | 70.56 | 0 | 0 | 0 | 6.12 | 48.72 | 0
2025-05-31 14:00 | 71.7 | 120.63 | 71.7 | 0 | 0 | 0 | 6.12 | 48.93 | 0
2025-05-31 15:00 | 71.86 | 119.35 | 71.86 | 0 | 0 | 0 | 6.12 | 47.49 | 0
2025-05-31 16:00 | 71.19 | 115.02 | 71.19 | 0 | 0 | 0 | 6.12 | 43.83 | 0
2025-05-31 17:00 | 70.01 | 100.58 | 70.01 | 0 | 0 | 0 | 6.12 | 30.56 | 0
2025-05-31 18:00 | 67.71 | 74.6 | 67.71 | 0 | 0 | 0 | 6.12 | 6.89 | 0
2025-05-31 19:00 | 65.64 | 8.12 | 8.12 | 54.11 | 0 | 3.4 | 2.54 | 0 | 0
2025-05-31 20:00 | 62.97 | 0 | 0 | 61.2 | 0 | 1.77 | 0.68 | 0 | 0
2025-05-31 21:00 | 59.73 | 0 | 0 | 59.73 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 22:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 0.68 | 0 | 0
2025-05-31 23:00 | 55.06 | 0 | 0 | 55.06 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 01:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 02:00 | 48.54 | 0 | 0 | 48.54 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 03:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 04:00 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 05:00 | 50.54 | 30.5 | 30.5 | 20.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 06:00 | 51.73 | 93.28 | 55.13 | 0 | 3.4 | 0 | 3.91 | 38.16 | 0
2025-06-01 07:00 | 54.87 | 113.48 | 57.2 | 0 | 2.33 | 0 | 6.12 | 56.27 | 0
2025-06-01 08:00 | 56.8 | 121.91 | 56.8 | 0 | 0 | 0 | 6.12 | 65.11 | 0
2025-06-01 09:00 | 59.2 | 124.1 | 59.2 | 0 | 0 | 0 | 6.12 | 64.9 | 0
2025-06-01 10:00 | 61.35 | 122.98 | 61.35 | 0 | 0 | 0 | 6.12 | 61.63 | 0
2025-06-01 11:00 | 64.25 | 121 | 64.25 | 0 | 0 | 0 | 6.12 | 56.75 | 0
2025-06-01 12:00 | 66.31 | 119.56 | 66.31 | 0 | 0 | 0 | 6.12 | 53.25 | 0
2025-06-01 13:00 | 67.27 | 120.29 | 67.27 | 0 | 0 | 0 | 6.12 | 53.02 | 0
2025-06-01 14:00 | 69.03 | 120.92 | 69.03 | 0 | 0 | 0 | 6.12 | 51.9 | 0
2025-06-01 15:00 | 68.88 | 120.48 | 68.88 | 0 | 0 | 0 | 6.12 | 51.6 | 0
2025-06-01 16:00 | 67.75 | 115.21 | 67.75 | 0 | 0 | 0 | 6.12 | 47.46 | 0
2025-06-01 17:00 | 66.98 | 104.89 | 66.98 | 0 | 0 | 0 | 6.12 | 37.91 | 0
2025-06-01 18:00 | 66.1 | 79.57 | 66.1 | 0 | 0 | 0 | 6.12 | 13.47 | 0
2025-06-01 19:00 | 63.7 | 8.44 | 8.44 | 51.86 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-01 20:00 | 62.56 | 0 | 0 | 60.79 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-01 21:00 | 59.71 | 0 | 0 | 59.71 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 22:00 | 57.05 | 0 | 0 | 57.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-01 23:00 | 54.71 | 0 | 0 | 54.71 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 | 53 | 0 | 0 | 53 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 01:00 | 50.42 | 0 | 0 | 50.42 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 02:00 | 49.11 | 0 | 0 | 49.11 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 03:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 04:00 | 49.65 | 0 | 0 | 49.65 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 05:00 | 50.18 | 28.22 | 28.22 | 21.96 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 06:00 | 52.14 | 85.54 | 55.54 | 0 | 3.4 | 0 | 3.91 | 30.01 | 0
2025-06-02 07:00 | 54.43 | 105.29 | 56.76 | 0 | 2.33 | 0 | 6.12 | 48.54 | 0
2025-06-02 08:00 | 56.88 | 114.17 | 56.88 | 0 | 0 | 0 | 6.12 | 57.29 | 0
2025-06-02 09:00 | 58.32 | 116.57 | 58.32 | 0 | 0 | 0 | 6.12 | 58.25 | 0
2025-06-02 10:00 | 60.29 | 117.43 | 60.29 | 0 | 0 | 0 | 6.12 | 57.14 | 0
2025-06-02 11:00 | 62.32 | 115.6 | 62.32 | 0 | 0 | 0 | 6.12 | 53.29 | 0
2025-06-02 12:00 | 63.57 | 113.86 | 63.57 | 0 | 0 | 0 | 6.12 | 50.3 | 0
2025-06-02 13:00 | 64.61 | 113.78 | 64.61 | 0 | 0 | 0 | 6.12 | 49.16 | 0
2025-06-02 14:00 | 65.76 | 114.74 | 65.76 | 0 | 0 | 0 | 6.12 | 48.97 | 0
2025-06-02 15:00 | 65.53 | 112.94 | 65.53 | 0 | 0 | 0 | 6.12 | 47.41 | 0
2025-06-02 16:00 | 65.54 | 108.82 | 65.54 | 0 | 0 | 0 | 6.12 | 43.27 | 0
2025-06-02 17:00 | 64.32 | 97.42 | 64.32 | 0 | 0 | 0 | 6.12 | 33.09 | 0
2025-06-02 18:00 | 63.82 | 72.76 | 63.82 | 0 | 0 | 0 | 6.12 | 8.94 | 0
2025-06-02 19:00 | 63.05 | 8.52 | 8.52 | 51.13 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-02 20:00 | 61.36 | 0 | 0 | 59.59 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-02 21:00 | 58.64 | 0 | 0 | 58.64 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 22:00 | 56.78 | 0 | 0 | 56.78 | 0 | 0 | 0.68 | 0 | 0
2025-06-02 23:00 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 02:00 | 49.18 | 0 | 0 | 49.18 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 03:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 04:00 | 49.2 | 0 | 0 | 49.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 05:00 | 50.46 | 26.46 | 26.46 | 24 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 06:00 | 51.64 | 85.99 | 55.04 | 0 | 3.4 | 0 | 3.91 | 30.94 | 0
2025-06-03 07:00 | 54.31 | 109.48 | 56.64 | 0 | 2.33 | 0 | 6.12 | 52.84 | 0
2025-06-03 08:00 | 57.49 | 119.12 | 57.49 | 0 | 0 | 0 | 6.12 | 61.64 | 0
2025-06-03 09:00 | 60.38 | 121.73 | 60.38 | 0 | 0 | 0 | 6.12 | 61.35 | 0
2025-06-03 10:00 | 63.01 | 120.87 | 63.01 | 0 | 0 | 0 | 6.12 | 57.86 | 0
2025-06-03 11:00 | 65.78 | 118.83 | 65.78 | 0 | 0 | 0 | 6.12 | 53.05 | 0
2025-06-03 12:00 | 68.06 | 117.59 | 68.06 | 0 | 0 | 0 | 6.12 | 49.53 | 0
2025-06-03 13:00 | 70.1 | 118.27 | 70.1 | 0 | 0 | 0 | 6.12 | 48.17 | 0
2025-06-03 14:00 | 70.62 | 119.1 | 70.62 | 0 | 0 | 0 | 6.12 | 48.48 | 0
2025-06-03 15:00 | 71.21 | 117.31 | 71.21 | 0 | 0 | 0 | 6.12 | 46.1 | 0
2025-06-03 16:00 | 70.4 | 111.01 | 70.4 | 0 | 0 | 0 | 6.12 | 40.61 | 0
2025-06-03 17:00 | 69.94 | 97.52 | 69.94 | 0 | 0 | 0 | 6.12 | 27.57 | 0
2025-06-03 18:00 | 68.22 | 70.09 | 68.22 | 0 | 0 | 0 | 6.12 | 1.87 | 0
2025-06-03 19:00 | 66.3 | 9.96 | 9.96 | 52.95 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-03 20:00 | 63.65 | 0 | 0 | 61.88 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-03 21:00 | 60.76 | 0 | 0 | 60.76 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 22:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 0.68 | 0 | 0
2025-06-03 23:00 | 54.92 | 0 | 0 | 54.92 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 | 53.06 | 0 | 0 | 53.06 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 01:00 | 50.27 | 0 | 0 | 50.27 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 02:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 03:00 | 49.05 | 0 | 0 | 49.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 04:00 | 49.58 | 0 | 0 | 49.58 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 05:00 | 50.18 | 23.1 | 23.1 | 27.08 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 06:00 | 52.49 | 77.45 | 55.89 | 0 | 3.4 | 0 | 3.91 | 21.56 | 0
2025-06-04 07:00 | 55 | 100.88 | 57.33 | 0 | 2.33 | 0 | 6.12 | 43.55 | 0
2025-06-04 08:00 | 56.87 | 111.86 | 56.87 | 0 | 0 | 0 | 6.12 | 54.99 | 0
2025-06-04 09:00 | 61 | 118.01 | 61 | 0 | 0 | 0 | 6.12 | 57.01 | 0
2025-06-04 10:00 | 64.16 | 117.83 | 64.16 | 0 | 0 | 0 | 6.12 | 53.68 | 0
2025-06-04 11:00 | 67.06 | 116.17 | 67.06 | 0 | 0 | 0 | 6.12 | 49.11 | 0
2025-06-04 12:00 | 70.34 | 115.41 | 70.34 | 0 | 0 | 0 | 6.12 | 45.07 | 0
2025-06-04 13:00 | 70.93 | 116.16 | 70.93 | 0 | 0 | 0 | 6.12 | 45.23 | 0
2025-06-04 14:00 | 72.32 | 116.11 | 72.32 | 0 | 0 | 0 | 6.12 | 43.79 | 0
2025-06-04 15:00 | 71.83 | 114.52 | 71.83 | 0 | 0 | 0 | 6.12 | 42.68 | 0
2025-06-04 16:00 | 72.49 | 107.36 | 72.49 | 0 | 0 | 0 | 6.12 | 34.86 | 0
2025-06-04 17:00 | 71.34 | 93.03 | 71.34 | 0 | 0 | 0 | 6.12 | 21.69 | 0
2025-06-04 18:00 | 69.37 | 64.81 | 64.81 | 1.16 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-04 19:00 | 67.69 | 9.78 | 9.78 | 56.14 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-04 20:00 | 64.66 | 0 | 0 | 64.66 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 21:00 | 61.15 | 0 | 0 | 61.15 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 22:00 | 57.79 | 0 | 0 | 57.79 | 0 | 0 | 0.68 | 0 | 0
2025-06-04 23:00 | 55.56 | 0 | 0 | 55.56 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 | 52.81 | 0 | 0 | 52.81 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 01:00 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 02:00 | 48.62 | 0 | 0 | 48.62 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 04:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 05:00 | 51.88 | 18.75 | 18.75 | 33.13 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 06:00 | 52.85 | 64.49 | 56.25 | 0 | 3.4 | 0 | 3.91 | 8.24 | 0
2025-06-05 07:00 | 55.3 | 84.83 | 57.63 | 0 | 2.33 | 0 | 6.12 | 27.2 | 0
2025-06-05 08:00 | 58.64 | 106.6 | 58.64 | 0 | 0 | 0 | 6.12 | 47.96 | 0
2025-06-05 09:00 | 63.57 | 103.18 | 63.57 | 0 | 0 | 0 | 6.12 | 39.61 | 0
2025-06-05 10:00 | 66.73 | 102.33 | 66.73 | 0 | 0 | 0 | 6.12 | 35.6 | 0
2025-06-05 11:00 | 72.15 | 106.94 | 72.15 | 0 | 0 | 0 | 6.12 | 34.79 | 0
2025-06-05 12:00 | 76.12 | 103.54 | 76.12 | 0 | 0 | 0 | 6.12 | 27.42 | 0
2025-06-05 13:00 | 78.99 | 102.44 | 78.99 | 0 | 0 | 0 | 6.12 | 23.45 | 0
2025-06-05 14:00 | 80.64 | 106.76 | 80.64 | 0 | 0 | 0 | 6.12 | 26.12 | 0
2025-06-05 15:00 | 81.72 | 99.97 | 81.72 | 0 | 0 | 0 | 6.12 | 18.25 | 0
2025-06-05 16:00 | 80.84 | 89.19 | 80.84 | 0 | 0 | 0 | 6.12 | 8.35 | 0
2025-06-05 17:00 | 78.39 | 73.16 | 73.16 | 1.83 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-05 18:00 | 76.64 | 52.25 | 52.25 | 22.63 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-05 19:00 | 71.7 | 8.85 | 8.85 | 62.85 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 20:00 | 68 | 0 | 0 | 68 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 21:00 | 62.08 | 0 | 0 | 62.08 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 22:00 | 59.87 | 0 | 0 | 59.87 | 0 | 0 | 0.68 | 0 | 0
2025-06-05 23:00 | 56.42 | 0 | 0 | 56.42 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 | 52.8 | 0 | 0 | 52.8 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 01:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 02:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 04:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 05:00 | 50.41 | 3.27 | 3.27 | 47.14 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 06:00 | 52.48 | 6.99 | 6.99 | 45.49 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 07:00 | 55.93 | 17.27 | 17.27 | 38.65 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 08:00 | 58.87 | 33.84 | 33.84 | 25.03 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 09:00 | 61.3 | 80.72 | 64.7 | 0 | 3.4 | 0 | 3.91 | 16.03 | 0
2025-06-06 10:00 | 64.56 | 129.79 | 66.89 | 0 | 2.33 | 0 | 6.12 | 62.9 | 0
2025-06-06 11:00 | 67.68 | 90.35 | 67.68 | 0 | 0 | 0 | 6.12 | 22.67 | 0
2025-06-06 12:00 | 71.03 | 32.46 | 32.46 | 35.17 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-06 13:00 | 72.2 | 34.49 | 34.49 | 35.94 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-06 14:00 | 74.17 | 29.18 | 29.18 | 44.99 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 15:00 | 74.81 | 35.39 | 35.39 | 39.42 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 16:00 | 73.95 | 3.85 | 3.85 | 70.1 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 17:00 | 73.21 | 2.16 | 2.16 | 71.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 18:00 | 70.51 | 0.63 | 0.63 | 69.87 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 19:00 | 67.9 | 0 | 0 | 67.9 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 20:00 | 64.44 | 0 | 0 | 64.44 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 21:00 | 62.16 | 0 | 0 | 62.16 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 22:00 | 58 | 0 | 0 | 58 | 0 | 0 | 0.68 | 0 | 0
2025-06-06 23:00 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 | 52.94 | 0 | 0 | 52.94 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 01:00 | 50.41 | 0 | 0 | 50.41 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 02:00 | 49.37 | 0 | 0 | 49.37 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 03:00 | 49.94 | 0 | 0 | 49.94 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 04:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 05:00 | 50.43 | 19.15 | 19.15 | 31.28 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 06:00 | 53.13 | 13.31 | 13.31 | 39.83 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 07:00 | 55.66 | 43.2 | 43.2 | 12.46 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 08:00 | 60.78 | 19.19 | 19.19 | 41.59 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 09:00 | 62.91 | 39.6 | 39.6 | 23.31 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 10:00 | 66.43 | 73.82 | 69.83 | 0 | 3.4 | 0 | 3.91 | 3.99 | 0
2025-06-07 11:00 | 71.06 | 87.76 | 73.39 | 0 | 2.33 | 0 | 6.12 | 14.37 | 0
2025-06-07 12:00 | 72.73 | 122.07 | 72.73 | 0 | 0 | 0 | 6.12 | 49.34 | 0
2025-06-07 13:00 | 76.3 | 99.16 | 76.3 | 0 | 0 | 0 | 6.12 | 22.87 | 0
2025-06-07 14:00 | 78.91 | 108.31 | 78.91 | 0 | 0 | 0 | 6.12 | 29.4 | 0
2025-06-07 15:00 | 78.43 | 101.03 | 78.43 | 0 | 0 | 0 | 6.12 | 22.61 | 0
2025-06-07 16:00 | 77.05 | 96.24 | 77.05 | 0 | 0 | 0 | 6.12 | 19.19 | 0
2025-06-07 17:00 | 76.05 | 32.92 | 32.92 | 39.73 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-07 18:00 | 74.38 | 27.11 | 27.11 | 45.5 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-07 19:00 | 70.54 | 4.56 | 4.56 | 65.98 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 20:00 | 66.2 | 0 | 0 | 66.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 21:00 | 62.42 | 0 | 0 | 62.42 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 22:00 | 58.78 | 0 | 0 | 58.78 | 0 | 0 | 0.68 | 0 | 0
2025-06-07 23:00 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 | 53.62 | 0 | 0 | 53.62 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 01:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 02:00 | 50 | 0 | 0 | 50 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 03:00 | 48.68 | 0 | 0 | 48.68 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 04:00 | 49.1 | 0 | 0 | 49.1 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 05:00 | 51.27 | 18.5 | 18.5 | 32.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 06:00 | 52.28 | 18.04 | 18.04 | 34.24 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 07:00 | 55.33 | 75.48 | 58.73 | 0 | 3.4 | 0 | 3.91 | 16.75 | 0
2025-06-08 08:00 | 58.44 | 94.84 | 60.77 | 0 | 2.33 | 0 | 6.12 | 34.07 | 0
2025-06-08 09:00 | 60.7 | 98.08 | 60.7 | 0 | 0 | 0 | 6.12 | 37.38 | 0
2025-06-08 10:00 | 63.66 | 91.39 | 63.66 | 0 | 0 | 0 | 6.12 | 27.72 | 0
2025-06-08 11:00 | 66.77 | 73.79 | 66.77 | 0 | 0 | 0 | 6.12 | 7.03 | 0
2025-06-08 12:00 | 69.28 | 36.52 | 36.52 | 29.35 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-08 13:00 | 71.22 | 60.03 | 60.03 | 9.43 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-08 14:00 | 72.03 | 95.12 | 75.43 | 0 | 3.4 | 0 | 3.91 | 19.69 | 0
2025-06-08 15:00 | 72.11 | 82.69 | 74.44 | 0 | 2.33 | 0 | 6.12 | 8.25 | 0
2025-06-08 16:00 | 71.35 | 62.59 | 62.59 | 5.36 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-08 17:00 | 70.16 | 52.11 | 52.11 | 16.28 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-08 18:00 | 68.77 | 64.21 | 64.21 | 4.56 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 19:00 | 67.02 | 9.76 | 9.76 | 57.26 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 20:00 | 64.34 | 0 | 0 | 64.34 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 21:00 | 60.22 | 0 | 0 | 60.22 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 22:00 | 57.9 | 0 | 0 | 57.9 | 0 | 0 | 0.68 | 0 | 0
2025-06-08 23:00 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 01:00 | 50.39 | 0 | 0 | 50.39 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 02:00 | 51.04 | 0 | 0 | 51.04 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 03:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 04:00 | 50.05 | 0 | 0 | 50.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 05:00 | 51.29 | 24.58 | 24.58 | 26.72 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 06:00 | 52.81 | 79.03 | 56.21 | 0 | 3.4 | 0 | 3.91 | 22.82 | 0
2025-06-09 07:00 | 55.02 | 103.01 | 57.34 | 0 | 2.33 | 0 | 6.12 | 45.67 | 0
2025-06-09 08:00 | 59.07 | 112.22 | 59.07 | 0 | 0 | 0 | 6.12 | 53.15 | 0
2025-06-09 09:00 | 61.15 | 116.22 | 61.15 | 0 | 0 | 0 | 6.12 | 55.07 | 0
2025-06-09 10:00 | 63.53 | 118.83 | 63.53 | 0 | 0 | 0 | 6.12 | 55.3 | 0
2025-06-09 11:00 | 65.54 | 116.54 | 65.54 | 0 | 0 | 0 | 6.12 | 51 | 0
2025-06-09 12:00 | 66.46 | 115.36 | 66.46 | 0 | 0 | 0 | 6.12 | 48.89 | 0
2025-06-09 13:00 | 68.84 | 115.39 | 68.84 | 0 | 0 | 0 | 6.12 | 46.55 | 0
2025-06-09 14:00 | 68.52 | 114.89 | 68.52 | 0 | 0 | 0 | 6.12 | 46.37 | 0
2025-06-09 15:00 | 69.33 | 113.16 | 69.33 | 0 | 0 | 0 | 6.12 | 43.83 | 0
2025-06-09 16:00 | 68.12 | 107.98 | 68.12 | 0 | 0 | 0 | 6.12 | 39.85 | 0
2025-06-09 17:00 | 67.18 | 95.84 | 67.18 | 0 | 0 | 0 | 6.12 | 28.66 | 0
2025-06-09 18:00 | 67.13 | 70.03 | 67.13 | 0 | 0 | 0 | 6.12 | 2.9 | 0
2025-06-09 19:00 | 64.85 | 12.74 | 12.74 | 48.71 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-09 20:00 | 62.12 | 0 | 0 | 60.36 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-09 21:00 | 60.92 | 0 | 0 | 60.92 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 22:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 0.68 | 0 | 0
2025-06-09 23:00 | 56.07 | 0 | 0 | 56.07 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 | 53 | 0 | 0 | 53 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 01:00 | 51.2 | 0 | 0 | 51.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 02:00 | 50.4 | 0 | 0 | 50.4 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 03:00 | 50.09 | 0 | 0 | 50.09 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 04:00 | 49.78 | 0 | 0 | 49.78 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 05:00 | 51.22 | 20.67 | 20.67 | 30.55 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 06:00 | 53.28 | 65.83 | 56.68 | 0 | 3.4 | 0 | 3.91 | 9.15 | 0
2025-06-10 07:00 | 55.84 | 68.69 | 58.17 | 0 | 2.33 | 0 | 6.12 | 10.52 | 0
2025-06-10 08:00 | 58.21 | 91.61 | 58.21 | 0 | 0 | 0 | 6.12 | 33.4 | 0
2025-06-10 09:00 | 60.99 | 98.19 | 60.99 | 0 | 0 | 0 | 6.12 | 37.2 | 0
2025-06-10 10:00 | 64.37 | 104.41 | 64.37 | 0 | 0 | 0 | 6.12 | 40.04 | 0
2025-06-10 11:00 | 66.6 | 105.08 | 66.6 | 0 | 0 | 0 | 6.12 | 38.48 | 0
2025-06-10 12:00 | 68.12 | 106.76 | 68.12 | 0 | 0 | 0 | 6.12 | 38.64 | 0
2025-06-10 13:00 | 70.12 | 111.06 | 70.12 | 0 | 0 | 0 | 6.12 | 40.94 | 0
2025-06-10 14:00 | 69.91 | 111.34 | 69.91 | 0 | 0 | 0 | 6.12 | 41.43 | 0
2025-06-10 15:00 | 71.19 | 103.69 | 71.19 | 0 | 0 | 0 | 6.12 | 32.49 | 0
2025-06-10 16:00 | 70.37 | 106.29 | 70.37 | 0 | 0 | 0 | 6.12 | 35.92 | 0
2025-06-10 17:00 | 70.9 | 88.93 | 70.9 | 0 | 0 | 0 | 6.12 | 18.03 | 0
2025-06-10 18:00 | 67.28 | 58.76 | 58.76 | 5.13 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-10 19:00 | 65.65 | 11.54 | 11.54 | 52.34 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-10 20:00 | 63.89 | 0 | 0 | 63.89 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 21:00 | 61.25 | 0 | 0 | 61.25 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 22:00 | 59.25 | 0 | 0 | 59.25 | 0 | 0 | 0.68 | 0 | 0
2025-06-10 23:00 | 55.23 | 0 | 0 | 55.23 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 | 53.71 | 0 | 0 | 53.71 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 01:00 | 51.88 | 0 | 0 | 51.88 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 02:00 | 50.4 | 0 | 0 | 50.4 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 03:00 | 49.14 | 0 | 0 | 49.14 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 04:00 | 50.75 | 0 | 0 | 50.75 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 05:00 | 51.92 | 25.02 | 25.02 | 26.89 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 06:00 | 53.56 | 67.06 | 56.96 | 0 | 3.4 | 0 | 3.91 | 10.1 | 0
2025-06-11 07:00 | 55.85 | 88.62 | 58.18 | 0 | 2.33 | 0 | 6.12 | 30.44 | 0
2025-06-11 08:00 | 58.68 | 119.08 | 58.68 | 0 | 0 | 0 | 6.12 | 60.41 | 0
2025-06-11 09:00 | 61.43 | 128.89 | 61.43 | 0 | 0 | 0 | 6.12 | 67.45 | 0
2025-06-11 10:00 | 64.59 | 129.16 | 64.59 | 0 | 0 | 0 | 6.12 | 64.57 | 0
2025-06-11 11:00 | 66.8 | 85.62 | 66.8 | 0 | 0 | 0 | 6.12 | 18.82 | 0
2025-06-11 12:00 | 68.44 | 65.97 | 65.97 | 0 | 0 | 2.46 | 3.53 | 0 | 0
2025-06-11 13:00 | 69.88 | 67.34 | 67.34 | 0 | 0 | 2.54 | 0.86 | 0 | 0
2025-06-11 14:00 | 70.98 | 47.51 | 47.51 | 23.3 | 0 | 0.17 | 0.68 | 0 | 0
2025-06-11 15:00 | 71.79 | 23.87 | 23.87 | 47.91 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 16:00 | 71.34 | 17.39 | 17.39 | 53.95 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 17:00 | 70.51 | 5.43 | 5.43 | 65.08 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 18:00 | 69.11 | 0.76 | 0.76 | 68.35 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 19:00 | 66.47 | 0 | 0 | 66.47 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 20:00 | 65.01 | 0 | 0 | 65.01 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 21:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 22:00 | 58.35 | 0 | 0 | 58.35 | 0 | 0 | 0.68 | 0 | 0
2025-06-11 23:00 | 55.99 | 0 | 0 | 55.99 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 | 52.73 | 0 | 0 | 52.73 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 01:00 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 04:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 05:00 | 52.21 | 23.48 | 23.48 | 28.73 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 06:00 | 53.46 | 71.72 | 56.86 | 0 | 3.4 | 0 | 3.91 | 14.85 | 0
2025-06-12 07:00 | 56.84 | 98.38 | 59.16 | 0 | 2.33 | 0 | 6.12 | 39.22 | 0
2025-06-12 08:00 | 61.06 | 106.83 | 61.06 | 0 | 0 | 0 | 6.12 | 45.78 | 0
2025-06-12 09:00 | 64.66 | 110.99 | 64.66 | 0 | 0 | 0 | 6.12 | 46.33 | 0
2025-06-12 10:00 | 70.06 | 115.39 | 70.06 | 0 | 0 | 0 | 6.12 | 45.33 | 0
2025-06-12 11:00 | 73.99 | 113.4 | 73.99 | 0 | 0 | 0 | 6.12 | 39.41 | 0
2025-06-12 12:00 | 78.35 | 113.32 | 78.35 | 0 | 0 | 0 | 6.12 | 34.97 | 0
2025-06-12 13:00 | 81.6 | 111.26 | 81.6 | 0 | 0 | 0 | 6.12 | 29.66 | 0
2025-06-12 14:00 | 84.38 | 111.27 | 84.38 | 0 | 0 | 0 | 6.12 | 26.89 | 0
2025-06-12 15:00 | 85.55 | 109.98 | 85.55 | 0 | 0 | 0 | 6.12 | 24.43 | 0
2025-06-12 16:00 | 84.12 | 108.16 | 84.12 | 0 | 0 | 0 | 6.12 | 24.05 | 0
2025-06-12 17:00 | 81.36 | 86.01 | 81.36 | 0 | 0 | 0 | 6.12 | 4.65 | 0
2025-06-12 18:00 | 78.04 | 60.74 | 60.74 | 13.9 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-12 19:00 | 74.52 | 14.14 | 14.14 | 58.61 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-12 20:00 | 70.54 | 0 | 0 | 70.54 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 21:00 | 65.09 | 0 | 0 | 65.09 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 22:00 | 60.3 | 0 | 0 | 60.3 | 0 | 0 | 0.68 | 0 | 0
2025-06-12 23:00 | 57.07 | 0 | 0 | 57.07 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 01:00 | 51.3 | 0 | 0 | 51.3 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 02:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 03:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 04:00 | 48.96 | 0 | 0 | 48.96 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 05:00 | 51.89 | 22.46 | 22.46 | 29.43 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 06:00 | 53.23 | 19.46 | 19.46 | 33.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 07:00 | 55.75 | 53.32 | 53.32 | 2.44 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 08:00 | 59.61 | 23.47 | 23.47 | 36.14 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 09:00 | 61.3 | 63.45 | 63.45 | 0 | 2.15 | 0 | 2.72 | 0 | 0
2025-06-13 10:00 | 64.08 | 92.13 | 67.48 | 0 | 3.4 | 0 | 5.95 | 24.65 | 0
2025-06-13 11:00 | 66.81 | 86.6 | 66.99 | 0 | 0.18 | 0 | 6.12 | 19.61 | 0
2025-06-13 12:00 | 69.11 | 16.89 | 16.89 | 48.82 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-13 13:00 | 70.18 | 76.48 | 73.58 | 0 | 3.4 | 0 | 5.77 | 2.91 | 0
2025-06-13 14:00 | 70.53 | 76.07 | 70.9 | 0 | 0.37 | 0 | 6.12 | 5.18 | 0
2025-06-13 15:00 | 71.19 | 41.92 | 41.92 | 25.88 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-13 16:00 | 71.96 | 49.33 | 49.33 | 20.86 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-13 17:00 | 70.44 | 5.93 | 5.93 | 64.5 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 18:00 | 69.13 | 59.11 | 59.11 | 10.02 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 19:00 | 66.75 | 1.14 | 1.14 | 65.6 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 20:00 | 64.09 | 0 | 0 | 64.09 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 21:00 | 62.49 | 0 | 0 | 62.49 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 22:00 | 58.67 | 0 | 0 | 58.67 | 0 | 0 | 0.68 | 0 | 0
2025-06-13 23:00 | 55.74 | 0 | 0 | 55.74 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 01:00 | 51.26 | 0 | 0 | 51.26 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 02:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 03:00 | 49.88 | 0 | 0 | 49.88 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 04:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 05:00 | 51.75 | 27.39 | 27.39 | 24.35 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 06:00 | 54.77 | 65.14 | 58.17 | 0 | 3.4 | 0 | 3.91 | 6.96 | 0
2025-06-14 07:00 | 56.72 | 96.14 | 59.05 | 0 | 2.33 | 0 | 6.12 | 37.09 | 0
2025-06-14 08:00 | 58.76 | 86.57 | 58.76 | 0 | 0 | 0 | 6.12 | 27.8 | 0
2025-06-14 09:00 | 63.88 | 60.74 | 60.74 | 0 | 0 | 3.15 | 2.81 | 0 | 0
2025-06-14 10:00 | 67.64 | 71.66 | 71.04 | 0 | 3.4 | 0 | 6.04 | 0.62 | 0
2025-06-14 11:00 | 71.39 | 123.15 | 71.48 | 0 | 0.09 | 0 | 6.12 | 51.67 | 0
2025-06-14 12:00 | 74.8 | 104.69 | 74.8 | 0 | 0 | 0 | 6.12 | 29.89 | 0
2025-06-14 13:00 | 77.26 | 60.72 | 60.72 | 13.15 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-14 14:00 | 78.91 | 63.53 | 63.53 | 13.61 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-14 15:00 | 79.81 | 104.97 | 83.21 | 0 | 3.4 | 0 | 3.91 | 21.76 | 0
2025-06-14 16:00 | 78.66 | 122.41 | 80.99 | 0 | 2.33 | 0 | 6.12 | 41.42 | 0
2025-06-14 17:00 | 76.8 | 111.53 | 76.8 | 0 | 0 | 0 | 6.12 | 34.73 | 0
2025-06-14 18:00 | 76.19 | 85.52 | 76.19 | 0 | 0 | 0 | 6.12 | 9.32 | 0
2025-06-14 19:00 | 71.01 | 18.72 | 18.72 | 48.89 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-14 20:00 | 67.67 | 0 | 0 | 65.9 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-14 21:00 | 62.97 | 0 | 0 | 62.97 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 22:00 | 60.01 | 0 | 0 | 60.01 | 0 | 0 | 0.68 | 0 | 0
2025-06-14 23:00 | 56.09 | 0 | 0 | 56.09 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 | 53.43 | 0 | 0 | 53.43 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 01:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 03:00 | 50.24 | 0 | 0 | 50.24 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 04:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 05:00 | 52.59 | 24.19 | 24.19 | 28.4 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 06:00 | 53.06 | 47.97 | 47.97 | 5.09 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 07:00 | 56.93 | 94.91 | 60.33 | 0 | 3.4 | 0 | 3.91 | 34.59 | 0
2025-06-15 08:00 | 59.48 | 68.88 | 61.8 | 0 | 2.33 | 0 | 6.12 | 7.07 | 0
2025-06-15 09:00 | 62.13 | 105.04 | 62.13 | 0 | 0 | 0 | 6.12 | 42.91 | 0
2025-06-15 10:00 | 64.15 | 90.88 | 64.15 | 0 | 0 | 0 | 6.12 | 26.74 | 0
2025-06-15 11:00 | 67.07 | 103.41 | 67.07 | 0 | 0 | 0 | 6.12 | 36.34 | 0
2025-06-15 12:00 | 68.74 | 105.96 | 68.74 | 0 | 0 | 0 | 6.12 | 37.22 | 0
2025-06-15 13:00 | 70.45 | 112.26 | 70.45 | 0 | 0 | 0 | 6.12 | 41.81 | 0
2025-06-15 14:00 | 71.2 | 106.18 | 71.2 | 0 | 0 | 0 | 6.12 | 34.98 | 0
2025-06-15 15:00 | 70.6 | 81.22 | 70.6 | 0 | 0 | 0 | 6.12 | 10.62 | 0
2025-06-15 16:00 | 71.88 | 80.12 | 71.88 | 0 | 0 | 0 | 6.12 | 8.24 | 0
2025-06-15 17:00 | 70.39 | 67.17 | 67.17 | 0 | 0 | 3.22 | 2.73 | 0 | 0
2025-06-15 18:00 | 68.73 | 56.61 | 56.61 | 10.17 | 0 | 1.95 | 0.68 | 0 | 0
2025-06-15 19:00 | 66.71 | 20.37 | 20.37 | 46.34 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 20:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 21:00 | 61.39 | 0 | 0 | 61.39 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 22:00 | 57.84 | 0 | 0 | 57.84 | 0 | 0 | 0.68 | 0 | 0
2025-06-15 23:00 | 56.37 | 0 | 0 | 56.37 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 | 54.2 | 0 | 0 | 54.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 01:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 02:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 03:00 | 50.08 | 0 | 0 | 50.08 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 04:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 05:00 | 51.29 | 33.48 | 33.48 | 17.81 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 06:00 | 53.56 | 108.26 | 56.96 | 0 | 3.4 | 0 | 3.91 | 51.29 | 0
2025-06-16 07:00 | 57.23 | 128.84 | 59.56 | 0 | 2.33 | 0 | 6.12 | 69.29 | 0
2025-06-16 08:00 | 60.08 | 137.15 | 60.08 | 0 | 0 | 0 | 6.12 | 77.06 | 0
2025-06-16 09:00 | 63.9 | 134.32 | 63.9 | 0 | 0 | 0 | 6.12 | 70.42 | 0
2025-06-16 10:00 | 69.1 | 121.64 | 69.1 | 0 | 0 | 0 | 6.12 | 52.54 | 0
2025-06-16 11:00 | 72.15 | 99.58 | 72.15 | 0 | 0 | 0 | 6.12 | 27.43 | 0
2025-06-16 12:00 | 75.56 | 86.85 | 75.56 | 0 | 0 | 0 | 6.12 | 11.29 | 0
2025-06-16 13:00 | 77.89 | 81.28 | 77.89 | 0 | 0 | 0 | 6.12 | 3.39 | 0
2025-06-16 14:00 | 79.49 | 67.11 | 67.11 | 8.98 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-16 15:00 | 79.28 | 38.57 | 38.57 | 38.95 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-16 16:00 | 80.27 | 29.7 | 29.7 | 50.57 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 17:00 | 78.3 | 16.19 | 16.19 | 62.11 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 18:00 | 75.3 | 7.39 | 7.39 | 67.91 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 19:00 | 71.91 | 0 | 0 | 71.9 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 20:00 | 68.49 | 0 | 0 | 68.49 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 21:00 | 63.34 | 0 | 0 | 63.34 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 22:00 | 59.97 | 0 | 0 | 59.97 | 0 | 0 | 0.68 | 0 | 0
2025-06-16 23:00 | 56.24 | 0 | 0 | 56.24 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 | 54.86 | 0 | 0 | 54.86 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 01:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 02:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 03:00 | 49.36 | 0 | 0 | 49.36 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 04:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 05:00 | 51.64 | 2.53 | 2.53 | 49.11 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 06:00 | 53.32 | 7.82 | 7.82 | 45.5 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 07:00 | 57.73 | 54.5 | 54.5 | 3.23 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 08:00 | 60.19 | 65.83 | 63.59 | 0 | 3.4 | 0 | 3.91 | 2.23 | 0
2025-06-17 09:00 | 63.86 | 91.73 | 66.18 | 0 | 2.33 | 0 | 6.12 | 25.55 | 0
2025-06-17 10:00 | 66.91 | 71.58 | 66.91 | 0 | 0 | 0 | 6.12 | 4.66 | 0
2025-06-17 11:00 | 71.07 | 61.89 | 61.89 | 5.78 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-17 12:00 | 73.52 | 58.06 | 58.06 | 13.69 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-17 13:00 | 75.9 | 36.21 | 36.21 | 39.69 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 14:00 | 77.82 | 34.42 | 34.42 | 43.4 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 15:00 | 77.21 | 50.88 | 50.88 | 26.33 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 16:00 | 78.32 | 110.84 | 81.72 | 0 | 3.4 | 0 | 3.91 | 29.12 | 0
2025-06-17 17:00 | 76.13 | 58.92 | 58.92 | 14.14 | 0 | 3.07 | 0.68 | 0 | 0
2025-06-17 18:00 | 74.35 | 74.35 | 74.35 | 0 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 19:00 | 70.17 | 20.47 | 20.47 | 49.7 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 20:00 | 66.8 | 0 | 0 | 66.8 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 21:00 | 63.04 | 0 | 0 | 63.04 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 22:00 | 60.16 | 0 | 0 | 60.16 | 0 | 0 | 0.68 | 0 | 0
2025-06-17 23:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 | 53.79 | 0 | 0 | 53.79 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 01:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 02:00 | 50.01 | 0 | 0 | 50.01 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 03:00 | 50.17 | 0 | 0 | 50.17 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 04:00 | 50.41 | 0 | 0 | 50.41 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 05:00 | 51.61 | 24.19 | 24.19 | 27.42 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 06:00 | 54.79 | 82.69 | 58.19 | 0 | 3.4 | 0 | 3.91 | 24.5 | 0
2025-06-18 07:00 | 56.66 | 89.71 | 58.99 | 0 | 2.33 | 0 | 6.12 | 30.72 | 0
2025-06-18 08:00 | 60.44 | 76.48 | 60.44 | 0 | 0 | 0 | 6.12 | 16.03 | 0
2025-06-18 09:00 | 62.85 | 126.23 | 62.85 | 0 | 0 | 0 | 6.12 | 63.38 | 0
2025-06-18 10:00 | 66.52 | 114.39 | 66.52 | 0 | 0 | 0 | 6.12 | 47.87 | 0
2025-06-18 11:00 | 69.41 | 113.42 | 69.41 | 0 | 0 | 0 | 6.12 | 44 | 0
2025-06-18 12:00 | 71.18 | 91.99 | 71.18 | 0 | 0 | 0 | 6.12 | 20.82 | 0
2025-06-18 13:00 | 74.72 | 97.81 | 74.72 | 0 | 0 | 0 | 6.12 | 23.09 | 0
2025-06-18 14:00 | 75.18 | 74.44 | 74.44 | 0 | 0 | 0.74 | 5.35 | 0 | 0
2025-06-18 15:00 | 76.04 | 49.89 | 49.89 | 22.75 | 0 | 3.4 | 1.77 | 0 | 0
2025-06-18 16:00 | 74.87 | 35.37 | 35.37 | 38.46 | 0 | 1.03 | 0.68 | 0 | 0
2025-06-18 17:00 | 73.92 | 26.15 | 26.15 | 47.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 18:00 | 71.6 | 1.53 | 1.53 | 70.07 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 19:00 | 70.06 | 0.26 | 0.26 | 69.8 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 20:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 21:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 22:00 | 60.49 | 0 | 0 | 60.49 | 0 | 0 | 0.68 | 0 | 0
2025-06-18 23:00 | 57.28 | 0 | 0 | 57.28 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 01:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 02:00 | 50.37 | 0 | 0 | 50.37 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 03:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 04:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 05:00 | 52.12 | 11.85 | 11.85 | 40.27 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 06:00 | 53.43 | 55.3 | 55.3 | 0 | 1.87 | 0 | 2.46 | 0 | 0
2025-06-19 07:00 | 56.74 | 90.86 | 60.14 | 0 | 3.4 | 0 | 5.69 | 30.71 | 0
2025-06-19 08:00 | 59.25 | 112.68 | 59.71 | 0 | 0.46 | 0 | 6.12 | 52.97 | 0
2025-06-19 09:00 | 63.36 | 113.8 | 63.36 | 0 | 0 | 0 | 6.12 | 50.44 | 0
2025-06-19 10:00 | 65.93 | 109.24 | 65.93 | 0 | 0 | 0 | 6.12 | 43.3 | 0
2025-06-19 11:00 | 70.17 | 103.82 | 70.17 | 0 | 0 | 0 | 6.12 | 33.65 | 0
2025-06-19 12:00 | 72.78 | 101.62 | 72.78 | 0 | 0 | 0 | 6.12 | 28.84 | 0
2025-06-19 13:00 | 75.61 | 103.29 | 75.61 | 0 | 0 | 0 | 6.12 | 27.68 | 0
2025-06-19 14:00 | 76.38 | 98.56 | 76.38 | 0 | 0 | 0 | 6.12 | 22.18 | 0
2025-06-19 15:00 | 76.19 | 90.87 | 76.19 | 0 | 0 | 0 | 6.12 | 14.68 | 0
2025-06-19 16:00 | 76.37 | 78.14 | 76.37 | 0 | 0 | 0 | 6.12 | 1.77 | 0
2025-06-19 17:00 | 73.96 | 54.17 | 54.17 | 16.39 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-19 18:00 | 72.11 | 33.87 | 33.87 | 36.48 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-19 19:00 | 70.07 | 8.45 | 8.45 | 61.62 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 20:00 | 65.68 | 0 | 0 | 65.68 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 21:00 | 63.36 | 0 | 0 | 63.36 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 22:00 | 59.49 | 0 | 0 | 59.49 | 0 | 0 | 0.68 | 0 | 0
2025-06-19 23:00 | 56.89 | 0 | 0 | 56.89 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 | 53.61 | 0 | 0 | 53.61 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 01:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 02:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 03:00 | 51.05 | 0 | 0 | 51.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 04:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 05:00 | 51.72 | 25.01 | 25.01 | 26.71 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 06:00 | 54.03 | 81.65 | 57.43 | 0 | 3.4 | 0 | 3.91 | 24.23 | 0
2025-06-20 07:00 | 56.09 | 108.1 | 58.41 | 0 | 2.33 | 0 | 6.12 | 49.69 | 0
2025-06-20 08:00 | 59.91 | 120.57 | 59.91 | 0 | 0 | 0 | 6.12 | 60.66 | 0
2025-06-20 09:00 | 63.08 | 124.42 | 63.08 | 0 | 0 | 0 | 6.12 | 61.34 | 0
2025-06-20 10:00 | 66.98 | 124.96 | 66.98 | 0 | 0 | 0 | 6.12 | 57.98 | 0
2025-06-20 11:00 | 68.1 | 123.57 | 68.1 | 0 | 0 | 0 | 6.12 | 55.47 | 0
2025-06-20 12:00 | 70.5 | 122.57 | 70.5 | 0 | 0 | 0 | 6.12 | 52.07 | 0
2025-06-20 13:00 | 72 | 109.1 | 72 | 0 | 0 | 0 | 6.12 | 37.1 | 0
2025-06-20 14:00 | 73.42 | 42.5 | 42.5 | 27.52 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-20 15:00 | 73.85 | 47.09 | 47.09 | 24.99 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-20 16:00 | 73.29 | 41.03 | 41.03 | 32.25 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 17:00 | 72.83 | 98.21 | 76.23 | 0 | 3.4 | 0 | 3.91 | 21.98 | 0
2025-06-20 18:00 | 70.32 | 74.96 | 72.65 | 0 | 2.33 | 0 | 6.12 | 2.31 | 0
2025-06-20 19:00 | 68.91 | 17.57 | 17.57 | 47.94 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-20 20:00 | 66.01 | 0 | 0 | 64.25 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-20 21:00 | 62.77 | 0 | 0 | 62.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 22:00 | 59.55 | 0 | 0 | 59.55 | 0 | 0 | 0.68 | 0 | 0
2025-06-20 23:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 | 53.94 | 0 | 0 | 53.94 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 01:00 | 52.35 | 0 | 0 | 52.35 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 02:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 03:00 | 51.31 | 0 | 0 | 51.31 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 04:00 | 51.31 | 0 | 0 | 51.31 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 05:00 | 51.87 | 13.05 | 13.05 | 38.82 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 06:00 | 54.61 | 61.58 | 58.01 | 0 | 3.4 | 0 | 3.91 | 3.58 | 0
2025-06-21 07:00 | 57.31 | 96.5 | 59.64 | 0 | 2.33 | 0 | 6.12 | 36.86 | 0
2025-06-21 08:00 | 60.28 | 109.14 | 60.28 | 0 | 0 | 0 | 6.12 | 48.86 | 0
2025-06-21 09:00 | 64.59 | 119.79 | 64.59 | 0 | 0 | 0 | 6.12 | 55.2 | 0
2025-06-21 10:00 | 68.16 | 119.38 | 68.16 | 0 | 0 | 0 | 6.12 | 51.22 | 0
2025-06-21 11:00 | 71.62 | 109.79 | 71.62 | 0 | 0 | 0 | 6.12 | 38.17 | 0
2025-06-21 12:00 | 74.59 | 94.08 | 74.59 | 0 | 0 | 0 | 6.12 | 19.49 | 0
2025-06-21 13:00 | 77.24 | 106.55 | 77.24 | 0 | 0 | 0 | 6.12 | 29.31 | 0
2025-06-21 14:00 | 78.67 | 122.68 | 78.67 | 0 | 0 | 0 | 6.12 | 44.02 | 0
2025-06-21 15:00 | 79.11 | 126.38 | 79.11 | 0 | 0 | 0 | 6.12 | 47.27 | 0
2025-06-21 16:00 | 78.23 | 121.83 | 78.23 | 0 | 0 | 0 | 6.12 | 43.6 | 0
2025-06-21 17:00 | 77.87 | 110.23 | 77.87 | 0 | 0 | 0 | 6.12 | 32.36 | 0
2025-06-21 18:00 | 74.09 | 84.98 | 74.09 | 0 | 0 | 0 | 6.12 | 10.88 | 0
2025-06-21 19:00 | 71.73 | 20.53 | 20.53 | 47.8 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-21 20:00 | 67.8 | 0 | 0 | 66.03 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-21 21:00 | 65.1 | 0 | 0 | 65.1 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 22:00 | 60.09 | 0 | 0 | 60.09 | 0 | 0 | 0.68 | 0 | 0
2025-06-21 23:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 | 53.86 | 0 | 0 | 53.86 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 01:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 02:00 | 50.26 | 0 | 0 | 50.26 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 03:00 | 50.25 | 0 | 0 | 50.25 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 04:00 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 05:00 | 52.38 | 8.82 | 8.82 | 43.56 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 06:00 | 54.09 | 49.29 | 49.29 | 4.81 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 07:00 | 56.27 | 27.74 | 27.74 | 28.53 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 08:00 | 60.6 | 62.99 | 62.99 | 0 | 2.39 | 0 | 2.95 | 0 | 0
2025-06-22 09:00 | 62.61 | 92.17 | 65.94 | 0 | 3.33 | 0 | 6.12 | 26.23 | 0
2025-06-22 10:00 | 66.79 | 91.21 | 66.79 | 0 | 0 | 0 | 6.12 | 24.42 | 0
2025-06-22 11:00 | 68.89 | 97.39 | 68.89 | 0 | 0 | 0 | 6.12 | 28.5 | 0
2025-06-22 12:00 | 72.43 | 92.7 | 72.43 | 0 | 0 | 0 | 6.12 | 20.27 | 0
2025-06-22 13:00 | 73.81 | 96.58 | 73.81 | 0 | 0 | 0 | 6.12 | 22.77 | 0
2025-06-22 14:00 | 74.06 | 108.73 | 74.06 | 0 | 0 | 0 | 6.12 | 34.67 | 0
2025-06-22 15:00 | 74.48 | 79.6 | 74.48 | 0 | 0 | 0 | 6.12 | 5.12 | 0
2025-06-22 16:00 | 74.86 | 88.4 | 74.86 | 0 | 0 | 0 | 6.12 | 13.54 | 0
2025-06-22 17:00 | 73.31 | 63.14 | 63.14 | 6.77 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-22 18:00 | 71.55 | 11.07 | 11.07 | 58.71 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-22 19:00 | 69.87 | 2.67 | 2.67 | 67.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 20:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 21:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 22:00 | 60.54 | 0 | 0 | 60.54 | 0 | 0 | 0.68 | 0 | 0
2025-06-22 23:00 | 57.41 | 0 | 0 | 57.41 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 | 54.27 | 0 | 0 | 54.27 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 01:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 02:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 03:00 | 50.03 | 0 | 0 | 50.03 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 04:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 05:00 | 52.25 | 8.74 | 8.74 | 43.52 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 06:00 | 54.38 | 39.08 | 39.08 | 15.3 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 07:00 | 57.39 | 57.81 | 57.81 | 0 | 0.42 | 0 | 1.08 | 0 | 0
2025-06-23 08:00 | 59.06 | 61.35 | 61.35 | 0 | 2.29 | 0 | 3.25 | 0 | 0
2025-06-23 09:00 | 62.33 | 74.41 | 65.35 | 0 | 3.02 | 0 | 6.12 | 9.06 | 0
2025-06-23 10:00 | 65.14 | 108.2 | 65.14 | 0 | 0 | 0 | 6.12 | 43.05 | 0
2025-06-23 11:00 | 66.94 | 115.94 | 66.94 | 0 | 0 | 0 | 6.12 | 49 | 0
2025-06-23 12:00 | 69.79 | 116.05 | 69.79 | 0 | 0 | 0 | 6.12 | 46.25 | 0
2025-06-23 13:00 | 70.82 | 99.38 | 70.82 | 0 | 0 | 0 | 6.12 | 28.56 | 0
2025-06-23 14:00 | 71.28 | 97.38 | 71.28 | 0 | 0 | 0 | 6.12 | 26.1 | 0
2025-06-23 15:00 | 72.29 | 92.9 | 72.29 | 0 | 0 | 0 | 6.12 | 20.61 | 0
2025-06-23 16:00 | 70.38 | 55.51 | 55.51 | 11.48 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-23 17:00 | 70.36 | 50.25 | 50.25 | 18.35 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-23 18:00 | 69.26 | 20.26 | 20.26 | 49 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 19:00 | 66.83 | 6.24 | 6.24 | 60.59 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 20:00 | 65.2 | 0 | 0 | 65.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 21:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 22:00 | 60 | 0 | 0 | 60 | 0 | 0 | 0.68 | 0 | 0
2025-06-23 23:00 | 57.4 | 0 | 0 | 57.4 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 01:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 02:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 03:00 | 50.91 | 0 | 0 | 50.91 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 04:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 05:00 | 51.05 | 21.29 | 21.29 | 29.76 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 06:00 | 55.04 | 73.65 | 58.44 | 0 | 3.4 | 0 | 3.91 | 15.21 | 0
2025-06-24 07:00 | 57.01 | 92.31 | 59.34 | 0 | 2.33 | 0 | 6.12 | 32.97 | 0
2025-06-24 08:00 | 59.31 | 102.51 | 59.31 | 0 | 0 | 0 | 6.12 | 43.2 | 0
2025-06-24 09:00 | 62.99 | 107.06 | 62.99 | 0 | 0 | 0 | 6.12 | 44.06 | 0
2025-06-24 10:00 | 64.73 | 103.39 | 64.73 | 0 | 0 | 0 | 6.12 | 38.66 | 0
2025-06-24 11:00 | 66.93 | 102.34 | 66.93 | 0 | 0 | 0 | 6.12 | 35.41 | 0
2025-06-24 12:00 | 69.21 | 103.38 | 69.21 | 0 | 0 | 0 | 6.12 | 34.17 | 0
2025-06-24 13:00 | 71.17 | 102.41 | 71.17 | 0 | 0 | 0 | 6.12 | 31.23 | 0
2025-06-24 14:00 | 71.84 | 106.34 | 71.84 | 0 | 0 | 0 | 6.12 | 34.5 | 0
2025-06-24 15:00 | 71.46 | 110.41 | 71.46 | 0 | 0 | 0 | 6.12 | 38.95 | 0
2025-06-24 16:00 | 71.26 | 96.48 | 71.26 | 0 | 0 | 0 | 6.12 | 25.22 | 0
2025-06-24 17:00 | 70.68 | 77.93 | 70.68 | 0 | 0 | 0 | 6.12 | 7.25 | 0
2025-06-24 18:00 | 68.4 | 64.02 | 64.02 | 0.98 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-24 19:00 | 67.6 | 12.92 | 12.92 | 52.91 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-24 20:00 | 64.7 | 0 | 0 | 64.7 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 21:00 | 62.65 | 0 | 0 | 62.65 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 22:00 | 59.6 | 0 | 0 | 59.6 | 0 | 0 | 0.68 | 0 | 0
2025-06-24 23:00 | 57.2 | 0 | 0 | 57.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 | 54.71 | 0 | 0 | 54.71 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 01:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 02:00 | 51.24 | 0 | 0 | 51.24 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 03:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 04:00 | 51.37 | 0 | 0 | 51.37 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 05:00 | 52.44 | 2.55 | 2.55 | 49.9 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 06:00 | 55.47 | 9.48 | 9.48 | 45.99 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 07:00 | 57.63 | 22.43 | 22.43 | 35.19 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 08:00 | 61 | 30.7 | 30.7 | 30.3 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 09:00 | 64.88 | 36.5 | 36.5 | 28.38 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 10:00 | 68.14 | 38.23 | 38.23 | 29.91 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 11:00 | 70.9 | 40.85 | 40.85 | 30.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 12:00 | 73.06 | 59.97 | 59.97 | 13.08 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 13:00 | 76.3 | 55.71 | 55.71 | 20.58 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 14:00 | 78.34 | 45.82 | 45.82 | 32.52 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 15:00 | 78.27 | 82.1 | 81.67 | 0 | 3.4 | 0 | 3.91 | 0.43 | 0
2025-06-25 16:00 | 78.36 | 66 | 66 | 9.29 | 0 | 3.07 | 0.68 | 0 | 0
2025-06-25 17:00 | 76.61 | 70.2 | 70.2 | 6.41 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 18:00 | 74.92 | 80.9 | 78.32 | 0 | 3.4 | 0 | 3.91 | 2.58 | 0
2025-06-25 19:00 | 71.2 | 24.3 | 24.3 | 43.83 | 0 | 3.07 | 0.68 | 0 | 0
2025-06-25 20:00 | 68.2 | 0 | 0 | 68.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 21:00 | 64.61 | 0 | 0 | 64.61 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 22:00 | 61.53 | 0 | 0 | 61.53 | 0 | 0 | 0.68 | 0 | 0
2025-06-25 23:00 | 56.62 | 0 | 0 | 56.62 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 01:00 | 53.02 | 0 | 0 | 53.02 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 02:00 | 51.99 | 0 | 0 | 51.99 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 03:00 | 50.87 | 0 | 0 | 50.87 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 04:00 | 51.07 | 0 | 0 | 51.07 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 05:00 | 52.97 | 3.21 | 3.21 | 49.76 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 06:00 | 55.31 | 13.27 | 13.27 | 42.03 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 07:00 | 57.8 | 24.88 | 24.88 | 32.93 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 08:00 | 61.98 | 41.01 | 41.01 | 20.97 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 09:00 | 66.77 | 46.1 | 46.1 | 20.66 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 10:00 | 71.74 | 59.35 | 59.35 | 12.39 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 11:00 | 75.7 | 73.27 | 73.27 | 2.43 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 12:00 | 79.42 | 55.26 | 55.26 | 24.16 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 13:00 | 82.61 | 45.37 | 45.37 | 37.24 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 14:00 | 85 | 52.88 | 52.88 | 32.12 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 15:00 | 85.38 | 42.62 | 42.62 | 42.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 16:00 | 84.82 | 21.94 | 21.94 | 62.88 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 17:00 | 82.11 | 12.1 | 12.1 | 70.01 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 18:00 | 80.05 | 5.22 | 5.22 | 74.83 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 19:00 | 74.76 | 0 | 0 | 74.76 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 20:00 | 70.58 | 0 | 0 | 70.58 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 21:00 | 66.22 | 0 | 0 | 66.22 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 22:00 | 62.81 | 0 | 0 | 62.81 | 0 | 0 | 0.68 | 0 | 0
2025-06-26 23:00 | 57.77 | 0 | 0 | 57.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 | 54.46 | 0 | 0 | 54.46 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 01:00 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 02:00 | 52.1 | 0 | 0 | 52.1 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 03:00 | 49.41 | 0 | 0 | 49.41 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 04:00 | 50.77 | 0 | 0 | 50.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 05:00 | 54 | 30.67 | 30.67 | 23.32 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 06:00 | 55.09 | 89.48 | 58.49 | 0 | 3.4 | 0 | 3.91 | 30.99 | 0
2025-06-27 07:00 | 57.08 | 111.4 | 59.41 | 0 | 2.33 | 0 | 6.12 | 52 | 0
2025-06-27 08:00 | 60.94 | 119.75 | 60.94 | 0 | 0 | 0 | 6.12 | 58.81 | 0
2025-06-27 09:00 | 64.59 | 120.52 | 64.59 | 0 | 0 | 0 | 6.12 | 55.93 | 0
2025-06-27 10:00 | 68.6 | 120.22 | 68.6 | 0 | 0 | 0 | 6.12 | 51.62 | 0
2025-06-27 11:00 | 72.5 | 117.71 | 72.5 | 0 | 0 | 0 | 6.12 | 45.21 | 0
2025-06-27 12:00 | 74.71 | 115.41 | 74.71 | 0 | 0 | 0 | 6.12 | 40.7 | 0
2025-06-27 13:00 | 76.51 | 116.03 | 76.51 | 0 | 0 | 0 | 6.12 | 39.53 | 0
2025-06-27 14:00 | 78.6 | 116.62 | 78.6 | 0 | 0 | 0 | 6.12 | 38.03 | 0
2025-06-27 15:00 | 78.34 | 116.12 | 78.34 | 0 | 0 | 0 | 6.12 | 37.77 | 0
2025-06-27 16:00 | 77.69 | 113.85 | 77.69 | 0 | 0 | 0 | 6.12 | 36.16 | 0
2025-06-27 17:00 | 75.9 | 100.84 | 75.9 | 0 | 0 | 0 | 6.12 | 24.95 | 0
2025-06-27 18:00 | 73.73 | 78.94 | 73.73 | 0 | 0 | 0 | 6.12 | 5.21 | 0
2025-06-27 19:00 | 71.13 | 20.66 | 20.66 | 47.07 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-27 20:00 | 67.59 | 0 | 0 | 65.82 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-27 21:00 | 64.71 | 0 | 0 | 64.71 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 22:00 | 60.36 | 0 | 0 | 60.36 | 0 | 0 | 0.68 | 0 | 0
2025-06-27 23:00 | 56.06 | 0 | 0 | 56.06 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 | 54.32 | 0 | 0 | 54.32 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 01:00 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 02:00 | 51.03 | 0 | 0 | 51.03 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 03:00 | 51.63 | 0 | 0 | 51.63 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 04:00 | 51.03 | 0 | 0 | 51.03 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 05:00 | 53.13 | 33.71 | 33.71 | 19.42 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 06:00 | 54.83 | 86.86 | 58.23 | 0 | 3.4 | 0 | 3.91 | 28.63 | 0
2025-06-28 07:00 | 57.61 | 108.02 | 59.94 | 0 | 2.33 | 0 | 6.12 | 48.08 | 0
2025-06-28 08:00 | 60.45 | 113.88 | 60.45 | 0 | 0 | 0 | 6.12 | 53.43 | 0
2025-06-28 09:00 | 64.29 | 82.11 | 64.29 | 0 | 0 | 0 | 6.12 | 17.82 | 0
2025-06-28 10:00 | 67.37 | 11.75 | 11.75 | 52.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-28 11:00 | 71.02 | 31.07 | 31.07 | 38.18 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-28 12:00 | 73.53 | 48.46 | 48.46 | 25.08 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 13:00 | 75.26 | 55.63 | 55.63 | 19.63 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 14:00 | 77.53 | 104.32 | 80.93 | 0 | 3.4 | 0 | 3.91 | 23.39 | 0
2025-06-28 15:00 | 77.69 | 86.45 | 80.01 | 0 | 2.33 | 0 | 6.12 | 6.44 | 0
2025-06-28 16:00 | 76.81 | 122.89 | 76.81 | 0 | 0 | 0 | 6.12 | 46.09 | 0
2025-06-28 17:00 | 75.8 | 125.64 | 75.8 | 0 | 0 | 0 | 6.12 | 49.84 | 0
2025-06-28 18:00 | 73.61 | 103.5 | 73.61 | 0 | 0 | 0 | 6.12 | 29.89 | 0
2025-06-28 19:00 | 70.5 | 21.41 | 21.41 | 45.69 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-28 20:00 | 67.79 | 0 | 0 | 66.02 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-28 21:00 | 64.01 | 0 | 0 | 64.01 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 22:00 | 60.39 | 0 | 0 | 60.39 | 0 | 0 | 0.68 | 0 | 0
2025-06-28 23:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 | 54.77 | 0 | 0 | 54.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 01:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 02:00 | 51.05 | 0 | 0 | 51.05 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 03:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 04:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 05:00 | 53.41 | 30.43 | 30.43 | 22.99 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 06:00 | 55.35 | 91.12 | 58.75 | 0 | 3.4 | 0 | 3.91 | 32.37 | 0
2025-06-29 07:00 | 58.76 | 111.16 | 61.08 | 0 | 2.33 | 0 | 6.12 | 50.08 | 0
2025-06-29 08:00 | 60.83 | 120.18 | 60.83 | 0 | 0 | 0 | 6.12 | 59.35 | 0
2025-06-29 09:00 | 63.63 | 121.68 | 63.63 | 0 | 0 | 0 | 6.12 | 58.05 | 0
2025-06-29 10:00 | 68.42 | 119.62 | 68.42 | 0 | 0 | 0 | 6.12 | 51.2 | 0
2025-06-29 11:00 | 72.45 | 118.28 | 72.45 | 0 | 0 | 0 | 6.12 | 45.83 | 0
2025-06-29 12:00 | 75.3 | 116 | 75.3 | 0 | 0 | 0 | 6.12 | 40.7 | 0
2025-06-29 13:00 | 77.73 | 117.48 | 77.73 | 0 | 0 | 0 | 6.12 | 39.75 | 0
2025-06-29 14:00 | 79.75 | 118.1 | 79.75 | 0 | 0 | 0 | 6.12 | 38.35 | 0
2025-06-29 15:00 | 79.79 | 118.03 | 79.79 | 0 | 0 | 0 | 6.12 | 38.24 | 0
2025-06-29 16:00 | 79.48 | 113.45 | 79.48 | 0 | 0 | 0 | 6.12 | 33.97 | 0
2025-06-29 17:00 | 77.12 | 104.38 | 77.12 | 0 | 0 | 0 | 6.12 | 27.26 | 0
2025-06-29 18:00 | 74.68 | 84.08 | 74.68 | 0 | 0 | 0 | 6.12 | 9.4 | 0
2025-06-29 19:00 | 72.97 | 21.36 | 21.36 | 48.21 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-29 20:00 | 68.7 | 0 | 0 | 66.93 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-29 21:00 | 64.6 | 0 | 0 | 64.6 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 22:00 | 60.91 | 0 | 0 | 60.91 | 0 | 0 | 0.68 | 0 | 0
2025-06-29 23:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 | 54.77 | 0 | 0 | 54.77 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 01:00 | 52.2 | 0 | 0 | 52.2 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 02:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 03:00 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 04:00 | 51.15 | 0 | 0 | 51.15 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 05:00 | 53.4 | 24.92 | 24.92 | 28.48 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 06:00 | 55.27 | 87.22 | 58.67 | 0 | 3.4 | 0 | 3.91 | 28.55 | 0
2025-06-30 07:00 | 58.35 | 100.18 | 60.68 | 0 | 2.33 | 0 | 6.12 | 39.5 | 0
2025-06-30 08:00 | 61.63 | 119.41 | 61.63 | 0 | 0 | 0 | 6.12 | 57.78 | 0
2025-06-30 09:00 | 66.2 | 140.67 | 66.2 | 0 | 0 | 0 | 6.12 | 74.47 | 0
2025-06-30 10:00 | 70.92 | 133.34 | 70.92 | 0 | 0 | 0 | 6.12 | 62.42 | 0
2025-06-30 11:00 | 75.47 | 81.76 | 75.47 | 0 | 0 | 0 | 6.12 | 6.29 | 0
2025-06-30 12:00 | 78.96 | 79.1 | 78.96 | 0 | 0 | 0 | 6.12 | 0.14 | 0
2025-06-30 13:00 | 82.63 | 61.87 | 61.87 | 17.36 | 0 | 3.4 | 2.54 | 0 | 0
2025-06-30 14:00 | 84.08 | 70.99 | 70.99 | 11.32 | 0 | 1.77 | 0.68 | 0 | 0
2025-06-30 15:00 | 85.15 | 66.72 | 66.72 | 18.43 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 16:00 | 83.83 | 56.76 | 56.76 | 27.07 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 17:00 | 81.19 | 47.29 | 47.29 | 33.9 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 18:00 | 79.14 | 20.78 | 20.78 | 58.37 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 19:00 | 75.47 | 5.22 | 5.22 | 70.25 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 20:00 | 71.03 | 0 | 0 | 71.03 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 21:00 | 66.47 | 0 | 0 | 66.47 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 22:00 | 61.82 | 0 | 0 | 61.82 | 0 | 0 | 0.68 | 0 | 0
2025-06-30 23:00 | 57.82 | 0 | 0 | 57.82 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 | 55.35 | 0 | 0 | 55.35 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 01:00 | 53.09 | 0 | 0 | 53.09 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 02:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 03:00 | 51.59 | 0 | 0 | 51.59 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 04:00 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 05:00 | 52.59 | 20.34 | 20.34 | 32.25 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 06:00 | 55.89 | 37.41 | 37.41 | 18.48 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 07:00 | 58.39 | 71.05 | 61.79 | 0 | 3.4 | 0 | 3.91 | 9.25 | 0
2025-07-01 08:00 | 61.17 | 89.48 | 63.49 | 0 | 2.33 | 0 | 6.12 | 25.99 | 0
2025-07-01 09:00 | 65.16 | 107.57 | 65.16 | 0 | 0 | 0 | 6.12 | 42.41 | 0
2025-07-01 10:00 | 68.8 | 108.89 | 68.8 | 0 | 0 | 0 | 6.12 | 40.09 | 0
2025-07-01 11:00 | 70.84 | 112.96 | 70.84 | 0 | 0 | 0 | 6.12 | 42.12 | 0
2025-07-01 12:00 | 74.78 | 102.5 | 74.78 | 0 | 0 | 0 | 6.12 | 27.72 | 0
2025-07-01 13:00 | 77.54 | 112.8 | 77.54 | 0 | 0 | 0 | 6.12 | 35.26 | 0
2025-07-01 14:00 | 78.86 | 114.77 | 78.86 | 0 | 0 | 0 | 6.12 | 35.91 | 0
2025-07-01 15:00 | 79.66 | 123.8 | 79.66 | 0 | 0 | 0 | 6.12 | 44.14 | 0
2025-07-01 16:00 | 79.6 | 124.96 | 79.6 | 0 | 0 | 0 | 6.12 | 45.36 | 0
2025-07-01 17:00 | 77.4 | 120.71 | 77.4 | 0 | 0 | 0 | 6.12 | 43.31 | 0
2025-07-01 18:00 | 74.7 | 100.34 | 74.7 | 0 | 0 | 0 | 6.12 | 25.63 | 0
2025-07-01 19:00 | 72.37 | 27.1 | 27.1 | 41.87 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-01 20:00 | 68.56 | 0 | 0 | 66.79 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-01 21:00 | 64.94 | 0 | 0 | 64.94 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 22:00 | 61.2 | 0 | 0 | 61.2 | 0 | 0 | 0.68 | 0 | 0
2025-07-01 23:00 | 59.08 | 0 | 0 | 59.08 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 | 53.95 | 0 | 0 | 53.95 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 01:00 | 52.72 | 0 | 0 | 52.72 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 02:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 03:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 04:00 | 52 | 0 | 0 | 52 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 05:00 | 53.33 | 30.42 | 30.42 | 22.9 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 06:00 | 55.05 | 96.84 | 58.45 | 0 | 3.4 | 0 | 3.91 | 38.39 | 0
2025-07-02 07:00 | 57.7 | 118.62 | 60.02 | 0 | 2.33 | 0 | 6.12 | 58.6 | 0
2025-07-02 08:00 | 60.94 | 128.52 | 60.94 | 0 | 0 | 0 | 6.12 | 67.58 | 0
2025-07-02 09:00 | 64.27 | 130.92 | 64.27 | 0 | 0 | 0 | 6.12 | 66.65 | 0
2025-07-02 10:00 | 67.55 | 130.13 | 67.55 | 0 | 0 | 0 | 6.12 | 62.58 | 0
2025-07-02 11:00 | 70.47 | 128.14 | 70.47 | 0 | 0 | 0 | 6.12 | 57.67 | 0
2025-07-02 12:00 | 73.2 | 96.02 | 73.2 | 0 | 0 | 0 | 6.12 | 22.82 | 0
2025-07-02 13:00 | 75.35 | 84.02 | 75.35 | 0 | 0 | 0 | 6.12 | 8.68 | 0
2025-07-02 14:00 | 75.53 | 123.56 | 75.53 | 0 | 0 | 0 | 6.12 | 48.02 | 0
2025-07-02 15:00 | 76.02 | 111.71 | 76.02 | 0 | 0 | 0 | 6.12 | 35.69 | 0
2025-07-02 16:00 | 75.27 | 124.52 | 75.27 | 0 | 0 | 0 | 6.12 | 49.25 | 0
2025-07-02 17:00 | 75.4 | 114.56 | 75.4 | 0 | 0 | 0 | 6.12 | 39.15 | 0
2025-07-02 18:00 | 73.2 | 83.57 | 73.2 | 0 | 0 | 0 | 6.12 | 10.37 | 0
2025-07-02 19:00 | 70.82 | 17.3 | 17.3 | 50.12 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-02 20:00 | 66.87 | 0 | 0 | 65.1 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-02 21:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 22:00 | 60.69 | 0 | 0 | 60.69 | 0 | 0 | 0.68 | 0 | 0
2025-07-02 23:00 | 57.92 | 0 | 0 | 57.92 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 | 55.72 | 0 | 0 | 55.72 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 01:00 | 52.51 | 0 | 0 | 52.51 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 02:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 04:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 05:00 | 53.16 | 26.82 | 26.82 | 26.33 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 06:00 | 56.09 | 87.85 | 59.49 | 0 | 3.4 | 0 | 3.91 | 28.35 | 0
2025-07-03 07:00 | 58.97 | 109.3 | 61.3 | 0 | 2.33 | 0 | 6.12 | 48 | 0
2025-07-03 08:00 | 62.29 | 118.65 | 62.29 | 0 | 0 | 0 | 6.12 | 56.36 | 0
2025-07-03 09:00 | 65.8 | 120.39 | 65.8 | 0 | 0 | 0 | 6.12 | 54.59 | 0
2025-07-03 10:00 | 71.19 | 120.48 | 71.19 | 0 | 0 | 0 | 6.12 | 49.29 | 0
2025-07-03 11:00 | 74.15 | 118.63 | 74.15 | 0 | 0 | 0 | 6.12 | 44.48 | 0
2025-07-03 12:00 | 79.46 | 116.22 | 79.46 | 0 | 0 | 0 | 6.12 | 36.76 | 0
2025-07-03 13:00 | 81.73 | 116.89 | 81.73 | 0 | 0 | 0 | 6.12 | 35.16 | 0
2025-07-03 14:00 | 82.21 | 118.15 | 82.21 | 0 | 0 | 0 | 6.12 | 35.94 | 0
2025-07-03 15:00 | 84.02 | 117.56 | 84.02 | 0 | 0 | 0 | 6.12 | 33.54 | 0
2025-07-03 16:00 | 83.86 | 114.26 | 83.86 | 0 | 0 | 0 | 6.12 | 30.4 | 0
2025-07-03 17:00 | 81.51 | 103.72 | 81.51 | 0 | 0 | 0 | 6.12 | 22.21 | 0
2025-07-03 18:00 | 79.02 | 82.43 | 79.02 | 0 | 0 | 0 | 6.12 | 3.41 | 0
2025-07-03 19:00 | 74.47 | 20.04 | 20.04 | 51.04 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-03 20:00 | 70.01 | 0 | 0 | 68.24 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-03 21:00 | 66.26 | 0 | 0 | 66.26 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 22:00 | 62.12 | 0 | 0 | 62.12 | 0 | 0 | 0.68 | 0 | 0
2025-07-03 23:00 | 58.2 | 0 | 0 | 58.2 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 | 55.89 | 0 | 0 | 55.89 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 01:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 02:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 04:00 | 50.87 | 0 | 0 | 50.87 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 05:00 | 52.38 | 21.79 | 21.79 | 30.6 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 06:00 | 55.28 | 75.2 | 58.68 | 0 | 3.4 | 0 | 3.91 | 16.52 | 0
2025-07-04 07:00 | 59.21 | 99.26 | 61.54 | 0 | 2.33 | 0 | 6.12 | 37.71 | 0
2025-07-04 08:00 | 62.01 | 110.72 | 62.01 | 0 | 0 | 0 | 6.12 | 48.71 | 0
2025-07-04 09:00 | 64.67 | 117.28 | 64.67 | 0 | 0 | 0 | 6.12 | 52.62 | 0
2025-07-04 10:00 | 67.86 | 117.04 | 67.86 | 0 | 0 | 0 | 6.12 | 49.17 | 0
2025-07-04 11:00 | 73.47 | 112.27 | 73.47 | 0 | 0 | 0 | 6.12 | 38.79 | 0
2025-07-04 12:00 | 76.27 | 111.41 | 76.27 | 0 | 0 | 0 | 6.12 | 35.14 | 0
2025-07-04 13:00 | 79.39 | 111.17 | 79.39 | 0 | 0 | 0 | 6.12 | 31.78 | 0
2025-07-04 14:00 | 79.96 | 110.18 | 79.96 | 0 | 0 | 0 | 6.12 | 30.21 | 0
2025-07-04 15:00 | 81.12 | 107.73 | 81.12 | 0 | 0 | 0 | 6.12 | 26.61 | 0
2025-07-04 16:00 | 80.83 | 102.02 | 80.83 | 0 | 0 | 0 | 6.12 | 21.19 | 0
2025-07-04 17:00 | 78.6 | 93.09 | 78.6 | 0 | 0 | 0 | 6.12 | 14.49 | 0
2025-07-04 18:00 | 76.11 | 64.7 | 64.7 | 8.01 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-04 19:00 | 73.12 | 16.37 | 16.37 | 54.98 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-04 20:00 | 69.69 | 0 | 0 | 69.69 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 21:00 | 65.52 | 0 | 0 | 65.52 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 22:00 | 62.2 | 0 | 0 | 62.2 | 0 | 0 | 0.68 | 0 | 0
2025-07-04 23:00 | 57.99 | 0 | 0 | 57.99 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 | 54.78 | 0 | 0 | 54.78 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 01:00 | 54.1 | 0 | 0 | 54.1 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 02:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 03:00 | 50.94 | 0 | 0 | 50.94 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 04:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 05:00 | 53.15 | 1.6 | 1.6 | 51.55 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 06:00 | 55.25 | 38.61 | 38.61 | 16.64 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 07:00 | 58.62 | 39.13 | 39.13 | 19.49 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 08:00 | 62.52 | 38.64 | 38.64 | 23.89 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 09:00 | 67.08 | 57.27 | 57.27 | 9.81 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 10:00 | 70.51 | 75.94 | 73.91 | 0 | 3.4 | 0 | 3.91 | 2.03 | 0
2025-07-05 11:00 | 77.25 | 93.21 | 79.57 | 0 | 2.33 | 0 | 6.12 | 13.64 | 0
2025-07-05 12:00 | 80.37 | 105.11 | 80.37 | 0 | 0 | 0 | 6.12 | 24.73 | 0
2025-07-05 13:00 | 84.02 | 115.43 | 84.02 | 0 | 0 | 0 | 6.12 | 31.41 | 0
2025-07-05 14:00 | 85.16 | 67.77 | 67.77 | 13.99 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-05 15:00 | 86.34 | 63.96 | 63.96 | 20.62 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-05 16:00 | 85.51 | 81.43 | 81.43 | 4.09 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 17:00 | 84.47 | 58.47 | 58.47 | 26 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 18:00 | 80.15 | 3.54 | 3.54 | 76.61 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 19:00 | 76.69 | 1.92 | 1.92 | 74.77 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 20:00 | 71.37 | 0 | 0 | 71.37 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 21:00 | 66.76 | 0 | 0 | 66.76 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 22:00 | 62.42 | 0 | 0 | 62.42 | 0 | 0 | 0.68 | 0 | 0
2025-07-05 23:00 | 59.27 | 0 | 0 | 59.27 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 01:00 | 52.47 | 0 | 0 | 52.47 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 02:00 | 50.77 | 0 | 0 | 50.77 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 03:00 | 50.72 | 0 | 0 | 50.72 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 04:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 05:00 | 52.33 | 24.8 | 24.8 | 27.52 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 06:00 | 54.99 | 91.6 | 58.39 | 0 | 3.4 | 0 | 3.91 | 33.21 | 0
2025-07-06 07:00 | 57.26 | 106.19 | 59.58 | 0 | 2.33 | 0 | 6.12 | 46.61 | 0
2025-07-06 08:00 | 61.17 | 109.66 | 61.17 | 0 | 0 | 0 | 6.12 | 48.48 | 0
2025-07-06 09:00 | 65.98 | 83.41 | 65.98 | 0 | 0 | 0 | 6.12 | 17.43 | 0
2025-07-06 10:00 | 69.3 | 62.04 | 62.04 | 3.87 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-06 11:00 | 72.7 | 83.31 | 76.1 | 0 | 3.4 | 0 | 5.77 | 7.21 | 0
2025-07-06 12:00 | 75.13 | 55.54 | 55.54 | 16.19 | 0 | 3.4 | 2.19 | 0 | 0
2025-07-06 13:00 | 77.2 | 59.91 | 59.91 | 15.86 | 0 | 1.44 | 0.68 | 0 | 0
2025-07-06 14:00 | 78.87 | 86.98 | 82.27 | 0 | 3.4 | 0 | 3.91 | 4.71 | 0
2025-07-06 15:00 | 79.92 | 88.53 | 82.25 | 0 | 2.33 | 0 | 6.12 | 6.28 | 0
2025-07-06 16:00 | 79.87 | 79.43 | 79.43 | 0 | 0 | 0.44 | 5.66 | 0 | 0
2025-07-06 17:00 | 78.42 | 68.97 | 68.97 | 6.04 | 0 | 3.4 | 2.08 | 0 | 0
2025-07-06 18:00 | 75.94 | 61.51 | 61.51 | 13.11 | 0 | 1.33 | 0.68 | 0 | 0
2025-07-06 19:00 | 72.23 | 20.65 | 20.65 | 51.59 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 20:00 | 69.12 | 0 | 0 | 69.12 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 21:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 22:00 | 61.58 | 0 | 0 | 61.58 | 0 | 0 | 0.68 | 0 | 0
2025-07-06 23:00 | 59.28 | 0 | 0 | 59.28 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 | 54.37 | 0 | 0 | 54.37 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 01:00 | 53.03 | 0 | 0 | 53.03 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 02:00 | 52.39 | 0 | 0 | 52.39 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 03:00 | 50.58 | 0 | 0 | 50.58 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 04:00 | 51.46 | 0 | 0 | 51.46 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 05:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 06:00 | 55.14 | 10.02 | 10.02 | 45.12 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 07:00 | 57.08 | 26.98 | 26.98 | 30.1 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 08:00 | 61.07 | 36.2 | 36.2 | 24.88 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 09:00 | 64.02 | 42.95 | 42.95 | 21.07 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 10:00 | 66.64 | 43.59 | 43.59 | 23.05 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 11:00 | 68.29 | 60.61 | 60.61 | 7.68 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 12:00 | 70.63 | 90.38 | 74.03 | 0 | 3.4 | 0 | 3.91 | 16.34 | 0
2025-07-07 13:00 | 71.48 | 122.54 | 73.8 | 0 | 2.33 | 0 | 6.12 | 48.74 | 0
2025-07-07 14:00 | 72.56 | 118.81 | 72.56 | 0 | 0 | 0 | 6.12 | 46.24 | 0
2025-07-07 15:00 | 74.07 | 109.64 | 74.07 | 0 | 0 | 0 | 6.12 | 35.57 | 0
2025-07-07 16:00 | 72.78 | 116.84 | 72.78 | 0 | 0 | 0 | 6.12 | 44.07 | 0
2025-07-07 17:00 | 71.33 | 50.87 | 50.87 | 17.06 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-07 18:00 | 70.68 | 29.85 | 29.85 | 39.06 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-07 19:00 | 68.05 | 11.12 | 11.12 | 56.93 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 20:00 | 65.79 | 0 | 0 | 65.79 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 21:00 | 63.17 | 0 | 0 | 63.17 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 22:00 | 60.55 | 0 | 0 | 60.55 | 0 | 0 | 0.68 | 0 | 0
2025-07-07 23:00 | 58.35 | 0 | 0 | 58.35 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 | 55.57 | 0 | 0 | 55.57 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 01:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 02:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 03:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 04:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 05:00 | 52.87 | 20.87 | 20.87 | 32 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 06:00 | 55.14 | 82.04 | 58.54 | 0 | 3.4 | 0 | 3.91 | 23.5 | 0
2025-07-08 07:00 | 58.11 | 109.06 | 60.43 | 0 | 2.33 | 0 | 6.12 | 48.62 | 0
2025-07-08 08:00 | 60.56 | 121.36 | 60.56 | 0 | 0 | 0 | 6.12 | 60.81 | 0
2025-07-08 09:00 | 63.68 | 124.07 | 63.68 | 0 | 0 | 0 | 6.12 | 60.39 | 0
2025-07-08 10:00 | 66.97 | 119.53 | 66.97 | 0 | 0 | 0 | 6.12 | 52.56 | 0
2025-07-08 11:00 | 68.3 | 7.29 | 7.29 | 57.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-08 12:00 | 70.73 | 93.7 | 74.13 | 0 | 3.4 | 0 | 5.77 | 19.58 | 0
2025-07-08 13:00 | 71.66 | 123.66 | 72.02 | 0 | 0.37 | 0 | 6.12 | 51.64 | 0
2025-07-08 14:00 | 71.38 | 6.52 | 6.52 | 61.46 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-08 15:00 | 71.8 | 119.8 | 75.2 | 0 | 3.4 | 0 | 5.77 | 44.6 | 0
2025-07-08 16:00 | 71.7 | 120.51 | 72.06 | 0 | 0.37 | 0 | 6.12 | 48.45 | 0
2025-07-08 17:00 | 70.95 | 107.59 | 70.95 | 0 | 0 | 0 | 6.12 | 36.64 | 0
2025-07-08 18:00 | 70.09 | 80.46 | 70.09 | 0 | 0 | 0 | 6.12 | 10.37 | 0
2025-07-08 19:00 | 68.7 | 17.89 | 17.89 | 47.4 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-08 20:00 | 66.8 | 0 | 0 | 65.03 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-08 21:00 | 63.72 | 0 | 0 | 63.72 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 22:00 | 60.51 | 0 | 0 | 60.51 | 0 | 0 | 0.68 | 0 | 0
2025-07-08 23:00 | 56.85 | 0 | 0 | 56.85 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 | 55.69 | 0 | 0 | 55.69 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 01:00 | 53.3 | 0 | 0 | 53.3 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 03:00 | 52.44 | 0 | 0 | 52.44 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 04:00 | 52.48 | 0 | 0 | 52.48 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 05:00 | 53.68 | 10.75 | 10.75 | 42.93 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 06:00 | 55.17 | 64.79 | 58.57 | 0 | 3.4 | 0 | 3.91 | 6.21 | 0
2025-07-09 07:00 | 58.63 | 98.08 | 60.95 | 0 | 2.33 | 0 | 6.12 | 37.12 | 0
2025-07-09 08:00 | 62.82 | 90.46 | 62.82 | 0 | 0 | 0 | 6.12 | 27.64 | 0
2025-07-09 09:00 | 67.03 | 100.18 | 67.03 | 0 | 0 | 0 | 6.12 | 33.15 | 0
2025-07-09 10:00 | 72.5 | 119.47 | 72.5 | 0 | 0 | 0 | 6.12 | 46.97 | 0
2025-07-09 11:00 | 77.17 | 109.21 | 77.17 | 0 | 0 | 0 | 6.12 | 32.04 | 0
2025-07-09 12:00 | 80.72 | 102.1 | 80.72 | 0 | 0 | 0 | 6.12 | 21.38 | 0
2025-07-09 13:00 | 85.26 | 87.94 | 85.26 | 0 | 0 | 0 | 6.12 | 2.68 | 0
2025-07-09 14:00 | 86.9 | 76.35 | 76.35 | 7.15 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-09 15:00 | 86.74 | 56.23 | 56.23 | 28.75 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-09 16:00 | 86.83 | 56.84 | 56.84 | 29.98 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 17:00 | 84.8 | 48.59 | 48.59 | 36.21 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 18:00 | 81.75 | 12.03 | 12.03 | 69.72 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 19:00 | 76.83 | 1.01 | 1.01 | 75.81 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 20:00 | 72.66 | 0 | 0 | 72.66 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 21:00 | 67.52 | 0 | 0 | 67.52 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 22:00 | 62.22 | 0 | 0 | 62.22 | 0 | 0 | 0.68 | 0 | 0
2025-07-09 23:00 | 58.18 | 0 | 0 | 58.18 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 | 56.26 | 0 | 0 | 56.26 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 01:00 | 53.93 | 0 | 0 | 53.93 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 02:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 03:00 | 52.17 | 0 | 0 | 52.17 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 04:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 05:00 | 53.67 | 15.9 | 15.9 | 37.77 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 06:00 | 55.24 | 70.16 | 58.64 | 0 | 3.4 | 0 | 3.91 | 11.51 | 0
2025-07-10 07:00 | 59.82 | 97.88 | 62.15 | 0 | 2.33 | 0 | 6.12 | 35.73 | 0
2025-07-10 08:00 | 63.24 | 107.27 | 63.24 | 0 | 0 | 0 | 6.12 | 44.03 | 0
2025-07-10 09:00 | 67.38 | 105.47 | 67.38 | 0 | 0 | 0 | 6.12 | 38.09 | 0
2025-07-10 10:00 | 72.13 | 109.26 | 72.13 | 0 | 0 | 0 | 6.12 | 37.13 | 0
2025-07-10 11:00 | 77.41 | 108.47 | 77.41 | 0 | 0 | 0 | 6.12 | 31.06 | 0
2025-07-10 12:00 | 80.78 | 107.02 | 80.78 | 0 | 0 | 0 | 6.12 | 26.23 | 0
2025-07-10 13:00 | 85.42 | 108.99 | 85.42 | 0 | 0 | 0 | 6.12 | 23.57 | 0
2025-07-10 14:00 | 86.82 | 109.97 | 86.82 | 0 | 0 | 0 | 6.12 | 23.15 | 0
2025-07-10 15:00 | 88.26 | 109.52 | 88.26 | 0 | 0 | 0 | 6.12 | 21.26 | 0
2025-07-10 16:00 | 87.04 | 102.26 | 87.04 | 0 | 0 | 0 | 6.12 | 15.22 | 0
2025-07-10 17:00 | 84.94 | 81.87 | 81.87 | 0 | 0 | 3.07 | 2.89 | 0 | 0
2025-07-10 18:00 | 81.24 | 61 | 61 | 18.15 | 0 | 2.1 | 0.68 | 0 | 0
2025-07-10 19:00 | 77.2 | 15.27 | 15.27 | 61.93 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 20:00 | 73.41 | 0 | 0 | 73.41 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 21:00 | 68.27 | 0 | 0 | 68.27 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 22:00 | 63.15 | 0 | 0 | 63.15 | 0 | 0 | 0.68 | 0 | 0
2025-07-10 23:00 | 58.94 | 0 | 0 | 58.94 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 | 55.96 | 0 | 0 | 55.96 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 01:00 | 53.89 | 0 | 0 | 53.89 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 02:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 03:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 04:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 05:00 | 53.88 | 1.51 | 1.51 | 52.38 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 06:00 | 56.57 | 10.44 | 10.44 | 46.13 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 07:00 | 58.44 | 12.22 | 12.22 | 46.22 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 08:00 | 60.65 | 26.25 | 26.25 | 34.4 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 09:00 | 65.54 | 43.08 | 43.08 | 22.46 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 10:00 | 68.28 | 49.52 | 49.52 | 18.76 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 11:00 | 71.62 | 52.27 | 52.27 | 19.36 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 12:00 | 75.02 | 73.95 | 73.95 | 1.07 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 13:00 | 76.93 | 78.18 | 78.18 | 0 | 1.25 | 0 | 1.87 | 0 | 0
2025-07-11 14:00 | 77.87 | 53.67 | 53.67 | 23.08 | 0 | 1.13 | 0.68 | 0 | 0
2025-07-11 15:00 | 78.24 | 26.63 | 26.63 | 51.61 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 16:00 | 78.18 | 4.22 | 4.22 | 73.96 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 17:00 | 76.6 | 3.12 | 3.12 | 73.48 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 18:00 | 74.15 | 8.42 | 8.42 | 65.74 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 19:00 | 71.79 | 1.32 | 1.32 | 70.47 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 20:00 | 68.9 | 0 | 0 | 68.9 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 21:00 | 65.15 | 0 | 0 | 65.15 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 22:00 | 61 | 0 | 0 | 61 | 0 | 0 | 0.68 | 0 | 0
2025-07-11 23:00 | 58.89 | 0 | 0 | 58.89 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 | 54.18 | 0 | 0 | 54.18 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 01:00 | 53.13 | 0 | 0 | 53.13 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 02:00 | 51.65 | 0 | 0 | 51.65 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 03:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 04:00 | 52.24 | 0 | 0 | 52.24 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 05:00 | 53.91 | 18.4 | 18.4 | 35.51 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 06:00 | 55.19 | 77.63 | 58.59 | 0 | 3.4 | 0 | 3.91 | 19.04 | 0
2025-07-12 07:00 | 58.67 | 91.5 | 60.99 | 0 | 2.33 | 0 | 6.12 | 30.51 | 0
2025-07-12 08:00 | 61.71 | 105.15 | 61.71 | 0 | 0 | 0 | 6.12 | 43.44 | 0
2025-07-12 09:00 | 64.17 | 108.86 | 64.17 | 0 | 0 | 0 | 6.12 | 44.69 | 0
2025-07-12 10:00 | 69.33 | 111.08 | 69.33 | 0 | 0 | 0 | 6.12 | 41.75 | 0
2025-07-12 11:00 | 70.72 | 109.46 | 70.72 | 0 | 0 | 0 | 6.12 | 38.74 | 0
2025-07-12 12:00 | 74.23 | 106.16 | 74.23 | 0 | 0 | 0 | 6.12 | 31.93 | 0
2025-07-12 13:00 | 76.17 | 107.32 | 76.17 | 0 | 0 | 0 | 6.12 | 31.15 | 0
2025-07-12 14:00 | 77.33 | 108.22 | 77.33 | 0 | 0 | 0 | 6.12 | 30.88 | 0
2025-07-12 15:00 | 77.36 | 101.46 | 77.36 | 0 | 0 | 0 | 6.12 | 24.1 | 0
2025-07-12 16:00 | 77.61 | 96.32 | 77.61 | 0 | 0 | 0 | 6.12 | 18.71 | 0
2025-07-12 17:00 | 75.2 | 85.72 | 75.2 | 0 | 0 | 0 | 6.12 | 10.52 | 0
2025-07-12 18:00 | 73.99 | 75.41 | 73.99 | 0 | 0 | 0 | 6.12 | 1.42 | 0
2025-07-12 19:00 | 71.16 | 15.51 | 15.51 | 52.25 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-12 20:00 | 68.04 | 0 | 0 | 66.27 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-12 21:00 | 65.24 | 0 | 0 | 65.24 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 22:00 | 62.15 | 0 | 0 | 62.15 | 0 | 0 | 0.68 | 0 | 0
2025-07-12 23:00 | 58.2 | 0 | 0 | 58.2 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 | 56.17 | 0 | 0 | 56.17 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 01:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 02:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 03:00 | 51.38 | 0 | 0 | 51.38 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 04:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 05:00 | 53.08 | 17.9 | 17.9 | 35.18 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 06:00 | 56 | 81.16 | 59.4 | 0 | 3.4 | 0 | 3.91 | 21.76 | 0
2025-07-13 07:00 | 59.11 | 105.58 | 61.44 | 0 | 2.33 | 0 | 6.12 | 44.15 | 0
2025-07-13 08:00 | 62.14 | 115.26 | 62.14 | 0 | 0 | 0 | 6.12 | 53.12 | 0
2025-07-13 09:00 | 66.58 | 118.5 | 66.58 | 0 | 0 | 0 | 6.12 | 51.92 | 0
2025-07-13 10:00 | 72.34 | 118.46 | 72.34 | 0 | 0 | 0 | 6.12 | 46.12 | 0
2025-07-13 11:00 | 76.34 | 115.63 | 76.34 | 0 | 0 | 0 | 6.12 | 39.29 | 0
2025-07-13 12:00 | 81.03 | 114.14 | 81.03 | 0 | 0 | 0 | 6.12 | 33.11 | 0
2025-07-13 13:00 | 84.55 | 115.4 | 84.55 | 0 | 0 | 0 | 6.12 | 30.85 | 0
2025-07-13 14:00 | 85.64 | 115.11 | 85.64 | 0 | 0 | 0 | 6.12 | 29.47 | 0
2025-07-13 15:00 | 86.3 | 114.6 | 86.3 | 0 | 0 | 0 | 6.12 | 28.3 | 0
2025-07-13 16:00 | 87.11 | 109.53 | 87.11 | 0 | 0 | 0 | 6.12 | 22.42 | 0
2025-07-13 17:00 | 84.34 | 94.03 | 84.34 | 0 | 0 | 0 | 6.12 | 9.69 | 0
2025-07-13 18:00 | 80.67 | 68.65 | 68.65 | 8.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-13 19:00 | 76.28 | 13.55 | 13.55 | 60.96 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-13 20:00 | 71.87 | 0 | 0 | 71.87 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 21:00 | 66.81 | 0 | 0 | 66.81 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 22:00 | 63.38 | 0 | 0 | 63.38 | 0 | 0 | 0.68 | 0 | 0
2025-07-13 23:00 | 58.61 | 0 | 0 | 58.61 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 01:00 | 53.19 | 0 | 0 | 53.19 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 02:00 | 51.49 | 0 | 0 | 51.49 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 03:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 04:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 05:00 | 53.33 | 17.51 | 17.51 | 35.82 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 06:00 | 55.45 | 76.77 | 58.85 | 0 | 3.4 | 0 | 3.91 | 17.92 | 0
2025-07-14 07:00 | 58.63 | 95.94 | 60.96 | 0 | 2.33 | 0 | 6.12 | 34.98 | 0
2025-07-14 08:00 | 60.25 | 107.74 | 60.25 | 0 | 0 | 0 | 6.12 | 47.49 | 0
2025-07-14 09:00 | 64.78 | 112.55 | 64.78 | 0 | 0 | 0 | 6.12 | 47.77 | 0
2025-07-14 10:00 | 67.43 | 114.01 | 67.43 | 0 | 0 | 0 | 6.12 | 46.58 | 0
2025-07-14 11:00 | 70.11 | 112.24 | 70.11 | 0 | 0 | 0 | 6.12 | 42.13 | 0
2025-07-14 12:00 | 71.44 | 112.96 | 71.44 | 0 | 0 | 0 | 6.12 | 41.53 | 0
2025-07-14 13:00 | 73.41 | 114.59 | 73.41 | 0 | 0 | 0 | 6.12 | 41.18 | 0
2025-07-14 14:00 | 73.04 | 118.09 | 73.04 | 0 | 0 | 0 | 6.12 | 45.05 | 0
2025-07-14 15:00 | 74.42 | 120.46 | 74.42 | 0 | 0 | 0 | 6.12 | 46.04 | 0
2025-07-14 16:00 | 73.39 | 117.68 | 73.39 | 0 | 0 | 0 | 6.12 | 44.29 | 0
2025-07-14 17:00 | 72.08 | 109.92 | 72.08 | 0 | 0 | 0 | 6.12 | 37.84 | 0
2025-07-14 18:00 | 70.9 | 91.74 | 70.9 | 0 | 0 | 0 | 6.12 | 20.84 | 0
2025-07-14 19:00 | 69.49 | 19.59 | 19.59 | 46.49 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-14 20:00 | 66.61 | 0 | 0 | 64.84 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-14 21:00 | 64.39 | 0 | 0 | 64.39 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 22:00 | 60.29 | 0 | 0 | 60.29 | 0 | 0 | 0.68 | 0 | 0
2025-07-14 23:00 | 57.15 | 0 | 0 | 57.15 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 | 56.27 | 0 | 0 | 56.27 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 01:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 02:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 03:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 04:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 05:00 | 53.63 | 15.52 | 15.52 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 06:00 | 55.66 | 76.23 | 59.06 | 0 | 3.4 | 0 | 3.91 | 17.17 | 0
2025-07-15 07:00 | 58.86 | 99.21 | 61.19 | 0 | 2.33 | 0 | 6.12 | 38.02 | 0
2025-07-15 08:00 | 61.01 | 112.53 | 61.01 | 0 | 0 | 0 | 6.12 | 51.52 | 0
2025-07-15 09:00 | 64.52 | 115.29 | 64.52 | 0 | 0 | 0 | 6.12 | 50.77 | 0
2025-07-15 10:00 | 67.48 | 116.91 | 67.48 | 0 | 0 | 0 | 6.12 | 49.43 | 0
2025-07-15 11:00 | 70 | 116.37 | 70 | 0 | 0 | 0 | 6.12 | 46.37 | 0
2025-07-15 12:00 | 72.1 | 115.64 | 72.1 | 0 | 0 | 0 | 6.12 | 43.54 | 0
2025-07-15 13:00 | 73.93 | 116.96 | 73.93 | 0 | 0 | 0 | 6.12 | 43.03 | 0
2025-07-15 14:00 | 74.88 | 116.46 | 74.88 | 0 | 0 | 0 | 6.12 | 41.58 | 0
2025-07-15 15:00 | 74.67 | 115.88 | 74.67 | 0 | 0 | 0 | 6.12 | 41.21 | 0
2025-07-15 16:00 | 75.27 | 110.2 | 75.27 | 0 | 0 | 0 | 6.12 | 34.94 | 0
2025-07-15 17:00 | 73.4 | 95.62 | 73.4 | 0 | 0 | 0 | 6.12 | 22.21 | 0
2025-07-15 18:00 | 72.19 | 75.88 | 72.19 | 0 | 0 | 0 | 6.12 | 3.69 | 0
2025-07-15 19:00 | 69.99 | 14.69 | 14.69 | 51.9 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-15 20:00 | 67.67 | 0 | 0 | 65.9 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-15 21:00 | 63.45 | 0 | 0 | 63.45 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 22:00 | 61.82 | 0 | 0 | 61.82 | 0 | 0 | 0.68 | 0 | 0
2025-07-15 23:00 | 57.98 | 0 | 0 | 57.98 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 | 56.39 | 0 | 0 | 56.39 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 01:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 02:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 03:00 | 52.53 | 0 | 0 | 52.53 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 04:00 | 51.92 | 0 | 0 | 51.92 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 05:00 | 54.1 | 10.09 | 10.09 | 44.01 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 06:00 | 55.8 | 22 | 22 | 33.8 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 07:00 | 59.04 | 37.18 | 37.18 | 21.86 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 08:00 | 62.51 | 70.97 | 65.91 | 0 | 3.4 | 0 | 3.91 | 5.06 | 0
2025-07-16 09:00 | 66.92 | 122.33 | 69.25 | 0 | 2.33 | 0 | 6.12 | 53.09 | 0
2025-07-16 10:00 | 70.28 | 89 | 70.28 | 0 | 0 | 0 | 6.12 | 18.72 | 0
2025-07-16 11:00 | 74.08 | 96.06 | 74.08 | 0 | 0 | 0 | 6.12 | 21.98 | 0
2025-07-16 12:00 | 77.71 | 101.3 | 77.71 | 0 | 0 | 0 | 6.12 | 23.59 | 0
2025-07-16 13:00 | 80.78 | 104.37 | 80.78 | 0 | 0 | 0 | 6.12 | 23.59 | 0
2025-07-16 14:00 | 82.34 | 85.66 | 82.34 | 0 | 0 | 0 | 6.12 | 3.32 | 0
2025-07-16 15:00 | 83.4 | 83.84 | 83.4 | 0 | 0 | 0 | 6.12 | 0.43 | 0
2025-07-16 16:00 | 83.11 | 64.15 | 64.15 | 15.55 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-16 17:00 | 80.25 | 15.72 | 15.72 | 62.76 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-16 18:00 | 77.66 | 10.6 | 10.6 | 67.06 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 19:00 | 73.85 | 1.34 | 1.34 | 72.51 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 20:00 | 71.64 | 0 | 0 | 71.64 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 21:00 | 66.65 | 0 | 0 | 66.65 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 22:00 | 62.72 | 0 | 0 | 62.72 | 0 | 0 | 0.68 | 0 | 0
2025-07-16 23:00 | 58.16 | 0 | 0 | 58.16 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 | 55.69 | 0 | 0 | 55.69 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 01:00 | 53.73 | 0 | 0 | 53.73 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 03:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 04:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 05:00 | 53 | 10.28 | 10.28 | 42.73 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 06:00 | 55.18 | 48.68 | 48.68 | 6.5 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 07:00 | 58.09 | 89.81 | 61.49 | 0 | 3.4 | 0 | 3.91 | 28.32 | 0
2025-07-17 08:00 | 62.59 | 79.56 | 64.91 | 0 | 2.33 | 0 | 6.12 | 14.65 | 0
2025-07-17 09:00 | 65.73 | 96.06 | 65.73 | 0 | 0 | 0 | 6.12 | 30.33 | 0
2025-07-17 10:00 | 68.5 | 101.09 | 68.5 | 0 | 0 | 0 | 6.12 | 32.59 | 0
2025-07-17 11:00 | 71.66 | 109.39 | 71.66 | 0 | 0 | 0 | 6.12 | 37.73 | 0
2025-07-17 12:00 | 73.82 | 96.28 | 73.82 | 0 | 0 | 0 | 6.12 | 22.45 | 0
2025-07-17 13:00 | 76.63 | 97.83 | 76.63 | 0 | 0 | 0 | 6.12 | 21.2 | 0
2025-07-17 14:00 | 77.22 | 101.76 | 77.22 | 0 | 0 | 0 | 6.12 | 24.54 | 0
2025-07-17 15:00 | 77.69 | 88.57 | 77.69 | 0 | 0 | 0 | 6.12 | 10.88 | 0
2025-07-17 16:00 | 77.71 | 91 | 77.71 | 0 | 0 | 0 | 6.12 | 13.29 | 0
2025-07-17 17:00 | 76.1 | 86.47 | 76.1 | 0 | 0 | 0 | 6.12 | 10.37 | 0
2025-07-17 18:00 | 74.11 | 76.18 | 74.11 | 0 | 0 | 0 | 6.12 | 2.07 | 0
2025-07-17 19:00 | 71.65 | 11.17 | 11.17 | 57.08 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-17 20:00 | 68.97 | 0 | 0 | 67.2 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-17 21:00 | 66.03 | 0 | 0 | 66.03 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 22:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 0.68 | 0 | 0
2025-07-17 23:00 | 58.93 | 0 | 0 | 58.93 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 | 55.65 | 0 | 0 | 55.65 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 01:00 | 53.15 | 0 | 0 | 53.15 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 02:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 03:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 04:00 | 51.38 | 0 | 0 | 51.38 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 05:00 | 53.34 | 12.91 | 12.91 | 40.43 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 06:00 | 55.71 | 76.14 | 59.11 | 0 | 3.4 | 0 | 3.91 | 17.03 | 0
2025-07-18 07:00 | 58.42 | 97.39 | 60.75 | 0 | 2.33 | 0 | 6.12 | 36.64 | 0
2025-07-18 08:00 | 62.82 | 110.96 | 62.82 | 0 | 0 | 0 | 6.12 | 48.14 | 0
2025-07-18 09:00 | 65.97 | 113.72 | 65.97 | 0 | 0 | 0 | 6.12 | 47.74 | 0
2025-07-18 10:00 | 70.07 | 114.14 | 70.07 | 0 | 0 | 0 | 6.12 | 44.07 | 0
2025-07-18 11:00 | 72.92 | 114.88 | 72.92 | 0 | 0 | 0 | 6.12 | 41.96 | 0
2025-07-18 12:00 | 75.75 | 112.98 | 75.75 | 0 | 0 | 0 | 6.12 | 37.23 | 0
2025-07-18 13:00 | 77.48 | 115.3 | 77.48 | 0 | 0 | 0 | 6.12 | 37.81 | 0
2025-07-18 14:00 | 79.37 | 115.89 | 79.37 | 0 | 0 | 0 | 6.12 | 36.52 | 0
2025-07-18 15:00 | 79.85 | 114.02 | 79.85 | 0 | 0 | 0 | 6.12 | 34.17 | 0
2025-07-18 16:00 | 78.68 | 107.69 | 78.68 | 0 | 0 | 0 | 6.12 | 29.02 | 0
2025-07-18 17:00 | 77.68 | 94.82 | 77.68 | 0 | 0 | 0 | 6.12 | 17.13 | 0
2025-07-18 18:00 | 75.55 | 68.09 | 68.09 | 4.06 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-18 19:00 | 73 | 11.85 | 11.85 | 59.38 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-18 20:00 | 69.62 | 0 | 0 | 69.62 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 21:00 | 65.44 | 0 | 0 | 65.44 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 22:00 | 62.31 | 0 | 0 | 62.31 | 0 | 0 | 0.68 | 0 | 0
2025-07-18 23:00 | 58.58 | 0 | 0 | 58.58 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 | 54.32 | 0 | 0 | 54.32 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 01:00 | 53.27 | 0 | 0 | 53.27 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 02:00 | 52.65 | 0 | 0 | 52.65 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 03:00 | 50.79 | 0 | 0 | 50.79 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 04:00 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 05:00 | 54.31 | 11.78 | 11.78 | 42.53 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 06:00 | 55.37 | 72.05 | 58.77 | 0 | 3.4 | 0 | 3.91 | 13.28 | 0
2025-07-19 07:00 | 58.64 | 97.88 | 60.97 | 0 | 2.33 | 0 | 6.12 | 36.91 | 0
2025-07-19 08:00 | 61.34 | 111.66 | 61.34 | 0 | 0 | 0 | 6.12 | 50.32 | 0
2025-07-19 09:00 | 66.37 | 117.26 | 66.37 | 0 | 0 | 0 | 6.12 | 50.89 | 0
2025-07-19 10:00 | 69.05 | 117.77 | 69.05 | 0 | 0 | 0 | 6.12 | 48.72 | 0
2025-07-19 11:00 | 72.39 | 115.41 | 72.39 | 0 | 0 | 0 | 6.12 | 43.02 | 0
2025-07-19 12:00 | 75.83 | 116.32 | 75.83 | 0 | 0 | 0 | 6.12 | 40.49 | 0
2025-07-19 13:00 | 77.61 | 116.04 | 77.61 | 0 | 0 | 0 | 6.12 | 38.43 | 0
2025-07-19 14:00 | 78.18 | 116.36 | 78.18 | 0 | 0 | 0 | 6.12 | 38.18 | 0
2025-07-19 15:00 | 78.75 | 116.51 | 78.75 | 0 | 0 | 0 | 6.12 | 37.77 | 0
2025-07-19 16:00 | 78.86 | 113.79 | 78.86 | 0 | 0 | 0 | 6.12 | 34.93 | 0
2025-07-19 17:00 | 76.97 | 103.88 | 76.97 | 0 | 0 | 0 | 6.12 | 26.9 | 0
2025-07-19 18:00 | 74.1 | 77.99 | 74.1 | 0 | 0 | 0 | 6.12 | 3.9 | 0
2025-07-19 19:00 | 72.34 | 12.55 | 12.55 | 56.39 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-19 20:00 | 68.35 | 0 | 0 | 66.59 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-19 21:00 | 66.37 | 0 | 0 | 66.37 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 22:00 | 62.08 | 0 | 0 | 62.08 | 0 | 0 | 0.68 | 0 | 0
2025-07-19 23:00 | 58.19 | 0 | 0 | 58.19 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 | 55.47 | 0 | 0 | 55.47 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 01:00 | 52.6 | 0 | 0 | 52.6 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 02:00 | 51.57 | 0 | 0 | 51.57 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 03:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 04:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 05:00 | 53.9 | 12.13 | 12.13 | 41.78 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 06:00 | 55.77 | 76.65 | 59.17 | 0 | 3.4 | 0 | 3.91 | 17.48 | 0
2025-07-20 07:00 | 58.6 | 101.3 | 60.93 | 0 | 2.33 | 0 | 6.12 | 40.37 | 0
2025-07-20 08:00 | 61.88 | 114.14 | 61.88 | 0 | 0 | 0 | 6.12 | 52.26 | 0
2025-07-20 09:00 | 67.24 | 116.53 | 67.24 | 0 | 0 | 0 | 6.12 | 49.29 | 0
2025-07-20 10:00 | 70.03 | 116.92 | 70.03 | 0 | 0 | 0 | 6.12 | 46.89 | 0
2025-07-20 11:00 | 74.88 | 114.67 | 74.88 | 0 | 0 | 0 | 6.12 | 39.78 | 0
2025-07-20 12:00 | 77.74 | 113.78 | 77.74 | 0 | 0 | 0 | 6.12 | 36.04 | 0
2025-07-20 13:00 | 78.66 | 114.47 | 78.66 | 0 | 0 | 0 | 6.12 | 35.81 | 0
2025-07-20 14:00 | 80.78 | 115.82 | 80.78 | 0 | 0 | 0 | 6.12 | 35.04 | 0
2025-07-20 15:00 | 81.32 | 114.5 | 81.32 | 0 | 0 | 0 | 6.12 | 33.19 | 0
2025-07-20 16:00 | 81.07 | 110.93 | 81.07 | 0 | 0 | 0 | 6.12 | 29.85 | 0
2025-07-20 17:00 | 79.5 | 97.36 | 79.5 | 0 | 0 | 0 | 6.12 | 17.85 | 0
2025-07-20 18:00 | 78.54 | 70.65 | 70.65 | 4.49 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-20 19:00 | 73.29 | 11.16 | 11.16 | 60.36 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-20 20:00 | 70.24 | 0 | 0 | 70.24 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 21:00 | 66.52 | 0 | 0 | 66.52 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 22:00 | 62.36 | 0 | 0 | 62.36 | 0 | 0 | 0.68 | 0 | 0
2025-07-20 23:00 | 58.88 | 0 | 0 | 58.88 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 01:00 | 53.63 | 0 | 0 | 53.63 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 02:00 | 52.39 | 0 | 0 | 52.39 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 03:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 04:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 05:00 | 54.28 | 10.48 | 10.48 | 43.8 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 06:00 | 56.42 | 66.4 | 59.82 | 0 | 3.4 | 0 | 3.91 | 6.58 | 0
2025-07-21 07:00 | 59.21 | 90.83 | 61.54 | 0 | 2.33 | 0 | 6.12 | 29.3 | 0
2025-07-21 08:00 | 62.54 | 107.84 | 62.54 | 0 | 0 | 0 | 6.12 | 45.3 | 0
2025-07-21 09:00 | 67.3 | 110.26 | 67.3 | 0 | 0 | 0 | 6.12 | 42.96 | 0
2025-07-21 10:00 | 72.2 | 114.16 | 72.2 | 0 | 0 | 0 | 6.12 | 41.96 | 0
2025-07-21 11:00 | 77.04 | 111.88 | 77.04 | 0 | 0 | 0 | 6.12 | 34.85 | 0
2025-07-21 12:00 | 80.8 | 111.03 | 80.8 | 0 | 0 | 0 | 6.12 | 30.23 | 0
2025-07-21 13:00 | 83.84 | 111.56 | 83.84 | 0 | 0 | 0 | 6.12 | 27.72 | 0
2025-07-21 14:00 | 85.81 | 109.78 | 85.81 | 0 | 0 | 0 | 6.12 | 23.98 | 0
2025-07-21 15:00 | 86.3 | 105.19 | 86.3 | 0 | 0 | 0 | 6.12 | 18.88 | 0
2025-07-21 16:00 | 86.29 | 97.47 | 86.29 | 0 | 0 | 0 | 6.12 | 11.18 | 0
2025-07-21 17:00 | 83.57 | 81.36 | 81.36 | 0 | 0 | 2.21 | 3.8 | 0 | 0
2025-07-21 18:00 | 80.54 | 58.34 | 58.34 | 19.23 | 0 | 2.96 | 0.68 | 0 | 0
2025-07-21 19:00 | 76.72 | 9.35 | 9.35 | 67.37 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 20:00 | 71.64 | 0 | 0 | 71.64 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 21:00 | 67.79 | 0 | 0 | 67.79 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 22:00 | 63.49 | 0 | 0 | 63.49 | 0 | 0 | 0.68 | 0 | 0
2025-07-21 23:00 | 58.9 | 0 | 0 | 58.9 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 | 55.59 | 0 | 0 | 55.59 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 01:00 | 53.82 | 0 | 0 | 53.82 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 02:00 | 51.78 | 0 | 0 | 51.78 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 03:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 04:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 05:00 | 54 | 9.79 | 9.79 | 44.21 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 06:00 | 56.11 | 62.41 | 59.51 | 0 | 3.4 | 0 | 3.91 | 2.89 | 0
2025-07-22 07:00 | 59.23 | 85.18 | 61.55 | 0 | 2.33 | 0 | 6.12 | 23.63 | 0
2025-07-22 08:00 | 61.23 | 104.86 | 61.23 | 0 | 0 | 0 | 6.12 | 43.63 | 0
2025-07-22 09:00 | 66.61 | 108.84 | 66.61 | 0 | 0 | 0 | 6.12 | 42.23 | 0
2025-07-22 10:00 | 69.86 | 109.91 | 69.86 | 0 | 0 | 0 | 6.12 | 40.05 | 0
2025-07-22 11:00 | 73.66 | 104.89 | 73.66 | 0 | 0 | 0 | 6.12 | 31.23 | 0
2025-07-22 12:00 | 76.36 | 102.65 | 76.36 | 0 | 0 | 0 | 6.12 | 26.29 | 0
2025-07-22 13:00 | 78.5 | 103.8 | 78.5 | 0 | 0 | 0 | 6.12 | 25.3 | 0
2025-07-22 14:00 | 79.8 | 104.84 | 79.8 | 0 | 0 | 0 | 6.12 | 25.03 | 0
2025-07-22 15:00 | 80.62 | 102.73 | 80.62 | 0 | 0 | 0 | 6.12 | 22.11 | 0
2025-07-22 16:00 | 79.78 | 91.61 | 79.78 | 0 | 0 | 0 | 6.12 | 11.83 | 0
2025-07-22 17:00 | 78.91 | 77.74 | 77.74 | 0 | 0 | 1.18 | 4.88 | 0 | 0
2025-07-22 18:00 | 75.37 | 56.05 | 56.05 | 15.93 | 0 | 3.4 | 1.3 | 0 | 0
2025-07-22 19:00 | 72.89 | 8.94 | 8.94 | 63.36 | 0 | 0.59 | 0.68 | 0 | 0
2025-07-22 20:00 | 70.69 | 0 | 0 | 70.69 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 21:00 | 65.62 | 0 | 0 | 65.62 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 22:00 | 62.1 | 0 | 0 | 62.1 | 0 | 0 | 0.68 | 0 | 0
2025-07-22 23:00 | 58.32 | 0 | 0 | 58.32 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 01:00 | 53.21 | 0 | 0 | 53.21 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 02:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 03:00 | 52.09 | 0 | 0 | 52.09 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 04:00 | 51.8 | 0 | 0 | 51.8 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 05:00 | 53.97 | 8.99 | 8.99 | 44.98 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 06:00 | 56.29 | 64.98 | 59.69 | 0 | 3.4 | 0 | 3.91 | 5.29 | 0
2025-07-23 07:00 | 59.48 | 92.82 | 61.8 | 0 | 2.33 | 0 | 6.12 | 31.02 | 0
2025-07-23 08:00 | 62.68 | 107.68 | 62.68 | 0 | 0 | 0 | 6.12 | 45 | 0
2025-07-23 09:00 | 68.27 | 113.52 | 68.27 | 0 | 0 | 0 | 6.12 | 45.25 | 0
2025-07-23 10:00 | 71.32 | 115.36 | 71.32 | 0 | 0 | 0 | 6.12 | 44.04 | 0
2025-07-23 11:00 | 74.92 | 114.39 | 74.92 | 0 | 0 | 0 | 6.12 | 39.47 | 0
2025-07-23 12:00 | 77.8 | 112.57 | 77.8 | 0 | 0 | 0 | 6.12 | 34.78 | 0
2025-07-23 13:00 | 80.9 | 113.31 | 80.9 | 0 | 0 | 0 | 6.12 | 32.41 | 0
2025-07-23 14:00 | 83.39 | 114.04 | 83.39 | 0 | 0 | 0 | 6.12 | 30.65 | 0
2025-07-23 15:00 | 84.13 | 112.66 | 84.13 | 0 | 0 | 0 | 6.12 | 28.54 | 0
2025-07-23 16:00 | 83.42 | 105.26 | 83.42 | 0 | 0 | 0 | 6.12 | 21.84 | 0
2025-07-23 17:00 | 81.34 | 91.44 | 81.34 | 0 | 0 | 0 | 6.12 | 10.1 | 0
2025-07-23 18:00 | 77.6 | 65.4 | 65.4 | 8.81 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-23 19:00 | 75 | 8.54 | 8.54 | 64.69 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-23 20:00 | 70.17 | 0 | 0 | 70.17 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 21:00 | 65.9 | 0 | 0 | 65.9 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 22:00 | 62.73 | 0 | 0 | 62.73 | 0 | 0 | 0.68 | 0 | 0
2025-07-23 23:00 | 59.21 | 0 | 0 | 59.21 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 | 56.04 | 0 | 0 | 56.04 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 01:00 | 53.76 | 0 | 0 | 53.76 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 02:00 | 52.41 | 0 | 0 | 52.41 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 03:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 04:00 | 52.09 | 0 | 0 | 52.09 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 05:00 | 52.76 | 6.73 | 6.73 | 46.03 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 06:00 | 54.59 | 60.36 | 57.99 | 0 | 3.4 | 0 | 3.91 | 2.37 | 0
2025-07-24 07:00 | 58.46 | 87.78 | 60.79 | 0 | 2.33 | 0 | 6.12 | 26.99 | 0
2025-07-24 08:00 | 60.35 | 101.23 | 60.35 | 0 | 0 | 0 | 6.12 | 40.88 | 0
2025-07-24 09:00 | 63.65 | 105.31 | 63.65 | 0 | 0 | 0 | 6.12 | 41.65 | 0
2025-07-24 10:00 | 65.91 | 108.4 | 65.91 | 0 | 0 | 0 | 6.12 | 42.5 | 0
2025-07-24 11:00 | 66.72 | 104.11 | 66.72 | 0 | 0 | 0 | 6.12 | 37.38 | 0
2025-07-24 12:00 | 68.53 | 100.8 | 68.53 | 0 | 0 | 0 | 6.12 | 32.27 | 0
2025-07-24 13:00 | 68.67 | 101.92 | 68.67 | 0 | 0 | 0 | 6.12 | 33.26 | 0
2025-07-24 14:00 | 68.49 | 106.57 | 68.49 | 0 | 0 | 0 | 6.12 | 38.08 | 0
2025-07-24 15:00 | 69.6 | 103.99 | 69.6 | 0 | 0 | 0 | 6.12 | 34.38 | 0
2025-07-24 16:00 | 69.18 | 95.65 | 69.18 | 0 | 0 | 0 | 6.12 | 26.47 | 0
2025-07-24 17:00 | 68.78 | 83.98 | 68.78 | 0 | 0 | 0 | 6.12 | 15.21 | 0
2025-07-24 18:00 | 69.22 | 62.72 | 62.72 | 3.1 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-24 19:00 | 66.27 | 7.61 | 7.61 | 56.89 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-24 20:00 | 65.55 | 0 | 0 | 65.55 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 21:00 | 62.72 | 0 | 0 | 62.72 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 22:00 | 61.18 | 0 | 0 | 61.18 | 0 | 0 | 0.68 | 0 | 0
2025-07-24 23:00 | 58.24 | 0 | 0 | 58.24 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 | 56 | 0 | 0 | 56 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 01:00 | 53.09 | 0 | 0 | 53.09 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 02:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 03:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 04:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 05:00 | 53.8 | 8.71 | 8.71 | 45.09 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 06:00 | 55.36 | 78.4 | 58.76 | 0 | 3.4 | 0 | 3.91 | 19.64 | 0
2025-07-25 07:00 | 58.9 | 106.63 | 61.23 | 0 | 2.33 | 0 | 6.12 | 45.4 | 0
2025-07-25 08:00 | 63.35 | 119.37 | 63.35 | 0 | 0 | 0 | 6.12 | 56.02 | 0
2025-07-25 09:00 | 65.82 | 120.68 | 65.82 | 0 | 0 | 0 | 6.12 | 54.86 | 0
2025-07-25 10:00 | 70.13 | 120.73 | 70.13 | 0 | 0 | 0 | 6.12 | 50.6 | 0
2025-07-25 11:00 | 72.41 | 118.24 | 72.41 | 0 | 0 | 0 | 6.12 | 45.83 | 0
2025-07-25 12:00 | 75.65 | 116.39 | 75.65 | 0 | 0 | 0 | 6.12 | 40.74 | 0
2025-07-25 13:00 | 78.2 | 117.4 | 78.2 | 0 | 0 | 0 | 6.12 | 39.2 | 0
2025-07-25 14:00 | 79.48 | 118.64 | 79.48 | 0 | 0 | 0 | 6.12 | 39.17 | 0
2025-07-25 15:00 | 79.37 | 119.6 | 79.37 | 0 | 0 | 0 | 6.12 | 40.23 | 0
2025-07-25 16:00 | 78.87 | 116.75 | 78.87 | 0 | 0 | 0 | 6.12 | 37.88 | 0
2025-07-25 17:00 | 78.38 | 105.49 | 78.38 | 0 | 0 | 0 | 6.12 | 27.11 | 0
2025-07-25 18:00 | 76.27 | 78.95 | 76.27 | 0 | 0 | 0 | 6.12 | 2.69 | 0
2025-07-25 19:00 | 73.53 | 8.2 | 8.2 | 61.94 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-25 20:00 | 70.3 | 0 | 0 | 68.54 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-25 21:00 | 65.84 | 0 | 0 | 65.84 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 22:00 | 61.98 | 0 | 0 | 61.98 | 0 | 0 | 0.68 | 0 | 0
2025-07-25 23:00 | 59.41 | 0 | 0 | 59.41 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 01:00 | 53.05 | 0 | 0 | 53.05 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 02:00 | 51.63 | 0 | 0 | 51.63 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 03:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 04:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 05:00 | 53.53 | 9.93 | 9.93 | 43.6 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 06:00 | 56.26 | 8.9 | 8.9 | 47.36 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 07:00 | 58.86 | 55.83 | 55.83 | 3.03 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 08:00 | 62.24 | 95.9 | 65.64 | 0 | 3.4 | 0 | 3.91 | 30.26 | 0
2025-07-26 09:00 | 63.79 | 111.69 | 66.12 | 0 | 2.33 | 0 | 6.12 | 45.57 | 0
2025-07-26 10:00 | 67.92 | 104.11 | 67.92 | 0 | 0 | 0 | 6.12 | 36.19 | 0
2025-07-26 11:00 | 70.84 | 85.09 | 70.84 | 0 | 0 | 0 | 6.12 | 14.25 | 0
2025-07-26 12:00 | 71.95 | 45.58 | 45.58 | 22.97 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-26 13:00 | 74.03 | 26.67 | 26.67 | 45.59 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-26 14:00 | 74.94 | 111.76 | 78.34 | 0 | 3.4 | 0 | 3.91 | 33.42 | 0
2025-07-26 15:00 | 75.71 | 42.52 | 42.52 | 30.11 | 0 | 3.07 | 0.68 | 0 | 0
2025-07-26 16:00 | 76.17 | 36.28 | 36.28 | 39.9 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 17:00 | 75.37 | 18.04 | 18.04 | 57.33 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 18:00 | 72.31 | 0.85 | 0.85 | 71.46 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 19:00 | 70.76 | 10.68 | 10.68 | 60.08 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 20:00 | 68.07 | 0 | 0 | 68.07 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 21:00 | 64.95 | 0 | 0 | 64.95 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 22:00 | 61.77 | 0 | 0 | 61.77 | 0 | 0 | 0.68 | 0 | 0
2025-07-26 23:00 | 58.63 | 0 | 0 | 58.63 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 | 56.52 | 0 | 0 | 56.52 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 01:00 | 54.08 | 0 | 0 | 54.08 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 02:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 03:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 04:00 | 52.59 | 0 | 0 | 52.59 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 05:00 | 53.69 | 7.23 | 7.23 | 46.46 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 06:00 | 56.24 | 74.55 | 59.64 | 0 | 3.4 | 0 | 3.91 | 14.9 | 0
2025-07-27 07:00 | 58.45 | 102.17 | 60.78 | 0 | 2.33 | 0 | 6.12 | 41.4 | 0
2025-07-27 08:00 | 61.41 | 112.7 | 61.41 | 0 | 0 | 0 | 6.12 | 51.29 | 0
2025-07-27 09:00 | 64.33 | 116.54 | 64.33 | 0 | 0 | 0 | 6.12 | 52.21 | 0
2025-07-27 10:00 | 66.02 | 116.2 | 66.02 | 0 | 0 | 0 | 6.12 | 50.18 | 0
2025-07-27 11:00 | 69.37 | 113.6 | 69.37 | 0 | 0 | 0 | 6.12 | 44.23 | 0
2025-07-27 12:00 | 70.98 | 111.26 | 70.98 | 0 | 0 | 0 | 6.12 | 40.28 | 0
2025-07-27 13:00 | 72.09 | 112.72 | 72.09 | 0 | 0 | 0 | 6.12 | 40.64 | 0
2025-07-27 14:00 | 74.22 | 114.53 | 74.22 | 0 | 0 | 0 | 6.12 | 40.31 | 0
2025-07-27 15:00 | 74.03 | 115.06 | 74.03 | 0 | 0 | 0 | 6.12 | 41.03 | 0
2025-07-27 16:00 | 73.49 | 112.18 | 73.49 | 0 | 0 | 0 | 6.12 | 38.7 | 0
2025-07-27 17:00 | 72.4 | 102.36 | 72.4 | 0 | 0 | 0 | 6.12 | 29.96 | 0
2025-07-27 18:00 | 71.46 | 76.27 | 71.46 | 0 | 0 | 0 | 6.12 | 4.81 | 0
2025-07-27 19:00 | 69.91 | 6.88 | 6.88 | 59.63 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-27 20:00 | 66.62 | 0 | 0 | 64.85 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-27 21:00 | 64.27 | 0 | 0 | 64.27 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 22:00 | 61.74 | 0 | 0 | 61.74 | 0 | 0 | 0.68 | 0 | 0
2025-07-27 23:00 | 57.39 | 0 | 0 | 57.39 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 | 55.68 | 0 | 0 | 55.68 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 01:00 | 53.32 | 0 | 0 | 53.32 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 02:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 03:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 04:00 | 52.21 | 0 | 0 | 52.21 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 05:00 | 54.5 | 1.76 | 1.76 | 52.74 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 06:00 | 55.55 | 34.42 | 34.42 | 21.12 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 07:00 | 58.6 | 72.48 | 62 | 0 | 3.4 | 0 | 3.91 | 10.48 | 0
2025-07-28 08:00 | 62.53 | 104.53 | 64.86 | 0 | 2.33 | 0 | 6.12 | 39.67 | 0
2025-07-28 09:00 | 64.42 | 107.54 | 64.42 | 0 | 0 | 0 | 6.12 | 43.12 | 0
2025-07-28 10:00 | 68.61 | 90.78 | 68.61 | 0 | 0 | 0 | 6.12 | 22.17 | 0
2025-07-28 11:00 | 70.38 | 92.16 | 70.38 | 0 | 0 | 0 | 6.12 | 21.78 | 0
2025-07-28 12:00 | 73.46 | 69.64 | 69.64 | 0.42 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-28 13:00 | 74.56 | 67.42 | 67.42 | 5.37 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-28 14:00 | 75.32 | 70.45 | 70.45 | 4.87 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 15:00 | 75.47 | 88.94 | 78.87 | 0 | 3.4 | 0 | 3.91 | 10.08 | 0
2025-07-28 16:00 | 74.86 | 110.59 | 77.18 | 0 | 2.33 | 0 | 6.12 | 33.41 | 0
2025-07-28 17:00 | 74.22 | 116.87 | 74.22 | 0 | 0 | 0 | 6.12 | 42.65 | 0
2025-07-28 18:00 | 73.02 | 92.69 | 73.02 | 0 | 0 | 0 | 6.12 | 19.68 | 0
2025-07-28 19:00 | 70.37 | 10.98 | 10.98 | 55.99 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-28 20:00 | 67.55 | 0 | 0 | 65.78 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-28 21:00 | 64.57 | 0 | 0 | 64.57 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 22:00 | 62.03 | 0 | 0 | 62.03 | 0 | 0 | 0.68 | 0 | 0
2025-07-28 23:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 | 55.42 | 0 | 0 | 55.42 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 01:00 | 53.2 | 0 | 0 | 53.2 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 02:00 | 52.32 | 0 | 0 | 52.32 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 03:00 | 52.41 | 0 | 0 | 52.41 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 04:00 | 52.7 | 0 | 0 | 52.7 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 05:00 | 52.91 | 0.87 | 0.87 | 52.04 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 06:00 | 55.63 | 55.55 | 55.55 | 0.07 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 07:00 | 58.15 | 115.14 | 61.55 | 0 | 3.4 | 0 | 3.91 | 53.59 | 0
2025-07-29 08:00 | 61.77 | 117.4 | 64.1 | 0 | 2.33 | 0 | 6.12 | 53.3 | 0
2025-07-29 09:00 | 66.18 | 90.38 | 66.18 | 0 | 0 | 0 | 6.12 | 24.2 | 0
2025-07-29 10:00 | 68.08 | 87.19 | 68.08 | 0 | 0 | 0 | 6.12 | 19.11 | 0
2025-07-29 11:00 | 71.11 | 66.03 | 66.03 | 1.68 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-29 12:00 | 74.16 | 87.75 | 77.56 | 0 | 3.4 | 0 | 5.77 | 10.19 | 0
2025-07-29 13:00 | 76.72 | 20.34 | 20.34 | 52.98 | 0 | 3.4 | 2.19 | 0 | 0
2025-07-29 14:00 | 78.14 | 7.29 | 7.29 | 69.41 | 0 | 1.44 | 0.68 | 0 | 0
2025-07-29 15:00 | 78.47 | 21.16 | 21.16 | 57.31 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 16:00 | 78.42 | 4.23 | 4.23 | 74.19 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 17:00 | 75.7 | 2.37 | 2.37 | 73.32 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 18:00 | 75.16 | 0.72 | 0.72 | 74.44 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 19:00 | 71.77 | 0 | 0 | 71.77 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 20:00 | 69.16 | 0 | 0 | 69.16 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 21:00 | 64.72 | 0 | 0 | 64.72 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 22:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 0.68 | 0 | 0
2025-07-29 23:00 | 58.74 | 0 | 0 | 58.74 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 | 56.46 | 0 | 0 | 56.46 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 01:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 02:00 | 52.14 | 0 | 0 | 52.14 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 03:00 | 51.1 | 0 | 0 | 51.1 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 04:00 | 52.38 | 0 | 0 | 52.38 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 05:00 | 53.94 | 0.02 | 0.02 | 53.93 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 06:00 | 56.53 | 15.89 | 15.89 | 40.63 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 07:00 | 58.74 | 9.34 | 9.34 | 49.4 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 08:00 | 63.23 | 64.1 | 64.1 | 0 | 0.87 | 0 | 1.51 | 0 | 0
2025-07-30 09:00 | 67.63 | 68.63 | 68.63 | 0 | 1 | 0 | 2.46 | 0 | 0
2025-07-30 10:00 | 70.47 | 14.56 | 14.56 | 54.22 | 0 | 1.69 | 0.68 | 0 | 0
2025-07-30 11:00 | 75.79 | 7.51 | 7.51 | 68.28 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 12:00 | 79.67 | 39.52 | 39.52 | 40.15 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 13:00 | 81.97 | 94.27 | 85.37 | 0 | 3.4 | 0 | 3.91 | 8.9 | 0
2025-07-30 14:00 | 83.35 | 93.09 | 85.68 | 0 | 2.33 | 0 | 6.12 | 7.41 | 0
2025-07-30 15:00 | 85.07 | 5.87 | 5.87 | 75.8 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-30 16:00 | 83.36 | 88.06 | 86.76 | 0 | 3.4 | 0 | 5.77 | 1.3 | 0
2025-07-30 17:00 | 82.01 | 96.7 | 82.38 | 0 | 0.37 | 0 | 6.12 | 14.32 | 0
2025-07-30 18:00 | 79.17 | 59.22 | 59.22 | 16.55 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-30 19:00 | 75.84 | 2.83 | 2.83 | 71.25 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-30 20:00 | 70.98 | 0 | 0 | 70.98 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 21:00 | 66.61 | 0 | 0 | 66.61 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 22:00 | 62.81 | 0 | 0 | 62.81 | 0 | 0 | 0.68 | 0 | 0
2025-07-30 23:00 | 59.51 | 0 | 0 | 59.51 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 | 56.77 | 0 | 0 | 56.77 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 01:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 02:00 | 52.26 | 0 | 0 | 52.26 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 03:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 04:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 05:00 | 53.02 | 8.51 | 8.51 | 44.51 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 06:00 | 55.29 | 82.69 | 58.69 | 0 | 3.4 | 0 | 3.91 | 24.01 | 0
2025-07-31 07:00 | 57.98 | 105.96 | 60.31 | 0 | 2.33 | 0 | 6.12 | 45.65 | 0
2025-07-31 08:00 | 61.14 | 130.17 | 61.14 | 0 | 0 | 0 | 6.12 | 69.03 | 0
2025-07-31 09:00 | 64.24 | 132.89 | 64.24 | 0 | 0 | 0 | 6.12 | 68.65 | 0
2025-07-31 10:00 | 66.99 | 131.21 | 66.99 | 0 | 0 | 0 | 6.12 | 64.22 | 0
2025-07-31 11:00 | 69.03 | 93.86 | 69.03 | 0 | 0 | 0 | 6.12 | 24.82 | 0
2025-07-31 12:00 | 70.18 | 59.59 | 59.59 | 7.19 | 0 | 3.4 | 2.54 | 0 | 0
2025-07-31 13:00 | 72.5 | 68.13 | 68.13 | 2.59 | 0 | 1.77 | 0.68 | 0 | 0
2025-07-31 14:00 | 72.87 | 53.84 | 53.84 | 19.04 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 15:00 | 73.73 | 53.47 | 53.47 | 20.26 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 16:00 | 72.54 | 13.78 | 13.78 | 58.76 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 17:00 | 71.33 | 6.93 | 6.93 | 64.4 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 18:00 | 70.83 | 0.78 | 0.78 | 70.05 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 19:00 | 69.68 | 0 | 0 | 69.68 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 20:00 | 66.83 | 0 | 0 | 66.83 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 21:00 | 63.98 | 0 | 0 | 63.98 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 22:00 | 60.74 | 0 | 0 | 60.74 | 0 | 0 | 0.68 | 0 | 0
2025-07-31 23:00 | 59.15 | 0 | 0 | 59.15 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 | 55.24 | 0 | 0 | 55.24 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 01:00 | 53.14 | 0 | 0 | 53.14 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 02:00 | 52.38 | 0 | 0 | 52.38 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 03:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 04:00 | 52.73 | 0 | 0 | 52.73 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 05:00 | 53.82 | 0.03 | 0.03 | 53.78 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 06:00 | 56.2 | 9.5 | 9.5 | 46.7 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 07:00 | 58.96 | 30.39 | 30.39 | 28.58 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 08:00 | 62.02 | 64.65 | 64.65 | 0 | 2.62 | 0 | 3.17 | 0 | 0
2025-08-01 09:00 | 65.25 | 55.41 | 55.41 | 7.47 | 0 | 2.37 | 0.68 | 0 | 0
2025-08-01 10:00 | 69.39 | 48.7 | 48.7 | 20.69 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 11:00 | 72.4 | 41.39 | 41.39 | 31.02 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 12:00 | 76.09 | 8.05 | 8.05 | 68.04 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 13:00 | 78.51 | 8.05 | 8.05 | 70.47 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 14:00 | 80.27 | 20.11 | 20.11 | 60.16 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 15:00 | 80.21 | 24.2 | 24.2 | 56.01 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 16:00 | 80 | 14.48 | 14.48 | 65.52 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 17:00 | 77.96 | 11.6 | 11.6 | 66.36 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 18:00 | 75.6 | 2.03 | 2.03 | 73.57 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 19:00 | 73.13 | 0 | 0 | 73.13 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 20:00 | 69.26 | 0 | 0 | 69.26 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 21:00 | 65.91 | 0 | 0 | 65.91 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 22:00 | 61.57 | 0 | 0 | 61.57 | 0 | 0 | 0.68 | 0 | 0
2025-08-01 23:00 | 58.24 | 0 | 0 | 58.24 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 | 56 | 0 | 0 | 56 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 01:00 | 53.92 | 0 | 0 | 53.92 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 02:00 | 51.58 | 0 | 0 | 51.58 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 03:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 04:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 05:00 | 53.48 | 1.68 | 1.68 | 51.81 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 06:00 | 56.39 | 20.79 | 20.79 | 35.6 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 07:00 | 58.9 | 38.09 | 38.09 | 20.82 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 08:00 | 62.12 | 72.48 | 65.52 | 0 | 3.4 | 0 | 3.91 | 6.96 | 0
2025-08-02 09:00 | 66.05 | 101.7 | 68.38 | 0 | 2.33 | 0 | 6.12 | 33.32 | 0
2025-08-02 10:00 | 68.04 | 106.4 | 68.04 | 0 | 0 | 0 | 6.12 | 38.36 | 0
2025-08-02 11:00 | 70.89 | 88.94 | 70.89 | 0 | 0 | 0 | 6.12 | 18.04 | 0
2025-08-02 12:00 | 73.54 | 86.72 | 73.54 | 0 | 0 | 0 | 6.12 | 13.18 | 0
2025-08-02 13:00 | 75.67 | 87.77 | 75.67 | 0 | 0 | 0 | 6.12 | 12.11 | 0
2025-08-02 14:00 | 75.79 | 100.46 | 75.79 | 0 | 0 | 0 | 6.12 | 24.67 | 0
2025-08-02 15:00 | 77.26 | 69.25 | 69.25 | 4.61 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-02 16:00 | 76.7 | 57.18 | 57.18 | 17.74 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-02 17:00 | 76.19 | 38.14 | 38.14 | 38.04 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 18:00 | 74.08 | 27.25 | 27.25 | 46.82 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 19:00 | 71.08 | 2.48 | 2.48 | 68.61 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 20:00 | 68.68 | 0 | 0 | 68.68 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 21:00 | 65.46 | 0 | 0 | 65.46 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 22:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 0.68 | 0 | 0
2025-08-02 23:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 01:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 02:00 | 51.69 | 0 | 0 | 51.69 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 03:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 04:00 | 51.58 | 0 | 0 | 51.58 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 05:00 | 53.2 | 3.55 | 3.55 | 49.65 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 06:00 | 55.06 | 71.57 | 58.46 | 0 | 3.4 | 0 | 3.91 | 13.11 | 0
2025-08-03 07:00 | 58.61 | 113.33 | 60.94 | 0 | 2.33 | 0 | 6.12 | 52.4 | 0
2025-08-03 08:00 | 62.01 | 126.72 | 62.01 | 0 | 0 | 0 | 6.12 | 64.71 | 0
2025-08-03 09:00 | 65.46 | 124.76 | 65.46 | 0 | 0 | 0 | 6.12 | 59.3 | 0
2025-08-03 10:00 | 68.68 | 116.48 | 68.68 | 0 | 0 | 0 | 6.12 | 47.81 | 0
2025-08-03 11:00 | 71.02 | 55.64 | 55.64 | 11.98 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-03 12:00 | 74.13 | 75.94 | 75.94 | 0 | 1.82 | 0 | 4.27 | 0 | 0
2025-08-03 13:00 | 76.24 | 75.27 | 75.27 | 0 | 0 | 0.97 | 3.25 | 0 | 0
2025-08-03 14:00 | 77.49 | 65.24 | 65.24 | 9.81 | 0 | 2.44 | 0.68 | 0 | 0
2025-08-03 15:00 | 78.15 | 64.68 | 64.68 | 13.48 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 16:00 | 78.4 | 47.8 | 47.8 | 30.6 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 17:00 | 76.85 | 32.05 | 32.05 | 44.8 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 18:00 | 73.94 | 16.1 | 16.1 | 57.84 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 19:00 | 72.13 | 1.2 | 1.2 | 70.94 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 20:00 | 68.99 | 0 | 0 | 68.99 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 21:00 | 64.86 | 0 | 0 | 64.86 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 22:00 | 62.22 | 0 | 0 | 62.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-03 23:00 | 58.44 | 0 | 0 | 58.44 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 | 55.09 | 0 | 0 | 55.09 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 01:00 | 53.69 | 0 | 0 | 53.69 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 02:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 03:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 04:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 05:00 | 53.11 | 2.68 | 2.68 | 50.43 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 06:00 | 56.1 | 57.25 | 57.25 | 0 | 1.16 | 0 | 1.78 | 0 | 0
2025-08-04 07:00 | 58.9 | 91.65 | 62.3 | 0 | 3.4 | 0 | 5.01 | 29.35 | 0
2025-08-04 08:00 | 62.78 | 103.52 | 63.95 | 0 | 1.17 | 0 | 6.12 | 39.57 | 0
2025-08-04 09:00 | 67.09 | 111.52 | 67.09 | 0 | 0 | 0 | 6.12 | 44.43 | 0
2025-08-04 10:00 | 70.73 | 110.2 | 70.73 | 0 | 0 | 0 | 6.12 | 39.48 | 0
2025-08-04 11:00 | 75.1 | 111.82 | 75.1 | 0 | 0 | 0 | 6.12 | 36.73 | 0
2025-08-04 12:00 | 78.2 | 108.56 | 78.2 | 0 | 0 | 0 | 6.12 | 30.35 | 0
2025-08-04 13:00 | 82.55 | 106.04 | 82.55 | 0 | 0 | 0 | 6.12 | 23.49 | 0
2025-08-04 14:00 | 83.56 | 105.9 | 83.56 | 0 | 0 | 0 | 6.12 | 22.34 | 0
2025-08-04 15:00 | 84.88 | 104.83 | 84.88 | 0 | 0 | 0 | 6.12 | 19.95 | 0
2025-08-04 16:00 | 84.35 | 103.73 | 84.35 | 0 | 0 | 0 | 6.12 | 19.39 | 0
2025-08-04 17:00 | 82.57 | 82.17 | 82.17 | 0 | 0 | 0.4 | 5.7 | 0 | 0
2025-08-04 18:00 | 78.71 | 49.7 | 49.7 | 25.61 | 0 | 3.4 | 2.12 | 0 | 0
2025-08-04 19:00 | 75.51 | 2.49 | 2.49 | 71.66 | 0 | 1.37 | 0.68 | 0 | 0
2025-08-04 20:00 | 72.14 | 0 | 0 | 72.14 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 21:00 | 67.77 | 0 | 0 | 67.77 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 22:00 | 63.19 | 0 | 0 | 63.19 | 0 | 0 | 0.68 | 0 | 0
2025-08-04 23:00 | 59.09 | 0 | 0 | 59.09 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 01:00 | 53.79 | 0 | 0 | 53.79 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 02:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 03:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 04:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 05:00 | 53.34 | 1.82 | 1.82 | 51.52 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 06:00 | 55.79 | 48.65 | 48.65 | 7.14 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 07:00 | 58.86 | 81.38 | 62.26 | 0 | 3.4 | 0 | 3.91 | 19.11 | 0
2025-08-05 08:00 | 62.58 | 94.12 | 64.91 | 0 | 2.33 | 0 | 6.12 | 29.21 | 0
2025-08-05 09:00 | 65.99 | 99.43 | 65.99 | 0 | 0 | 0 | 6.12 | 33.43 | 0
2025-08-05 10:00 | 69.65 | 104.29 | 69.65 | 0 | 0 | 0 | 6.12 | 34.64 | 0
2025-08-05 11:00 | 74.98 | 104.69 | 74.98 | 0 | 0 | 0 | 6.12 | 29.71 | 0
2025-08-05 12:00 | 78.78 | 101.65 | 78.78 | 0 | 0 | 0 | 6.12 | 22.87 | 0
2025-08-05 13:00 | 80.38 | 103.22 | 80.38 | 0 | 0 | 0 | 6.12 | 22.83 | 0
2025-08-05 14:00 | 81.16 | 105.53 | 81.16 | 0 | 0 | 0 | 6.12 | 24.37 | 0
2025-08-05 15:00 | 82.01 | 106.68 | 82.01 | 0 | 0 | 0 | 6.12 | 24.67 | 0
2025-08-05 16:00 | 82.08 | 95.23 | 82.08 | 0 | 0 | 0 | 6.12 | 13.15 | 0
2025-08-05 17:00 | 80.83 | 75.42 | 75.42 | 2.01 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-05 18:00 | 76.93 | 38.1 | 38.1 | 37.07 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-05 19:00 | 74.11 | 1.83 | 1.83 | 72.28 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 20:00 | 70.42 | 0 | 0 | 70.42 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 21:00 | 66.72 | 0 | 0 | 66.72 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 22:00 | 62.16 | 0 | 0 | 62.16 | 0 | 0 | 0.68 | 0 | 0
2025-08-05 23:00 | 57.96 | 0 | 0 | 57.96 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 01:00 | 53.98 | 0 | 0 | 53.98 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 03:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 04:00 | 51.75 | 0 | 0 | 51.75 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 05:00 | 53 | 3.05 | 3.05 | 49.95 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 06:00 | 56.28 | 71.84 | 59.68 | 0 | 3.4 | 0 | 3.91 | 12.16 | 0
2025-08-06 07:00 | 59.15 | 114.68 | 61.48 | 0 | 2.33 | 0 | 6.12 | 53.21 | 0
2025-08-06 08:00 | 63.1 | 125.67 | 63.1 | 0 | 0 | 0 | 6.12 | 62.57 | 0
2025-08-06 09:00 | 68 | 127.84 | 68 | 0 | 0 | 0 | 6.12 | 59.84 | 0
2025-08-06 10:00 | 71.35 | 126.04 | 71.35 | 0 | 0 | 0 | 6.12 | 54.69 | 0
2025-08-06 11:00 | 76.11 | 119.86 | 76.11 | 0 | 0 | 0 | 6.12 | 43.75 | 0
2025-08-06 12:00 | 80.5 | 121.21 | 80.5 | 0 | 0 | 0 | 6.12 | 40.7 | 0
2025-08-06 13:00 | 83.34 | 122.61 | 83.34 | 0 | 0 | 0 | 6.12 | 39.28 | 0
2025-08-06 14:00 | 86.06 | 76.11 | 76.11 | 6.55 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-06 15:00 | 86.28 | 26.62 | 26.62 | 57.89 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-06 16:00 | 85.17 | 108.05 | 88.57 | 0 | 3.4 | 0 | 3.91 | 19.48 | 0
2025-08-06 17:00 | 83.65 | 60.44 | 60.44 | 20.14 | 0 | 3.07 | 0.68 | 0 | 0
2025-08-06 18:00 | 80.51 | 44.02 | 44.02 | 36.48 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 19:00 | 76.86 | 4.46 | 4.46 | 72.4 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 20:00 | 72.07 | 0 | 0 | 72.07 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 21:00 | 67.48 | 0 | 0 | 67.48 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 22:00 | 63.01 | 0 | 0 | 63.01 | 0 | 0 | 0.68 | 0 | 0
2025-08-06 23:00 | 58.86 | 0 | 0 | 58.86 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 01:00 | 53.5 | 0 | 0 | 53.5 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 02:00 | 51.79 | 0 | 0 | 51.79 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 03:00 | 52.32 | 0 | 0 | 52.32 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 04:00 | 52.63 | 0 | 0 | 52.63 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 05:00 | 53.67 | 1.34 | 1.34 | 52.33 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 06:00 | 55.76 | 35.2 | 35.2 | 20.56 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 07:00 | 58.4 | 82.91 | 61.8 | 0 | 3.4 | 0 | 3.91 | 21.1 | 0
2025-08-07 08:00 | 61.14 | 101.54 | 63.47 | 0 | 2.33 | 0 | 6.12 | 38.07 | 0
2025-08-07 09:00 | 65.21 | 105.79 | 65.21 | 0 | 0 | 0 | 6.12 | 40.58 | 0
2025-08-07 10:00 | 68.88 | 107.88 | 68.88 | 0 | 0 | 0 | 6.12 | 39 | 0
2025-08-07 11:00 | 72.2 | 102.86 | 72.2 | 0 | 0 | 0 | 6.12 | 30.66 | 0
2025-08-07 12:00 | 75.1 | 95.51 | 75.1 | 0 | 0 | 0 | 6.12 | 20.41 | 0
2025-08-07 13:00 | 77.44 | 94.52 | 77.44 | 0 | 0 | 0 | 6.12 | 17.08 | 0
2025-08-07 14:00 | 77.96 | 96.74 | 77.96 | 0 | 0 | 0 | 6.12 | 18.78 | 0
2025-08-07 15:00 | 78.42 | 78.55 | 78.42 | 0 | 0 | 0 | 6.12 | 0.13 | 0
2025-08-07 16:00 | 79.04 | 77.44 | 77.44 | 0 | 0 | 1.6 | 4.44 | 0 | 0
2025-08-07 17:00 | 77.37 | 64.61 | 64.61 | 9.36 | 0 | 3.4 | 0.86 | 0 | 0
2025-08-07 18:00 | 74.67 | 35.99 | 35.99 | 38.51 | 0 | 0.17 | 0.68 | 0 | 0
2025-08-07 19:00 | 72.03 | 1.14 | 1.14 | 70.89 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 20:00 | 68.78 | 0 | 0 | 68.78 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 21:00 | 65.33 | 0 | 0 | 65.33 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 22:00 | 62.01 | 0 | 0 | 62.01 | 0 | 0 | 0.68 | 0 | 0
2025-08-07 23:00 | 59.71 | 0 | 0 | 59.71 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 | 55.57 | 0 | 0 | 55.57 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 01:00 | 53.64 | 0 | 0 | 53.64 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 02:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 03:00 | 51.21 | 0 | 0 | 51.21 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 04:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 05:00 | 53.51 | 2.9 | 2.9 | 50.62 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 06:00 | 53.28 | 32.28 | 32.28 | 21 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 07:00 | 58.57 | 29.11 | 29.11 | 29.46 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 08:00 | 62.31 | 55.4 | 55.4 | 6.91 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 09:00 | 63.58 | 107.68 | 66.98 | 0 | 3.4 | 0 | 3.91 | 40.69 | 0
2025-08-08 10:00 | 68.46 | 134.54 | 70.78 | 0 | 2.33 | 0 | 6.12 | 63.75 | 0
2025-08-08 11:00 | 69.1 | 119.27 | 69.1 | 0 | 0 | 0 | 6.12 | 50.17 | 0
2025-08-08 12:00 | 73.28 | 54.22 | 54.22 | 15.66 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-08 13:00 | 74.53 | 9.08 | 9.08 | 63.69 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-08 14:00 | 74.43 | 8.18 | 8.18 | 66.24 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 15:00 | 76.18 | 17.96 | 17.96 | 58.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 16:00 | 76.18 | 53.71 | 53.71 | 22.46 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 17:00 | 74.72 | 62.09 | 62.09 | 12.63 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 18:00 | 73.1 | 63.25 | 63.25 | 9.85 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 19:00 | 70.28 | 2.28 | 2.28 | 68 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 20:00 | 66.76 | 0 | 0 | 66.76 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 21:00 | 64.93 | 0 | 0 | 64.93 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 22:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 0.68 | 0 | 0
2025-08-08 23:00 | 58.8 | 0 | 0 | 58.8 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 01:00 | 52.53 | 0 | 0 | 52.53 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 02:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 03:00 | 50.62 | 0 | 0 | 50.62 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 04:00 | 51.92 | 0 | 0 | 51.92 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 05:00 | 53.48 | 0.06 | 0.06 | 53.43 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 06:00 | 54.78 | 7.34 | 7.34 | 47.44 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 07:00 | 58.73 | 11.16 | 11.16 | 47.57 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 08:00 | 61.93 | 17.12 | 17.12 | 44.81 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 09:00 | 64.85 | 37.63 | 37.63 | 27.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 10:00 | 68.49 | 66.1 | 66.1 | 2.39 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 11:00 | 70.79 | 44.63 | 44.63 | 26.16 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 12:00 | 74.31 | 54.55 | 54.55 | 19.75 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 13:00 | 76.54 | 63.43 | 63.43 | 13.11 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 14:00 | 77.91 | 59.23 | 59.23 | 18.68 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 15:00 | 78.45 | 45.1 | 45.1 | 33.35 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 16:00 | 77.95 | 22.63 | 22.63 | 55.32 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 17:00 | 76.4 | 9.81 | 9.81 | 66.6 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 18:00 | 74.62 | 0 | 0 | 74.62 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 19:00 | 72.27 | 0 | 0 | 72.27 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 20:00 | 68.53 | 0 | 0 | 68.53 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 21:00 | 65.28 | 0 | 0 | 65.28 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 22:00 | 61.54 | 0 | 0 | 61.54 | 0 | 0 | 0.68 | 0 | 0
2025-08-09 23:00 | 58.02 | 0 | 0 | 58.02 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 01:00 | 52.98 | 0 | 0 | 52.98 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 02:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 03:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 04:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 05:00 | 53.1 | 1.02 | 1.02 | 52.08 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 06:00 | 55.25 | 66.56 | 58.65 | 0 | 3.4 | 0 | 3.91 | 7.92 | 0
2025-08-10 07:00 | 57.62 | 111.57 | 59.94 | 0 | 2.33 | 0 | 6.12 | 51.63 | 0
2025-08-10 08:00 | 62.09 | 121.92 | 62.09 | 0 | 0 | 0 | 6.12 | 59.83 | 0
2025-08-10 09:00 | 65.77 | 123.12 | 65.77 | 0 | 0 | 0 | 6.12 | 57.35 | 0
2025-08-10 10:00 | 69.87 | 120.86 | 69.87 | 0 | 0 | 0 | 6.12 | 50.99 | 0
2025-08-10 11:00 | 72.75 | 117.57 | 72.75 | 0 | 0 | 0 | 6.12 | 44.82 | 0
2025-08-10 12:00 | 77.05 | 115.54 | 77.05 | 0 | 0 | 0 | 6.12 | 38.48 | 0
2025-08-10 13:00 | 78.31 | 116.64 | 78.31 | 0 | 0 | 0 | 6.12 | 38.33 | 0
2025-08-10 14:00 | 79.57 | 119.19 | 79.57 | 0 | 0 | 0 | 6.12 | 39.62 | 0
2025-08-10 15:00 | 80.03 | 120.22 | 80.03 | 0 | 0 | 0 | 6.12 | 40.19 | 0
2025-08-10 16:00 | 79.14 | 118.19 | 79.14 | 0 | 0 | 0 | 6.12 | 39.05 | 0
2025-08-10 17:00 | 79.27 | 107.48 | 79.27 | 0 | 0 | 0 | 6.12 | 28.21 | 0
2025-08-10 18:00 | 76.79 | 62.66 | 62.66 | 10.73 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-10 19:00 | 73.31 | 0.89 | 0.89 | 70.66 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-10 20:00 | 68.99 | 0 | 0 | 68.99 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 21:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 22:00 | 61.72 | 0 | 0 | 61.72 | 0 | 0 | 0.68 | 0 | 0
2025-08-10 23:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 | 56.17 | 0 | 0 | 56.17 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 01:00 | 53.55 | 0 | 0 | 53.55 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 02:00 | 52.92 | 0 | 0 | 52.92 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 03:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 04:00 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 05:00 | 52.91 | 0.92 | 0.92 | 51.99 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 06:00 | 54.52 | 47.79 | 47.79 | 6.74 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 07:00 | 58.23 | 65.95 | 61.63 | 0 | 3.4 | 0 | 3.91 | 4.32 | 0
2025-08-11 08:00 | 62.37 | 97.16 | 64.7 | 0 | 2.33 | 0 | 6.12 | 32.46 | 0
2025-08-11 09:00 | 65.8 | 87.26 | 65.8 | 0 | 0 | 0 | 6.12 | 21.45 | 0
2025-08-11 10:00 | 69.25 | 97.06 | 69.25 | 0 | 0 | 0 | 6.12 | 27.81 | 0
2025-08-11 11:00 | 72.25 | 111.28 | 72.25 | 0 | 0 | 0 | 6.12 | 39.03 | 0
2025-08-11 12:00 | 75.9 | 124.36 | 75.9 | 0 | 0 | 0 | 6.12 | 48.46 | 0
2025-08-11 13:00 | 78.63 | 124.52 | 78.63 | 0 | 0 | 0 | 6.12 | 45.89 | 0
2025-08-11 14:00 | 79.82 | 128.06 | 79.82 | 0 | 0 | 0 | 6.12 | 48.25 | 0
2025-08-11 15:00 | 80.19 | 129.49 | 80.19 | 0 | 0 | 0 | 6.12 | 49.3 | 0
2025-08-11 16:00 | 79.2 | 127.28 | 79.2 | 0 | 0 | 0 | 6.12 | 48.08 | 0
2025-08-11 17:00 | 78.56 | 116.18 | 78.56 | 0 | 0 | 0 | 6.12 | 37.62 | 0
2025-08-11 18:00 | 74.22 | 69.63 | 69.63 | 1.19 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-11 19:00 | 72.94 | 1.86 | 1.86 | 69.32 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-11 20:00 | 70.53 | 0 | 0 | 70.53 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 21:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 22:00 | 61.68 | 0 | 0 | 61.68 | 0 | 0 | 0.68 | 0 | 0
2025-08-11 23:00 | 58.37 | 0 | 0 | 58.37 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 | 55.04 | 0 | 0 | 55.04 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 01:00 | 53.67 | 0 | 0 | 53.67 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 02:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 03:00 | 51.39 | 0 | 0 | 51.39 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 04:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 05:00 | 53.16 | 0.77 | 0.77 | 52.39 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 06:00 | 56.86 | 48.65 | 48.65 | 8.21 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 07:00 | 58 | 92.58 | 61.4 | 0 | 3.4 | 0 | 3.91 | 31.18 | 0
2025-08-12 08:00 | 60.97 | 108.95 | 63.3 | 0 | 2.33 | 0 | 6.12 | 45.66 | 0
2025-08-12 09:00 | 63.01 | 113.12 | 63.01 | 0 | 0 | 0 | 6.12 | 50.11 | 0
2025-08-12 10:00 | 66.4 | 110.61 | 66.4 | 0 | 0 | 0 | 6.12 | 44.21 | 0
2025-08-12 11:00 | 69.69 | 109.43 | 69.69 | 0 | 0 | 0 | 6.12 | 39.74 | 0
2025-08-12 12:00 | 70.43 | 107.87 | 70.43 | 0 | 0 | 0 | 6.12 | 37.44 | 0
2025-08-12 13:00 | 71.46 | 108.52 | 71.46 | 0 | 0 | 0 | 6.12 | 37.07 | 0
2025-08-12 14:00 | 73.42 | 109.97 | 73.42 | 0 | 0 | 0 | 6.12 | 36.55 | 0
2025-08-12 15:00 | 74.38 | 111.29 | 74.38 | 0 | 0 | 0 | 6.12 | 36.91 | 0
2025-08-12 16:00 | 73.43 | 108.28 | 73.43 | 0 | 0 | 0 | 6.12 | 34.85 | 0
2025-08-12 17:00 | 72.37 | 92.48 | 72.37 | 0 | 0 | 0 | 6.12 | 20.11 | 0
2025-08-12 18:00 | 70.17 | 47.84 | 47.84 | 18.93 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-12 19:00 | 69.34 | 0.64 | 0.64 | 66.94 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-12 20:00 | 67 | 0 | 0 | 67 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 21:00 | 62.97 | 0 | 0 | 62.97 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 22:00 | 61.44 | 0 | 0 | 61.44 | 0 | 0 | 0.68 | 0 | 0
2025-08-12 23:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 01:00 | 53.42 | 0 | 0 | 53.42 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 02:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 03:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 04:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 05:00 | 52.22 | 0.62 | 0.62 | 51.61 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 06:00 | 54.59 | 13.18 | 13.18 | 41.41 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 07:00 | 57.87 | 2.23 | 2.23 | 55.64 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 08:00 | 61.55 | 21.47 | 21.47 | 40.09 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 09:00 | 65.46 | 23.96 | 23.96 | 41.5 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 10:00 | 69.08 | 44.7 | 44.7 | 24.38 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 11:00 | 72.9 | 37.2 | 37.2 | 35.7 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 12:00 | 75.87 | 81 | 79.27 | 0 | 3.4 | 0 | 3.91 | 1.73 | 0
2025-08-13 13:00 | 77.13 | 129.61 | 79.45 | 0 | 2.33 | 0 | 6.12 | 50.16 | 0
2025-08-13 14:00 | 79.11 | 124.17 | 79.11 | 0 | 0 | 0 | 6.12 | 45.06 | 0
2025-08-13 15:00 | 79.06 | 124.52 | 79.06 | 0 | 0 | 0 | 6.12 | 45.47 | 0
2025-08-13 16:00 | 78.9 | 99.67 | 78.9 | 0 | 0 | 0 | 6.12 | 20.77 | 0
2025-08-13 17:00 | 77.72 | 45.69 | 45.69 | 28.63 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-13 18:00 | 73.59 | 20.63 | 20.63 | 51.19 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-13 19:00 | 73.55 | 0.13 | 0.13 | 73.42 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 20:00 | 69.2 | 0 | 0 | 69.2 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 21:00 | 64.96 | 0 | 0 | 64.96 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 22:00 | 62.58 | 0 | 0 | 62.58 | 0 | 0 | 0.68 | 0 | 0
2025-08-13 23:00 | 58.06 | 0 | 0 | 58.06 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 | 55.37 | 0 | 0 | 55.37 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 01:00 | 52.84 | 0 | 0 | 52.84 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 02:00 | 52.52 | 0 | 0 | 52.52 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 03:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 04:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 05:00 | 53.69 | 0.53 | 0.53 | 53.16 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 06:00 | 55.6 | 55.05 | 55.05 | 0.55 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 07:00 | 58.2 | 103.93 | 61.6 | 0 | 3.4 | 0 | 3.91 | 42.33 | 0
2025-08-14 08:00 | 62.2 | 115.2 | 64.53 | 0 | 2.33 | 0 | 6.12 | 50.67 | 0
2025-08-14 09:00 | 66.63 | 117 | 66.63 | 0 | 0 | 0 | 6.12 | 50.37 | 0
2025-08-14 10:00 | 69.27 | 115.36 | 69.27 | 0 | 0 | 0 | 6.12 | 46.09 | 0
2025-08-14 11:00 | 72.7 | 112.78 | 72.7 | 0 | 0 | 0 | 6.12 | 40.08 | 0
2025-08-14 12:00 | 75.78 | 110.89 | 75.78 | 0 | 0 | 0 | 6.12 | 35.1 | 0
2025-08-14 13:00 | 78.71 | 112.3 | 78.71 | 0 | 0 | 0 | 6.12 | 33.59 | 0
2025-08-14 14:00 | 79.25 | 114.07 | 79.25 | 0 | 0 | 0 | 6.12 | 34.82 | 0
2025-08-14 15:00 | 79.92 | 113.71 | 79.92 | 0 | 0 | 0 | 6.12 | 33.78 | 0
2025-08-14 16:00 | 78.78 | 112.54 | 78.78 | 0 | 0 | 0 | 6.12 | 33.75 | 0
2025-08-14 17:00 | 77.47 | 98.56 | 77.47 | 0 | 0 | 0 | 6.12 | 21.09 | 0
2025-08-14 18:00 | 75.44 | 50.58 | 50.58 | 21.45 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-14 19:00 | 72.61 | 0.33 | 0.33 | 70.52 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-14 20:00 | 69.99 | 0 | 0 | 69.99 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 21:00 | 65.63 | 0 | 0 | 65.63 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 22:00 | 61.19 | 0 | 0 | 61.19 | 0 | 0 | 0.68 | 0 | 0
2025-08-14 23:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 | 56.18 | 0 | 0 | 56.18 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 01:00 | 53.65 | 0 | 0 | 53.65 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 02:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 03:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 04:00 | 52.22 | 0 | 0 | 52.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 05:00 | 52.59 | 0.43 | 0.43 | 52.17 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 06:00 | 55.69 | 45.74 | 45.74 | 9.95 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 07:00 | 60.01 | 93.33 | 63.41 | 0 | 3.4 | 0 | 3.91 | 29.92 | 0
2025-08-15 08:00 | 63.24 | 107.21 | 65.57 | 0 | 2.33 | 0 | 6.12 | 41.64 | 0
2025-08-15 09:00 | 67.74 | 109.66 | 67.74 | 0 | 0 | 0 | 6.12 | 41.92 | 0
2025-08-15 10:00 | 73.74 | 110.22 | 73.74 | 0 | 0 | 0 | 6.12 | 36.48 | 0
2025-08-15 11:00 | 78.72 | 105.34 | 78.72 | 0 | 0 | 0 | 6.12 | 26.62 | 0
2025-08-15 12:00 | 83.19 | 103.48 | 83.19 | 0 | 0 | 0 | 6.12 | 20.29 | 0
2025-08-15 13:00 | 88.22 | 107.01 | 88.22 | 0 | 0 | 0 | 6.12 | 18.79 | 0
2025-08-15 14:00 | 91 | 109.73 | 91 | 0 | 0 | 0 | 6.12 | 18.73 | 0
2025-08-15 15:00 | 91.18 | 108.42 | 91.18 | 0 | 0 | 0 | 6.12 | 17.24 | 0
2025-08-15 16:00 | 90.25 | 102.98 | 90.25 | 0 | 0 | 0 | 6.12 | 12.73 | 0
2025-08-15 17:00 | 87.38 | 86.28 | 86.28 | 0 | 0 | 1.1 | 4.96 | 0 | 0
2025-08-15 18:00 | 83.82 | 38.55 | 38.55 | 41.87 | 0 | 3.4 | 1.38 | 0 | 0
2025-08-15 19:00 | 78.67 | 0.24 | 0.24 | 77.76 | 0 | 0.66 | 0.68 | 0 | 0
2025-08-15 20:00 | 73.03 | 0 | 0 | 73.03 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 21:00 | 69.08 | 0 | 0 | 69.08 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 22:00 | 63.38 | 0 | 0 | 63.38 | 0 | 0 | 0.68 | 0 | 0
2025-08-15 23:00 | 59.16 | 0 | 0 | 59.16 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 | 55.81 | 0 | 0 | 55.81 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 01:00 | 53.41 | 0 | 0 | 53.41 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 02:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 03:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 04:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 05:00 | 53.24 | 0.34 | 0.34 | 52.9 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 06:00 | 55.54 | 44.03 | 44.03 | 11.51 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 07:00 | 58.42 | 93.76 | 61.82 | 0 | 3.4 | 0 | 3.91 | 31.94 | 0
2025-08-16 08:00 | 61.96 | 104.89 | 64.29 | 0 | 2.33 | 0 | 6.12 | 40.6 | 0
2025-08-16 09:00 | 67.32 | 110.06 | 67.32 | 0 | 0 | 0 | 6.12 | 42.74 | 0
2025-08-16 10:00 | 72.07 | 105.17 | 72.07 | 0 | 0 | 0 | 6.12 | 33.1 | 0
2025-08-16 11:00 | 76.1 | 98.33 | 76.1 | 0 | 0 | 0 | 6.12 | 22.23 | 0
2025-08-16 12:00 | 81.7 | 100.72 | 81.7 | 0 | 0 | 0 | 6.12 | 19.02 | 0
2025-08-16 13:00 | 85.44 | 101.44 | 85.44 | 0 | 0 | 0 | 6.12 | 16 | 0
2025-08-16 14:00 | 88.49 | 102.03 | 88.49 | 0 | 0 | 0 | 6.12 | 13.54 | 0
2025-08-16 15:00 | 87.82 | 94.62 | 87.82 | 0 | 0 | 0 | 6.12 | 6.8 | 0
2025-08-16 16:00 | 86.96 | 87.17 | 86.96 | 0 | 0 | 0 | 6.12 | 0.21 | 0
2025-08-16 17:00 | 84.41 | 74.99 | 74.99 | 6.02 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-16 18:00 | 81.55 | 33.37 | 33.37 | 46.41 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-16 19:00 | 77.15 | 0.13 | 0.13 | 77.02 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 20:00 | 71.77 | 0 | 0 | 71.77 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 21:00 | 67.16 | 0 | 0 | 67.16 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 22:00 | 61.64 | 0 | 0 | 61.64 | 0 | 0 | 0.68 | 0 | 0
2025-08-16 23:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 01:00 | 52.89 | 0 | 0 | 52.89 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 02:00 | 50.84 | 0 | 0 | 50.84 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 03:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 04:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 05:00 | 52.9 | 0.26 | 0.26 | 52.64 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 06:00 | 55.26 | 40.8 | 40.8 | 14.47 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 07:00 | 58.42 | 85.78 | 61.82 | 0 | 3.4 | 0 | 3.91 | 23.96 | 0
2025-08-17 08:00 | 61.06 | 101.54 | 63.39 | 0 | 2.33 | 0 | 6.12 | 38.15 | 0
2025-08-17 09:00 | 64.26 | 108.75 | 64.26 | 0 | 0 | 0 | 6.12 | 44.49 | 0
2025-08-17 10:00 | 67.44 | 109.31 | 67.44 | 0 | 0 | 0 | 6.12 | 41.87 | 0
2025-08-17 11:00 | 69.62 | 106.78 | 69.62 | 0 | 0 | 0 | 6.12 | 37.17 | 0
2025-08-17 12:00 | 71.46 | 107.25 | 71.46 | 0 | 0 | 0 | 6.12 | 35.79 | 0
2025-08-17 13:00 | 73.57 | 108.72 | 73.57 | 0 | 0 | 0 | 6.12 | 35.15 | 0
2025-08-17 14:00 | 74.57 | 110.81 | 74.57 | 0 | 0 | 0 | 6.12 | 36.24 | 0
2025-08-17 15:00 | 74.68 | 107.07 | 74.68 | 0 | 0 | 0 | 6.12 | 32.39 | 0
2025-08-17 16:00 | 73.31 | 98.26 | 73.31 | 0 | 0 | 0 | 6.12 | 24.96 | 0
2025-08-17 17:00 | 72.64 | 84.7 | 72.64 | 0 | 0 | 0 | 6.12 | 12.05 | 0
2025-08-17 18:00 | 71.34 | 35.13 | 35.13 | 32.81 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-17 19:00 | 69.72 | 0 | 0 | 67.95 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-17 20:00 | 66.71 | 0 | 0 | 66.71 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 21:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 22:00 | 61.35 | 0 | 0 | 61.35 | 0 | 0 | 0.68 | 0 | 0
2025-08-17 23:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 | 55.62 | 0 | 0 | 55.62 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 01:00 | 52.35 | 0 | 0 | 52.35 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 02:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 03:00 | 50.73 | 0 | 0 | 50.73 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 04:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 05:00 | 52.72 | 0.07 | 0.07 | 52.65 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 06:00 | 55.68 | 33.84 | 33.84 | 21.84 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 07:00 | 58.03 | 95.61 | 61.43 | 0 | 3.4 | 0 | 3.91 | 34.18 | 0
2025-08-18 08:00 | 62.01 | 116.35 | 64.34 | 0 | 2.33 | 0 | 6.12 | 52.01 | 0
2025-08-18 09:00 | 64.48 | 120.73 | 64.48 | 0 | 0 | 0 | 6.12 | 56.25 | 0
2025-08-18 10:00 | 68.96 | 99.4 | 68.96 | 0 | 0 | 0 | 6.12 | 30.44 | 0
2025-08-18 11:00 | 70.89 | 100.74 | 70.89 | 0 | 0 | 0 | 6.12 | 29.85 | 0
2025-08-18 12:00 | 73.42 | 77.99 | 73.42 | 0 | 0 | 0 | 6.12 | 4.57 | 0
2025-08-18 13:00 | 74.75 | 21.99 | 21.99 | 49.36 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-18 14:00 | 77.18 | 91.35 | 80.58 | 0 | 3.4 | 0 | 5.77 | 10.77 | 0
2025-08-18 15:00 | 76.79 | 78.59 | 77.16 | 0 | 0.37 | 0 | 6.12 | 1.44 | 0
2025-08-18 16:00 | 76.3 | 113.98 | 76.3 | 0 | 0 | 0 | 6.12 | 37.69 | 0
2025-08-18 17:00 | 76.03 | 95.56 | 76.03 | 0 | 0 | 0 | 6.12 | 19.53 | 0
2025-08-18 18:00 | 73.99 | 39.38 | 39.38 | 31.2 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-18 19:00 | 71.37 | 0.09 | 0.09 | 69.51 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-18 20:00 | 67.55 | 0 | 0 | 67.55 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 21:00 | 64.37 | 0 | 0 | 64.37 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 22:00 | 60.97 | 0 | 0 | 60.97 | 0 | 0 | 0.68 | 0 | 0
2025-08-18 23:00 | 58.19 | 0 | 0 | 58.19 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 | 55.61 | 0 | 0 | 55.61 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 01:00 | 52.97 | 0 | 0 | 52.97 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 02:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 03:00 | 51.43 | 0 | 0 | 51.43 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 04:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 05:00 | 53.2 | 0 | 0 | 53.2 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 06:00 | 55.69 | 6.37 | 6.37 | 49.31 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 07:00 | 58.37 | 29.57 | 29.57 | 28.8 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 08:00 | 60.72 | 75.18 | 64.12 | 0 | 3.4 | 0 | 3.91 | 11.06 | 0
2025-08-19 09:00 | 62.87 | 70.01 | 65.19 | 0 | 2.33 | 0 | 6.12 | 4.82 | 0
2025-08-19 10:00 | 65.23 | 73.23 | 65.23 | 0 | 0 | 0 | 6.12 | 8 | 0
2025-08-19 11:00 | 67.73 | 88.45 | 67.73 | 0 | 0 | 0 | 6.12 | 20.72 | 0
2025-08-19 12:00 | 69.91 | 89.1 | 69.91 | 0 | 0 | 0 | 6.12 | 19.19 | 0
2025-08-19 13:00 | 70.44 | 89.57 | 70.44 | 0 | 0 | 0 | 6.12 | 19.13 | 0
2025-08-19 14:00 | 71.13 | 96.25 | 71.13 | 0 | 0 | 0 | 6.12 | 25.12 | 0
2025-08-19 15:00 | 71.15 | 67.61 | 67.61 | 0.14 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-19 16:00 | 70.74 | 86.4 | 74.14 | 0 | 3.4 | 0 | 5.77 | 12.26 | 0
2025-08-19 17:00 | 70.14 | 94.62 | 70.51 | 0 | 0.37 | 0 | 6.12 | 24.11 | 0
2025-08-19 18:00 | 69.14 | 37.53 | 37.53 | 28.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-19 19:00 | 68.3 | 0 | 0 | 66.53 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-19 20:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 21:00 | 62.88 | 0 | 0 | 62.88 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 22:00 | 59.7 | 0 | 0 | 59.7 | 0 | 0 | 0.68 | 0 | 0
2025-08-19 23:00 | 57.73 | 0 | 0 | 57.73 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 01:00 | 53.55 | 0 | 0 | 53.55 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 02:00 | 51.49 | 0 | 0 | 51.49 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 04:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 05:00 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 06:00 | 55.02 | 27.23 | 27.23 | 27.78 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 07:00 | 57.59 | 60.54 | 60.54 | 0 | 2.95 | 0 | 3.48 | 0 | 0
2025-08-20 08:00 | 60.7 | 72.78 | 63.48 | 0 | 2.78 | 0 | 6.12 | 9.3 | 0
2025-08-20 09:00 | 64.06 | 82.12 | 64.06 | 0 | 0 | 0 | 6.12 | 18.06 | 0
2025-08-20 10:00 | 66.79 | 92.7 | 66.79 | 0 | 0 | 0 | 6.12 | 25.91 | 0
2025-08-20 11:00 | 69.63 | 94.4 | 69.63 | 0 | 0 | 0 | 6.12 | 24.77 | 0
2025-08-20 12:00 | 72.94 | 96.22 | 72.94 | 0 | 0 | 0 | 6.12 | 23.28 | 0
2025-08-20 13:00 | 75.2 | 94.74 | 75.2 | 0 | 0 | 0 | 6.12 | 19.54 | 0
2025-08-20 14:00 | 74.33 | 101.89 | 74.33 | 0 | 0 | 0 | 6.12 | 27.57 | 0
2025-08-20 15:00 | 74.67 | 100.08 | 74.67 | 0 | 0 | 0 | 6.12 | 25.41 | 0
2025-08-20 16:00 | 74.45 | 104.43 | 74.45 | 0 | 0 | 0 | 6.12 | 29.98 | 0
2025-08-20 17:00 | 73.79 | 85.74 | 73.79 | 0 | 0 | 0 | 6.12 | 11.95 | 0
2025-08-20 18:00 | 72.54 | 30.92 | 30.92 | 38.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-20 19:00 | 70.04 | 0 | 0 | 68.27 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-20 20:00 | 67.03 | 0 | 0 | 67.03 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 21:00 | 64.1 | 0 | 0 | 64.1 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 22:00 | 60.29 | 0 | 0 | 60.29 | 0 | 0 | 0.68 | 0 | 0
2025-08-20 23:00 | 57.44 | 0 | 0 | 57.44 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 | 54.87 | 0 | 0 | 54.87 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 01:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 02:00 | 50.75 | 0 | 0 | 50.75 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 03:00 | 50.31 | 0 | 0 | 50.31 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 04:00 | 51.72 | 0 | 0 | 51.72 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 05:00 | 52.82 | 0.18 | 0.18 | 52.64 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 06:00 | 55.19 | 57.49 | 57.49 | 0 | 2.3 | 0 | 2.86 | 0 | 0
2025-08-21 07:00 | 56.84 | 118.97 | 60.24 | 0 | 3.4 | 0 | 6.09 | 58.73 | 0
2025-08-21 08:00 | 60.42 | 129.4 | 60.44 | 0 | 0.03 | 0 | 6.12 | 68.95 | 0
2025-08-21 09:00 | 65.18 | 130.71 | 65.18 | 0 | 0 | 0 | 6.12 | 65.53 | 0
2025-08-21 10:00 | 67.2 | 128.06 | 67.2 | 0 | 0 | 0 | 6.12 | 60.85 | 0
2025-08-21 11:00 | 72.74 | 124.36 | 72.74 | 0 | 0 | 0 | 6.12 | 51.63 | 0
2025-08-21 12:00 | 74.29 | 122.26 | 74.29 | 0 | 0 | 0 | 6.12 | 47.98 | 0
2025-08-21 13:00 | 78 | 115.29 | 78 | 0 | 0 | 0 | 6.12 | 37.29 | 0
2025-08-21 14:00 | 78.64 | 19.95 | 19.95 | 55.29 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-21 15:00 | 80.12 | 5.51 | 5.51 | 72.85 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-21 16:00 | 80.69 | 3.66 | 3.66 | 77.03 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 17:00 | 76.44 | 1.77 | 1.77 | 74.67 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 18:00 | 75.55 | 0 | 0 | 75.55 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 19:00 | 71.22 | 0 | 0 | 71.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 20:00 | 68.81 | 0 | 0 | 68.81 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 21:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 22:00 | 61.22 | 0 | 0 | 61.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-21 23:00 | 57.31 | 0 | 0 | 57.31 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 | 55.3 | 0 | 0 | 55.3 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 01:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 02:00 | 51.9 | 0 | 0 | 51.9 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 03:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 04:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 05:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 06:00 | 54.87 | 39.71 | 39.71 | 15.16 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 07:00 | 58.91 | 89.19 | 62.31 | 0 | 3.4 | 0 | 3.91 | 26.88 | 0
2025-08-22 08:00 | 62.27 | 23.77 | 23.77 | 35.44 | 0 | 3.07 | 0.68 | 0 | 0
2025-08-22 09:00 | 65.43 | 48.49 | 48.49 | 16.94 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 10:00 | 70.16 | 123.87 | 73.56 | 0 | 3.4 | 0 | 3.91 | 50.31 | 0
2025-08-22 11:00 | 74.51 | 96.28 | 76.83 | 0 | 2.33 | 0 | 6.12 | 19.45 | 0
2025-08-22 12:00 | 78.99 | 96.27 | 78.99 | 0 | 0 | 0 | 6.12 | 17.28 | 0
2025-08-22 13:00 | 81.43 | 94.9 | 81.43 | 0 | 0 | 0 | 6.12 | 13.46 | 0
2025-08-22 14:00 | 83.22 | 71.77 | 71.77 | 8.05 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-22 15:00 | 83.69 | 9.79 | 9.79 | 72.14 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-22 16:00 | 83.11 | 17.92 | 17.92 | 65.18 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 17:00 | 81.87 | 3.88 | 3.88 | 77.99 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 18:00 | 78.23 | 0 | 0 | 78.23 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 19:00 | 74.25 | 0 | 0 | 74.25 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 20:00 | 69.92 | 0 | 0 | 69.92 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 21:00 | 65.55 | 0 | 0 | 65.55 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 22:00 | 60.96 | 0 | 0 | 60.96 | 0 | 0 | 0.68 | 0 | 0
2025-08-22 23:00 | 57.58 | 0 | 0 | 57.58 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 | 55.38 | 0 | 0 | 55.38 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 01:00 | 52.44 | 0 | 0 | 52.44 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 02:00 | 51.56 | 0 | 0 | 51.56 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 03:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 04:00 | 51.5 | 0 | 0 | 51.5 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 05:00 | 52.46 | 0 | 0 | 52.46 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 06:00 | 54.39 | 42.23 | 42.23 | 12.16 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 07:00 | 57.37 | 104.42 | 60.77 | 0 | 3.4 | 0 | 3.91 | 43.65 | 0
2025-08-23 08:00 | 60.03 | 86.74 | 62.35 | 0 | 2.33 | 0 | 6.12 | 24.39 | 0
2025-08-23 09:00 | 62.31 | 68.01 | 62.31 | 0 | 0 | 0 | 6.12 | 5.7 | 0
2025-08-23 10:00 | 66.81 | 116.99 | 66.81 | 0 | 0 | 0 | 6.12 | 50.18 | 0
2025-08-23 11:00 | 69.14 | 105.25 | 69.14 | 0 | 0 | 0 | 6.12 | 36.11 | 0
2025-08-23 12:00 | 71.07 | 90.29 | 71.07 | 0 | 0 | 0 | 6.12 | 19.23 | 0
2025-08-23 13:00 | 72.38 | 84.26 | 72.38 | 0 | 0 | 0 | 6.12 | 11.88 | 0
2025-08-23 14:00 | 73.14 | 80.67 | 73.14 | 0 | 0 | 0 | 6.12 | 7.53 | 0
2025-08-23 15:00 | 74.33 | 50.83 | 50.83 | 20.1 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-23 16:00 | 74.68 | 67.71 | 67.71 | 5.21 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-23 17:00 | 72.97 | 68.41 | 68.41 | 4.56 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 18:00 | 70.53 | 29.35 | 29.35 | 41.18 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 19:00 | 69.13 | 0 | 0 | 69.13 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 20:00 | 66.32 | 0 | 0 | 66.32 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 21:00 | 63.8 | 0 | 0 | 63.8 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 22:00 | 60.58 | 0 | 0 | 60.58 | 0 | 0 | 0.68 | 0 | 0
2025-08-23 23:00 | 55.79 | 0 | 0 | 55.79 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 | 54.84 | 0 | 0 | 54.84 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 01:00 | 51.98 | 0 | 0 | 51.98 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 02:00 | 50.44 | 0 | 0 | 50.44 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 03:00 | 50.59 | 0 | 0 | 50.59 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 04:00 | 51.35 | 0 | 0 | 51.35 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 05:00 | 51.66 | 0 | 0 | 51.66 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 06:00 | 54.91 | 40.69 | 40.69 | 14.23 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 07:00 | 57.6 | 99.28 | 61 | 0 | 3.4 | 0 | 3.91 | 38.28 | 0
2025-08-24 08:00 | 60.25 | 112.93 | 62.58 | 0 | 2.33 | 0 | 6.12 | 50.35 | 0
2025-08-24 09:00 | 62.92 | 115.57 | 62.92 | 0 | 0 | 0 | 6.12 | 52.65 | 0
2025-08-24 10:00 | 65.89 | 112.67 | 65.89 | 0 | 0 | 0 | 6.12 | 46.78 | 0
2025-08-24 11:00 | 69.61 | 109.47 | 69.61 | 0 | 0 | 0 | 6.12 | 39.86 | 0
2025-08-24 12:00 | 70.6 | 105.79 | 70.6 | 0 | 0 | 0 | 6.12 | 35.19 | 0
2025-08-24 13:00 | 73.58 | 107.74 | 73.58 | 0 | 0 | 0 | 6.12 | 34.16 | 0
2025-08-24 14:00 | 74 | 109.88 | 74 | 0 | 0 | 0 | 6.12 | 35.87 | 0
2025-08-24 15:00 | 74.39 | 107.95 | 74.39 | 0 | 0 | 0 | 6.12 | 33.56 | 0
2025-08-24 16:00 | 73.23 | 101.54 | 73.23 | 0 | 0 | 0 | 6.12 | 28.31 | 0
2025-08-24 17:00 | 72.97 | 84.4 | 72.97 | 0 | 0 | 0 | 6.12 | 11.42 | 0
2025-08-24 18:00 | 71.66 | 25.64 | 25.64 | 42.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-24 19:00 | 68.43 | 0 | 0 | 66.66 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-24 20:00 | 66.63 | 0 | 0 | 66.63 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 21:00 | 63.4 | 0 | 0 | 63.4 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 22:00 | 59.91 | 0 | 0 | 59.91 | 0 | 0 | 0.68 | 0 | 0
2025-08-24 23:00 | 57.65 | 0 | 0 | 57.65 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 01:00 | 52.55 | 0 | 0 | 52.55 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 02:00 | 51.89 | 0 | 0 | 51.89 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 03:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 04:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 05:00 | 52.22 | 0 | 0 | 52.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 06:00 | 54.01 | 8.14 | 8.14 | 45.87 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 07:00 | 56.53 | 25.2 | 25.2 | 31.33 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 08:00 | 59.41 | 44.44 | 44.44 | 14.98 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 09:00 | 61.04 | 59 | 59 | 2.04 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 10:00 | 63.78 | 55.38 | 55.38 | 8.4 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 11:00 | 65.98 | 46.07 | 46.07 | 19.91 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 12:00 | 65.94 | 40.17 | 40.17 | 25.76 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 13:00 | 65.96 | 38.68 | 38.68 | 27.27 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 14:00 | 66.3 | 20.43 | 20.43 | 45.87 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 15:00 | 67.47 | 24.53 | 24.53 | 42.94 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 16:00 | 66.94 | 15.38 | 15.38 | 51.57 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 17:00 | 67.07 | 8.02 | 8.02 | 59.04 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 18:00 | 65.7 | 0 | 0 | 65.7 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 19:00 | 65.33 | 0 | 0 | 65.33 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 20:00 | 63.32 | 0 | 0 | 63.32 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 21:00 | 61.08 | 0 | 0 | 61.08 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 22:00 | 58.94 | 0 | 0 | 58.94 | 0 | 0 | 0.68 | 0 | 0
2025-08-25 23:00 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 | 55.45 | 0 | 0 | 55.45 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 01:00 | 52.3 | 0 | 0 | 52.3 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 02:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 03:00 | 50.29 | 0 | 0 | 50.29 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 04:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 05:00 | 52.23 | 0 | 0 | 52.23 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 06:00 | 55.01 | 30.93 | 30.93 | 24.08 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 07:00 | 56.93 | 78.34 | 60.33 | 0 | 3.4 | 0 | 3.91 | 18.01 | 0
2025-08-26 08:00 | 59.92 | 17.57 | 17.57 | 39.29 | 0 | 3.07 | 0.68 | 0 | 0
2025-08-26 09:00 | 63.8 | 42.46 | 42.46 | 21.34 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 10:00 | 67.32 | 81.44 | 70.72 | 0 | 3.4 | 0 | 3.91 | 10.72 | 0
2025-08-26 11:00 | 70.99 | 97.95 | 73.31 | 0 | 2.33 | 0 | 6.12 | 24.64 | 0
2025-08-26 12:00 | 72.98 | 70.36 | 70.36 | 0 | 0 | 2.62 | 3.36 | 0 | 0
2025-08-26 13:00 | 75.14 | 63.73 | 63.73 | 8.86 | 0 | 2.54 | 0.68 | 0 | 0
2025-08-26 14:00 | 76.44 | 97.88 | 79.84 | 0 | 3.4 | 0 | 3.91 | 18.05 | 0
2025-08-26 15:00 | 75.93 | 92.38 | 78.26 | 0 | 2.33 | 0 | 6.12 | 14.12 | 0
2025-08-26 16:00 | 75.6 | 107.22 | 75.6 | 0 | 0 | 0 | 6.12 | 31.62 | 0
2025-08-26 17:00 | 74.27 | 83.94 | 74.27 | 0 | 0 | 0 | 6.12 | 9.67 | 0
2025-08-26 18:00 | 72.14 | 23.39 | 23.39 | 45.34 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-26 19:00 | 70.56 | 0 | 0 | 68.79 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-26 20:00 | 67.22 | 0 | 0 | 67.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 21:00 | 63.77 | 0 | 0 | 63.77 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 22:00 | 59.06 | 0 | 0 | 59.06 | 0 | 0 | 0.68 | 0 | 0
2025-08-26 23:00 | 58.22 | 0 | 0 | 58.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 | 53.83 | 0 | 0 | 53.83 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 01:00 | 53.28 | 0 | 0 | 53.28 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 02:00 | 50.22 | 0 | 0 | 50.22 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 03:00 | 50.08 | 0 | 0 | 50.08 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 04:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 05:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 06:00 | 53.73 | 30.22 | 30.22 | 23.51 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 07:00 | 56.29 | 106.58 | 59.69 | 0 | 3.4 | 0 | 3.91 | 46.89 | 0
2025-08-27 08:00 | 58.97 | 110.94 | 61.3 | 0 | 2.33 | 0 | 6.12 | 49.64 | 0
2025-08-27 09:00 | 62.92 | 127.06 | 62.92 | 0 | 0 | 0 | 6.12 | 64.14 | 0
2025-08-27 10:00 | 65.59 | 119.26 | 65.59 | 0 | 0 | 0 | 6.12 | 53.67 | 0
2025-08-27 11:00 | 68.5 | 7.65 | 7.65 | 57.45 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-27 12:00 | 69.17 | 119.15 | 72.57 | 0 | 3.4 | 0 | 5.77 | 46.58 | 0
2025-08-27 13:00 | 71.01 | 120.28 | 71.38 | 0 | 0.37 | 0 | 6.12 | 48.91 | 0
2025-08-27 14:00 | 71.1 | 69.98 | 69.98 | 0 | 0 | 1.12 | 4.94 | 0 | 0
2025-08-27 15:00 | 71.86 | 34.58 | 34.58 | 33.88 | 0 | 3.4 | 1.36 | 0 | 0
2025-08-27 16:00 | 71.49 | 108.26 | 74.89 | 0 | 3.4 | 0 | 4.59 | 33.37 | 0
2025-08-27 17:00 | 71.13 | 1.44 | 1.44 | 66.3 | 0 | 3.4 | 1.01 | 0 | 0
2025-08-27 18:00 | 70.02 | 0 | 0 | 69.71 | 0 | 0.31 | 0.68 | 0 | 0
2025-08-27 19:00 | 68.09 | 0 | 0 | 68.09 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 20:00 | 64.81 | 0 | 0 | 64.81 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 21:00 | 63.03 | 0 | 0 | 63.03 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 22:00 | 59.64 | 0 | 0 | 59.64 | 0 | 0 | 0.68 | 0 | 0
2025-08-27 23:00 | 56.67 | 0 | 0 | 56.67 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 | 53.9 | 0 | 0 | 53.9 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 01:00 | 51.9 | 0 | 0 | 51.9 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 02:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 03:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 04:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 05:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 06:00 | 55.47 | 36.39 | 36.39 | 19.09 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 07:00 | 57.54 | 79.22 | 60.94 | 0 | 3.4 | 0 | 3.91 | 18.28 | 0
2025-08-28 08:00 | 59.54 | 99.28 | 61.87 | 0 | 2.33 | 0 | 6.12 | 37.41 | 0
2025-08-28 09:00 | 62.91 | 47.38 | 47.38 | 12.13 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-28 10:00 | 66.01 | 119.02 | 69.41 | 0 | 3.4 | 0 | 5.77 | 49.61 | 0
2025-08-28 11:00 | 68.97 | 83.28 | 69.33 | 0 | 0.37 | 0 | 6.12 | 13.95 | 0
2025-08-28 12:00 | 70.87 | 85.22 | 70.87 | 0 | 0 | 0 | 6.12 | 14.34 | 0
2025-08-28 13:00 | 73.19 | 48.13 | 48.13 | 21.66 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-28 14:00 | 74.78 | 61.46 | 61.46 | 11.55 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-28 15:00 | 73.76 | 120.36 | 77.16 | 0 | 3.4 | 0 | 3.91 | 43.2 | 0
2025-08-28 16:00 | 73.49 | 74.92 | 74.92 | 0 | 1.44 | 0 | 5.27 | 0 | 0
2025-08-28 17:00 | 72.73 | 34.77 | 34.77 | 34.56 | 0 | 3.4 | 1.69 | 0 | 0
2025-08-28 18:00 | 71 | 0 | 0 | 70.04 | 0 | 0.96 | 0.68 | 0 | 0
2025-08-28 19:00 | 69.89 | 0 | 0 | 69.89 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 20:00 | 66.62 | 0 | 0 | 66.62 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 21:00 | 63.52 | 0 | 0 | 63.52 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 22:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 0.68 | 0 | 0
2025-08-28 23:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 | 53.4 | 0 | 0 | 53.4 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 01:00 | 52.49 | 0 | 0 | 52.49 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 02:00 | 51.04 | 0 | 0 | 51.04 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 03:00 | 50.99 | 0 | 0 | 50.99 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 04:00 | 50.69 | 0 | 0 | 50.69 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 05:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 06:00 | 54.21 | 33.8 | 33.8 | 20.41 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 07:00 | 57.14 | 79.69 | 60.54 | 0 | 3.4 | 0 | 3.91 | 19.15 | 0
2025-08-29 08:00 | 58.83 | 120.22 | 61.16 | 0 | 2.33 | 0 | 6.12 | 59.06 | 0
2025-08-29 09:00 | 62.88 | 123.19 | 62.88 | 0 | 0 | 0 | 6.12 | 60.3 | 0
2025-08-29 10:00 | 65.32 | 118.77 | 65.32 | 0 | 0 | 0 | 6.12 | 53.45 | 0
2025-08-29 11:00 | 67.29 | 66.29 | 66.29 | 0 | 0 | 1 | 5.07 | 0 | 0
2025-08-29 12:00 | 68.82 | 66.24 | 66.24 | 0 | 0 | 2.58 | 2.35 | 0 | 0
2025-08-29 13:00 | 71.3 | 63.09 | 63.09 | 6.63 | 0 | 1.59 | 0.68 | 0 | 0
2025-08-29 14:00 | 73.02 | 51.11 | 51.11 | 21.91 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 15:00 | 73.44 | 61.91 | 61.91 | 11.53 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 16:00 | 72.47 | 35.22 | 35.22 | 37.25 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 17:00 | 72.35 | 27.94 | 27.94 | 44.41 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 18:00 | 69.84 | 6.98 | 6.98 | 62.86 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 19:00 | 68.3 | 0 | 0 | 68.3 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 20:00 | 65.1 | 0 | 0 | 65.1 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 21:00 | 62.26 | 0 | 0 | 62.26 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 22:00 | 59.23 | 0 | 0 | 59.23 | 0 | 0 | 0.68 | 0 | 0
2025-08-29 23:00 | 55.66 | 0 | 0 | 55.66 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 | 54.76 | 0 | 0 | 54.76 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 01:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 02:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 03:00 | 49.68 | 0 | 0 | 49.68 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 04:00 | 50.62 | 0 | 0 | 50.62 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 05:00 | 52.92 | 0 | 0 | 52.92 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 06:00 | 55.16 | 24.11 | 24.11 | 31.05 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 07:00 | 55.99 | 83.31 | 59.39 | 0 | 3.4 | 0 | 3.91 | 23.92 | 0
2025-08-30 08:00 | 59.79 | 101.86 | 62.11 | 0 | 2.33 | 0 | 6.12 | 39.74 | 0
2025-08-30 09:00 | 62.8 | 106.67 | 62.8 | 0 | 0 | 0 | 6.12 | 43.87 | 0
2025-08-30 10:00 | 67.16 | 105.28 | 67.16 | 0 | 0 | 0 | 6.12 | 38.13 | 0
2025-08-30 11:00 | 69.9 | 104.1 | 69.9 | 0 | 0 | 0 | 6.12 | 34.2 | 0
2025-08-30 12:00 | 72.09 | 101.73 | 72.09 | 0 | 0 | 0 | 6.12 | 29.64 | 0
2025-08-30 13:00 | 74.48 | 104.41 | 74.48 | 0 | 0 | 0 | 6.12 | 29.93 | 0
2025-08-30 14:00 | 75.47 | 109.77 | 75.47 | 0 | 0 | 0 | 6.12 | 34.3 | 0
2025-08-30 15:00 | 76.95 | 111.25 | 76.95 | 0 | 0 | 0 | 6.12 | 34.3 | 0
2025-08-30 16:00 | 75.98 | 107.5 | 75.98 | 0 | 0 | 0 | 6.12 | 31.51 | 0
2025-08-30 17:00 | 74.77 | 87.22 | 74.77 | 0 | 0 | 0 | 6.12 | 12.44 | 0
2025-08-30 18:00 | 71.08 | 18.3 | 18.3 | 49.38 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-30 19:00 | 69.73 | 0 | 0 | 67.96 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-30 20:00 | 67.7 | 0 | 0 | 67.7 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 21:00 | 63.98 | 0 | 0 | 63.98 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 22:00 | 59.04 | 0 | 0 | 59.04 | 0 | 0 | 0.68 | 0 | 0
2025-08-30 23:00 | 56.67 | 0 | 0 | 56.67 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 | 53.26 | 0 | 0 | 53.26 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 01:00 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 02:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 03:00 | 49.81 | 0 | 0 | 49.81 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 04:00 | 50.66 | 0 | 0 | 50.66 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 05:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 06:00 | 53.31 | 0 | 0 | 53.31 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 07:00 | 56.25 | 18.63 | 18.63 | 37.61 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 08:00 | 59.19 | 36.53 | 36.53 | 22.67 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 09:00 | 60.26 | 58.13 | 58.13 | 2.13 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 10:00 | 63.22 | 61.47 | 61.47 | 1.74 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 11:00 | 65.69 | 84.31 | 69.09 | 0 | 3.4 | 0 | 3.91 | 15.21 | 0
2025-08-31 12:00 | 65.8 | 80.85 | 68.13 | 0 | 2.33 | 0 | 6.12 | 12.72 | 0
2025-08-31 13:00 | 67.55 | 78.76 | 67.55 | 0 | 0 | 0 | 6.12 | 11.21 | 0
2025-08-31 14:00 | 67.98 | 52.85 | 52.85 | 11.73 | 0 | 3.4 | 2.54 | 0 | 0
2025-08-31 15:00 | 68.97 | 29.01 | 29.01 | 38.19 | 0 | 1.77 | 0.68 | 0 | 0
2025-08-31 16:00 | 67.83 | 28.95 | 28.95 | 38.88 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 17:00 | 67.34 | 5.42 | 5.42 | 61.93 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 18:00 | 66.95 | 0.72 | 0.72 | 66.23 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 19:00 | 64.53 | 0 | 0 | 64.53 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 20:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 21:00 | 61 | 0 | 0 | 61 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 22:00 | 58.7 | 0 | 0 | 58.7 | 0 | 0 | 0.68 | 0 | 0
2025-08-31 23:00 | 56.65 | 0 | 0 | 56.65 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 | 54.07 | 0 | 0 | 54.07 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 01:00 | 51.46 | 0 | 0 | 51.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 03:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 04:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 05:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 06:00 | 53.7 | 9.3 | 9.3 | 44.39 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 07:00 | 56.18 | 12.15 | 12.15 | 44.03 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 08:00 | 58.03 | 35.63 | 35.63 | 22.4 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 09:00 | 62.15 | 63.49 | 63.49 | 0 | 1.34 | 0 | 1.95 | 0 | 0
2025-09-01 10:00 | 63.43 | 70.28 | 66.83 | 0 | 3.4 | 0 | 5.18 | 3.45 | 0
2025-09-01 11:00 | 66.33 | 69.37 | 67.32 | 0 | 0.99 | 0 | 6.12 | 2.05 | 0
2025-09-01 12:00 | 67.06 | 73.5 | 67.06 | 0 | 0 | 0 | 6.12 | 6.44 | 0
2025-09-01 13:00 | 68.16 | 70.81 | 68.16 | 0 | 0 | 0 | 6.12 | 2.65 | 0
2025-09-01 14:00 | 69.72 | 55.64 | 55.64 | 10.67 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-01 15:00 | 69.82 | 87.64 | 73.22 | 0 | 3.4 | 0 | 5.77 | 14.42 | 0
2025-09-01 16:00 | 69.22 | 99.96 | 69.58 | 0 | 0.37 | 0 | 6.12 | 30.38 | 0
2025-09-01 17:00 | 68.85 | 48.13 | 48.13 | 17.32 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-01 18:00 | 67.23 | 14.3 | 14.3 | 51.16 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-01 19:00 | 65.81 | 0 | 0 | 65.81 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 20:00 | 63.48 | 0 | 0 | 63.48 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 21:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 22:00 | 58.5 | 0 | 0 | 58.5 | 0 | 0 | 0.68 | 0 | 0
2025-09-01 23:00 | 56.95 | 0 | 0 | 56.95 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 | 53.9 | 0 | 0 | 53.9 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 01:00 | 51.83 | 0 | 0 | 51.83 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 02:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 03:00 | 50.05 | 0 | 0 | 50.05 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 04:00 | 50.34 | 0 | 0 | 50.34 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 05:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 06:00 | 54.5 | 27.57 | 27.57 | 26.93 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 07:00 | 56.83 | 96.82 | 60.23 | 0 | 3.4 | 0 | 3.91 | 36.6 | 0
2025-09-02 08:00 | 60.97 | 114.8 | 63.3 | 0 | 2.33 | 0 | 6.12 | 51.5 | 0
2025-09-02 09:00 | 65.53 | 119.21 | 65.53 | 0 | 0 | 0 | 6.12 | 53.68 | 0
2025-09-02 10:00 | 70.77 | 115.88 | 70.77 | 0 | 0 | 0 | 6.12 | 45.1 | 0
2025-09-02 11:00 | 75.08 | 111.76 | 75.08 | 0 | 0 | 0 | 6.12 | 36.68 | 0
2025-09-02 12:00 | 80.38 | 103.39 | 80.38 | 0 | 0 | 0 | 6.12 | 23.02 | 0
2025-09-02 13:00 | 82.87 | 53.46 | 53.46 | 26.01 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-02 14:00 | 85.08 | 111.59 | 88.48 | 0 | 3.4 | 0 | 5.77 | 23.11 | 0
2025-09-02 15:00 | 85.89 | 64.9 | 64.9 | 17.6 | 0 | 3.4 | 2.19 | 0 | 0
2025-09-02 16:00 | 84.54 | 2.35 | 2.35 | 80.75 | 0 | 1.44 | 0.68 | 0 | 0
2025-09-02 17:00 | 82.43 | 0.78 | 0.78 | 81.65 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 18:00 | 79.21 | 0 | 0 | 79.21 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 19:00 | 75.7 | 0 | 0 | 75.7 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 20:00 | 70.32 | 0 | 0 | 70.32 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 21:00 | 65.28 | 0 | 0 | 65.28 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 22:00 | 61.65 | 0 | 0 | 61.65 | 0 | 0 | 0.68 | 0 | 0
2025-09-02 23:00 | 57.93 | 0 | 0 | 57.93 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 | 54.24 | 0 | 0 | 54.24 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 01:00 | 51.24 | 0 | 0 | 51.24 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 02:00 | 50.15 | 0 | 0 | 50.15 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 03:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 04:00 | 50.52 | 0 | 0 | 50.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 05:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 06:00 | 53.98 | 24.11 | 24.11 | 29.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 07:00 | 56.55 | 86.88 | 59.95 | 0 | 3.4 | 0 | 3.91 | 26.93 | 0
2025-09-03 08:00 | 58.43 | 100.83 | 60.76 | 0 | 2.33 | 0 | 6.12 | 40.07 | 0
2025-09-03 09:00 | 61.5 | 103.78 | 61.5 | 0 | 0 | 0 | 6.12 | 42.28 | 0
2025-09-03 10:00 | 64.33 | 107.03 | 64.33 | 0 | 0 | 0 | 6.12 | 42.71 | 0
2025-09-03 11:00 | 65.4 | 101.38 | 65.4 | 0 | 0 | 0 | 6.12 | 35.98 | 0
2025-09-03 12:00 | 67.67 | 99.62 | 67.67 | 0 | 0 | 0 | 6.12 | 31.95 | 0
2025-09-03 13:00 | 68.32 | 98.89 | 68.32 | 0 | 0 | 0 | 6.12 | 30.57 | 0
2025-09-03 14:00 | 69.1 | 103.35 | 69.1 | 0 | 0 | 0 | 6.12 | 34.25 | 0
2025-09-03 15:00 | 69.55 | 100.8 | 69.55 | 0 | 0 | 0 | 6.12 | 31.25 | 0
2025-09-03 16:00 | 69.83 | 90.98 | 69.83 | 0 | 0 | 0 | 6.12 | 21.15 | 0
2025-09-03 17:00 | 68.71 | 68.23 | 68.23 | 0 | 0 | 0.49 | 5.61 | 0 | 0
2025-09-03 18:00 | 67.34 | 9.54 | 9.54 | 54.41 | 0 | 3.4 | 2.03 | 0 | 0
2025-09-03 19:00 | 66.01 | 0 | 0 | 64.73 | 0 | 1.28 | 0.68 | 0 | 0
2025-09-03 20:00 | 63.29 | 0 | 0 | 63.29 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 21:00 | 61.61 | 0 | 0 | 61.61 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 22:00 | 59.29 | 0 | 0 | 59.29 | 0 | 0 | 0.68 | 0 | 0
2025-09-03 23:00 | 56.01 | 0 | 0 | 56.01 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 | 53.44 | 0 | 0 | 53.44 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 01:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 02:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 03:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 04:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 06:00 | 53.48 | 25.44 | 25.44 | 28.03 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 07:00 | 56.37 | 89.22 | 59.77 | 0 | 3.4 | 0 | 3.91 | 29.45 | 0
2025-09-04 08:00 | 59.54 | 109.36 | 61.87 | 0 | 2.33 | 0 | 6.12 | 47.49 | 0
2025-09-04 09:00 | 61.96 | 110.94 | 61.96 | 0 | 0 | 0 | 6.12 | 48.98 | 0
2025-09-04 10:00 | 62.99 | 107.6 | 62.99 | 0 | 0 | 0 | 6.12 | 44.61 | 0
2025-09-04 11:00 | 66.61 | 103.09 | 66.61 | 0 | 0 | 0 | 6.12 | 36.49 | 0
2025-09-04 12:00 | 69.43 | 101.58 | 69.43 | 0 | 0 | 0 | 6.12 | 32.15 | 0
2025-09-04 13:00 | 69.78 | 102.57 | 69.78 | 0 | 0 | 0 | 6.12 | 32.79 | 0
2025-09-04 14:00 | 69.69 | 104.55 | 69.69 | 0 | 0 | 0 | 6.12 | 34.86 | 0
2025-09-04 15:00 | 70.68 | 104.85 | 70.68 | 0 | 0 | 0 | 6.12 | 34.17 | 0
2025-09-04 16:00 | 69.63 | 95.95 | 69.63 | 0 | 0 | 0 | 6.12 | 26.32 | 0
2025-09-04 17:00 | 70.09 | 74.41 | 70.09 | 0 | 0 | 0 | 6.12 | 4.32 | 0
2025-09-04 18:00 | 67.67 | 8.92 | 8.92 | 55.35 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-04 19:00 | 66.36 | 0 | 0 | 64.59 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-04 20:00 | 63.64 | 0 | 0 | 63.64 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 21:00 | 61.2 | 0 | 0 | 61.2 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 22:00 | 59.46 | 0 | 0 | 59.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-04 23:00 | 56.04 | 0 | 0 | 56.04 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 | 53.44 | 0 | 0 | 53.44 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 01:00 | 50.97 | 0 | 0 | 50.97 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 02:00 | 49.29 | 0 | 0 | 49.29 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 03:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 04:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 05:00 | 52.04 | 0 | 0 | 52.04 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 06:00 | 53.44 | 22.76 | 22.76 | 30.68 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 07:00 | 57.51 | 87.82 | 60.91 | 0 | 3.4 | 0 | 3.91 | 26.91 | 0
2025-09-05 08:00 | 60.09 | 107.42 | 62.42 | 0 | 2.33 | 0 | 6.12 | 45.01 | 0
2025-09-05 09:00 | 64.6 | 110.1 | 64.6 | 0 | 0 | 0 | 6.12 | 45.5 | 0
2025-09-05 10:00 | 68.73 | 107.97 | 68.73 | 0 | 0 | 0 | 6.12 | 39.24 | 0
2025-09-05 11:00 | 74.27 | 104.39 | 74.27 | 0 | 0 | 0 | 6.12 | 30.12 | 0
2025-09-05 12:00 | 78.88 | 101.41 | 78.88 | 0 | 0 | 0 | 6.12 | 22.52 | 0
2025-09-05 13:00 | 80.19 | 103.39 | 80.19 | 0 | 0 | 0 | 6.12 | 23.2 | 0
2025-09-05 14:00 | 82.99 | 105.68 | 82.99 | 0 | 0 | 0 | 6.12 | 22.68 | 0
2025-09-05 15:00 | 84.52 | 104.89 | 84.52 | 0 | 0 | 0 | 6.12 | 20.38 | 0
2025-09-05 16:00 | 82.44 | 97.7 | 82.44 | 0 | 0 | 0 | 6.12 | 15.26 | 0
2025-09-05 17:00 | 81.36 | 76.46 | 76.46 | 1.5 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-05 18:00 | 78.44 | 7.71 | 7.71 | 68.96 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-05 19:00 | 73.81 | 0 | 0 | 73.81 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 20:00 | 69.55 | 0 | 0 | 69.55 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 21:00 | 65.6 | 0 | 0 | 65.6 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 22:00 | 61.42 | 0 | 0 | 61.42 | 0 | 0 | 0.68 | 0 | 0
2025-09-05 23:00 | 56.7 | 0 | 0 | 56.7 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 | 53.46 | 0 | 0 | 53.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 01:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 03:00 | 49.02 | 0 | 0 | 49.02 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 04:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 06:00 | 53.47 | 0.85 | 0.85 | 52.62 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 07:00 | 57.05 | 8.48 | 8.48 | 48.57 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 08:00 | 62.27 | 51.05 | 51.05 | 11.22 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 09:00 | 65.73 | 57.74 | 57.74 | 7.99 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 10:00 | 70.82 | 63.02 | 63.02 | 7.8 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 11:00 | 76.84 | 34.32 | 34.32 | 42.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 12:00 | 81.3 | 53.7 | 53.7 | 27.6 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 13:00 | 85.82 | 39.17 | 39.17 | 46.66 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 14:00 | 87.73 | 113.53 | 91.13 | 0 | 3.4 | 0 | 3.91 | 22.39 | 0
2025-09-06 15:00 | 88.41 | 109.47 | 90.74 | 0 | 2.33 | 0 | 6.12 | 18.73 | 0
2025-09-06 16:00 | 86.76 | 98.04 | 86.76 | 0 | 0 | 0 | 6.12 | 11.28 | 0
2025-09-06 17:00 | 84.29 | 42.73 | 42.73 | 38.16 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-06 18:00 | 80.26 | 1.08 | 1.08 | 77.42 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-06 19:00 | 76.52 | 0 | 0 | 76.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 20:00 | 70.35 | 0 | 0 | 70.35 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 21:00 | 66.41 | 0 | 0 | 66.41 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 22:00 | 61 | 0 | 0 | 61 | 0 | 0 | 0.68 | 0 | 0
2025-09-06 23:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 | 52.8 | 0 | 0 | 52.8 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 01:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 02:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 03:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 04:00 | 50.64 | 0 | 0 | 50.64 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 05:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 06:00 | 53.1 | 14.2 | 14.2 | 38.9 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 07:00 | 55.95 | 64.13 | 59.35 | 0 | 3.4 | 0 | 3.91 | 4.78 | 0
2025-09-07 08:00 | 58.29 | 77.38 | 60.61 | 0 | 2.33 | 0 | 6.12 | 16.76 | 0
2025-09-07 09:00 | 61.16 | 83.27 | 61.16 | 0 | 0 | 0 | 6.12 | 22.12 | 0
2025-09-07 10:00 | 63.06 | 75.39 | 63.06 | 0 | 0 | 0 | 6.12 | 12.33 | 0
2025-09-07 11:00 | 66.67 | 79.8 | 66.67 | 0 | 0 | 0 | 6.12 | 13.13 | 0
2025-09-07 12:00 | 67.08 | 95.54 | 67.08 | 0 | 0 | 0 | 6.12 | 28.45 | 0
2025-09-07 13:00 | 69.41 | 95.25 | 69.41 | 0 | 0 | 0 | 6.12 | 25.84 | 0
2025-09-07 14:00 | 69.29 | 99.94 | 69.29 | 0 | 0 | 0 | 6.12 | 30.65 | 0
2025-09-07 15:00 | 70.04 | 86.64 | 70.04 | 0 | 0 | 0 | 6.12 | 16.6 | 0
2025-09-07 16:00 | 69.75 | 106.64 | 69.75 | 0 | 0 | 0 | 6.12 | 36.88 | 0
2025-09-07 17:00 | 69.2 | 79.8 | 69.2 | 0 | 0 | 0 | 6.12 | 10.6 | 0
2025-09-07 18:00 | 66.95 | 9.15 | 9.15 | 54.4 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-07 19:00 | 66.17 | 0 | 0 | 64.41 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-07 20:00 | 64.39 | 0 | 0 | 64.39 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 21:00 | 60.83 | 0 | 0 | 60.83 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 22:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 0.68 | 0 | 0
2025-09-07 23:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 01:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 02:00 | 49.45 | 0 | 0 | 49.45 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 03:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 04:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 06:00 | 54.25 | 1.21 | 1.21 | 53.03 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 07:00 | 55.51 | 2.45 | 2.45 | 53.06 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 08:00 | 58.72 | 19.34 | 19.34 | 39.37 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 09:00 | 61.4 | 71.93 | 64.8 | 0 | 3.4 | 0 | 3.91 | 7.13 | 0
2025-09-08 10:00 | 64.82 | 101.38 | 67.15 | 0 | 2.33 | 0 | 6.12 | 34.23 | 0
2025-09-08 11:00 | 66.63 | 111.5 | 66.63 | 0 | 0 | 0 | 6.12 | 44.87 | 0
2025-09-08 12:00 | 70.2 | 100.92 | 70.2 | 0 | 0 | 0 | 6.12 | 30.72 | 0
2025-09-08 13:00 | 71.78 | 69.45 | 69.45 | 0 | 0 | 2.34 | 3.66 | 0 | 0
2025-09-08 14:00 | 72.69 | 10.43 | 10.43 | 59.43 | 0 | 2.83 | 0.68 | 0 | 0
2025-09-08 15:00 | 72.9 | 8.68 | 8.68 | 64.22 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 16:00 | 72.28 | 2.34 | 2.34 | 69.93 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 17:00 | 71.99 | 0.75 | 0.75 | 71.23 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 18:00 | 69.27 | 1.49 | 1.49 | 67.78 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 19:00 | 67.77 | 0 | 0 | 67.77 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 20:00 | 65.79 | 0 | 0 | 65.79 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 21:00 | 62.47 | 0 | 0 | 62.47 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 22:00 | 57.9 | 0 | 0 | 57.9 | 0 | 0 | 0.68 | 0 | 0
2025-09-08 23:00 | 55.46 | 0 | 0 | 55.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 | 53.36 | 0 | 0 | 53.36 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 01:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 02:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 03:00 | 49.63 | 0 | 0 | 49.63 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 04:00 | 49.86 | 0 | 0 | 49.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 05:00 | 52.08 | 0 | 0 | 52.08 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 06:00 | 53.02 | 17.02 | 17.02 | 36 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 07:00 | 56.39 | 83.09 | 59.79 | 0 | 3.4 | 0 | 3.91 | 23.3 | 0
2025-09-09 08:00 | 58.32 | 85.11 | 60.65 | 0 | 2.33 | 0 | 6.12 | 24.46 | 0
2025-09-09 09:00 | 61.86 | 98.58 | 61.86 | 0 | 0 | 0 | 6.12 | 36.72 | 0
2025-09-09 10:00 | 66.21 | 98.28 | 66.21 | 0 | 0 | 0 | 6.12 | 32.07 | 0
2025-09-09 11:00 | 69.68 | 93.14 | 69.68 | 0 | 0 | 0 | 6.12 | 23.46 | 0
2025-09-09 12:00 | 71.52 | 89.32 | 71.52 | 0 | 0 | 0 | 6.12 | 17.8 | 0
2025-09-09 13:00 | 74.22 | 93.94 | 74.22 | 0 | 0 | 0 | 6.12 | 19.72 | 0
2025-09-09 14:00 | 74.92 | 98.28 | 74.92 | 0 | 0 | 0 | 6.12 | 23.36 | 0
2025-09-09 15:00 | 76 | 90.09 | 76 | 0 | 0 | 0 | 6.12 | 14.09 | 0
2025-09-09 16:00 | 76.03 | 87.46 | 76.03 | 0 | 0 | 0 | 6.12 | 11.44 | 0
2025-09-09 17:00 | 73.99 | 54.75 | 54.75 | 15.84 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-09 18:00 | 71.87 | 3.21 | 3.21 | 66.9 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-09 19:00 | 68.57 | 0 | 0 | 68.57 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 20:00 | 65.53 | 0 | 0 | 65.53 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 21:00 | 63.26 | 0 | 0 | 63.26 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 22:00 | 58.99 | 0 | 0 | 58.99 | 0 | 0 | 0.68 | 0 | 0
2025-09-09 23:00 | 55.31 | 0 | 0 | 55.31 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 01:00 | 50.25 | 0 | 0 | 50.25 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 02:00 | 49.26 | 0 | 0 | 49.26 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 03:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 04:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 05:00 | 52 | 0 | 0 | 52 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 06:00 | 53.12 | 14.61 | 14.61 | 38.51 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 07:00 | 56.06 | 61.79 | 59.46 | 0 | 3.4 | 0 | 3.91 | 2.33 | 0
2025-09-10 08:00 | 59.99 | 89.07 | 62.31 | 0 | 2.33 | 0 | 6.12 | 26.76 | 0
2025-09-10 09:00 | 62.44 | 91.68 | 62.44 | 0 | 0 | 0 | 6.12 | 29.24 | 0
2025-09-10 10:00 | 68.24 | 87.37 | 68.24 | 0 | 0 | 0 | 6.12 | 19.12 | 0
2025-09-10 11:00 | 72.42 | 96.81 | 72.42 | 0 | 0 | 0 | 6.12 | 24.39 | 0
2025-09-10 12:00 | 77.07 | 93.66 | 77.07 | 0 | 0 | 0 | 6.12 | 16.59 | 0
2025-09-10 13:00 | 79.9 | 87.58 | 79.9 | 0 | 0 | 0 | 6.12 | 7.69 | 0
2025-09-10 14:00 | 80.84 | 63.45 | 63.45 | 13.99 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-10 15:00 | 82.71 | 47.44 | 47.44 | 33.51 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-10 16:00 | 81.27 | 16.67 | 16.67 | 64.6 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 17:00 | 78.96 | 0.2 | 0.2 | 78.76 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 18:00 | 76.42 | 0.24 | 0.24 | 76.18 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 19:00 | 72.35 | 0 | 0 | 72.35 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 20:00 | 68.91 | 0 | 0 | 68.91 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 21:00 | 63.94 | 0 | 0 | 63.94 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 22:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 0.68 | 0 | 0
2025-09-10 23:00 | 56.52 | 0 | 0 | 56.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 01:00 | 51.28 | 0 | 0 | 51.28 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 02:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 03:00 | 49.55 | 0 | 0 | 49.55 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 04:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 05:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 06:00 | 52.75 | 8.89 | 8.89 | 43.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 07:00 | 55.2 | 91.62 | 58.6 | 0 | 3.4 | 0 | 3.91 | 33.02 | 0
2025-09-11 08:00 | 58.71 | 86.72 | 61.04 | 0 | 2.33 | 0 | 6.12 | 25.69 | 0
2025-09-11 09:00 | 61.38 | 63.38 | 61.38 | 0 | 0 | 0 | 6.12 | 2.01 | 0
2025-09-11 10:00 | 63.13 | 70.5 | 63.13 | 0 | 0 | 0 | 6.12 | 7.37 | 0
2025-09-11 11:00 | 65.17 | 80.74 | 65.17 | 0 | 0 | 0 | 6.12 | 15.57 | 0
2025-09-11 12:00 | 67.97 | 72.33 | 67.97 | 0 | 0 | 0 | 6.12 | 4.36 | 0
2025-09-11 13:00 | 68.98 | 82.42 | 68.98 | 0 | 0 | 0 | 6.12 | 13.44 | 0
2025-09-11 14:00 | 69.56 | 78.67 | 69.56 | 0 | 0 | 0 | 6.12 | 9.11 | 0
2025-09-11 15:00 | 69.52 | 72.18 | 69.52 | 0 | 0 | 0 | 6.12 | 2.67 | 0
2025-09-11 16:00 | 69.57 | 35.72 | 35.72 | 30.45 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-11 17:00 | 68.57 | 11.91 | 11.91 | 54.9 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-11 18:00 | 66.9 | 0.84 | 0.84 | 66.06 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 19:00 | 65.46 | 0 | 0 | 65.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 20:00 | 63.27 | 0 | 0 | 63.27 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 21:00 | 60.38 | 0 | 0 | 60.38 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 22:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 0.68 | 0 | 0
2025-09-11 23:00 | 55.83 | 0 | 0 | 55.83 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 01:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 02:00 | 49.95 | 0 | 0 | 49.95 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 03:00 | 49.19 | 0 | 0 | 49.19 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 04:00 | 48.96 | 0 | 0 | 48.96 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 05:00 | 51.14 | 0 | 0 | 51.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 06:00 | 52.82 | 13.19 | 13.19 | 39.63 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 07:00 | 56.56 | 85.9 | 59.96 | 0 | 3.4 | 0 | 3.91 | 25.94 | 0
2025-09-12 08:00 | 58.89 | 105.5 | 61.21 | 0 | 2.33 | 0 | 6.12 | 44.29 | 0
2025-09-12 09:00 | 61.59 | 105.4 | 61.59 | 0 | 0 | 0 | 6.12 | 43.81 | 0
2025-09-12 10:00 | 64.39 | 94.96 | 64.39 | 0 | 0 | 0 | 6.12 | 30.56 | 0
2025-09-12 11:00 | 67.15 | 92.63 | 67.15 | 0 | 0 | 0 | 6.12 | 25.48 | 0
2025-09-12 12:00 | 68.94 | 92.33 | 68.94 | 0 | 0 | 0 | 6.12 | 23.39 | 0
2025-09-12 13:00 | 70.38 | 95.38 | 70.38 | 0 | 0 | 0 | 6.12 | 25 | 0
2025-09-12 14:00 | 71.95 | 96.77 | 71.95 | 0 | 0 | 0 | 6.12 | 24.83 | 0
2025-09-12 15:00 | 72.74 | 99.01 | 72.74 | 0 | 0 | 0 | 6.12 | 26.27 | 0
2025-09-12 16:00 | 71.33 | 92.01 | 71.33 | 0 | 0 | 0 | 6.12 | 20.68 | 0
2025-09-12 17:00 | 70.98 | 56.97 | 56.97 | 10.61 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-12 18:00 | 69.32 | 1.58 | 1.58 | 65.98 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-12 19:00 | 66.96 | 0 | 0 | 66.96 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 20:00 | 63.94 | 0 | 0 | 63.94 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 21:00 | 61.06 | 0 | 0 | 61.06 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 22:00 | 59.02 | 0 | 0 | 59.02 | 0 | 0 | 0.68 | 0 | 0
2025-09-12 23:00 | 55.59 | 0 | 0 | 55.59 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 01:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 02:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 03:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 04:00 | 49.09 | 0 | 0 | 49.09 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 05:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 06:00 | 52.52 | 5.94 | 5.94 | 46.57 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 07:00 | 54.86 | 3.52 | 3.52 | 51.34 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 08:00 | 58.61 | 12.02 | 12.02 | 46.59 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 09:00 | 62.26 | 31.91 | 31.91 | 30.34 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 10:00 | 64.89 | 47.53 | 47.53 | 17.36 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 11:00 | 69.39 | 51.23 | 51.23 | 18.16 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 12:00 | 72.96 | 80.68 | 76.36 | 0 | 3.4 | 0 | 3.91 | 4.33 | 0
2025-09-13 13:00 | 75.19 | 74.77 | 74.77 | 0 | 0 | 0.42 | 3.47 | 0 | 0
2025-09-13 14:00 | 77.64 | 85.94 | 80.42 | 0 | 2.79 | 0 | 6.12 | 5.52 | 0
2025-09-13 15:00 | 77.68 | 116.18 | 77.68 | 0 | 0 | 0 | 6.12 | 38.5 | 0
2025-09-13 16:00 | 77.24 | 113.73 | 77.24 | 0 | 0 | 0 | 6.12 | 36.49 | 0
2025-09-13 17:00 | 76.36 | 70.59 | 70.59 | 2.37 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-13 18:00 | 72.9 | 1.35 | 1.35 | 69.79 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-13 19:00 | 69.49 | 0 | 0 | 69.49 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 20:00 | 66.36 | 0 | 0 | 66.36 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 21:00 | 61.92 | 0 | 0 | 61.92 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 22:00 | 58.68 | 0 | 0 | 58.68 | 0 | 0 | 0.68 | 0 | 0
2025-09-13 23:00 | 55.09 | 0 | 0 | 55.09 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 01:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 02:00 | 49.03 | 0 | 0 | 49.03 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 03:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 04:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 05:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 06:00 | 51.85 | 6.99 | 6.99 | 44.85 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 07:00 | 54.61 | 66.16 | 58.01 | 0 | 3.4 | 0 | 3.91 | 8.15 | 0
2025-09-14 08:00 | 57.83 | 64.43 | 60.15 | 0 | 2.33 | 0 | 6.12 | 4.28 | 0
2025-09-14 09:00 | 61.85 | 112.56 | 61.85 | 0 | 0 | 0 | 6.12 | 50.71 | 0
2025-09-14 10:00 | 65.19 | 85.38 | 65.19 | 0 | 0 | 0 | 6.12 | 20.19 | 0
2025-09-14 11:00 | 68.88 | 47.66 | 47.66 | 17.82 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-14 12:00 | 71.57 | 54 | 54 | 15.81 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-14 13:00 | 73.94 | 37.34 | 37.34 | 36.61 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 14:00 | 75.11 | 37.44 | 37.44 | 37.67 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 15:00 | 75.39 | 35.46 | 35.46 | 39.93 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 16:00 | 75.36 | 75.48 | 75.48 | 0 | 0.12 | 0 | 0.8 | 0 | 0
2025-09-14 17:00 | 73.86 | 43.27 | 43.27 | 30.48 | 0 | 0.11 | 0.68 | 0 | 0
2025-09-14 18:00 | 71.38 | 1 | 1 | 70.38 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 19:00 | 68.98 | 0 | 0 | 68.98 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 20:00 | 63.91 | 0 | 0 | 63.91 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 21:00 | 61.5 | 0 | 0 | 61.5 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 22:00 | 58.12 | 0 | 0 | 58.12 | 0 | 0 | 0.68 | 0 | 0
2025-09-14 23:00 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 | 53.16 | 0 | 0 | 53.16 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 01:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 02:00 | 49.98 | 0 | 0 | 49.98 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 03:00 | 48.27 | 0 | 0 | 48.27 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 04:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 05:00 | 50.36 | 0 | 0 | 50.36 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 06:00 | 52.22 | 13.78 | 13.78 | 38.44 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 07:00 | 54.04 | 88.49 | 57.44 | 0 | 3.4 | 0 | 3.91 | 31.05 | 0
2025-09-15 08:00 | 57.95 | 108.03 | 60.28 | 0 | 2.33 | 0 | 6.12 | 47.75 | 0
2025-09-15 09:00 | 60.92 | 111.73 | 60.92 | 0 | 0 | 0 | 6.12 | 50.8 | 0
2025-09-15 10:00 | 64.01 | 107.36 | 64.01 | 0 | 0 | 0 | 6.12 | 43.34 | 0
2025-09-15 11:00 | 65.92 | 102.52 | 65.92 | 0 | 0 | 0 | 6.12 | 36.6 | 0
2025-09-15 12:00 | 68.36 | 100.36 | 68.36 | 0 | 0 | 0 | 6.12 | 32 | 0
2025-09-15 13:00 | 70.06 | 103.28 | 70.06 | 0 | 0 | 0 | 6.12 | 33.22 | 0
2025-09-15 14:00 | 71.97 | 105.83 | 71.97 | 0 | 0 | 0 | 6.12 | 33.86 | 0
2025-09-15 15:00 | 70.07 | 52.43 | 52.43 | 14.24 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-15 16:00 | 70.65 | 8.44 | 8.44 | 60.44 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-15 17:00 | 70.08 | 0.03 | 0.03 | 70.04 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 18:00 | 67.84 | 0 | 0 | 67.84 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 19:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 20:00 | 63.42 | 0 | 0 | 63.42 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 21:00 | 60.26 | 0 | 0 | 60.26 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 22:00 | 57.66 | 0 | 0 | 57.66 | 0 | 0 | 0.68 | 0 | 0
2025-09-15 23:00 | 55.14 | 0 | 0 | 55.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 01:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 02:00 | 49.08 | 0 | 0 | 49.08 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 03:00 | 48.75 | 0 | 0 | 48.75 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 04:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 05:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 06:00 | 52.05 | 2.17 | 2.17 | 49.89 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 07:00 | 55.38 | 1.7 | 1.7 | 53.69 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 08:00 | 57.91 | 36.39 | 36.39 | 21.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 09:00 | 61.26 | 32.29 | 32.29 | 28.97 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 10:00 | 63.21 | 59.74 | 59.74 | 3.47 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 11:00 | 66.34 | 58.98 | 58.98 | 7.36 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 12:00 | 68.31 | 52.3 | 52.3 | 16.01 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 13:00 | 70.41 | 58.51 | 58.51 | 11.9 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 14:00 | 72.54 | 64.73 | 64.73 | 7.81 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 15:00 | 73.05 | 107.2 | 76.45 | 0 | 3.4 | 0 | 3.91 | 30.76 | 0
2025-09-16 16:00 | 71.34 | 103.44 | 73.66 | 0 | 2.33 | 0 | 6.12 | 29.78 | 0
2025-09-16 17:00 | 70.53 | 59.11 | 59.11 | 8.02 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-16 18:00 | 68.89 | 1.21 | 1.21 | 65.92 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-16 19:00 | 66.82 | 0 | 0 | 66.82 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 20:00 | 62.83 | 0 | 0 | 62.83 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 21:00 | 59.87 | 0 | 0 | 59.87 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 22:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-16 23:00 | 53.78 | 0 | 0 | 53.78 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 01:00 | 50.31 | 0 | 0 | 50.31 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 02:00 | 49.27 | 0 | 0 | 49.27 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 03:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 04:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 05:00 | 50.66 | 0 | 0 | 50.66 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 06:00 | 52.18 | 2 | 2 | 50.18 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 07:00 | 53.95 | 79.82 | 57.35 | 0 | 3.4 | 0 | 3.91 | 22.46 | 0
2025-09-17 08:00 | 56.74 | 55.29 | 55.29 | 0 | 0 | 1.45 | 2.38 | 0 | 0
2025-09-17 09:00 | 59.35 | 19.2 | 19.2 | 38.53 | 0 | 1.62 | 0.68 | 0 | 0
2025-09-17 10:00 | 62.25 | 56.33 | 56.33 | 5.92 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 11:00 | 63.69 | 20.16 | 20.16 | 43.53 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 12:00 | 65.4 | 27.89 | 27.89 | 37.51 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 13:00 | 65.56 | 37.07 | 37.07 | 28.49 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 14:00 | 66.23 | 85.52 | 69.63 | 0 | 3.4 | 0 | 3.91 | 15.89 | 0
2025-09-17 15:00 | 66.58 | 65.97 | 65.97 | 0 | 0 | 0.61 | 3.26 | 0 | 0
2025-09-17 16:00 | 66.42 | 26.07 | 26.07 | 37.89 | 0 | 2.45 | 0.68 | 0 | 0
2025-09-17 17:00 | 65.36 | 9.98 | 9.98 | 55.38 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 18:00 | 65.43 | 0 | 0 | 65.43 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 19:00 | 63.74 | 0 | 0 | 63.74 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 20:00 | 61.24 | 0 | 0 | 61.24 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 21:00 | 59.48 | 0 | 0 | 59.48 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 22:00 | 56.84 | 0 | 0 | 56.84 | 0 | 0 | 0.68 | 0 | 0
2025-09-17 23:00 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 01:00 | 50.07 | 0 | 0 | 50.07 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 02:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 03:00 | 48.86 | 0 | 0 | 48.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 04:00 | 48.64 | 0 | 0 | 48.64 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 05:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 06:00 | 51.48 | 0.68 | 0.68 | 50.8 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 07:00 | 54.41 | 3.53 | 3.53 | 50.88 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 08:00 | 57.27 | 17.23 | 17.23 | 40.05 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 09:00 | 61.05 | 65.54 | 64.45 | 0 | 3.4 | 0 | 3.91 | 1.09 | 0
2025-09-18 10:00 | 63.43 | 51.69 | 51.69 | 8.68 | 0 | 3.07 | 0.68 | 0 | 0
2025-09-18 11:00 | 65.89 | 81.04 | 69.29 | 0 | 3.4 | 0 | 3.91 | 11.76 | 0
2025-09-18 12:00 | 68.13 | 27.86 | 27.86 | 37.2 | 0 | 3.07 | 0.68 | 0 | 0
2025-09-18 13:00 | 70.45 | 20.76 | 20.76 | 49.68 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 14:00 | 70.69 | 38.88 | 38.88 | 31.81 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 15:00 | 71.29 | 3.41 | 3.41 | 67.88 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 16:00 | 70.44 | 14.17 | 14.17 | 56.28 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 17:00 | 70.6 | 11.46 | 11.46 | 59.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 18:00 | 68.34 | 0 | 0 | 68.34 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 19:00 | 65.49 | 0 | 0 | 65.49 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 20:00 | 63.09 | 0 | 0 | 63.09 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 21:00 | 60.46 | 0 | 0 | 60.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 22:00 | 57.11 | 0 | 0 | 57.11 | 0 | 0 | 0.68 | 0 | 0
2025-09-18 23:00 | 54.18 | 0 | 0 | 54.18 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 | 51.56 | 0 | 0 | 51.56 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 01:00 | 50.19 | 0 | 0 | 50.19 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 02:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 03:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 04:00 | 48.18 | 0 | 0 | 48.18 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 05:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 06:00 | 51.8 | 4.81 | 4.81 | 46.98 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 07:00 | 54.13 | 69.84 | 57.53 | 0 | 3.4 | 0 | 3.91 | 12.31 | 0
2025-09-19 08:00 | 57.16 | 80.36 | 59.49 | 0 | 2.33 | 0 | 6.12 | 20.87 | 0
2025-09-19 09:00 | 60.37 | 84.17 | 60.37 | 0 | 0 | 0 | 6.12 | 23.8 | 0
2025-09-19 10:00 | 63.25 | 93.04 | 63.25 | 0 | 0 | 0 | 6.12 | 29.8 | 0
2025-09-19 11:00 | 65.84 | 94.36 | 65.84 | 0 | 0 | 0 | 6.12 | 28.53 | 0
2025-09-19 12:00 | 67.71 | 77.63 | 67.71 | 0 | 0 | 0 | 6.12 | 9.93 | 0
2025-09-19 13:00 | 69.26 | 76.04 | 69.26 | 0 | 0 | 0 | 6.12 | 6.77 | 0
2025-09-19 14:00 | 70.1 | 62.65 | 62.65 | 4.05 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-19 15:00 | 70.69 | 52.74 | 52.74 | 16.18 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-19 16:00 | 70.63 | 31.13 | 31.13 | 39.5 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 17:00 | 69.15 | 3.71 | 3.71 | 65.44 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 18:00 | 67.87 | 0 | 0 | 67.87 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 19:00 | 65.08 | 0 | 0 | 65.08 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 20:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 21:00 | 60.41 | 0 | 0 | 60.41 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 22:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 0.68 | 0 | 0
2025-09-19 23:00 | 53.87 | 0 | 0 | 53.87 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 | 51.26 | 0 | 0 | 51.26 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 02:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 03:00 | 48.14 | 0 | 0 | 48.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 04:00 | 48.63 | 0 | 0 | 48.63 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 05:00 | 50.45 | 0 | 0 | 50.45 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 06:00 | 50.9 | 1.89 | 1.89 | 49.01 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 07:00 | 55.26 | 37.72 | 37.72 | 17.54 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 08:00 | 58.41 | 52.02 | 52.02 | 6.39 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 09:00 | 58.99 | 56.89 | 56.89 | 2.1 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 10:00 | 63.48 | 50.64 | 50.64 | 12.85 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 11:00 | 66.17 | 31.02 | 31.02 | 35.15 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 12:00 | 69 | 31.14 | 31.14 | 37.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 13:00 | 70.93 | 39.58 | 39.58 | 31.35 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 14:00 | 72.82 | 24.83 | 24.83 | 47.98 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 15:00 | 72.79 | 20.76 | 20.76 | 52.02 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 16:00 | 71.95 | 7.37 | 7.37 | 64.58 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 17:00 | 71.05 | 0.02 | 0.02 | 71.03 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 18:00 | 69.39 | 0 | 0 | 69.39 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 19:00 | 65.94 | 0 | 0 | 65.94 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 20:00 | 62.71 | 0 | 0 | 62.71 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 21:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 22:00 | 56.87 | 0 | 0 | 56.87 | 0 | 0 | 0.68 | 0 | 0
2025-09-20 23:00 | 54.21 | 0 | 0 | 54.21 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 01:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 02:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 03:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 04:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 05:00 | 49.09 | 0 | 0 | 49.09 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 06:00 | 51.4 | 4.9 | 4.9 | 46.5 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 07:00 | 53.79 | 84.62 | 57.19 | 0 | 3.4 | 0 | 3.91 | 27.43 | 0
2025-09-21 08:00 | 55.71 | 108.55 | 58.03 | 0 | 2.33 | 0 | 6.12 | 50.51 | 0
2025-09-21 09:00 | 59.74 | 111.65 | 59.74 | 0 | 0 | 0 | 6.12 | 51.91 | 0
2025-09-21 10:00 | 61.47 | 86.61 | 61.47 | 0 | 0 | 0 | 6.12 | 25.14 | 0
2025-09-21 11:00 | 65.19 | 86.7 | 65.19 | 0 | 0 | 0 | 6.12 | 21.51 | 0
2025-09-21 12:00 | 67.38 | 78.3 | 67.38 | 0 | 0 | 0 | 6.12 | 10.92 | 0
2025-09-21 13:00 | 67.87 | 74.34 | 67.87 | 0 | 0 | 0 | 6.12 | 6.46 | 0
2025-09-21 14:00 | 69.16 | 38.15 | 38.15 | 27.61 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-21 15:00 | 68.64 | 18.71 | 18.71 | 48.17 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-21 16:00 | 69.25 | 13.4 | 13.4 | 55.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 17:00 | 67.75 | 0 | 0 | 67.75 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 18:00 | 65.93 | 0 | 0 | 65.93 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 19:00 | 64.3 | 0 | 0 | 64.3 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 20:00 | 61.78 | 0 | 0 | 61.78 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 21:00 | 59.17 | 0 | 0 | 59.17 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 22:00 | 57.04 | 0 | 0 | 57.04 | 0 | 0 | 0.68 | 0 | 0
2025-09-21 23:00 | 53.53 | 0 | 0 | 53.53 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 01:00 | 49.02 | 0 | 0 | 49.02 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 02:00 | 49.32 | 0 | 0 | 49.32 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 03:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 04:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 05:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 06:00 | 51.39 | 0.08 | 0.08 | 51.31 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 07:00 | 54.45 | 1.67 | 1.67 | 52.78 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 08:00 | 57.74 | 10.92 | 10.92 | 46.82 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 09:00 | 60.81 | 13.96 | 13.96 | 46.85 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 10:00 | 63.31 | 45.95 | 45.95 | 17.36 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 11:00 | 66.73 | 68.94 | 68.94 | 0 | 2.22 | 0 | 2.79 | 0 | 0
2025-09-22 12:00 | 68.97 | 80.77 | 72.38 | 0 | 3.4 | 0 | 6.02 | 8.4 | 0
2025-09-22 13:00 | 70.99 | 98.68 | 71.1 | 0 | 0.11 | 0 | 6.12 | 27.57 | 0
2025-09-22 14:00 | 72.26 | 56.19 | 56.19 | 12.67 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-22 15:00 | 73.08 | 37.66 | 37.66 | 33.66 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-22 16:00 | 72.96 | 27.06 | 27.06 | 45.9 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 17:00 | 70.53 | 19.96 | 19.96 | 50.58 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 18:00 | 69.34 | 0 | 0 | 69.34 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 19:00 | 67.39 | 0 | 0 | 67.39 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 20:00 | 64.07 | 0 | 0 | 64.07 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 21:00 | 59.92 | 0 | 0 | 59.92 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 22:00 | 56.29 | 0 | 0 | 56.29 | 0 | 0 | 0.68 | 0 | 0
2025-09-22 23:00 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 02:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 03:00 | 48.92 | 0 | 0 | 48.92 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 04:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 05:00 | 50.03 | 0 | 0 | 50.03 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 06:00 | 51.42 | 3.23 | 3.23 | 48.2 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 07:00 | 53.87 | 37.52 | 37.52 | 16.35 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 08:00 | 56.44 | 70.44 | 59.84 | 0 | 3.4 | 0 | 3.91 | 10.59 | 0
2025-09-23 09:00 | 60.88 | 86.04 | 63.21 | 0 | 2.33 | 0 | 6.12 | 22.83 | 0
2025-09-23 10:00 | 64.52 | 89.14 | 64.52 | 0 | 0 | 0 | 6.12 | 24.62 | 0
2025-09-23 11:00 | 68.55 | 92.03 | 68.55 | 0 | 0 | 0 | 6.12 | 23.48 | 0
2025-09-23 12:00 | 71.25 | 90.28 | 71.25 | 0 | 0 | 0 | 6.12 | 19.03 | 0
2025-09-23 13:00 | 72.88 | 87.62 | 72.88 | 0 | 0 | 0 | 6.12 | 14.74 | 0
2025-09-23 14:00 | 74.23 | 89.98 | 74.23 | 0 | 0 | 0 | 6.12 | 15.75 | 0
2025-09-23 15:00 | 74.58 | 82.45 | 74.58 | 0 | 0 | 0 | 6.12 | 7.87 | 0
2025-09-23 16:00 | 75.46 | 66.38 | 66.38 | 5.68 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-23 17:00 | 72.78 | 18.77 | 18.77 | 52.25 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-23 18:00 | 71.49 | 0 | 0 | 71.49 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 19:00 | 67.92 | 0 | 0 | 67.92 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 20:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 21:00 | 60.43 | 0 | 0 | 60.43 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 22:00 | 57.46 | 0 | 0 | 57.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-23 23:00 | 54.03 | 0 | 0 | 54.03 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 01:00 | 49.78 | 0 | 0 | 49.78 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 02:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 03:00 | 47.5 | 0 | 0 | 47.5 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 04:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 05:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 06:00 | 51.51 | 1.68 | 1.68 | 49.83 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 07:00 | 53.43 | 24.19 | 24.19 | 29.24 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 08:00 | 55.86 | 59.81 | 59.26 | 0 | 3.4 | 0 | 3.91 | 0.55 | 0
2025-09-24 09:00 | 60.37 | 87.49 | 62.7 | 0 | 2.33 | 0 | 6.12 | 24.79 | 0
2025-09-24 10:00 | 63.33 | 95.03 | 63.33 | 0 | 0 | 0 | 6.12 | 31.7 | 0
2025-09-24 11:00 | 65.87 | 81.53 | 65.87 | 0 | 0 | 0 | 6.12 | 15.66 | 0
2025-09-24 12:00 | 67.71 | 78.54 | 67.71 | 0 | 0 | 0 | 6.12 | 10.83 | 0
2025-09-24 13:00 | 69.66 | 91.04 | 69.66 | 0 | 0 | 0 | 6.12 | 21.38 | 0
2025-09-24 14:00 | 71.71 | 92.12 | 71.71 | 0 | 0 | 0 | 6.12 | 20.41 | 0
2025-09-24 15:00 | 71.25 | 68.22 | 68.22 | 0 | 0 | 3.03 | 2.93 | 0 | 0
2025-09-24 16:00 | 70.7 | 48.26 | 48.26 | 20.3 | 0 | 2.14 | 0.68 | 0 | 0
2025-09-24 17:00 | 70.75 | 11.91 | 11.91 | 58.84 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 18:00 | 67.88 | 0 | 0 | 67.88 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 19:00 | 66.31 | 0 | 0 | 66.31 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 20:00 | 61.86 | 0 | 0 | 61.86 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 21:00 | 59.76 | 0 | 0 | 59.76 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 22:00 | 57.5 | 0 | 0 | 57.5 | 0 | 0 | 0.68 | 0 | 0
2025-09-24 23:00 | 53.68 | 0 | 0 | 53.68 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 01:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 02:00 | 48.71 | 0 | 0 | 48.71 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 03:00 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 04:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 05:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 06:00 | 51.92 | 1.95 | 1.95 | 49.98 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 07:00 | 54.14 | 28.47 | 28.47 | 25.67 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 08:00 | 56.39 | 43.44 | 43.44 | 12.95 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 09:00 | 58.93 | 57.82 | 57.82 | 1.11 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 10:00 | 63.43 | 77.58 | 66.83 | 0 | 3.4 | 0 | 3.91 | 10.75 | 0
2025-09-25 11:00 | 65.46 | 76.12 | 67.78 | 0 | 2.33 | 0 | 6.12 | 8.33 | 0
2025-09-25 12:00 | 67.68 | 68.38 | 67.68 | 0 | 0 | 0 | 6.12 | 0.7 | 0
2025-09-25 13:00 | 69.36 | 82.01 | 69.36 | 0 | 0 | 0 | 6.12 | 12.64 | 0
2025-09-25 14:00 | 71.19 | 98.44 | 71.19 | 0 | 0 | 0 | 6.12 | 27.25 | 0
2025-09-25 15:00 | 71.22 | 96.93 | 71.22 | 0 | 0 | 0 | 6.12 | 25.71 | 0
2025-09-25 16:00 | 71.2 | 80.92 | 71.2 | 0 | 0 | 0 | 6.12 | 9.72 | 0
2025-09-25 17:00 | 70.61 | 27.44 | 27.44 | 39.78 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-25 18:00 | 68.04 | 0 | 0 | 66.28 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-25 19:00 | 65.82 | 0 | 0 | 65.82 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 20:00 | 62.3 | 0 | 0 | 62.3 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 21:00 | 59.54 | 0 | 0 | 59.54 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 22:00 | 57.37 | 0 | 0 | 57.37 | 0 | 0 | 0.68 | 0 | 0
2025-09-25 23:00 | 53.38 | 0 | 0 | 53.38 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 01:00 | 48.4 | 0 | 0 | 48.4 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 02:00 | 48.82 | 0 | 0 | 48.82 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 03:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 04:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 05:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 06:00 | 51.29 | 0.32 | 0.32 | 50.97 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 07:00 | 53.66 | 7.83 | 7.83 | 45.83 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 08:00 | 55.84 | 34.77 | 34.77 | 21.07 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 09:00 | 59.55 | 43.82 | 43.82 | 15.73 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 10:00 | 61.58 | 48.14 | 48.14 | 13.43 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 11:00 | 65.1 | 48.29 | 48.29 | 16.81 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 12:00 | 66.89 | 55.01 | 55.01 | 11.88 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 13:00 | 69.09 | 35.83 | 35.83 | 33.26 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 14:00 | 69.83 | 22.12 | 22.12 | 47.71 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 15:00 | 70.48 | 2.43 | 2.43 | 68.04 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 16:00 | 69.52 | 1.01 | 1.01 | 68.51 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 17:00 | 69.04 | 0.42 | 0.42 | 68.62 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 18:00 | 67.11 | 0 | 0 | 67.11 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 19:00 | 64.45 | 0 | 0 | 64.45 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 20:00 | 61.93 | 0 | 0 | 61.93 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 21:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 22:00 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 0.68 | 0 | 0
2025-09-26 23:00 | 53.26 | 0 | 0 | 53.26 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 01:00 | 50.23 | 0 | 0 | 50.23 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 02:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 03:00 | 47.69 | 0 | 0 | 47.69 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 04:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 05:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 06:00 | 49.56 | 0.5 | 0.5 | 49.06 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 07:00 | 52.96 | 9.5 | 9.5 | 43.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 08:00 | 55.17 | 13.31 | 13.31 | 41.85 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 09:00 | 58.64 | 31.85 | 31.85 | 26.79 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 10:00 | 61.76 | 28.66 | 28.66 | 33.1 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 11:00 | 64.82 | 22.67 | 22.67 | 42.15 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 12:00 | 66.11 | 55.31 | 55.31 | 10.8 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 13:00 | 68.65 | 76.42 | 72.05 | 0 | 3.4 | 0 | 3.91 | 4.37 | 0
2025-09-27 14:00 | 69.58 | 83.08 | 71.91 | 0 | 2.33 | 0 | 6.12 | 11.18 | 0
2025-09-27 15:00 | 70.13 | 87.86 | 70.13 | 0 | 0 | 0 | 6.12 | 17.73 | 0
2025-09-27 16:00 | 69.31 | 83.01 | 69.31 | 0 | 0 | 0 | 6.12 | 13.7 | 0
2025-09-27 17:00 | 69.15 | 26.07 | 26.07 | 39.68 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-27 18:00 | 66.62 | 0 | 0 | 64.86 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-27 19:00 | 65.24 | 0 | 0 | 65.24 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 20:00 | 61.26 | 0 | 0 | 61.26 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 21:00 | 59.13 | 0 | 0 | 59.13 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 22:00 | 55.83 | 0 | 0 | 55.83 | 0 | 0 | 0.68 | 0 | 0
2025-09-27 23:00 | 52.99 | 0 | 0 | 52.99 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 | 50.95 | 0 | 0 | 50.95 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 01:00 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 02:00 | 46.49 | 0 | 0 | 46.49 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 03:00 | 45.91 | 0 | 0 | 45.91 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 04:00 | 48.46 | 0 | 0 | 48.46 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 05:00 | 49.53 | 0 | 0 | 49.53 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 06:00 | 51.58 | 0.81 | 0.81 | 50.77 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 07:00 | 52.81 | 0.03 | 0.03 | 52.78 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 08:00 | 54.64 | 32.07 | 32.07 | 22.57 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 09:00 | 57.63 | 19.01 | 19.01 | 38.62 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 10:00 | 60.3 | 37.36 | 37.36 | 22.94 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 11:00 | 61.99 | 52.84 | 52.84 | 9.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 12:00 | 65.14 | 45.17 | 45.17 | 19.96 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 13:00 | 66.79 | 91.9 | 70.19 | 0 | 3.4 | 0 | 3.91 | 21.72 | 0
2025-09-28 14:00 | 66.74 | 83.23 | 69.07 | 0 | 2.33 | 0 | 6.12 | 14.17 | 0
2025-09-28 15:00 | 66.78 | 32.84 | 32.84 | 30.54 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-28 16:00 | 65.86 | 58.63 | 58.63 | 5.46 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-28 17:00 | 66.44 | 20.18 | 20.18 | 46.26 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 18:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 19:00 | 62.35 | 0 | 0 | 62.35 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 20:00 | 60.53 | 0 | 0 | 60.53 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 21:00 | 57.54 | 0 | 0 | 57.54 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 22:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 0.68 | 0 | 0
2025-09-28 23:00 | 52.1 | 0 | 0 | 52.1 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 | 51.13 | 0 | 0 | 51.13 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 01:00 | 48.76 | 0 | 0 | 48.76 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 02:00 | 48.28 | 0 | 0 | 48.28 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 03:00 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 04:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 05:00 | 48.2 | 0 | 0 | 48.2 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 06:00 | 50.96 | 0.92 | 0.92 | 50.04 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 07:00 | 52.48 | 50.94 | 50.94 | 1.54 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 08:00 | 55.43 | 58.8 | 58.8 | 0 | 3.37 | 0 | 3.88 | 0 | 0
2025-09-29 09:00 | 58.67 | 67.58 | 61.03 | 0 | 2.36 | 0 | 6.12 | 6.56 | 0
2025-09-29 10:00 | 61.77 | 70.38 | 61.77 | 0 | 0 | 0 | 6.12 | 8.61 | 0
2025-09-29 11:00 | 63.72 | 56.93 | 56.93 | 3.4 | 0 | 3.4 | 2.54 | 0 | 0
2025-09-29 12:00 | 66.96 | 50.46 | 50.46 | 14.73 | 0 | 1.77 | 0.68 | 0 | 0
2025-09-29 13:00 | 69.4 | 55.09 | 55.09 | 14.31 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 14:00 | 70.04 | 42.32 | 42.32 | 27.72 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 15:00 | 70.53 | 44.02 | 44.02 | 26.51 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 16:00 | 70.31 | 70.74 | 70.74 | 0 | 0.43 | 0 | 1.09 | 0 | 0
2025-09-29 17:00 | 68.94 | 23.15 | 23.15 | 45.4 | 0 | 0.39 | 0.68 | 0 | 0
2025-09-29 18:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 19:00 | 64.56 | 0 | 0 | 64.56 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 20:00 | 62.21 | 0 | 0 | 62.21 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 21:00 | 58.14 | 0 | 0 | 58.14 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 22:00 | 55.49 | 0 | 0 | 55.49 | 0 | 0 | 0.68 | 0 | 0
2025-09-29 23:00 | 52.23 | 0 | 0 | 52.23 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 | 50.88 | 0 | 0 | 50.88 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 01:00 | 48.63 | 0 | 0 | 48.63 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 02:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 03:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 04:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 05:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 06:00 | 49.68 | 1.18 | 1.18 | 48.49 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 07:00 | 52.12 | 49.43 | 49.43 | 2.69 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 08:00 | 55.95 | 64.59 | 59.35 | 0 | 3.4 | 0 | 3.91 | 5.24 | 0
2025-09-30 09:00 | 57.69 | 82.71 | 60.02 | 0 | 2.33 | 0 | 6.12 | 22.69 | 0
2025-09-30 10:00 | 61.07 | 85.65 | 61.07 | 0 | 0 | 0 | 6.12 | 24.58 | 0
2025-09-30 11:00 | 62.99 | 80.61 | 62.99 | 0 | 0 | 0 | 6.12 | 17.62 | 0
2025-09-30 12:00 | 65.99 | 77.23 | 65.99 | 0 | 0 | 0 | 6.12 | 11.23 | 0
2025-09-30 13:00 | 66.79 | 80.38 | 66.79 | 0 | 0 | 0 | 6.12 | 13.59 | 0
2025-09-30 14:00 | 68.38 | 89.78 | 68.38 | 0 | 0 | 0 | 6.12 | 21.4 | 0
2025-09-30 15:00 | 68.74 | 87.36 | 68.74 | 0 | 0 | 0 | 6.12 | 18.62 | 0
2025-09-30 16:00 | 69.52 | 68.03 | 68.03 | 0 | 0 | 1.5 | 4.55 | 0 | 0
2025-09-30 17:00 | 67.61 | 18.34 | 18.34 | 45.88 | 0 | 3.4 | 0.97 | 0 | 0
2025-09-30 18:00 | 65.32 | 0 | 0 | 65.04 | 0 | 0.27 | 0.68 | 0 | 0
2025-09-30 19:00 | 63.75 | 0 | 0 | 63.75 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 20:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 21:00 | 57.24 | 0 | 0 | 57.24 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 22:00 | 54.85 | 0 | 0 | 54.85 | 0 | 0 | 0.68 | 0 | 0
2025-09-30 23:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 | 50.24 | 0 | 0 | 50.24 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 01:00 | 48.41 | 0 | 0 | 48.41 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 02:00 | 46.81 | 0 | 0 | 46.81 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 03:00 | 47.79 | 0 | 0 | 47.79 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 04:00 | 46.75 | 0 | 0 | 46.75 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 05:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 06:00 | 50.97 | 0.84 | 0.84 | 50.13 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 07:00 | 53.02 | 51.23 | 51.23 | 1.79 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 08:00 | 55.77 | 90.39 | 59.17 | 0 | 3.4 | 0 | 3.91 | 31.22 | 0
2025-10-01 09:00 | 59.32 | 95.21 | 61.65 | 0 | 2.33 | 0 | 6.12 | 33.56 | 0
2025-10-01 10:00 | 63.89 | 92.94 | 63.89 | 0 | 0 | 0 | 6.12 | 29.05 | 0
2025-10-01 11:00 | 67.6 | 86.1 | 67.6 | 0 | 0 | 0 | 6.12 | 18.5 | 0
2025-10-01 12:00 | 71.69 | 86.91 | 71.69 | 0 | 0 | 0 | 6.12 | 15.22 | 0
2025-10-01 13:00 | 73.78 | 88.57 | 73.78 | 0 | 0 | 0 | 6.12 | 14.79 | 0
2025-10-01 14:00 | 76.75 | 90.98 | 76.75 | 0 | 0 | 0 | 6.12 | 14.23 | 0
2025-10-01 15:00 | 77.05 | 87.02 | 77.05 | 0 | 0 | 0 | 6.12 | 9.97 | 0
2025-10-01 16:00 | 76.44 | 76.38 | 76.38 | 0 | 0 | 0.06 | 6.05 | 0 | 0
2025-10-01 17:00 | 75.2 | 16.36 | 16.36 | 55.44 | 0 | 3.4 | 2.48 | 0 | 0
2025-10-01 18:00 | 71.37 | 0 | 0 | 69.67 | 0 | 1.71 | 0.68 | 0 | 0
2025-10-01 19:00 | 67.62 | 0 | 0 | 67.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 20:00 | 63.73 | 0 | 0 | 63.73 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 21:00 | 59.9 | 0 | 0 | 59.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 22:00 | 56.22 | 0 | 0 | 56.22 | 0 | 0 | 0.68 | 0 | 0
2025-10-01 23:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 | 49.24 | 0 | 0 | 49.24 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 01:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 02:00 | 47.52 | 0 | 0 | 47.52 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 03:00 | 47.04 | 0 | 0 | 47.04 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 04:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 05:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 06:00 | 50.64 | 0.54 | 0.54 | 50.1 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 07:00 | 53.43 | 26.33 | 26.33 | 27.1 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 08:00 | 56.18 | 79.48 | 59.58 | 0 | 3.4 | 0 | 3.91 | 19.91 | 0
2025-10-02 09:00 | 60.12 | 51.43 | 51.43 | 5.63 | 0 | 3.07 | 0.68 | 0 | 0
2025-10-02 10:00 | 63.88 | 47.89 | 47.89 | 15.98 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 11:00 | 67.04 | 60.96 | 60.96 | 6.08 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 12:00 | 70.16 | 44.99 | 44.99 | 25.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 13:00 | 72.28 | 76.99 | 75.68 | 0 | 3.4 | 0 | 3.91 | 1.31 | 0
2025-10-02 14:00 | 74.03 | 54.86 | 54.86 | 16.09 | 0 | 3.07 | 0.68 | 0 | 0
2025-10-02 15:00 | 74.45 | 92.81 | 77.85 | 0 | 3.4 | 0 | 3.91 | 14.96 | 0
2025-10-02 16:00 | 74.36 | 66.56 | 66.56 | 4.73 | 0 | 3.07 | 0.68 | 0 | 0
2025-10-02 17:00 | 72.03 | 1.4 | 1.4 | 70.63 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 18:00 | 69.71 | 0 | 0 | 69.71 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 19:00 | 65.39 | 0 | 0 | 65.39 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 20:00 | 63.81 | 0 | 0 | 63.81 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 21:00 | 59.16 | 0 | 0 | 59.16 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 22:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 0.68 | 0 | 0
2025-10-02 23:00 | 53.47 | 0 | 0 | 53.47 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 | 50.16 | 0 | 0 | 50.16 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 01:00 | 49.01 | 0 | 0 | 49.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 02:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 03:00 | 48.05 | 0 | 0 | 48.05 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 04:00 | 47.76 | 0 | 0 | 47.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 05:00 | 48.39 | 0 | 0 | 48.39 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 06:00 | 50.72 | 0.48 | 0.48 | 50.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 07:00 | 51.7 | 37.9 | 37.9 | 13.8 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 08:00 | 54.83 | 74.66 | 58.23 | 0 | 3.4 | 0 | 3.91 | 16.43 | 0
2025-10-03 09:00 | 58.63 | 92.42 | 60.96 | 0 | 2.33 | 0 | 6.12 | 31.46 | 0
2025-10-03 10:00 | 59.96 | 89.66 | 59.96 | 0 | 0 | 0 | 6.12 | 29.7 | 0
2025-10-03 11:00 | 64 | 83.05 | 64 | 0 | 0 | 0 | 6.12 | 19.05 | 0
2025-10-03 12:00 | 66.44 | 81.07 | 66.44 | 0 | 0 | 0 | 6.12 | 14.63 | 0
2025-10-03 13:00 | 69.07 | 74.46 | 69.07 | 0 | 0 | 0 | 6.12 | 5.4 | 0
2025-10-03 14:00 | 68.5 | 70.19 | 68.5 | 0 | 0 | 0 | 6.12 | 1.68 | 0
2025-10-03 15:00 | 70.51 | 65.82 | 65.82 | 1.3 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-03 16:00 | 69.01 | 36.7 | 36.7 | 30.55 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-03 17:00 | 67.86 | 10.22 | 10.22 | 57.64 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 18:00 | 65.56 | 0 | 0 | 65.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 19:00 | 63.17 | 0 | 0 | 63.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 21:00 | 57.35 | 0 | 0 | 57.35 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 22:00 | 55.34 | 0 | 0 | 55.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-03 23:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 01:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 02:00 | 47.26 | 0 | 0 | 47.26 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 03:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 04:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 05:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 06:00 | 50.31 | 0.09 | 0.09 | 50.23 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 07:00 | 51.69 | 25 | 25 | 26.69 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 08:00 | 53.66 | 42.57 | 42.57 | 11.09 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 09:00 | 56.64 | 15.96 | 15.96 | 40.68 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 10:00 | 59.15 | 41.47 | 41.47 | 17.69 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 11:00 | 60.26 | 48.33 | 48.33 | 11.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 12:00 | 62.26 | 65.1 | 65.1 | 0 | 2.85 | 0 | 3.38 | 0 | 0
2025-10-04 13:00 | 63.61 | 78.25 | 66.49 | 0 | 2.88 | 0 | 6.12 | 11.75 | 0
2025-10-04 14:00 | 64.65 | 51.04 | 51.04 | 10.21 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-04 15:00 | 64.64 | 42.25 | 42.25 | 20.62 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-04 16:00 | 65.11 | 77.17 | 68.51 | 0 | 3.4 | 0 | 3.91 | 8.66 | 0
2025-10-04 17:00 | 63.17 | 15.21 | 15.21 | 44.9 | 0 | 3.07 | 0.68 | 0 | 0
2025-10-04 18:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 19:00 | 60.82 | 0 | 0 | 60.82 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 20:00 | 58.83 | 0 | 0 | 58.83 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 21:00 | 55.87 | 0 | 0 | 55.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 22:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-04 23:00 | 51.65 | 0 | 0 | 51.65 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 01:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 02:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 03:00 | 47.35 | 0 | 0 | 47.35 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 04:00 | 47.21 | 0 | 0 | 47.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 05:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 06:00 | 49.64 | 0.45 | 0.45 | 49.19 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 07:00 | 51.66 | 39.65 | 39.65 | 12.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 08:00 | 54.43 | 66.65 | 57.83 | 0 | 3.4 | 0 | 3.91 | 8.83 | 0
2025-10-05 09:00 | 55.77 | 76.46 | 58.09 | 0 | 2.33 | 0 | 6.12 | 18.37 | 0
2025-10-05 10:00 | 58.56 | 79.95 | 58.56 | 0 | 0 | 0 | 6.12 | 21.39 | 0
2025-10-05 11:00 | 60.03 | 65.72 | 60.03 | 0 | 0 | 0 | 6.12 | 5.69 | 0
2025-10-05 12:00 | 62.23 | 72.82 | 62.23 | 0 | 0 | 0 | 6.12 | 10.59 | 0
2025-10-05 13:00 | 63.2 | 39.24 | 39.24 | 20.56 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-05 14:00 | 63.3 | 42.84 | 42.84 | 18.7 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-05 15:00 | 63.29 | 66.87 | 66.69 | 0 | 3.4 | 0 | 3.91 | 0.18 | 0
2025-10-05 16:00 | 63.46 | 54.37 | 54.37 | 6.02 | 0 | 3.07 | 0.68 | 0 | 0
2025-10-05 17:00 | 62.47 | 1.65 | 1.65 | 60.82 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 18:00 | 62.33 | 0 | 0 | 62.33 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 19:00 | 60.05 | 0 | 0 | 60.05 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 20:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 21:00 | 55.84 | 0 | 0 | 55.84 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 22:00 | 53.21 | 0 | 0 | 53.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-05 23:00 | 51.88 | 0 | 0 | 51.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 01:00 | 48.45 | 0 | 0 | 48.45 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 02:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 03:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 04:00 | 47.42 | 0 | 0 | 47.42 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 05:00 | 46.82 | 0 | 0 | 46.82 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 06:00 | 50.64 | 0 | 0 | 50.64 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 07:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 08:00 | 54.9 | 2.02 | 2.02 | 52.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 09:00 | 58.31 | 3.7 | 3.7 | 54.61 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 10:00 | 61.74 | 11.56 | 11.56 | 50.18 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 11:00 | 64.77 | 13.91 | 13.91 | 50.86 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 12:00 | 68.03 | 11 | 11 | 57.03 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 13:00 | 70.09 | 65.33 | 65.33 | 4.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 14:00 | 72.18 | 64.61 | 64.61 | 7.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 15:00 | 72.06 | 44.34 | 44.34 | 27.72 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 16:00 | 72.28 | 27.58 | 27.58 | 44.7 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 17:00 | 70.28 | 3.7 | 3.7 | 66.58 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 18:00 | 66.63 | 0 | 0 | 66.63 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 19:00 | 65.94 | 0 | 0 | 65.94 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 21:00 | 58.77 | 0 | 0 | 58.77 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 22:00 | 54.84 | 0 | 0 | 54.84 | 0 | 0 | 0.68 | 0 | 0
2025-10-06 23:00 | 52.51 | 0 | 0 | 52.51 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 01:00 | 48.06 | 0 | 0 | 48.06 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 02:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 03:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 04:00 | 46.93 | 0 | 0 | 46.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 05:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 06:00 | 48.33 | 0.28 | 0.28 | 48.04 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 07:00 | 51.55 | 41 | 41 | 10.54 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 08:00 | 54.36 | 83.96 | 57.76 | 0 | 3.4 | 0 | 3.91 | 26.19 | 0
2025-10-07 09:00 | 57.05 | 93.19 | 59.38 | 0 | 2.33 | 0 | 6.12 | 33.81 | 0
2025-10-07 10:00 | 60.24 | 78.48 | 60.24 | 0 | 0 | 0 | 6.12 | 18.24 | 0
2025-10-07 11:00 | 62.23 | 48.21 | 48.21 | 10.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-07 12:00 | 64.74 | 42.61 | 42.61 | 20.36 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-07 13:00 | 67.09 | 64.61 | 64.61 | 2.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 14:00 | 66.48 | 40.75 | 40.75 | 25.74 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 15:00 | 68.3 | 27.14 | 27.14 | 41.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 16:00 | 67.46 | 5.71 | 5.71 | 61.75 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 17:00 | 66.04 | 0.82 | 0.82 | 65.22 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 18:00 | 64.88 | 0 | 0 | 64.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 19:00 | 63.03 | 0 | 0 | 63.03 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 20:00 | 60.28 | 0 | 0 | 60.28 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 21:00 | 56.87 | 0 | 0 | 56.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 22:00 | 54.59 | 0 | 0 | 54.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-07 23:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 | 49.23 | 0 | 0 | 49.23 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 01:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 02:00 | 46.27 | 0 | 0 | 46.27 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 03:00 | 46.66 | 0 | 0 | 46.66 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 04:00 | 46.57 | 0 | 0 | 46.57 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 05:00 | 47.1 | 0 | 0 | 47.1 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 06:00 | 48.43 | 0 | 0 | 48.43 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 07:00 | 51.89 | 46.8 | 46.8 | 5.09 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 08:00 | 53.8 | 97.7 | 57.2 | 0 | 3.4 | 0 | 3.91 | 40.49 | 0
2025-10-08 09:00 | 57.09 | 99.25 | 59.42 | 0 | 2.33 | 0 | 6.12 | 39.83 | 0
2025-10-08 10:00 | 60.46 | 71.66 | 60.46 | 0 | 0 | 0 | 6.12 | 11.21 | 0
2025-10-08 11:00 | 61.95 | 21.42 | 21.42 | 37.13 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-08 12:00 | 65 | 31.52 | 31.52 | 31.71 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-08 13:00 | 66.81 | 60.65 | 60.65 | 6.16 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 14:00 | 68.28 | 47.35 | 47.35 | 20.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 15:00 | 69.12 | 58.01 | 58.01 | 11.11 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 16:00 | 67.43 | 4.57 | 4.57 | 62.86 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 17:00 | 67.18 | 0.03 | 0.03 | 67.16 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 18:00 | 65.53 | 0 | 0 | 65.53 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 19:00 | 62.51 | 0 | 0 | 62.51 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 20:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 21:00 | 57.14 | 0 | 0 | 57.14 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 22:00 | 54.25 | 0 | 0 | 54.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-08 23:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 | 49.23 | 0 | 0 | 49.23 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 01:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 02:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 03:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 04:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 05:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 06:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 07:00 | 50.89 | 0.1 | 0.1 | 50.79 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 08:00 | 52.19 | 2.92 | 2.92 | 49.27 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 09:00 | 54.49 | 4.84 | 4.84 | 49.65 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 10:00 | 55.67 | 6.71 | 6.71 | 48.96 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 11:00 | 58.06 | 8.17 | 8.17 | 49.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 12:00 | 58.89 | 8.7 | 8.7 | 50.19 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 13:00 | 58.69 | 7.48 | 7.48 | 51.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 14:00 | 60.09 | 6.13 | 6.13 | 53.96 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 15:00 | 60.02 | 3.69 | 3.69 | 56.33 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 16:00 | 60.17 | 1.57 | 1.57 | 58.6 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 17:00 | 59.32 | 0 | 0 | 59.32 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 18:00 | 58.4 | 0 | 0 | 58.4 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 19:00 | 57.37 | 0 | 0 | 57.37 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 20:00 | 56.1 | 0 | 0 | 56.1 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 21:00 | 54.68 | 0 | 0 | 54.68 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 22:00 | 52.84 | 0 | 0 | 52.84 | 0 | 0 | 0.68 | 0 | 0
2025-10-09 23:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 01:00 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 02:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 03:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 04:00 | 46.05 | 0 | 0 | 46.05 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 05:00 | 49 | 0 | 0 | 49 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 06:00 | 49.22 | 0 | 0 | 49.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 07:00 | 50.54 | 42.11 | 42.11 | 8.44 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 08:00 | 54.33 | 90.9 | 57.73 | 0 | 3.4 | 0 | 3.91 | 33.17 | 0
2025-10-10 09:00 | 56.44 | 68.19 | 58.76 | 0 | 2.33 | 0 | 6.12 | 9.43 | 0
2025-10-10 10:00 | 60.44 | 35.1 | 35.1 | 21.95 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-10 11:00 | 62.87 | 49.11 | 49.11 | 12 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-10 12:00 | 65.4 | 52.62 | 52.62 | 12.78 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 13:00 | 68.5 | 71.3 | 71.3 | 0 | 2.8 | 0 | 3.34 | 0 | 0
2025-10-10 14:00 | 69.31 | 90.4 | 72.23 | 0 | 2.92 | 0 | 6.12 | 18.18 | 0
2025-10-10 15:00 | 69.97 | 94.07 | 69.97 | 0 | 0 | 0 | 6.12 | 24.11 | 0
2025-10-10 16:00 | 69.24 | 70.16 | 69.24 | 0 | 0 | 0 | 6.12 | 0.91 | 0
2025-10-10 17:00 | 67.47 | 6.84 | 6.84 | 57.23 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-10 18:00 | 65.92 | 0 | 0 | 64.16 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-10 19:00 | 63.58 | 0 | 0 | 63.58 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 20:00 | 60.06 | 0 | 0 | 60.06 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 21:00 | 57.79 | 0 | 0 | 57.79 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 22:00 | 54.34 | 0 | 0 | 54.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-10 23:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 01:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 02:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 03:00 | 45.82 | 0 | 0 | 45.82 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 04:00 | 46.31 | 0 | 0 | 46.31 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 05:00 | 47 | 0 | 0 | 47 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 06:00 | 48.99 | 0 | 0 | 48.99 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 07:00 | 50.96 | 42.65 | 42.65 | 8.31 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 08:00 | 53.87 | 89.36 | 57.27 | 0 | 3.4 | 0 | 3.91 | 32.1 | 0
2025-10-11 09:00 | 56.58 | 93.07 | 58.9 | 0 | 2.33 | 0 | 6.12 | 34.16 | 0
2025-10-11 10:00 | 59.15 | 87.26 | 59.15 | 0 | 0 | 0 | 6.12 | 28.11 | 0
2025-10-11 11:00 | 61.06 | 79.52 | 61.06 | 0 | 0 | 0 | 6.12 | 18.46 | 0
2025-10-11 12:00 | 64.97 | 79.53 | 64.97 | 0 | 0 | 0 | 6.12 | 14.56 | 0
2025-10-11 13:00 | 65.82 | 85.64 | 65.82 | 0 | 0 | 0 | 6.12 | 19.81 | 0
2025-10-11 14:00 | 67.01 | 91.97 | 67.01 | 0 | 0 | 0 | 6.12 | 24.96 | 0
2025-10-11 15:00 | 67.27 | 89.87 | 67.27 | 0 | 0 | 0 | 6.12 | 22.6 | 0
2025-10-11 16:00 | 66.8 | 67.4 | 66.8 | 0 | 0 | 0 | 6.12 | 0.59 | 0
2025-10-11 17:00 | 66.67 | 2.29 | 2.29 | 60.98 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-11 18:00 | 64.77 | 0 | 0 | 63 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-11 19:00 | 61.96 | 0 | 0 | 61.96 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 20:00 | 59.01 | 0 | 0 | 59.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 21:00 | 56.56 | 0 | 0 | 56.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 22:00 | 53.52 | 0 | 0 | 53.52 | 0 | 0 | 0.68 | 0 | 0
2025-10-11 23:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 01:00 | 46.82 | 0 | 0 | 46.82 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 02:00 | 46.2 | 0 | 0 | 46.2 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 03:00 | 45.84 | 0 | 0 | 45.84 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 04:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 05:00 | 46.73 | 0 | 0 | 46.73 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 06:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 07:00 | 49.98 | 4.67 | 4.67 | 45.3 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 08:00 | 52.23 | 35.51 | 35.51 | 16.72 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 09:00 | 54.37 | 60.46 | 57.77 | 0 | 3.4 | 0 | 3.91 | 2.69 | 0
2025-10-12 10:00 | 56.08 | 68.84 | 58.4 | 0 | 2.33 | 0 | 6.12 | 10.43 | 0
2025-10-12 11:00 | 58.85 | 63.08 | 58.85 | 0 | 0 | 0 | 6.12 | 4.23 | 0
2025-10-12 12:00 | 59.25 | 65.41 | 59.25 | 0 | 0 | 0 | 6.12 | 6.16 | 0
2025-10-12 13:00 | 60.39 | 67.91 | 60.39 | 0 | 0 | 0 | 6.12 | 7.52 | 0
2025-10-12 14:00 | 61.98 | 77.76 | 61.98 | 0 | 0 | 0 | 6.12 | 15.78 | 0
2025-10-12 15:00 | 61.27 | 97.51 | 61.27 | 0 | 0 | 0 | 6.12 | 36.24 | 0
2025-10-12 16:00 | 61.26 | 72.36 | 61.26 | 0 | 0 | 0 | 6.12 | 11.1 | 0
2025-10-12 17:00 | 60.23 | 5.11 | 5.11 | 51.72 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-12 18:00 | 60.15 | 0 | 0 | 58.38 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-12 19:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 20:00 | 56.98 | 0 | 0 | 56.98 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 21:00 | 54.9 | 0 | 0 | 54.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 22:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-12 23:00 | 50.17 | 0 | 0 | 50.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 | 48.04 | 0 | 0 | 48.04 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 01:00 | 47.56 | 0 | 0 | 47.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 02:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 03:00 | 45.26 | 0 | 0 | 45.26 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 04:00 | 45.96 | 0 | 0 | 45.96 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 05:00 | 46.76 | 0 | 0 | 46.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 06:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 07:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 08:00 | 52.43 | 1.63 | 1.63 | 50.8 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 09:00 | 54.51 | 3.15 | 3.15 | 51.36 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 10:00 | 56.54 | 4.6 | 4.6 | 51.94 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 11:00 | 58.58 | 5.91 | 5.91 | 52.67 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 12:00 | 60.93 | 6.61 | 6.61 | 54.32 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 13:00 | 62.39 | 58.31 | 58.31 | 4.08 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 14:00 | 62.82 | 57.25 | 57.25 | 5.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 15:00 | 63.86 | 53.52 | 53.52 | 10.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 16:00 | 63.22 | 37.62 | 37.62 | 25.6 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 17:00 | 62.72 | 0.88 | 0.88 | 61.85 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 18:00 | 61.02 | 0 | 0 | 61.02 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 19:00 | 58.97 | 0 | 0 | 58.97 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 20:00 | 57.34 | 0 | 0 | 57.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 21:00 | 54.36 | 0 | 0 | 54.36 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 22:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 0.68 | 0 | 0
2025-10-13 23:00 | 49.93 | 0 | 0 | 49.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 01:00 | 46.62 | 0 | 0 | 46.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 02:00 | 46.34 | 0 | 0 | 46.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 03:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 04:00 | 45.48 | 0 | 0 | 45.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 05:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 06:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 07:00 | 51.22 | 21.89 | 21.89 | 29.33 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 08:00 | 52.82 | 78.45 | 56.22 | 0 | 3.4 | 0 | 3.91 | 22.23 | 0
2025-10-14 09:00 | 56.33 | 64.9 | 58.66 | 0 | 2.33 | 0 | 6.12 | 6.24 | 0
2025-10-14 10:00 | 57.92 | 36.55 | 36.55 | 17.96 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-14 11:00 | 61.1 | 52.95 | 52.95 | 6.39 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-14 12:00 | 62.24 | 68.24 | 65.64 | 0 | 3.4 | 0 | 3.91 | 2.59 | 0
2025-10-14 13:00 | 64.6 | 15.24 | 15.24 | 46.29 | 0 | 3.07 | 0.68 | 0 | 0
2025-10-14 14:00 | 64.27 | 8.45 | 8.45 | 55.83 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 15:00 | 65.24 | 8.68 | 8.68 | 56.57 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 16:00 | 65.68 | 0.66 | 0.66 | 65.02 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 17:00 | 63.73 | 0 | 0 | 63.73 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 18:00 | 62.93 | 0 | 0 | 62.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 19:00 | 61.01 | 0 | 0 | 61.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 20:00 | 57.81 | 0 | 0 | 57.81 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 21:00 | 54.93 | 0 | 0 | 54.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 22:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-14 23:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 | 48.12 | 0 | 0 | 48.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 01:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 02:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 03:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 04:00 | 45.32 | 0 | 0 | 45.32 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 05:00 | 47.34 | 0 | 0 | 47.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 06:00 | 47.65 | 0 | 0 | 47.65 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 07:00 | 50.21 | 0 | 0 | 50.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 08:00 | 53.09 | 25.93 | 25.93 | 27.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 09:00 | 55.58 | 2.74 | 2.74 | 52.84 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 10:00 | 57.31 | 13.57 | 13.57 | 43.74 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 11:00 | 60.15 | 45.75 | 45.75 | 14.4 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 12:00 | 62.1 | 56.7 | 56.7 | 5.41 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 13:00 | 63.17 | 42.83 | 42.83 | 20.35 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 14:00 | 64.73 | 75.01 | 68.13 | 0 | 3.4 | 0 | 3.91 | 6.88 | 0
2025-10-15 15:00 | 65.69 | 86.08 | 68.01 | 0 | 2.33 | 0 | 6.12 | 18.06 | 0
2025-10-15 16:00 | 64.66 | 32.6 | 32.6 | 28.66 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-15 17:00 | 63.73 | 0.78 | 0.78 | 61.18 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-15 18:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 19:00 | 59.14 | 0 | 0 | 59.14 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 20:00 | 57.75 | 0 | 0 | 57.75 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 21:00 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 22:00 | 52.21 | 0 | 0 | 52.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-15 23:00 | 51.25 | 0 | 0 | 51.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 01:00 | 46.13 | 0 | 0 | 46.13 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 02:00 | 46.13 | 0 | 0 | 46.13 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 03:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 04:00 | 45.33 | 0 | 0 | 45.33 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 05:00 | 47.12 | 0 | 0 | 47.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 06:00 | 48.02 | 0 | 0 | 48.02 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 07:00 | 49.14 | 8.93 | 8.93 | 40.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 08:00 | 52.42 | 36.3 | 36.3 | 16.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 09:00 | 54.3 | 54.54 | 54.54 | 0 | 0.25 | 0 | 0.91 | 0 | 0
2025-10-16 10:00 | 57.58 | 75.02 | 60.98 | 0 | 3.4 | 0 | 4.14 | 14.04 | 0
2025-10-16 11:00 | 58.64 | 64.46 | 60.72 | 0 | 2.08 | 0 | 6.12 | 3.74 | 0
2025-10-16 12:00 | 61.27 | 61.24 | 61.24 | 0 | 0 | 0.03 | 6.09 | 0 | 0
2025-10-16 13:00 | 63 | 50.54 | 50.54 | 9.06 | 0 | 3.4 | 2.51 | 0 | 0
2025-10-16 14:00 | 62.55 | 64.54 | 64.54 | 0 | 1.99 | 0 | 4.4 | 0 | 0
2025-10-16 15:00 | 63.16 | 80.77 | 64.97 | 0 | 1.81 | 0 | 6.12 | 15.8 | 0
2025-10-16 16:00 | 63.16 | 62.3 | 62.3 | 0 | 0 | 0.87 | 5.21 | 0 | 0
2025-10-16 17:00 | 61.69 | 1.59 | 1.59 | 56.7 | 0 | 3.4 | 1.63 | 0 | 0
2025-10-16 18:00 | 60.88 | 0 | 0 | 59.98 | 0 | 0.9 | 0.68 | 0 | 0
2025-10-16 19:00 | 58.83 | 0 | 0 | 58.83 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 20:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 21:00 | 54.52 | 0 | 0 | 54.52 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 22:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 0.68 | 0 | 0
2025-10-16 23:00 | 50.01 | 0 | 0 | 50.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 | 47.55 | 0 | 0 | 47.55 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 01:00 | 46.08 | 0 | 0 | 46.08 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 02:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 03:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 04:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 05:00 | 46.52 | 0 | 0 | 46.52 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 06:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 07:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 08:00 | 51.9 | 3.42 | 3.42 | 48.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 09:00 | 54.01 | 7.72 | 7.72 | 46.29 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 10:00 | 57.64 | 7.61 | 7.61 | 50.03 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 11:00 | 59.05 | 4.93 | 4.93 | 54.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 12:00 | 61.02 | 8.17 | 8.17 | 52.85 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 13:00 | 62.14 | 60.45 | 60.45 | 1.69 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 14:00 | 63.28 | 61.58 | 61.58 | 1.7 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 15:00 | 62.99 | 56.82 | 56.82 | 6.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 16:00 | 63.2 | 37.69 | 37.69 | 25.52 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 17:00 | 61.91 | 0.37 | 0.37 | 61.54 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 18:00 | 60.79 | 0 | 0 | 60.79 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 19:00 | 57.76 | 0 | 0 | 57.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 20:00 | 56.26 | 0 | 0 | 56.26 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 21:00 | 55.17 | 0 | 0 | 55.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 22:00 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 0.68 | 0 | 0
2025-10-17 23:00 | 50.45 | 0 | 0 | 50.45 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 | 48.38 | 0 | 0 | 48.38 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 01:00 | 46.56 | 0 | 0 | 46.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 02:00 | 45.06 | 0 | 0 | 45.06 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 03:00 | 44.45 | 0 | 0 | 44.45 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 04:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 05:00 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 06:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 07:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 08:00 | 52.76 | 7 | 7 | 45.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 09:00 | 54.01 | 4.68 | 4.68 | 49.33 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 10:00 | 57.05 | 3.94 | 3.94 | 53.11 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 11:00 | 59.34 | 11.2 | 11.2 | 48.14 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 12:00 | 59.77 | 67.57 | 63.17 | 0 | 3.4 | 0 | 3.91 | 4.4 | 0
2025-10-18 13:00 | 61.41 | 83.53 | 63.73 | 0 | 2.33 | 0 | 6.12 | 19.8 | 0
2025-10-18 14:00 | 61.98 | 92.96 | 61.98 | 0 | 0 | 0 | 6.12 | 30.97 | 0
2025-10-18 15:00 | 62.17 | 50.53 | 50.53 | 8.24 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-18 16:00 | 62.83 | 47.32 | 47.32 | 13.74 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-18 17:00 | 61.55 | 0.45 | 0.45 | 61.1 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 18:00 | 60.31 | 0 | 0 | 60.31 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 19:00 | 58.77 | 0 | 0 | 58.77 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 20:00 | 55.46 | 0 | 0 | 55.46 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 21:00 | 54.74 | 0 | 0 | 54.74 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 22:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 0.68 | 0 | 0
2025-10-18 23:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 01:00 | 46.77 | 0 | 0 | 46.77 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 02:00 | 45.11 | 0 | 0 | 45.11 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 03:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 04:00 | 45.19 | 0 | 0 | 45.19 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 05:00 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 06:00 | 47.04 | 0 | 0 | 47.04 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 07:00 | 49.57 | 12.74 | 12.74 | 36.83 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 08:00 | 51.58 | 14.99 | 14.99 | 36.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 09:00 | 53.54 | 54.87 | 54.87 | 0 | 1.33 | 0 | 1.95 | 0 | 0
2025-10-19 10:00 | 57.01 | 66.98 | 60.41 | 0 | 3.4 | 0 | 5.18 | 6.57 | 0
2025-10-19 11:00 | 58.7 | 38.35 | 38.35 | 16.96 | 0 | 3.4 | 1.6 | 0 | 0
2025-10-19 12:00 | 60.78 | 27.86 | 27.86 | 32.05 | 0 | 0.87 | 0.68 | 0 | 0
2025-10-19 13:00 | 62.29 | 27.99 | 27.99 | 34.31 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 14:00 | 64.11 | 13.3 | 13.3 | 50.82 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 15:00 | 63.81 | 6.12 | 6.12 | 57.69 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 16:00 | 63.54 | 5.28 | 5.28 | 58.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 17:00 | 62.3 | 0 | 0 | 62.3 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 18:00 | 61.22 | 0 | 0 | 61.22 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 19:00 | 59.66 | 0 | 0 | 59.66 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 20:00 | 57 | 0 | 0 | 57 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 21:00 | 54.55 | 0 | 0 | 54.55 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 22:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 0.68 | 0 | 0
2025-10-19 23:00 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 01:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 02:00 | 44.66 | 0 | 0 | 44.66 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 03:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 04:00 | 44.09 | 0 | 0 | 44.09 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 05:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 06:00 | 47.37 | 0 | 0 | 47.37 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 07:00 | 49.56 | 5.55 | 5.55 | 44.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 08:00 | 51.76 | 24.88 | 24.88 | 26.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 09:00 | 55.11 | 25.46 | 25.46 | 29.65 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 10:00 | 57.93 | 23.04 | 23.04 | 34.89 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 11:00 | 61.7 | 10.22 | 10.22 | 51.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 12:00 | 63.78 | 15.31 | 15.31 | 48.47 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 13:00 | 66.35 | 23.97 | 23.97 | 42.38 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 14:00 | 67.48 | 31.36 | 31.36 | 36.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 15:00 | 67.15 | 20.94 | 20.94 | 46.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 16:00 | 67.33 | 8.59 | 8.59 | 58.74 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 17:00 | 65.38 | 0 | 0 | 65.38 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 18:00 | 63.8 | 0 | 0 | 63.8 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 19:00 | 60.79 | 0 | 0 | 60.79 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 20:00 | 58.34 | 0 | 0 | 58.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 21:00 | 54.4 | 0 | 0 | 54.4 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 22:00 | 52.17 | 0 | 0 | 52.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-20 23:00 | 49.88 | 0 | 0 | 49.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 | 47.51 | 0 | 0 | 47.51 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 01:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 02:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 03:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 04:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 05:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 06:00 | 46.6 | 0 | 0 | 46.6 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 07:00 | 49.99 | 4.98 | 4.98 | 45.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 08:00 | 50.01 | 19.07 | 19.07 | 30.94 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 09:00 | 50.6 | 58.02 | 54 | 0 | 3.4 | 0 | 3.91 | 4.02 | 0
2025-10-21 10:00 | 52.38 | 50.37 | 50.37 | 0 | 0 | 2 | 1.8 | 0 | 0
2025-10-21 11:00 | 52.08 | 73.81 | 55.48 | 0 | 3.4 | 0 | 5.03 | 18.34 | 0
2025-10-21 12:00 | 54.07 | 74.73 | 55.21 | 0 | 1.15 | 0 | 6.12 | 19.52 | 0
2025-10-21 13:00 | 54.6 | 80.35 | 54.6 | 0 | 0 | 0 | 6.12 | 25.74 | 0
2025-10-21 14:00 | 53.84 | 85.91 | 53.84 | 0 | 0 | 0 | 6.12 | 32.07 | 0
2025-10-21 15:00 | 54.09 | 82.72 | 54.09 | 0 | 0 | 0 | 6.12 | 28.63 | 0
2025-10-21 16:00 | 54.76 | 42.29 | 42.29 | 9.08 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-21 17:00 | 53.32 | 0.29 | 0.29 | 51.26 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-21 18:00 | 53.28 | 0 | 0 | 53.28 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 19:00 | 53.35 | 0 | 0 | 53.35 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 20:00 | 52.29 | 0 | 0 | 52.29 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 21:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 22:00 | 49.52 | 0 | 0 | 49.52 | 0 | 0 | 0.68 | 0 | 0
2025-10-21 23:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 | 46.99 | 0 | 0 | 46.99 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 01:00 | 45.93 | 0 | 0 | 45.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 02:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 03:00 | 44.56 | 0 | 0 | 44.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 04:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 05:00 | 45.9 | 0 | 0 | 45.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 06:00 | 46.9 | 0 | 0 | 46.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 07:00 | 48.81 | 20.67 | 20.67 | 28.13 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 08:00 | 51.52 | 77.87 | 54.92 | 0 | 3.4 | 0 | 3.91 | 22.96 | 0
2025-10-22 09:00 | 52.87 | 85.15 | 55.19 | 0 | 2.33 | 0 | 6.12 | 29.96 | 0
2025-10-22 10:00 | 56.11 | 64.39 | 56.11 | 0 | 0 | 0 | 6.12 | 8.29 | 0
2025-10-22 11:00 | 58.19 | 55.36 | 55.36 | 0 | 0 | 2.83 | 3.14 | 0 | 0
2025-10-22 12:00 | 59.57 | 54.45 | 54.45 | 2.78 | 0 | 2.34 | 0.68 | 0 | 0
2025-10-22 13:00 | 60.02 | 68.98 | 63.42 | 0 | 3.4 | 0 | 3.91 | 5.56 | 0
2025-10-22 14:00 | 60.24 | 29.66 | 29.66 | 27.52 | 0 | 3.07 | 0.68 | 0 | 0
2025-10-22 15:00 | 62.15 | 13.13 | 13.13 | 49.02 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 16:00 | 61.39 | 6.26 | 6.26 | 55.13 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 17:00 | 60.14 | 0 | 0 | 60.14 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 18:00 | 59.78 | 0 | 0 | 59.78 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 19:00 | 57.04 | 0 | 0 | 57.04 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 20:00 | 55.22 | 0 | 0 | 55.22 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 21:00 | 53.49 | 0 | 0 | 53.49 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 22:00 | 50.44 | 0 | 0 | 50.44 | 0 | 0 | 0.68 | 0 | 0
2025-10-22 23:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 | 47.48 | 0 | 0 | 47.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 01:00 | 45.62 | 0 | 0 | 45.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 02:00 | 45.25 | 0 | 0 | 45.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 03:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 04:00 | 44.63 | 0 | 0 | 44.63 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 05:00 | 44.35 | 0 | 0 | 44.35 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 06:00 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 07:00 | 49.18 | 3.71 | 3.71 | 45.47 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 08:00 | 50.2 | 19.2 | 19.2 | 31 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 09:00 | 53.17 | 26.12 | 26.12 | 27.05 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 10:00 | 55.88 | 33.24 | 33.24 | 22.64 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 11:00 | 58.68 | 43.89 | 43.89 | 14.79 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 12:00 | 59.59 | 47 | 47 | 12.58 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 13:00 | 61.04 | 29.48 | 29.48 | 31.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 14:00 | 62.28 | 21.67 | 21.67 | 40.61 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 15:00 | 62.8 | 7.56 | 7.56 | 55.24 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 16:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 17:00 | 61.89 | 0 | 0 | 61.89 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 18:00 | 59.48 | 0 | 0 | 59.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 19:00 | 58 | 0 | 0 | 58 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 20:00 | 55.94 | 0 | 0 | 55.94 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 21:00 | 53.14 | 0 | 0 | 53.14 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 22:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 0.68 | 0 | 0
2025-10-23 23:00 | 48.87 | 0 | 0 | 48.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 01:00 | 45.48 | 0 | 0 | 45.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 02:00 | 44.69 | 0 | 0 | 44.69 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 03:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 04:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 05:00 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 06:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 07:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 08:00 | 50.92 | 10.36 | 10.36 | 40.56 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 09:00 | 52.02 | 18.85 | 18.85 | 33.16 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 10:00 | 55.33 | 8.08 | 8.08 | 47.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 11:00 | 58.36 | 4.44 | 4.44 | 53.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 12:00 | 59.79 | 11.03 | 11.03 | 48.77 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 13:00 | 61.44 | 79.97 | 64.84 | 0 | 3.4 | 0 | 3.91 | 15.13 | 0
2025-10-24 14:00 | 60.84 | 59.12 | 59.12 | 0 | 0 | 1.73 | 2.09 | 0 | 0
2025-10-24 15:00 | 62.48 | 32.51 | 32.51 | 28.64 | 0 | 1.34 | 0.68 | 0 | 0
2025-10-24 16:00 | 62.52 | 32.38 | 32.38 | 30.14 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 17:00 | 61.62 | 0 | 0 | 61.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 18:00 | 60.34 | 0 | 0 | 60.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 19:00 | 57.78 | 0 | 0 | 57.78 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 20:00 | 55.53 | 0 | 0 | 55.53 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 21:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 22:00 | 50.73 | 0 | 0 | 50.73 | 0 | 0 | 0.68 | 0 | 0
2025-10-24 23:00 | 48.01 | 0 | 0 | 48.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 | 45.66 | 0 | 0 | 45.66 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 01:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 02:00 | 45.12 | 0 | 0 | 45.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 03:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 04:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 05:00 | 44.97 | 0 | 0 | 44.97 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 06:00 | 45.69 | 0 | 0 | 45.69 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 07:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 08:00 | 49.26 | 7.75 | 7.75 | 41.5 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 09:00 | 52.18 | 41.01 | 41.01 | 11.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 10:00 | 54.51 | 38.7 | 38.7 | 15.81 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 11:00 | 56.55 | 38.68 | 38.68 | 17.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 12:00 | 57.68 | 33.97 | 33.97 | 23.71 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 13:00 | 58.34 | 33.76 | 33.76 | 24.58 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 14:00 | 59.61 | 13.37 | 13.37 | 46.24 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 15:00 | 59.89 | 1.43 | 1.43 | 58.46 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 16:00 | 59.62 | 1.86 | 1.86 | 57.77 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 17:00 | 59.74 | 0 | 0 | 59.74 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 18:00 | 57.43 | 0 | 0 | 57.43 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 19:00 | 56.59 | 0 | 0 | 56.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 20:00 | 54.62 | 0 | 0 | 54.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 21:00 | 52.94 | 0 | 0 | 52.94 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 22:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0.68 | 0 | 0
2025-10-25 23:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 01:00 | 45.28 | 0 | 0 | 45.28 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 02:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 03:00 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 04:00 | 44.42 | 0 | 0 | 44.42 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 05:00 | 45.28 | 0 | 0 | 45.28 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 06:00 | 46.58 | 0 | 0 | 46.58 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 07:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 08:00 | 50.3 | 1.08 | 1.08 | 49.22 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 09:00 | 50.94 | 2.57 | 2.57 | 48.37 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 10:00 | 52.81 | 82.06 | 56.21 | 0 | 3.4 | 0 | 3.91 | 25.85 | 0
2025-10-26 11:00 | 54.06 | 78.47 | 56.39 | 0 | 2.33 | 0 | 6.12 | 22.08 | 0
2025-10-26 12:00 | 55.5 | 76.59 | 55.5 | 0 | 0 | 0 | 6.12 | 21.09 | 0
2025-10-26 13:00 | 55.08 | 83.42 | 55.08 | 0 | 0 | 0 | 6.12 | 28.34 | 0
2025-10-26 14:00 | 55.25 | 91.5 | 55.25 | 0 | 0 | 0 | 6.12 | 36.25 | 0
2025-10-26 15:00 | 54.94 | 92.98 | 54.94 | 0 | 0 | 0 | 6.12 | 38.04 | 0
2025-10-26 16:00 | 56.35 | 42.52 | 42.52 | 10.43 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-26 17:00 | 55.45 | 0 | 0 | 53.68 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-26 18:00 | 54.87 | 0 | 0 | 54.87 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 19:00 | 55.32 | 0 | 0 | 55.32 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 20:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 21:00 | 50.52 | 0 | 0 | 50.52 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 22:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 0.68 | 0 | 0
2025-10-26 23:00 | 47.41 | 0 | 0 | 47.41 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 | 46.12 | 0 | 0 | 46.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 01:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 02:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 03:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 04:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 05:00 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 06:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 07:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 08:00 | 50.48 | 5.14 | 5.14 | 45.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 09:00 | 52.69 | 2.6 | 2.6 | 50.09 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 10:00 | 55.24 | 3.9 | 3.9 | 51.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 11:00 | 57.18 | 4.67 | 4.67 | 52.51 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 12:00 | 59.38 | 4.78 | 4.78 | 54.6 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 13:00 | 60.91 | 68.43 | 64.31 | 0 | 3.4 | 0 | 3.91 | 4.12 | 0
2025-10-27 14:00 | 61.56 | 93.64 | 63.89 | 0 | 2.33 | 0 | 6.12 | 29.76 | 0
2025-10-27 15:00 | 61.69 | 96.07 | 61.69 | 0 | 0 | 0 | 6.12 | 34.38 | 0
2025-10-27 16:00 | 62.24 | 43.22 | 43.22 | 15.62 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-27 17:00 | 60.3 | 0 | 0 | 58.53 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-27 18:00 | 59.24 | 0 | 0 | 59.24 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 19:00 | 57.32 | 0 | 0 | 57.32 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 20:00 | 54.6 | 0 | 0 | 54.6 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 21:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 22:00 | 50.07 | 0 | 0 | 50.07 | 0 | 0 | 0.68 | 0 | 0
2025-10-27 23:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 01:00 | 44.51 | 0 | 0 | 44.51 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 02:00 | 44.1 | 0 | 0 | 44.1 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 03:00 | 44.32 | 0 | 0 | 44.32 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 04:00 | 44.25 | 0 | 0 | 44.25 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 05:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 06:00 | 46.58 | 0 | 0 | 46.58 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 07:00 | 47.93 | 10.22 | 10.22 | 37.71 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 08:00 | 50.85 | 88.4 | 54.25 | 0 | 3.4 | 0 | 3.91 | 34.14 | 0
2025-10-28 09:00 | 53.38 | 92.23 | 55.71 | 0 | 2.33 | 0 | 6.12 | 36.52 | 0
2025-10-28 10:00 | 56.23 | 83.94 | 56.23 | 0 | 0 | 0 | 6.12 | 27.71 | 0
2025-10-28 11:00 | 59.17 | 74.88 | 59.17 | 0 | 0 | 0 | 6.12 | 15.71 | 0
2025-10-28 12:00 | 61.82 | 72.43 | 61.82 | 0 | 0 | 0 | 6.12 | 10.62 | 0
2025-10-28 13:00 | 64.58 | 79.01 | 64.58 | 0 | 0 | 0 | 6.12 | 14.43 | 0
2025-10-28 14:00 | 65.24 | 86.72 | 65.24 | 0 | 0 | 0 | 6.12 | 21.49 | 0
2025-10-28 15:00 | 66.25 | 85.97 | 66.25 | 0 | 0 | 0 | 6.12 | 19.72 | 0
2025-10-28 16:00 | 65.72 | 34.71 | 34.71 | 27.61 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-28 17:00 | 64.24 | 0 | 0 | 62.47 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-28 18:00 | 60.94 | 0 | 0 | 60.94 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 19:00 | 59.78 | 0 | 0 | 59.78 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 20:00 | 56.1 | 0 | 0 | 56.1 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 21:00 | 53.75 | 0 | 0 | 53.75 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 22:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0.68 | 0 | 0
2025-10-28 23:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 | 46.88 | 0 | 0 | 46.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 01:00 | 44.17 | 0 | 0 | 44.17 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 02:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 03:00 | 43.61 | 0 | 0 | 43.61 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 04:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 05:00 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 06:00 | 45.24 | 0 | 0 | 45.24 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 07:00 | 47.41 | 0 | 0 | 47.41 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 08:00 | 48.54 | 2.51 | 2.51 | 46.03 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 09:00 | 50.52 | 5.53 | 5.53 | 44.99 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 10:00 | 52.66 | 8.27 | 8.27 | 44.39 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 11:00 | 53.56 | 8.93 | 8.93 | 44.64 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 12:00 | 53.65 | 10.16 | 10.16 | 43.49 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 13:00 | 55.49 | 9.15 | 9.15 | 46.34 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 14:00 | 55.45 | 6.65 | 6.65 | 48.8 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 15:00 | 55.31 | 3.73 | 3.73 | 51.58 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 16:00 | 55.83 | 0.22 | 0.22 | 55.61 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 17:00 | 54.98 | 0 | 0 | 54.98 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 18:00 | 53.81 | 0 | 0 | 53.81 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 19:00 | 54.36 | 0 | 0 | 54.36 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 20:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 21:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 22:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 0.68 | 0 | 0
2025-10-29 23:00 | 48.01 | 0 | 0 | 48.01 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 | 45.62 | 0 | 0 | 45.62 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 01:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 02:00 | 43.37 | 0 | 0 | 43.37 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 03:00 | 44.09 | 0 | 0 | 44.09 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 04:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 05:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 06:00 | 46.57 | 0 | 0 | 46.57 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 07:00 | 48.07 | 9.33 | 9.33 | 38.74 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 08:00 | 49.73 | 81.6 | 53.13 | 0 | 3.4 | 0 | 3.91 | 28.47 | 0
2025-10-30 09:00 | 52.2 | 87.08 | 54.52 | 0 | 2.33 | 0 | 6.12 | 32.55 | 0
2025-10-30 10:00 | 54.94 | 76.26 | 54.94 | 0 | 0 | 0 | 6.12 | 21.32 | 0
2025-10-30 11:00 | 56.77 | 69.35 | 56.77 | 0 | 0 | 0 | 6.12 | 12.59 | 0
2025-10-30 12:00 | 59.31 | 65.61 | 59.31 | 0 | 0 | 0 | 6.12 | 6.3 | 0
2025-10-30 13:00 | 61.13 | 72.31 | 61.13 | 0 | 0 | 0 | 6.12 | 11.18 | 0
2025-10-30 14:00 | 61.2 | 77.98 | 61.2 | 0 | 0 | 0 | 6.12 | 16.79 | 0
2025-10-30 15:00 | 62.32 | 74.05 | 62.32 | 0 | 0 | 0 | 6.12 | 11.73 | 0
2025-10-30 16:00 | 61.89 | 25.5 | 25.5 | 32.99 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-30 17:00 | 61.49 | 0 | 0 | 59.72 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-30 18:00 | 58.39 | 0 | 0 | 58.39 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 19:00 | 56.99 | 0 | 0 | 56.99 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 20:00 | 54.54 | 0 | 0 | 54.54 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 21:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 22:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 0.68 | 0 | 0
2025-10-30 23:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 01:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 02:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 03:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 04:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 05:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 06:00 | 45.24 | 0 | 0 | 45.24 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 07:00 | 47.53 | 7.4 | 7.4 | 40.12 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 08:00 | 49.8 | 73.86 | 53.2 | 0 | 3.4 | 0 | 3.91 | 20.66 | 0
2025-10-31 09:00 | 50.08 | 83.02 | 52.4 | 0 | 2.33 | 0 | 6.12 | 30.61 | 0
2025-10-31 10:00 | 53.83 | 77.12 | 53.83 | 0 | 0 | 0 | 6.12 | 23.29 | 0
2025-10-31 11:00 | 54.87 | 69.56 | 54.87 | 0 | 0 | 0 | 6.12 | 14.69 | 0
2025-10-31 12:00 | 55.52 | 67.55 | 55.52 | 0 | 0 | 0 | 6.12 | 12.03 | 0
2025-10-31 13:00 | 56.12 | 71.26 | 56.12 | 0 | 0 | 0 | 6.12 | 15.14 | 0
2025-10-31 14:00 | 57.57 | 77.76 | 57.57 | 0 | 0 | 0 | 6.12 | 20.19 | 0
2025-10-31 15:00 | 58.57 | 71.61 | 58.57 | 0 | 0 | 0 | 6.12 | 13.04 | 0
2025-10-31 16:00 | 58.3 | 24.32 | 24.32 | 30.58 | 0 | 3.4 | 2.54 | 0 | 0
2025-10-31 17:00 | 57.93 | 0 | 0 | 56.17 | 0 | 1.77 | 0.68 | 0 | 0
2025-10-31 18:00 | 56.19 | 0 | 0 | 56.19 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 19:00 | 54.39 | 0 | 0 | 54.39 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 20:00 | 52.93 | 0 | 0 | 52.93 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 21:00 | 51.2 | 0 | 0 | 51.2 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 22:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 0.68 | 0 | 0
2025-10-31 23:00 | 46.9 | 0 | 0 | 46.9 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 | 45.97 | 0 | 0 | 45.97 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 01:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 02:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 03:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 04:00 | 43.98 | 0 | 0 | 43.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 05:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 06:00 | 45.17 | 0 | 0 | 45.17 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 07:00 | 47.64 | 8.66 | 8.66 | 38.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 08:00 | 50.17 | 78.96 | 53.57 | 0 | 3.4 | 0 | 3.91 | 25.39 | 0
2025-11-01 09:00 | 51.26 | 84.54 | 53.59 | 0 | 2.33 | 0 | 6.12 | 30.95 | 0
2025-11-01 10:00 | 53.82 | 75.31 | 53.82 | 0 | 0 | 0 | 6.12 | 21.48 | 0
2025-11-01 11:00 | 55.63 | 66.36 | 55.63 | 0 | 0 | 0 | 6.12 | 10.73 | 0
2025-11-01 12:00 | 56.44 | 64.83 | 56.44 | 0 | 0 | 0 | 6.12 | 8.38 | 0
2025-11-01 13:00 | 58.01 | 72.9 | 58.01 | 0 | 0 | 0 | 6.12 | 14.89 | 0
2025-11-01 14:00 | 58.14 | 81.99 | 58.14 | 0 | 0 | 0 | 6.12 | 23.85 | 0
2025-11-01 15:00 | 58.95 | 81.75 | 58.95 | 0 | 0 | 0 | 6.12 | 22.8 | 0
2025-11-01 16:00 | 58.47 | 25.92 | 25.92 | 29.15 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-01 17:00 | 57.8 | 0 | 0 | 56.03 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-01 18:00 | 56.37 | 0 | 0 | 56.37 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 19:00 | 54.97 | 0 | 0 | 54.97 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 20:00 | 53.47 | 0 | 0 | 53.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 21:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 22:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 0.68 | 0 | 0
2025-11-01 23:00 | 46.8 | 0 | 0 | 46.8 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 | 44.54 | 0 | 0 | 44.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 01:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 02:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 03:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 04:00 | 42.92 | 0 | 0 | 42.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 05:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 06:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 07:00 | 46.25 | 13.05 | 13.05 | 33.2 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 08:00 | 48.88 | 92.32 | 52.28 | 0 | 3.4 | 0 | 3.91 | 40.04 | 0
2025-11-02 09:00 | 50.64 | 97.09 | 52.96 | 0 | 2.33 | 0 | 6.12 | 44.13 | 0
2025-11-02 10:00 | 52.32 | 88.73 | 52.32 | 0 | 0 | 0 | 6.12 | 36.42 | 0
2025-11-02 11:00 | 52.95 | 77.86 | 52.95 | 0 | 0 | 0 | 6.12 | 24.91 | 0
2025-11-02 12:00 | 54.99 | 16.46 | 16.46 | 35.13 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-02 13:00 | 54.99 | 42.96 | 42.96 | 10.26 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-02 14:00 | 56.07 | 34.96 | 34.96 | 21.11 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 15:00 | 55.65 | 1.17 | 1.17 | 54.48 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 16:00 | 55.63 | 0 | 0 | 55.63 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 17:00 | 54.02 | 0 | 0 | 54.02 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 18:00 | 54.25 | 0 | 0 | 54.25 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 19:00 | 53.3 | 0 | 0 | 53.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 20:00 | 51.64 | 0 | 0 | 51.64 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 21:00 | 51.1 | 0 | 0 | 51.1 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 22:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-02 23:00 | 46.54 | 0 | 0 | 46.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 | 44.74 | 0 | 0 | 44.74 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 01:00 | 43.68 | 0 | 0 | 43.68 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 02:00 | 43.7 | 0 | 0 | 43.7 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 03:00 | 43.65 | 0 | 0 | 43.65 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 04:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 05:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 06:00 | 44.61 | 0 | 0 | 44.61 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 07:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 08:00 | 49.16 | 0.9 | 0.9 | 48.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 09:00 | 50.47 | 2.13 | 2.13 | 48.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 10:00 | 51.72 | 3.34 | 3.34 | 48.37 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 11:00 | 53.5 | 4.62 | 4.62 | 48.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 12:00 | 55.7 | 5.43 | 5.43 | 50.27 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 13:00 | 57 | 53.1 | 53.1 | 3.9 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 14:00 | 56.39 | 55.58 | 55.58 | 0.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 15:00 | 57.5 | 52.71 | 52.71 | 4.78 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 16:00 | 58.23 | 17.33 | 17.33 | 40.91 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 17:00 | 56.62 | 0 | 0 | 56.62 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 18:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 19:00 | 54.48 | 0 | 0 | 54.48 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 20:00 | 51.87 | 0 | 0 | 51.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 21:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 22:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 0.68 | 0 | 0
2025-11-03 23:00 | 46.3 | 0 | 0 | 46.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 | 44.65 | 0 | 0 | 44.65 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 01:00 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 02:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 03:00 | 43.33 | 0 | 0 | 43.33 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 04:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 05:00 | 43.83 | 0 | 0 | 43.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 06:00 | 45.42 | 0 | 0 | 45.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 07:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 08:00 | 49.32 | 5.42 | 5.42 | 43.89 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 09:00 | 50.42 | 10.87 | 10.87 | 39.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 10:00 | 54.2 | 16.98 | 16.98 | 37.22 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 11:00 | 55.22 | 16.53 | 16.53 | 38.7 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 12:00 | 58.55 | 16.47 | 16.47 | 42.08 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 13:00 | 60.84 | 13.74 | 13.74 | 47.1 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 14:00 | 61.85 | 12.16 | 12.16 | 49.69 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 15:00 | 61.27 | 4.95 | 4.95 | 56.32 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 16:00 | 60.95 | 0.5 | 0.5 | 60.45 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 17:00 | 60.07 | 0 | 0 | 60.07 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 18:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 19:00 | 55.44 | 0 | 0 | 55.44 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 20:00 | 53.98 | 0 | 0 | 53.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 21:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 22:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 0.68 | 0 | 0
2025-11-04 23:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 | 45.05 | 0 | 0 | 45.05 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 01:00 | 43.42 | 0 | 0 | 43.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 02:00 | 41.95 | 0 | 0 | 41.95 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 03:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 04:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 05:00 | 43.4 | 0 | 0 | 43.4 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 06:00 | 45.18 | 0 | 0 | 45.18 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 07:00 | 47.3 | 0 | 0 | 47.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 08:00 | 48.54 | 1.4 | 1.4 | 47.14 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 09:00 | 51 | 3.46 | 3.46 | 47.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 10:00 | 52.22 | 5.29 | 5.29 | 46.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 11:00 | 55.18 | 6.75 | 6.75 | 48.43 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 12:00 | 56.88 | 6.83 | 6.83 | 50.05 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 13:00 | 58.97 | 6.08 | 6.08 | 52.89 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 14:00 | 59 | 4.48 | 4.48 | 54.52 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 15:00 | 59.47 | 2.25 | 2.25 | 57.22 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 16:00 | 59.81 | 0 | 0 | 59.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 17:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 18:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 19:00 | 56.33 | 0 | 0 | 56.33 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 20:00 | 52.4 | 0 | 0 | 52.4 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 21:00 | 50.69 | 0 | 0 | 50.69 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 22:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-05 23:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 | 44.76 | 0 | 0 | 44.76 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 01:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 02:00 | 42.68 | 0 | 0 | 42.68 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 03:00 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 04:00 | 43.87 | 0 | 0 | 43.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 05:00 | 43.46 | 0 | 0 | 43.46 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 06:00 | 45.15 | 0 | 0 | 45.15 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 07:00 | 46.45 | 0.26 | 0.26 | 46.19 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 08:00 | 48.62 | 7.19 | 7.19 | 41.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 09:00 | 51.06 | 11.84 | 11.84 | 39.22 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 10:00 | 53.16 | 13.9 | 13.9 | 39.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 11:00 | 56.46 | 17.53 | 17.53 | 38.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 12:00 | 58.69 | 16.46 | 16.46 | 42.24 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 13:00 | 61.36 | 16.65 | 16.65 | 44.71 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 14:00 | 61.38 | 12.91 | 12.91 | 48.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 15:00 | 62.11 | 9.48 | 9.48 | 52.63 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 16:00 | 61.53 | 3.8 | 3.8 | 57.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 17:00 | 61.49 | 0 | 0 | 61.49 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 18:00 | 58.46 | 0 | 0 | 58.46 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 19:00 | 56.83 | 0 | 0 | 56.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 20:00 | 54.42 | 0 | 0 | 54.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 21:00 | 51.21 | 0 | 0 | 51.21 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 22:00 | 48.1 | 0 | 0 | 48.1 | 0 | 0 | 0.68 | 0 | 0
2025-11-06 23:00 | 45.93 | 0 | 0 | 45.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 01:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 02:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 03:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 04:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 05:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 06:00 | 44.2 | 0 | 0 | 44.2 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 07:00 | 45.86 | 1.77 | 1.77 | 44.09 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 08:00 | 48.74 | 7.53 | 7.53 | 41.21 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 09:00 | 50.37 | 58.58 | 53.77 | 0 | 3.4 | 0 | 3.91 | 4.81 | 0
2025-11-07 10:00 | 51.7 | 57.71 | 54.03 | 0 | 2.33 | 0 | 6.12 | 3.68 | 0
2025-11-07 11:00 | 55.74 | 40.3 | 40.3 | 12.04 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-07 12:00 | 56.97 | 51.62 | 51.62 | 3.58 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-07 13:00 | 59.36 | 58.44 | 58.44 | 0.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 14:00 | 60.87 | 22.09 | 22.09 | 38.78 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 15:00 | 60.55 | 38.12 | 38.12 | 22.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 16:00 | 60.67 | 0 | 0 | 60.67 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 17:00 | 59.2 | 0 | 0 | 59.2 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 18:00 | 58.28 | 0 | 0 | 58.28 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 19:00 | 54.88 | 0 | 0 | 54.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 20:00 | 53.08 | 0 | 0 | 53.08 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 21:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 22:00 | 48.29 | 0 | 0 | 48.29 | 0 | 0 | 0.68 | 0 | 0
2025-11-07 23:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 01:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 02:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 03:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 04:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 05:00 | 43.87 | 0 | 0 | 43.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 06:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 07:00 | 45.39 | 0.27 | 0.27 | 45.12 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 08:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 09:00 | 50.1 | 2.11 | 2.11 | 47.99 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 10:00 | 51.93 | 17.94 | 17.94 | 33.99 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 11:00 | 54.03 | 75.13 | 57.43 | 0 | 3.4 | 0 | 3.91 | 17.7 | 0
2025-11-08 12:00 | 54.56 | 19.7 | 19.7 | 31.79 | 0 | 3.07 | 0.68 | 0 | 0
2025-11-08 13:00 | 56.99 | 20.22 | 20.22 | 36.78 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 14:00 | 57.56 | 79.27 | 60.96 | 0 | 3.4 | 0 | 3.91 | 18.31 | 0
2025-11-08 15:00 | 58.69 | 16.65 | 16.65 | 38.97 | 0 | 3.07 | 0.68 | 0 | 0
2025-11-08 16:00 | 58.44 | 15.89 | 15.89 | 42.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 17:00 | 57.38 | 0 | 0 | 57.38 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 18:00 | 55.95 | 0 | 0 | 55.95 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 19:00 | 53.27 | 0 | 0 | 53.27 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 20:00 | 52.34 | 0 | 0 | 52.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 21:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 22:00 | 48.54 | 0 | 0 | 48.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-08 23:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 01:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 02:00 | 42.04 | 0 | 0 | 42.04 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 03:00 | 42.24 | 0 | 0 | 42.24 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 04:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 05:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 06:00 | 44.91 | 0 | 0 | 44.91 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 07:00 | 45.54 | 4.72 | 4.72 | 40.82 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 08:00 | 47.68 | 77.59 | 51.08 | 0 | 3.4 | 0 | 3.91 | 26.51 | 0
2025-11-09 09:00 | 50.09 | 91.38 | 52.42 | 0 | 2.33 | 0 | 6.12 | 38.96 | 0
2025-11-09 10:00 | 52.98 | 77.83 | 52.98 | 0 | 0 | 0 | 6.12 | 24.85 | 0
2025-11-09 11:00 | 55.07 | 22.06 | 22.06 | 29.61 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-09 12:00 | 57.93 | 5.94 | 5.94 | 50.22 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-09 13:00 | 59.68 | 3.17 | 3.17 | 56.51 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 14:00 | 60.54 | 2.19 | 2.19 | 58.35 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 15:00 | 61.78 | 0.88 | 0.88 | 60.9 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 16:00 | 60.91 | 0 | 0 | 60.91 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 17:00 | 60.3 | 0 | 0 | 60.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 18:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 19:00 | 55.67 | 0 | 0 | 55.67 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 20:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 21:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 22:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-09 23:00 | 45.89 | 0 | 0 | 45.89 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 01:00 | 42.6 | 0 | 0 | 42.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 02:00 | 42.66 | 0 | 0 | 42.66 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 03:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 04:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 05:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 06:00 | 44.93 | 0 | 0 | 44.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 07:00 | 45.13 | 0 | 0 | 45.13 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 08:00 | 46.8 | 0.95 | 0.95 | 45.85 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 09:00 | 49.22 | 2.96 | 2.96 | 46.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 10:00 | 50.87 | 5.26 | 5.26 | 45.61 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 11:00 | 52.8 | 6.29 | 6.29 | 46.51 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 12:00 | 55.48 | 6.61 | 6.61 | 48.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 13:00 | 56.48 | 5.69 | 5.69 | 50.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 14:00 | 57.07 | 3.91 | 3.91 | 53.16 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 15:00 | 57.4 | 1.78 | 1.78 | 55.62 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 16:00 | 57.01 | 0 | 0 | 57.01 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 17:00 | 57.3 | 0 | 0 | 57.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 18:00 | 54.8 | 0 | 0 | 54.8 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 19:00 | 52.83 | 0 | 0 | 52.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 20:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 21:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 22:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-10 23:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 01:00 | 43.42 | 0 | 0 | 43.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 02:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 03:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 04:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 05:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 06:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 07:00 | 45.04 | 0 | 0 | 45.04 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 08:00 | 46.21 | 3.7 | 3.7 | 42.51 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 09:00 | 49.86 | 10.26 | 10.26 | 39.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 10:00 | 51.58 | 3.68 | 3.68 | 47.91 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 11:00 | 53.7 | 13.61 | 13.61 | 40.09 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 12:00 | 54.77 | 22.77 | 22.77 | 32 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 13:00 | 56.5 | 24.66 | 24.66 | 31.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 14:00 | 57.72 | 21.18 | 21.18 | 36.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 15:00 | 57.94 | 10.05 | 10.05 | 47.89 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 16:00 | 58.02 | 0.73 | 0.73 | 57.29 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 17:00 | 57.34 | 0 | 0 | 57.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 18:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 19:00 | 53.78 | 0 | 0 | 53.78 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 20:00 | 52.27 | 0 | 0 | 52.27 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 21:00 | 49.15 | 0 | 0 | 49.15 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 22:00 | 46.64 | 0 | 0 | 46.64 | 0 | 0 | 0.68 | 0 | 0
2025-11-11 23:00 | 45.43 | 0 | 0 | 45.43 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 01:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 02:00 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 03:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 04:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 05:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 06:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 07:00 | 45.71 | 1.16 | 1.16 | 44.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 08:00 | 46.53 | 43.76 | 43.76 | 2.77 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 09:00 | 49.18 | 57.49 | 52.58 | 0 | 3.4 | 0 | 3.91 | 4.91 | 0
2025-11-12 10:00 | 49.98 | 45.12 | 45.12 | 1.78 | 0 | 3.07 | 0.68 | 0 | 0
2025-11-12 11:00 | 51.64 | 49.62 | 49.62 | 2.02 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 12:00 | 53.42 | 49.28 | 49.28 | 4.14 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 13:00 | 54.55 | 53.67 | 53.67 | 0.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 14:00 | 55.27 | 69.08 | 58.67 | 0 | 3.4 | 0 | 3.91 | 10.41 | 0
2025-11-12 15:00 | 55.06 | 77.54 | 57.38 | 0 | 2.33 | 0 | 6.12 | 20.15 | 0
2025-11-12 16:00 | 55.15 | 14.43 | 14.43 | 37.32 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-12 17:00 | 54.63 | 0 | 0 | 52.86 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-12 18:00 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 19:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 20:00 | 49.62 | 0 | 0 | 49.62 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 21:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 22:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-12 23:00 | 45.05 | 0 | 0 | 45.05 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 | 44.34 | 0 | 0 | 44.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 01:00 | 41.88 | 0 | 0 | 41.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 02:00 | 42.72 | 0 | 0 | 42.72 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 03:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 04:00 | 42.06 | 0 | 0 | 42.06 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 05:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 06:00 | 42.87 | 0 | 0 | 42.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 07:00 | 45.08 | 0.68 | 0.68 | 44.4 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 08:00 | 47 | 45.31 | 45.31 | 1.69 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 09:00 | 48.99 | 54.07 | 52.39 | 0 | 3.4 | 0 | 3.91 | 1.68 | 0
2025-11-13 10:00 | 50.37 | 61.67 | 52.7 | 0 | 2.33 | 0 | 6.12 | 8.97 | 0
2025-11-13 11:00 | 51.08 | 55 | 51.08 | 0 | 0 | 0 | 6.12 | 3.92 | 0
2025-11-13 12:00 | 52.87 | 48.74 | 48.74 | 0.73 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-13 13:00 | 55.79 | 47.27 | 47.27 | 6.76 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-13 14:00 | 54.93 | 35.88 | 35.88 | 19.05 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 15:00 | 56.43 | 23.31 | 23.31 | 33.12 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 16:00 | 55.01 | 3.52 | 3.52 | 51.49 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 17:00 | 54.68 | 0 | 0 | 54.68 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 18:00 | 53.95 | 0 | 0 | 53.95 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 19:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 20:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 21:00 | 48.69 | 0 | 0 | 48.69 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 22:00 | 47.07 | 0 | 0 | 47.07 | 0 | 0 | 0.68 | 0 | 0
2025-11-13 23:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 01:00 | 43.24 | 0 | 0 | 43.24 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 02:00 | 41.71 | 0 | 0 | 41.71 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 03:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 04:00 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 05:00 | 42.84 | 0 | 0 | 42.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 06:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 07:00 | 44.33 | 0 | 0 | 44.33 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 08:00 | 46.5 | 1.29 | 1.29 | 45.21 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 09:00 | 47.97 | 6.61 | 6.61 | 41.37 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 10:00 | 49.07 | 25.82 | 25.82 | 23.25 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 11:00 | 51.04 | 28.6 | 28.6 | 22.44 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 12:00 | 52.07 | 43.01 | 43.01 | 9.06 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 13:00 | 52.8 | 42.12 | 42.12 | 10.69 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 14:00 | 53.32 | 11.32 | 11.32 | 42 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 15:00 | 53.49 | 4.89 | 4.89 | 48.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 16:00 | 53.18 | 0.7 | 0.7 | 52.48 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 17:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 18:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 19:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 20:00 | 48.79 | 0 | 0 | 48.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 21:00 | 47.68 | 0 | 0 | 47.68 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 22:00 | 46.14 | 0 | 0 | 46.14 | 0 | 0 | 0.68 | 0 | 0
2025-11-14 23:00 | 45.88 | 0 | 0 | 45.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 01:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 02:00 | 41.78 | 0 | 0 | 41.78 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 03:00 | 41.59 | 0 | 0 | 41.59 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 04:00 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 05:00 | 42.95 | 0 | 0 | 42.95 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 06:00 | 43.23 | 0 | 0 | 43.23 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 07:00 | 45.06 | 0.33 | 0.33 | 44.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 08:00 | 45.84 | 23.22 | 23.22 | 22.62 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 09:00 | 48.84 | 52.96 | 52.24 | 0 | 3.4 | 0 | 3.91 | 0.71 | 0
2025-11-15 10:00 | 50.5 | 62.63 | 52.83 | 0 | 2.33 | 0 | 6.12 | 9.8 | 0
2025-11-15 11:00 | 52.84 | 51.12 | 51.12 | 0 | 0 | 1.72 | 4.31 | 0 | 0
2025-11-15 12:00 | 53.89 | 40.63 | 40.63 | 9.86 | 0 | 3.4 | 0.73 | 0 | 0
2025-11-15 13:00 | 56.36 | 46.06 | 46.06 | 10.25 | 0 | 0.05 | 0.68 | 0 | 0
2025-11-15 14:00 | 56.21 | 66.14 | 59.61 | 0 | 3.4 | 0 | 3.91 | 6.53 | 0
2025-11-15 15:00 | 57.45 | 78.4 | 59.77 | 0 | 2.33 | 0 | 6.12 | 18.62 | 0
2025-11-15 16:00 | 56.45 | 9.74 | 9.74 | 43.31 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-15 17:00 | 55.73 | 0 | 0 | 53.96 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-15 18:00 | 55.31 | 0 | 0 | 55.31 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 19:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 20:00 | 51.48 | 0 | 0 | 51.48 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 21:00 | 49.58 | 0 | 0 | 49.58 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 22:00 | 46.39 | 0 | 0 | 46.39 | 0 | 0 | 0.68 | 0 | 0
2025-11-15 23:00 | 45.71 | 0 | 0 | 45.71 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 | 42.47 | 0 | 0 | 42.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 01:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 02:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 04:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 05:00 | 42.66 | 0 | 0 | 42.66 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 06:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 07:00 | 44.58 | 0 | 0 | 44.58 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 08:00 | 45.93 | 37.26 | 37.26 | 8.67 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 09:00 | 47.54 | 22.44 | 22.44 | 25.1 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 10:00 | 48.74 | 42.77 | 42.77 | 5.97 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 11:00 | 50 | 46.41 | 46.41 | 3.59 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 12:00 | 50.75 | 21.76 | 21.76 | 28.99 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 13:00 | 51.73 | 18.69 | 18.69 | 33.03 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 14:00 | 50.89 | 1.59 | 1.59 | 49.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 15:00 | 51.77 | 2.8 | 2.8 | 48.97 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 16:00 | 51.01 | 0.82 | 0.82 | 50.19 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 17:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 18:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 19:00 | 49.5 | 0 | 0 | 49.5 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 20:00 | 48.66 | 0 | 0 | 48.66 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 21:00 | 47.66 | 0 | 0 | 47.66 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 22:00 | 44.83 | 0 | 0 | 44.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-16 23:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 01:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 02:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 03:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 04:00 | 41.91 | 0 | 0 | 41.91 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 05:00 | 42.26 | 0 | 0 | 42.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 06:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 07:00 | 44.71 | 0 | 0 | 44.71 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 08:00 | 46.61 | 8.43 | 8.43 | 38.18 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 09:00 | 48.09 | 17.22 | 17.22 | 30.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 10:00 | 50.28 | 29.37 | 29.37 | 20.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 11:00 | 51.81 | 40.77 | 40.77 | 11.04 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 12:00 | 54.43 | 18.25 | 18.25 | 36.19 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 13:00 | 55.87 | 62.34 | 59.27 | 0 | 3.4 | 0 | 3.91 | 3.06 | 0
2025-11-17 14:00 | 56.64 | 20.53 | 20.53 | 33.04 | 0 | 3.07 | 0.68 | 0 | 0
2025-11-17 15:00 | 56.03 | 0 | 0 | 56.03 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 16:00 | 55.47 | 0 | 0 | 55.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 17:00 | 55.75 | 0 | 0 | 55.75 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 18:00 | 54.07 | 0 | 0 | 54.07 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 19:00 | 52.29 | 0 | 0 | 52.29 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 20:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 21:00 | 48.46 | 0 | 0 | 48.46 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 22:00 | 45.79 | 0 | 0 | 45.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-17 23:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 | 43.65 | 0 | 0 | 43.65 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 01:00 | 42.75 | 0 | 0 | 42.75 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 02:00 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 03:00 | 40.38 | 0 | 0 | 40.38 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 04:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 05:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 06:00 | 42.53 | 0 | 0 | 42.53 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 07:00 | 44.27 | 0.18 | 0.18 | 44.09 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 08:00 | 46.54 | 53.4 | 49.94 | 0 | 3.4 | 0 | 3.91 | 3.46 | 0
2025-11-18 09:00 | 47.78 | 79.11 | 50.1 | 0 | 2.33 | 0 | 6.12 | 29.01 | 0
2025-11-18 10:00 | 50.33 | 70.82 | 50.33 | 0 | 0 | 0 | 6.12 | 20.5 | 0
2025-11-18 11:00 | 50.22 | 59.18 | 50.22 | 0 | 0 | 0 | 6.12 | 8.96 | 0
2025-11-18 12:00 | 51.36 | 57.37 | 51.36 | 0 | 0 | 0 | 6.12 | 6.01 | 0
2025-11-18 13:00 | 53.44 | 66.25 | 53.44 | 0 | 0 | 0 | 6.12 | 12.81 | 0
2025-11-18 14:00 | 52.84 | 74.62 | 52.84 | 0 | 0 | 0 | 6.12 | 21.78 | 0
2025-11-18 15:00 | 53.55 | 75.34 | 53.55 | 0 | 0 | 0 | 6.12 | 21.79 | 0
2025-11-18 16:00 | 53.4 | 3.74 | 3.74 | 46.26 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-18 17:00 | 53.35 | 0 | 0 | 51.58 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-18 18:00 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 19:00 | 50.81 | 0 | 0 | 50.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 20:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 21:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 22:00 | 47.84 | 0 | 0 | 47.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-18 23:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 01:00 | 41.17 | 0 | 0 | 41.17 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 02:00 | 40.85 | 0 | 0 | 40.85 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 04:00 | 40.9 | 0 | 0 | 40.9 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 05:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 06:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 07:00 | 44.96 | 0 | 0 | 44.96 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 08:00 | 46.01 | 17.02 | 17.02 | 28.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 09:00 | 47.45 | 45.98 | 45.98 | 1.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 10:00 | 50.78 | 47.48 | 47.48 | 3.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 11:00 | 52.09 | 54.21 | 54.21 | 0 | 2.12 | 0 | 2.69 | 0 | 0
2025-11-19 12:00 | 53.03 | 50.53 | 50.53 | 0.59 | 0 | 1.91 | 0.68 | 0 | 0
2025-11-19 13:00 | 55.66 | 53.35 | 53.35 | 2.31 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 14:00 | 56.72 | 40.56 | 40.56 | 16.16 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 15:00 | 55.3 | 6.88 | 6.88 | 48.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 16:00 | 55.79 | 1 | 1 | 54.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 17:00 | 55.25 | 0 | 0 | 55.25 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 18:00 | 54.26 | 0 | 0 | 54.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 19:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 20:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 21:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 22:00 | 45.85 | 0 | 0 | 45.85 | 0 | 0 | 0.68 | 0 | 0
2025-11-19 23:00 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 | 42.17 | 0 | 0 | 42.17 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 01:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 02:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 03:00 | 40.96 | 0 | 0 | 40.96 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 04:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 05:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 06:00 | 42.33 | 0 | 0 | 42.33 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 07:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 08:00 | 45.01 | 26.2 | 26.2 | 18.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 09:00 | 48.23 | 59.6 | 51.63 | 0 | 3.4 | 0 | 3.91 | 7.96 | 0
2025-11-20 10:00 | 50.16 | 69.03 | 52.48 | 0 | 2.33 | 0 | 6.12 | 16.54 | 0
2025-11-20 11:00 | 51.74 | 62.24 | 51.74 | 0 | 0 | 0 | 6.12 | 10.5 | 0
2025-11-20 12:00 | 52.57 | 39.02 | 39.02 | 10.14 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-20 13:00 | 53.75 | 52.56 | 52.56 | 0 | 0 | 1.19 | 1.29 | 0 | 0
2025-11-20 14:00 | 54.86 | 45.86 | 45.86 | 8.42 | 0 | 0.58 | 0.68 | 0 | 0
2025-11-20 15:00 | 54.59 | 48.79 | 48.79 | 5.8 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 16:00 | 54.48 | 6.06 | 6.06 | 48.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 17:00 | 54.49 | 0 | 0 | 54.49 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 18:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 19:00 | 50.79 | 0 | 0 | 50.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 20:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 21:00 | 47.83 | 0 | 0 | 47.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 22:00 | 46.53 | 0 | 0 | 46.53 | 0 | 0 | 0.68 | 0 | 0
2025-11-20 23:00 | 44.4 | 0 | 0 | 44.4 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 01:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 02:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 03:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 04:00 | 40.87 | 0 | 0 | 40.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 05:00 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 06:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 07:00 | 44.33 | 0 | 0 | 44.33 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 08:00 | 46.24 | 17.32 | 17.32 | 28.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 09:00 | 48.2 | 48.77 | 48.77 | 0 | 0.57 | 0 | 1.22 | 0 | 0
2025-11-21 10:00 | 50.14 | 23.17 | 23.17 | 26.46 | 0 | 0.51 | 0.68 | 0 | 0
2025-11-21 11:00 | 52.05 | 38.27 | 38.27 | 13.77 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 12:00 | 54.94 | 42.45 | 42.45 | 12.5 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 13:00 | 56.15 | 63.4 | 59.55 | 0 | 3.4 | 0 | 3.91 | 3.86 | 0
2025-11-21 14:00 | 56.48 | 60.74 | 58.81 | 0 | 2.33 | 0 | 6.12 | 1.94 | 0
2025-11-21 15:00 | 57.24 | 52.79 | 52.79 | 1.05 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-21 16:00 | 56.12 | 3.04 | 3.04 | 51.31 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-21 17:00 | 55.99 | 0 | 0 | 55.99 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 18:00 | 54.29 | 0 | 0 | 54.29 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 19:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 20:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 21:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 22:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 0.68 | 0 | 0
2025-11-21 23:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 | 42.99 | 0 | 0 | 42.99 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 01:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 02:00 | 40.25 | 0 | 0 | 40.25 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 03:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 04:00 | 40.61 | 0 | 0 | 40.61 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 05:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 06:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 07:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 08:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 09:00 | 47.43 | 4.29 | 4.29 | 43.14 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 10:00 | 48.41 | 21.86 | 21.86 | 26.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 11:00 | 50.44 | 49.94 | 49.94 | 0.5 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 12:00 | 52.25 | 49.09 | 49.09 | 3.17 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 13:00 | 53.45 | 33.62 | 33.62 | 19.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 14:00 | 55.24 | 57.32 | 57.32 | 0 | 2.09 | 0 | 2.66 | 0 | 0
2025-11-22 15:00 | 54.7 | 4.39 | 4.39 | 48.42 | 0 | 1.88 | 0.68 | 0 | 0
2025-11-22 16:00 | 53.51 | 1.74 | 1.74 | 51.78 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 17:00 | 53.76 | 0 | 0 | 53.76 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 18:00 | 52.61 | 0 | 0 | 52.61 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 19:00 | 50.72 | 0 | 0 | 50.72 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 20:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 21:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 22:00 | 44.87 | 0 | 0 | 44.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-22 23:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 01:00 | 41.59 | 0 | 0 | 41.59 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 02:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 03:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 04:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 05:00 | 41.85 | 0 | 0 | 41.85 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 06:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 07:00 | 43.41 | 0 | 0 | 43.41 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 08:00 | 43.89 | 37.79 | 37.79 | 6.1 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 09:00 | 45.21 | 67.53 | 48.61 | 0 | 3.4 | 0 | 3.91 | 18.92 | 0
2025-11-23 10:00 | 46.82 | 57.62 | 49.15 | 0 | 2.33 | 0 | 6.12 | 8.47 | 0
2025-11-23 11:00 | 47.88 | 44.27 | 44.27 | 0.21 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-23 12:00 | 47.53 | 47.31 | 47.31 | 0 | 0 | 0.22 | 2.31 | 0 | 0
2025-11-23 13:00 | 49.11 | 61.03 | 52.51 | 0 | 3.4 | 0 | 5.54 | 8.51 | 0
2025-11-23 14:00 | 48.73 | 74.86 | 49.34 | 0 | 0.61 | 0 | 6.12 | 25.51 | 0
2025-11-23 15:00 | 49.87 | 68.79 | 49.87 | 0 | 0 | 0 | 6.12 | 18.91 | 0
2025-11-23 16:00 | 48.97 | 5.72 | 5.72 | 39.85 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-23 17:00 | 48.3 | 0 | 0 | 46.53 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-23 18:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 19:00 | 47.24 | 0 | 0 | 47.24 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 20:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 21:00 | 45.72 | 0 | 0 | 45.72 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 22:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0.68 | 0 | 0
2025-11-23 23:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 01:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 02:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 03:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 04:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 05:00 | 41.6 | 0 | 0 | 41.6 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 06:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 07:00 | 42.75 | 0 | 0 | 42.75 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 08:00 | 44.51 | 3.59 | 3.59 | 40.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 09:00 | 45.91 | 22.64 | 22.64 | 23.27 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 10:00 | 48.78 | 8.72 | 8.72 | 40.06 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 11:00 | 49.77 | 22.27 | 22.27 | 27.5 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 12:00 | 50.33 | 27.16 | 27.16 | 23.17 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 13:00 | 51.77 | 46.92 | 46.92 | 4.85 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 14:00 | 51.39 | 71.88 | 54.79 | 0 | 3.4 | 0 | 3.91 | 17.09 | 0
2025-11-24 15:00 | 51.93 | 65.1 | 54.25 | 0 | 2.33 | 0 | 6.12 | 10.85 | 0
2025-11-24 16:00 | 52.12 | 1.83 | 1.83 | 46.89 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-24 17:00 | 51.7 | 0 | 0 | 49.94 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-24 18:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 19:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 20:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 21:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 22:00 | 44.67 | 0 | 0 | 44.67 | 0 | 0 | 0.68 | 0 | 0
2025-11-24 23:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 | 42.07 | 0 | 0 | 42.07 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 01:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 02:00 | 40.57 | 0 | 0 | 40.57 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 03:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 04:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 05:00 | 41.25 | 0 | 0 | 41.25 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 06:00 | 42.69 | 0 | 0 | 42.69 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 07:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 08:00 | 44.12 | 0.32 | 0.32 | 43.8 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 09:00 | 45.69 | 0.96 | 0.96 | 44.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 10:00 | 46.18 | 1.84 | 1.84 | 44.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 11:00 | 48.42 | 7.85 | 7.85 | 40.57 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 12:00 | 48.67 | 8.52 | 8.52 | 40.15 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 13:00 | 48.83 | 43.67 | 43.67 | 5.15 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 14:00 | 49.43 | 52.03 | 52.03 | 0 | 2.6 | 0 | 3.15 | 0 | 0
2025-11-25 15:00 | 49.37 | 37.53 | 37.53 | 9.5 | 0 | 2.34 | 0.68 | 0 | 0
2025-11-25 16:00 | 50.17 | 1.2 | 1.2 | 48.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 17:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 18:00 | 48.65 | 0 | 0 | 48.65 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 19:00 | 48.05 | 0 | 0 | 48.05 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 20:00 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 21:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 22:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0.68 | 0 | 0
2025-11-25 23:00 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 01:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 02:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 03:00 | 40.18 | 0 | 0 | 40.18 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 04:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 05:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 06:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 07:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 08:00 | 44.68 | 29.67 | 29.67 | 15.02 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 09:00 | 45.98 | 55.08 | 49.38 | 0 | 3.4 | 0 | 3.91 | 5.7 | 0
2025-11-26 10:00 | 47.33 | 61.87 | 49.65 | 0 | 2.33 | 0 | 6.12 | 12.21 | 0
2025-11-26 11:00 | 49.7 | 51.38 | 49.7 | 0 | 0 | 0 | 6.12 | 1.68 | 0
2025-11-26 12:00 | 49.67 | 46.69 | 46.69 | 0 | 0 | 2.97 | 2.99 | 0 | 0
2025-11-26 13:00 | 50.7 | 38.99 | 38.99 | 9.51 | 0 | 2.19 | 0.68 | 0 | 0
2025-11-26 14:00 | 50.46 | 52.3 | 52.3 | 0 | 1.83 | 0 | 2.42 | 0 | 0
2025-11-26 15:00 | 50.28 | 30.58 | 30.58 | 18.04 | 0 | 1.66 | 0.68 | 0 | 0
2025-11-26 16:00 | 50.46 | 1.09 | 1.09 | 49.36 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 17:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 18:00 | 49.56 | 0 | 0 | 49.56 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 19:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 20:00 | 46.99 | 0 | 0 | 46.99 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 21:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 22:00 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 0.68 | 0 | 0
2025-11-26 23:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 | 42.23 | 0 | 0 | 42.23 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 01:00 | 40.34 | 0 | 0 | 40.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 02:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 03:00 | 39.72 | 0 | 0 | 39.72 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 04:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 05:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 06:00 | 42.59 | 0 | 0 | 42.59 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 07:00 | 42.93 | 0 | 0 | 42.93 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 08:00 | 44.85 | 9.88 | 9.88 | 34.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 09:00 | 46.92 | 22.21 | 22.21 | 24.71 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 10:00 | 48.13 | 37.63 | 37.63 | 10.5 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 11:00 | 50.45 | 52.6 | 52.6 | 0 | 2.16 | 0 | 2.73 | 0 | 0
2025-11-27 12:00 | 52.07 | 46.44 | 46.44 | 3.68 | 0 | 1.95 | 0.68 | 0 | 0
2025-11-27 13:00 | 53.31 | 48.34 | 48.34 | 4.97 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 14:00 | 54.22 | 47.5 | 47.5 | 6.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 15:00 | 55.3 | 47.59 | 47.59 | 7.72 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 16:00 | 54.14 | 3.49 | 3.49 | 50.66 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 17:00 | 53.85 | 0 | 0 | 53.85 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 18:00 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 19:00 | 49.79 | 0 | 0 | 49.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 20:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 21:00 | 45.91 | 0 | 0 | 45.91 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 22:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 0.68 | 0 | 0
2025-11-27 23:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 01:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 02:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 03:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 04:00 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 05:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 06:00 | 41.87 | 0 | 0 | 41.87 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 07:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 08:00 | 43.13 | 35.85 | 35.85 | 7.28 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 09:00 | 46.98 | 76.71 | 50.38 | 0 | 3.4 | 0 | 3.91 | 26.33 | 0
2025-11-28 10:00 | 47.9 | 64.69 | 50.23 | 0 | 2.33 | 0 | 6.12 | 14.46 | 0
2025-11-28 11:00 | 49.58 | 49.3 | 49.3 | 0 | 0 | 0.28 | 5.82 | 0 | 0
2025-11-28 12:00 | 50.55 | 48.13 | 48.13 | 0 | 0 | 2.42 | 3.28 | 0 | 0
2025-11-28 13:00 | 50.79 | 54.48 | 53.78 | 0 | 2.99 | 0 | 6.12 | 0.7 | 0
2025-11-28 14:00 | 52.75 | 37.12 | 37.12 | 12.22 | 0 | 3.4 | 2.54 | 0 | 0
2025-11-28 15:00 | 52.37 | 5.43 | 5.43 | 45.17 | 0 | 1.77 | 0.68 | 0 | 0
2025-11-28 16:00 | 52.68 | 0.21 | 0.21 | 52.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 17:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 18:00 | 50.74 | 0 | 0 | 50.74 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 19:00 | 48.84 | 0 | 0 | 48.84 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 20:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 21:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 22:00 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-28 23:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 01:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 02:00 | 39.99 | 0 | 0 | 39.99 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 03:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 04:00 | 39.98 | 0 | 0 | 39.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 05:00 | 39.81 | 0 | 0 | 39.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 06:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 07:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 08:00 | 43.8 | 0.28 | 0.28 | 43.52 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 09:00 | 44.49 | 3 | 3 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 10:00 | 46.06 | 5.74 | 5.74 | 40.32 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 11:00 | 46.56 | 7.02 | 7.02 | 39.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 12:00 | 48.88 | 7.9 | 7.9 | 40.98 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 13:00 | 48.3 | 6.42 | 6.42 | 41.88 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 14:00 | 49.67 | 4.51 | 4.51 | 45.16 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 15:00 | 49.25 | 1.8 | 1.8 | 47.44 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 16:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 17:00 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 18:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 19:00 | 47.9 | 0 | 0 | 47.9 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 20:00 | 45.72 | 0 | 0 | 45.72 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 21:00 | 44.73 | 0 | 0 | 44.73 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 22:00 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 0.68 | 0 | 0
2025-11-29 23:00 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 | 42.21 | 0 | 0 | 42.21 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 01:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 02:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 03:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 04:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 05:00 | 40.9 | 0 | 0 | 40.9 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 06:00 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 07:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 08:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 09:00 | 44.49 | 4.08 | 4.08 | 40.41 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 10:00 | 45.65 | 37.02 | 37.02 | 8.63 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 11:00 | 47.06 | 24.37 | 24.37 | 22.69 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 12:00 | 47.24 | 21.5 | 21.5 | 25.74 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 13:00 | 48.55 | 28.78 | 28.78 | 19.76 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 14:00 | 48.45 | 41.9 | 41.9 | 6.54 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 15:00 | 48.87 | 45.52 | 45.52 | 3.34 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 16:00 | 49.37 | 0.67 | 0.67 | 48.71 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 17:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 18:00 | 48.19 | 0 | 0 | 48.19 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 19:00 | 46.02 | 0 | 0 | 46.02 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 20:00 | 45.68 | 0 | 0 | 45.68 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 21:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 22:00 | 44.53 | 0 | 0 | 44.53 | 0 | 0 | 0.68 | 0 | 0
2025-11-30 23:00 | 41.4 | 0 | 0 | 41.4 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 01:00 | 41.09 | 0 | 0 | 41.09 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 02:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 03:00 | 39.52 | 0 | 0 | 39.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 04:00 | 39.98 | 0 | 0 | 39.98 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 05:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 06:00 | 42.02 | 0 | 0 | 42.02 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 07:00 | 42.59 | 0 | 0 | 42.59 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 08:00 | 44.36 | 27.53 | 27.53 | 16.82 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 09:00 | 44.94 | 69.51 | 48.34 | 0 | 3.4 | 0 | 3.91 | 21.17 | 0
2025-12-01 10:00 | 46.17 | 65.44 | 48.5 | 0 | 2.33 | 0 | 6.12 | 16.94 | 0
2025-12-01 11:00 | 47.76 | 55.53 | 47.76 | 0 | 0 | 0 | 6.12 | 7.77 | 0
2025-12-01 12:00 | 48.44 | 33.58 | 33.58 | 11.45 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-01 13:00 | 50.14 | 25.47 | 25.47 | 22.9 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-01 14:00 | 50.26 | 1.23 | 1.23 | 49.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 15:00 | 50.3 | 0 | 0 | 50.3 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 16:00 | 50.7 | 1.95 | 1.95 | 48.75 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 17:00 | 49.32 | 0 | 0 | 49.32 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 18:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 19:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 20:00 | 47.12 | 0 | 0 | 47.12 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 21:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 22:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 0.68 | 0 | 0
2025-12-01 23:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 01:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 02:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 03:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 04:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 05:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 06:00 | 41.4 | 0 | 0 | 41.4 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 07:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 08:00 | 42.75 | 12.74 | 12.74 | 30 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 09:00 | 44.66 | 69.63 | 48.06 | 0 | 3.4 | 0 | 3.91 | 21.57 | 0
2025-12-02 10:00 | 45.23 | 70 | 47.56 | 0 | 2.33 | 0 | 6.12 | 22.44 | 0
2025-12-02 11:00 | 46.76 | 56.85 | 46.76 | 0 | 0 | 0 | 6.12 | 10.09 | 0
2025-12-02 12:00 | 46.93 | 2.61 | 2.61 | 40.92 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-02 13:00 | 48.05 | 14.35 | 14.35 | 31.94 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-02 14:00 | 48.07 | 23.8 | 23.8 | 24.27 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 15:00 | 48.1 | 2.32 | 2.32 | 45.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 16:00 | 47.67 | 2.22 | 2.22 | 45.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 17:00 | 47.66 | 0 | 0 | 47.66 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 18:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 19:00 | 46.27 | 0 | 0 | 46.27 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 20:00 | 45.65 | 0 | 0 | 45.65 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 21:00 | 44.36 | 0 | 0 | 44.36 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 22:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 0.68 | 0 | 0
2025-12-02 23:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 01:00 | 40.17 | 0 | 0 | 40.17 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 02:00 | 39.71 | 0 | 0 | 39.71 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 04:00 | 39.52 | 0 | 0 | 39.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 05:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 06:00 | 41.38 | 0 | 0 | 41.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 07:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 08:00 | 42.64 | 1.8 | 1.8 | 40.84 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 09:00 | 44.92 | 6.22 | 6.22 | 38.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 10:00 | 45.58 | 10.59 | 10.59 | 34.99 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 11:00 | 46.2 | 11.99 | 11.99 | 34.2 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 12:00 | 48.25 | 14.2 | 14.2 | 34.04 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 13:00 | 48.98 | 10.9 | 10.9 | 38.07 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 14:00 | 48.78 | 5.48 | 5.48 | 43.3 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 15:00 | 49.15 | 2.36 | 2.36 | 46.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 16:00 | 49.04 | 0 | 0 | 49.04 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 17:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 18:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 19:00 | 46.03 | 0 | 0 | 46.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 20:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 21:00 | 44.96 | 0 | 0 | 44.96 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-03 23:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 01:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 02:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 03:00 | 39.7 | 0 | 0 | 39.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 05:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 06:00 | 41.07 | 0 | 0 | 41.07 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 07:00 | 41.72 | 0 | 0 | 41.72 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 08:00 | 43.38 | 15.74 | 15.74 | 27.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 09:00 | 44.06 | 9.59 | 9.59 | 34.47 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 10:00 | 46.05 | 16.52 | 16.52 | 29.53 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 11:00 | 47.9 | 19.85 | 19.85 | 28.05 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 12:00 | 49.03 | 53.12 | 52.43 | 0 | 3.4 | 0 | 3.91 | 0.69 | 0
2025-12-04 13:00 | 49.25 | 64.73 | 51.58 | 0 | 2.33 | 0 | 6.12 | 13.16 | 0
2025-12-04 14:00 | 49.64 | 69.63 | 49.64 | 0 | 0 | 0 | 6.12 | 19.99 | 0
2025-12-04 15:00 | 50.43 | 60.34 | 50.43 | 0 | 0 | 0 | 6.12 | 9.9 | 0
2025-12-04 16:00 | 50.51 | 0.62 | 0.62 | 46.49 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-04 17:00 | 49.85 | 0 | 0 | 48.08 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-04 18:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 19:00 | 47.69 | 0 | 0 | 47.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 20:00 | 46.93 | 0 | 0 | 46.93 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 21:00 | 44.83 | 0 | 0 | 44.83 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 22:00 | 42.49 | 0 | 0 | 42.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-04 23:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 01:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 02:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 03:00 | 39.12 | 0 | 0 | 39.12 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 04:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 05:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 06:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 07:00 | 42 | 0 | 0 | 42 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 08:00 | 44 | 2.43 | 2.43 | 41.57 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 09:00 | 44.89 | 13.4 | 13.4 | 31.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 10:00 | 46.43 | 63.25 | 49.83 | 0 | 3.4 | 0 | 3.91 | 13.42 | 0
2025-12-05 11:00 | 47.88 | 56.42 | 50.21 | 0 | 2.33 | 0 | 6.12 | 6.21 | 0
2025-12-05 12:00 | 48.74 | 31.17 | 31.17 | 14.17 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-05 13:00 | 50.92 | 17 | 17 | 32.15 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-05 14:00 | 52.53 | 27.71 | 27.71 | 24.82 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 15:00 | 51.98 | 0 | 0 | 51.98 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 16:00 | 51.85 | 0 | 0 | 51.85 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 17:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 18:00 | 49.53 | 0 | 0 | 49.53 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 19:00 | 48.71 | 0 | 0 | 48.71 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 20:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 21:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 22:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-05 23:00 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 | 40.76 | 0 | 0 | 40.76 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 01:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 02:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 03:00 | 38.57 | 0 | 0 | 38.57 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 04:00 | 39.33 | 0 | 0 | 39.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 05:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 06:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 07:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 08:00 | 42.92 | 0 | 0 | 42.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 09:00 | 43.94 | 1.56 | 1.56 | 42.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 10:00 | 45.83 | 2.97 | 2.97 | 42.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 11:00 | 47.27 | 6.58 | 6.58 | 40.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 12:00 | 48.37 | 8.09 | 8.09 | 40.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 13:00 | 50.11 | 45.2 | 45.2 | 4.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 14:00 | 49.32 | 48.49 | 48.49 | 0.83 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 15:00 | 49.49 | 36.19 | 36.19 | 13.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 16:00 | 50.27 | 0.51 | 0.51 | 49.76 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 17:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 18:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 19:00 | 47.16 | 0 | 0 | 47.16 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 20:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 21:00 | 44.52 | 0 | 0 | 44.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 22:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-06 23:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 | 40.26 | 0 | 0 | 40.26 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 01:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 02:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 03:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 04:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 05:00 | 40.02 | 0 | 0 | 40.02 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 06:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 07:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 08:00 | 42.3 | 0.81 | 0.81 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 09:00 | 43.09 | 3.57 | 3.57 | 39.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 10:00 | 43.45 | 7.95 | 7.95 | 35.51 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 11:00 | 44.43 | 11.24 | 11.24 | 33.19 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 12:00 | 45.63 | 11.75 | 11.75 | 33.88 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 13:00 | 45.43 | 8.79 | 8.79 | 36.65 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 14:00 | 45.09 | 6.12 | 6.12 | 38.97 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 15:00 | 45.39 | 1.97 | 1.97 | 43.43 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 16:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 17:00 | 44.7 | 0 | 0 | 44.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 18:00 | 45.09 | 0 | 0 | 45.09 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 19:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 20:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 21:00 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 22:00 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 0.68 | 0 | 0
2025-12-07 23:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 | 41.32 | 0 | 0 | 41.32 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 01:00 | 39.72 | 0 | 0 | 39.72 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 02:00 | 39.24 | 0 | 0 | 39.24 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 03:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 04:00 | 39.58 | 0 | 0 | 39.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 05:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 06:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 07:00 | 41.29 | 0 | 0 | 41.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 08:00 | 43.17 | 5.55 | 5.55 | 37.62 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 09:00 | 43.99 | 7.12 | 7.12 | 36.87 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 10:00 | 45.18 | 3.51 | 3.51 | 41.67 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 11:00 | 47.22 | 17.79 | 17.79 | 29.44 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 12:00 | 48.39 | 20.01 | 20.01 | 28.39 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 13:00 | 48.48 | 32.84 | 32.84 | 15.65 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 14:00 | 49.36 | 24.34 | 24.34 | 25.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 15:00 | 48.84 | 4.05 | 4.05 | 44.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 16:00 | 48.81 | 0.04 | 0.04 | 48.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 17:00 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 18:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 19:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 20:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 21:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-08 23:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 01:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 02:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 03:00 | 37.95 | 0 | 0 | 37.95 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 04:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 05:00 | 40.33 | 0 | 0 | 40.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 06:00 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 07:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 08:00 | 42.66 | 12.51 | 12.51 | 30.15 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 09:00 | 43.3 | 33.35 | 33.35 | 9.95 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 10:00 | 44.49 | 8.56 | 8.56 | 35.93 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 11:00 | 46.23 | 14.13 | 14.13 | 32.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 12:00 | 47.94 | 25.88 | 25.88 | 22.07 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 13:00 | 48.43 | 35.95 | 35.95 | 12.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 14:00 | 48.27 | 66.16 | 51.67 | 0 | 3.4 | 0 | 3.91 | 14.49 | 0
2025-12-09 15:00 | 49.16 | 60.31 | 51.48 | 0 | 2.33 | 0 | 6.12 | 8.83 | 0
2025-12-09 16:00 | 47.51 | 1.87 | 1.87 | 42.24 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-09 17:00 | 47.75 | 0 | 0 | 45.98 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-09 18:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 19:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 20:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 21:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 22:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 0.68 | 0 | 0
2025-12-09 23:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 | 40.47 | 0 | 0 | 40.47 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 01:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 02:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 03:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 04:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 06:00 | 40.17 | 0 | 0 | 40.17 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 07:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 08:00 | 41.9 | 15.38 | 15.38 | 26.53 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 09:00 | 44.69 | 36.51 | 36.51 | 8.19 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 10:00 | 44.48 | 33.48 | 33.48 | 11 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 11:00 | 46.26 | 9.01 | 9.01 | 37.26 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 12:00 | 47.09 | 40.82 | 40.82 | 6.27 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 13:00 | 49.53 | 18.92 | 18.92 | 30.61 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 14:00 | 48.74 | 39.35 | 39.35 | 9.39 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 15:00 | 48.93 | 46.36 | 46.36 | 2.57 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 16:00 | 48.8 | 1.51 | 1.51 | 47.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 17:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 18:00 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 19:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 20:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 21:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 22:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0.68 | 0 | 0
2025-12-10 23:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 01:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 02:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 03:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 05:00 | 39.04 | 0 | 0 | 39.04 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 06:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 07:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 08:00 | 43.3 | 9.29 | 9.29 | 34.01 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 09:00 | 44.24 | 53.27 | 47.64 | 0 | 3.4 | 0 | 3.91 | 5.63 | 0
2025-12-11 10:00 | 46.54 | 37.5 | 37.5 | 5.98 | 0 | 3.07 | 0.68 | 0 | 0
2025-12-11 11:00 | 47.04 | 53.11 | 50.44 | 0 | 3.4 | 0 | 3.91 | 2.68 | 0
2025-12-11 12:00 | 49.39 | 32.9 | 32.9 | 13.42 | 0 | 3.07 | 0.68 | 0 | 0
2025-12-11 13:00 | 49.69 | 36.55 | 36.55 | 13.15 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 14:00 | 50.88 | 25.76 | 25.76 | 25.12 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 15:00 | 51.13 | 3.38 | 3.38 | 47.75 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 16:00 | 51.09 | 0.25 | 0.25 | 50.84 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 17:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 18:00 | 48.49 | 0 | 0 | 48.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 19:00 | 47.85 | 0 | 0 | 47.85 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 20:00 | 46.66 | 0 | 0 | 46.66 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 21:00 | 43.86 | 0 | 0 | 43.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 22:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-11 23:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 01:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 02:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 03:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 04:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 06:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 07:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 08:00 | 40.98 | 11.2 | 11.2 | 29.78 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 09:00 | 41.83 | 73.88 | 45.23 | 0 | 3.4 | 0 | 3.91 | 28.65 | 0
2025-12-12 10:00 | 43.21 | 67.45 | 45.53 | 0 | 2.33 | 0 | 6.12 | 21.91 | 0
2025-12-12 11:00 | 43.13 | 54.94 | 43.13 | 0 | 0 | 0 | 6.12 | 11.82 | 0
2025-12-12 12:00 | 43.31 | 50.5 | 43.31 | 0 | 0 | 0 | 6.12 | 7.19 | 0
2025-12-12 13:00 | 44.66 | 58.41 | 44.66 | 0 | 0 | 0 | 6.12 | 13.75 | 0
2025-12-12 14:00 | 44.82 | 68.25 | 44.82 | 0 | 0 | 0 | 6.12 | 23.43 | 0
2025-12-12 15:00 | 44.33 | 56.24 | 44.33 | 0 | 0 | 0 | 6.12 | 11.9 | 0
2025-12-12 16:00 | 44.62 | 0.66 | 0.66 | 40.56 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-12 17:00 | 44.44 | 0 | 0 | 42.67 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-12 18:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 19:00 | 44 | 0 | 0 | 44 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 20:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 21:00 | 42.31 | 0 | 0 | 42.31 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 22:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-12 23:00 | 40.52 | 0 | 0 | 40.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 | 39.86 | 0 | 0 | 39.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 01:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 02:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 03:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 05:00 | 39.06 | 0 | 0 | 39.06 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 06:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 07:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 08:00 | 41.65 | 8.13 | 8.13 | 33.53 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 09:00 | 42.23 | 52.39 | 45.63 | 0 | 3.4 | 0 | 3.91 | 6.76 | 0
2025-12-13 10:00 | 44.08 | 56.58 | 46.41 | 0 | 2.33 | 0 | 6.12 | 10.17 | 0
2025-12-13 11:00 | 45.01 | 48.76 | 45.01 | 0 | 0 | 0 | 6.12 | 3.76 | 0
2025-12-13 12:00 | 46.08 | 44.83 | 44.83 | 0 | 0 | 1.24 | 4.81 | 0 | 0
2025-12-13 13:00 | 47.03 | 45.63 | 45.63 | 0 | 0 | 1.4 | 3.34 | 0 | 0
2025-12-13 14:00 | 46.69 | 45.2 | 45.2 | 0 | 0 | 1.48 | 1.78 | 0 | 0
2025-12-13 15:00 | 47.96 | 36.52 | 36.52 | 10.4 | 0 | 1.04 | 0.68 | 0 | 0
2025-12-13 16:00 | 46.82 | 0.59 | 0.59 | 46.22 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 17:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 18:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 19:00 | 44.74 | 0 | 0 | 44.74 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 20:00 | 44.27 | 0 | 0 | 44.27 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 21:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 22:00 | 41.67 | 0 | 0 | 41.67 | 0 | 0 | 0.68 | 0 | 0
2025-12-13 23:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 | 39.56 | 0 | 0 | 39.56 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 01:00 | 39.44 | 0 | 0 | 39.44 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 02:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 03:00 | 39 | 0 | 0 | 39 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 04:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 05:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 06:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 07:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 08:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 09:00 | 43.26 | 0 | 0 | 43.26 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 10:00 | 45.19 | 2.57 | 2.57 | 42.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 11:00 | 45.56 | 10.81 | 10.81 | 34.76 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 12:00 | 46.74 | 7.61 | 7.61 | 39.13 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 13:00 | 47.74 | 45.81 | 45.81 | 1.93 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 14:00 | 48.69 | 54.42 | 52.09 | 0 | 3.4 | 0 | 3.91 | 2.34 | 0
2025-12-14 15:00 | 48.35 | 37.93 | 37.93 | 7.35 | 0 | 3.07 | 0.68 | 0 | 0
2025-12-14 16:00 | 48.13 | 0.49 | 0.49 | 47.64 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 17:00 | 47.17 | 0 | 0 | 47.17 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 18:00 | 46.69 | 0 | 0 | 46.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 19:00 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 20:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 21:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 22:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-14 23:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 | 40.32 | 0 | 0 | 40.32 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 01:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 02:00 | 38.52 | 0 | 0 | 38.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 03:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 04:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 05:00 | 39.13 | 0 | 0 | 39.13 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 06:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 07:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 08:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 09:00 | 42.88 | 0.95 | 0.95 | 41.93 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 10:00 | 42.69 | 1.73 | 1.73 | 40.97 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 11:00 | 43.85 | 2.88 | 2.88 | 40.97 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 12:00 | 43.61 | 6.16 | 6.16 | 37.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 13:00 | 44.89 | 42.42 | 42.42 | 2.47 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 14:00 | 44.75 | 47.84 | 47.84 | 0 | 3.09 | 0 | 3.62 | 0 | 0
2025-12-15 15:00 | 44.97 | 40.21 | 40.21 | 1.96 | 0 | 2.79 | 0.68 | 0 | 0
2025-12-15 16:00 | 44.69 | 0.59 | 0.59 | 44.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 17:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 18:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 19:00 | 44.08 | 0 | 0 | 44.08 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 20:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 21:00 | 41.95 | 0 | 0 | 41.95 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 22:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 0.68 | 0 | 0
2025-12-15 23:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 01:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 03:00 | 37.86 | 0 | 0 | 37.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 04:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 05:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 06:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 07:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 08:00 | 40.81 | 0.55 | 0.55 | 40.25 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 09:00 | 42.42 | 4.72 | 4.72 | 37.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 10:00 | 44.84 | 11.31 | 11.31 | 33.53 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 11:00 | 47.3 | 12.25 | 12.25 | 35.05 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 12:00 | 47.29 | 14.59 | 14.59 | 32.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 13:00 | 49.12 | 15.33 | 15.33 | 33.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 14:00 | 49.12 | 6.08 | 6.08 | 43.04 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 15:00 | 49.62 | 2.94 | 2.94 | 46.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 16:00 | 49.97 | 0 | 0 | 49.97 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 17:00 | 48.51 | 0 | 0 | 48.51 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 18:00 | 47.29 | 0 | 0 | 47.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 19:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 20:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 21:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 22:00 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 0.68 | 0 | 0
2025-12-16 23:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 01:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 02:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 03:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 04:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 05:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 06:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 07:00 | 40.32 | 0 | 0 | 40.32 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 08:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 09:00 | 41.91 | 35.16 | 35.16 | 6.74 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 10:00 | 43.11 | 1.7 | 1.7 | 41.42 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 11:00 | 45.45 | 56.46 | 48.85 | 0 | 3.4 | 0 | 3.91 | 7.61 | 0
2025-12-17 12:00 | 45.58 | 53.24 | 47.9 | 0 | 2.33 | 0 | 6.12 | 5.34 | 0
2025-12-17 13:00 | 47.09 | 61.55 | 47.09 | 0 | 0 | 0 | 6.12 | 14.46 | 0
2025-12-17 14:00 | 47.51 | 71.57 | 47.51 | 0 | 0 | 0 | 6.12 | 24.07 | 0
2025-12-17 15:00 | 47.58 | 61.09 | 47.58 | 0 | 0 | 0 | 6.12 | 13.51 | 0
2025-12-17 16:00 | 47.66 | 1.39 | 1.39 | 42.87 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-17 17:00 | 47.02 | 0 | 0 | 45.25 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-17 18:00 | 44.8 | 0 | 0 | 44.8 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 19:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 20:00 | 44.19 | 0 | 0 | 44.19 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 21:00 | 43.57 | 0 | 0 | 43.57 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 22:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-17 23:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 01:00 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 02:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 03:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 04:00 | 38.42 | 0 | 0 | 38.42 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 05:00 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 06:00 | 40.1 | 0 | 0 | 40.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 07:00 | 40.97 | 0 | 0 | 40.97 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 08:00 | 42.1 | 7.54 | 7.54 | 34.55 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 09:00 | 43.03 | 71.08 | 46.43 | 0 | 3.4 | 0 | 3.91 | 24.65 | 0
2025-12-18 10:00 | 43.95 | 65.23 | 46.28 | 0 | 2.33 | 0 | 6.12 | 18.96 | 0
2025-12-18 11:00 | 45.78 | 52.28 | 45.78 | 0 | 0 | 0 | 6.12 | 6.49 | 0
2025-12-18 12:00 | 46.93 | 47.87 | 46.93 | 0 | 0 | 0 | 6.12 | 0.93 | 0
2025-12-18 13:00 | 47.31 | 55.93 | 47.31 | 0 | 0 | 0 | 6.12 | 8.62 | 0
2025-12-18 14:00 | 47.8 | 65.34 | 47.8 | 0 | 0 | 0 | 6.12 | 17.55 | 0
2025-12-18 15:00 | 48.73 | 54.97 | 48.73 | 0 | 0 | 0 | 6.12 | 6.24 | 0
2025-12-18 16:00 | 48.8 | 0.81 | 0.81 | 44.59 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-18 17:00 | 47.03 | 0 | 0 | 45.27 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-18 18:00 | 46.39 | 0 | 0 | 46.39 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 19:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 20:00 | 44.37 | 0 | 0 | 44.37 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 21:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 22:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 0.68 | 0 | 0
2025-12-18 23:00 | 40.58 | 0 | 0 | 40.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 | 39.53 | 0 | 0 | 39.53 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 01:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 02:00 | 37.95 | 0 | 0 | 37.95 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 03:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 04:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 05:00 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 06:00 | 38.52 | 0 | 0 | 38.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 07:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 08:00 | 41.31 | 7.38 | 7.38 | 33.93 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 09:00 | 41.98 | 55.49 | 45.38 | 0 | 3.4 | 0 | 3.91 | 10.11 | 0
2025-12-19 10:00 | 43.05 | 37.82 | 37.82 | 2.16 | 0 | 3.07 | 0.68 | 0 | 0
2025-12-19 11:00 | 44.38 | 48.92 | 47.78 | 0 | 3.4 | 0 | 3.91 | 1.14 | 0
2025-12-19 12:00 | 44.17 | 15.04 | 15.04 | 26.06 | 0 | 3.07 | 0.68 | 0 | 0
2025-12-19 13:00 | 45.4 | 19.94 | 19.94 | 25.46 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 14:00 | 46 | 10.28 | 10.28 | 35.71 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 15:00 | 44.87 | 2.72 | 2.72 | 42.15 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 16:00 | 45.99 | 0.47 | 0.47 | 45.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 17:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 18:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 19:00 | 43.41 | 0 | 0 | 43.41 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 20:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 21:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 22:00 | 40.27 | 0 | 0 | 40.27 | 0 | 0 | 0.68 | 0 | 0
2025-12-19 23:00 | 40.19 | 0 | 0 | 40.19 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 01:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 02:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 03:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 04:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 05:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 06:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 07:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 08:00 | 41.83 | 6.94 | 6.94 | 34.89 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 09:00 | 42.45 | 57.74 | 45.85 | 0 | 3.4 | 0 | 3.91 | 11.89 | 0
2025-12-20 10:00 | 42.6 | 57.04 | 44.92 | 0 | 2.33 | 0 | 6.12 | 12.12 | 0
2025-12-20 11:00 | 45.24 | 50.14 | 45.24 | 0 | 0 | 0 | 6.12 | 4.9 | 0
2025-12-20 12:00 | 46.87 | 41.76 | 41.76 | 1.71 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-20 13:00 | 47.6 | 50.76 | 50.76 | 0 | 3.16 | 0 | 5.54 | 0 | 0
2025-12-20 14:00 | 47.76 | 61.07 | 48.38 | 0 | 0.61 | 0 | 6.12 | 12.7 | 0
2025-12-20 15:00 | 47.13 | 44.41 | 44.41 | 0 | 0 | 2.72 | 3.26 | 0 | 0
2025-12-20 16:00 | 47.27 | 0.82 | 0.82 | 44 | 0 | 2.45 | 0.68 | 0 | 0
2025-12-20 17:00 | 47.96 | 0 | 0 | 47.96 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 18:00 | 45.43 | 0 | 0 | 45.43 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 19:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 20:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 21:00 | 42.31 | 0 | 0 | 42.31 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 22:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-20 23:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 01:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 02:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 03:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 04:00 | 38.01 | 0 | 0 | 38.01 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 06:00 | 39.59 | 0 | 0 | 39.59 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 07:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 08:00 | 40.96 | 6.32 | 6.32 | 34.64 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 09:00 | 43.22 | 51.06 | 46.62 | 0 | 3.4 | 0 | 3.91 | 4.44 | 0
2025-12-21 10:00 | 44.55 | 57.26 | 46.88 | 0 | 2.33 | 0 | 6.12 | 10.38 | 0
2025-12-21 11:00 | 44.17 | 51.15 | 44.17 | 0 | 0 | 0 | 6.12 | 6.99 | 0
2025-12-21 12:00 | 46.52 | 45.12 | 45.12 | 0 | 0 | 1.4 | 4.65 | 0 | 0
2025-12-21 13:00 | 47.08 | 46.26 | 46.26 | 0 | 0 | 0.82 | 3.79 | 0 | 0
2025-12-21 14:00 | 47.2 | 54.44 | 49.66 | 0 | 2.45 | 0 | 6.12 | 4.78 | 0
2025-12-21 15:00 | 48.05 | 43.47 | 43.47 | 1.17 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-21 16:00 | 47.04 | 0.9 | 0.9 | 44.38 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-21 17:00 | 46.91 | 0 | 0 | 46.91 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 18:00 | 45.85 | 0 | 0 | 45.85 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 19:00 | 44.85 | 0 | 0 | 44.85 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 20:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 21:00 | 41.99 | 0 | 0 | 41.99 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 22:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 0.68 | 0 | 0
2025-12-21 23:00 | 40.33 | 0 | 0 | 40.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 | 39.93 | 0 | 0 | 39.93 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 01:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 02:00 | 37.68 | 0 | 0 | 37.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 03:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 04:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 06:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 08:00 | 41.3 | 6.67 | 6.67 | 34.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 09:00 | 42.35 | 68.52 | 45.75 | 0 | 3.4 | 0 | 3.91 | 22.77 | 0
2025-12-22 10:00 | 43.82 | 64.47 | 46.14 | 0 | 2.33 | 0 | 6.12 | 18.33 | 0
2025-12-22 11:00 | 44.69 | 52.58 | 44.69 | 0 | 0 | 0 | 6.12 | 7.88 | 0
2025-12-22 12:00 | 45.81 | 30.65 | 30.65 | 11.77 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-22 13:00 | 45.82 | 38.27 | 38.27 | 5.78 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-22 14:00 | 45.89 | 62.67 | 49.29 | 0 | 3.4 | 0 | 3.91 | 13.38 | 0
2025-12-22 15:00 | 47.53 | 59.37 | 49.86 | 0 | 2.33 | 0 | 6.12 | 9.51 | 0
2025-12-22 16:00 | 45.56 | 2.11 | 2.11 | 40.05 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-22 17:00 | 45.16 | 0 | 0 | 43.39 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-22 18:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 19:00 | 45.06 | 0 | 0 | 45.06 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 20:00 | 43.28 | 0 | 0 | 43.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 21:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 22:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-22 23:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 01:00 | 38.68 | 0 | 0 | 38.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 03:00 | 37.1 | 0 | 0 | 37.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 04:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 05:00 | 38.83 | 0 | 0 | 38.83 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 06:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 07:00 | 40.1 | 0 | 0 | 40.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 08:00 | 41.11 | 0 | 0 | 41.11 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 09:00 | 41.83 | 30.36 | 30.36 | 11.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 10:00 | 42.51 | 1.39 | 1.39 | 41.11 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 11:00 | 44.39 | 39.99 | 39.99 | 4.39 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 12:00 | 45.32 | 45.52 | 45.52 | 0 | 0.21 | 0 | 0.88 | 0 | 0
2025-12-23 13:00 | 46.16 | 52.62 | 49.56 | 0 | 3.4 | 0 | 4.11 | 3.06 | 0
2025-12-23 14:00 | 46.31 | 60.86 | 48.43 | 0 | 2.12 | 0 | 6.12 | 12.43 | 0
2025-12-23 15:00 | 45.73 | 52.09 | 45.73 | 0 | 0 | 0 | 6.12 | 6.37 | 0
2025-12-23 16:00 | 46.5 | 2.39 | 2.39 | 40.71 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-23 17:00 | 45.71 | 0 | 0 | 43.95 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-23 18:00 | 44.77 | 0 | 0 | 44.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 19:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 20:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 21:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 22:00 | 40.13 | 0 | 0 | 40.13 | 0 | 0 | 0.68 | 0 | 0
2025-12-23 23:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 | 38.71 | 0 | 0 | 38.71 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 01:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 02:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 04:00 | 38.49 | 0 | 0 | 38.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 05:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 06:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 07:00 | 38.47 | 0 | 0 | 38.47 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 08:00 | 40.71 | 0 | 0 | 40.71 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 09:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 10:00 | 43.74 | 1.5 | 1.5 | 42.24 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 11:00 | 43.56 | 2.49 | 2.49 | 41.07 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 12:00 | 45.78 | 2.61 | 2.61 | 43.17 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 13:00 | 44.49 | 33.87 | 33.87 | 10.62 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 14:00 | 45.86 | 35.06 | 35.06 | 10.81 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 15:00 | 45.99 | 27.93 | 27.93 | 18.06 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 16:00 | 46.62 | 0.77 | 0.77 | 45.85 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 17:00 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 18:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 19:00 | 43.32 | 0 | 0 | 43.32 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 20:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 21:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 22:00 | 39.91 | 0 | 0 | 39.91 | 0 | 0 | 0.68 | 0 | 0
2025-12-24 23:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 | 39.28 | 0 | 0 | 39.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 01:00 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 03:00 | 37.51 | 0 | 0 | 37.51 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 04:00 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 05:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 07:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 08:00 | 40.92 | 5.51 | 5.51 | 35.41 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 09:00 | 41.15 | 30.96 | 30.96 | 10.19 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 10:00 | 42.03 | 23.64 | 23.64 | 18.39 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 11:00 | 43.12 | 26.11 | 26.11 | 17 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 12:00 | 43 | 30.88 | 30.88 | 12.11 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 13:00 | 44.18 | 49.53 | 47.58 | 0 | 3.4 | 0 | 3.91 | 1.94 | 0
2025-12-25 14:00 | 43.64 | 56.96 | 45.96 | 0 | 2.33 | 0 | 6.12 | 10.99 | 0
2025-12-25 15:00 | 44.36 | 47.82 | 44.36 | 0 | 0 | 0 | 6.12 | 3.46 | 0
2025-12-25 16:00 | 43.72 | 2.47 | 2.47 | 37.85 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-25 17:00 | 43.46 | 0 | 0 | 41.69 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-25 18:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 19:00 | 42.97 | 0 | 0 | 42.97 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 20:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 21:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 22:00 | 40.12 | 0 | 0 | 40.12 | 0 | 0 | 0.68 | 0 | 0
2025-12-25 23:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 01:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 02:00 | 37.79 | 0 | 0 | 37.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 03:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 04:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 05:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 06:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 07:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 08:00 | 39.92 | 4.49 | 4.49 | 35.43 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 09:00 | 41.84 | 50.98 | 45.24 | 0 | 3.4 | 0 | 3.91 | 5.74 | 0
2025-12-26 10:00 | 41.11 | 57.88 | 43.44 | 0 | 2.33 | 0 | 6.12 | 14.44 | 0
2025-12-26 11:00 | 43.17 | 48.67 | 43.17 | 0 | 0 | 0 | 6.12 | 5.5 | 0
2025-12-26 12:00 | 44.89 | 36.25 | 36.25 | 5.24 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-26 13:00 | 44.78 | 28.2 | 28.2 | 14.82 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-26 14:00 | 45.6 | 15.06 | 15.06 | 30.55 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 15:00 | 44.46 | 6.19 | 6.19 | 38.27 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 16:00 | 44.36 | 0.84 | 0.84 | 43.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 17:00 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 18:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 19:00 | 43.44 | 0 | 0 | 43.44 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 20:00 | 41.91 | 0 | 0 | 41.91 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 21:00 | 41.52 | 0 | 0 | 41.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 22:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 0.68 | 0 | 0
2025-12-26 23:00 | 40.12 | 0 | 0 | 40.12 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 | 40 | 0 | 0 | 40 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 01:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 02:00 | 37.31 | 0 | 0 | 37.31 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 03:00 | 36.22 | 0 | 0 | 36.22 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 04:00 | 36.78 | 0 | 0 | 36.78 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 05:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 06:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 07:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 08:00 | 40.7 | 0 | 0 | 40.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 09:00 | 42.11 | 1.65 | 1.65 | 40.46 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 10:00 | 42.25 | 4.31 | 4.31 | 37.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 11:00 | 43.06 | 6 | 6 | 37.06 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 12:00 | 44.08 | 6.12 | 6.12 | 37.96 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 13:00 | 44.32 | 5.68 | 5.68 | 38.64 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 14:00 | 44.72 | 4.63 | 4.63 | 40.09 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 15:00 | 45.34 | 2.01 | 2.01 | 43.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 16:00 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 17:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 18:00 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 19:00 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 20:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 21:00 | 41.63 | 0 | 0 | 41.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 22:00 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 0.68 | 0 | 0
2025-12-27 23:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 01:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 02:00 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 03:00 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 04:00 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 05:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 06:00 | 39.47 | 0 | 0 | 39.47 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 07:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 08:00 | 41.07 | 1.27 | 1.27 | 39.8 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 09:00 | 40.96 | 7.21 | 7.21 | 33.75 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 10:00 | 42.26 | 24.56 | 24.56 | 17.7 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 11:00 | 43.85 | 35.14 | 35.14 | 8.71 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 12:00 | 45.08 | 24.58 | 24.58 | 20.5 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 13:00 | 44.58 | 23.44 | 23.44 | 21.14 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 14:00 | 45.34 | 13.97 | 13.97 | 31.37 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 15:00 | 45.79 | 0 | 0 | 45.79 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 16:00 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 17:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 18:00 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 19:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 20:00 | 42.17 | 0 | 0 | 42.17 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 21:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 0.68 | 0 | 0
2025-12-28 23:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 01:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 02:00 | 37.28 | 0 | 0 | 37.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 03:00 | 38.37 | 0 | 0 | 38.37 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 04:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 05:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 06:00 | 38.85 | 0 | 0 | 38.85 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 07:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 08:00 | 41.06 | 1.44 | 1.44 | 39.62 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 09:00 | 41.78 | 42.2 | 42.2 | 0 | 0.42 | 0 | 1.08 | 0 | 0
2025-12-29 10:00 | 43.29 | 52.54 | 46.69 | 0 | 3.4 | 0 | 4.31 | 5.85 | 0
2025-12-29 11:00 | 43.59 | 30.65 | 30.65 | 9.54 | 0 | 3.4 | 0.73 | 0 | 0
2025-12-29 12:00 | 45.41 | 26.19 | 26.19 | 19.18 | 0 | 0.05 | 0.68 | 0 | 0
2025-12-29 13:00 | 46.21 | 21.87 | 21.87 | 24.34 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 14:00 | 47.04 | 7.55 | 7.55 | 39.49 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 15:00 | 45.62 | 1.11 | 1.11 | 44.51 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 16:00 | 45.82 | 0.49 | 0.49 | 45.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 17:00 | 46.17 | 0 | 0 | 46.17 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 18:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 19:00 | 44.17 | 0 | 0 | 44.17 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 20:00 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 21:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 22:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 0.68 | 0 | 0
2025-12-29 23:00 | 38.85 | 0 | 0 | 38.85 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 01:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 03:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 04:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 05:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 06:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 07:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 08:00 | 40.12 | 0.6 | 0.6 | 39.52 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 09:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 10:00 | 41.25 | 14.1 | 14.1 | 27.15 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 11:00 | 41.37 | 25.69 | 25.69 | 15.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 12:00 | 41.98 | 28.94 | 28.94 | 13.04 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 13:00 | 42.56 | 25.88 | 25.88 | 16.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 14:00 | 43.5 | 41.17 | 41.17 | 2.33 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 15:00 | 44.03 | 44.8 | 44.8 | 0 | 0.78 | 0 | 1.42 | 0 | 0
2025-12-30 16:00 | 42.52 | 4.24 | 4.24 | 37.57 | 0 | 0.7 | 0.68 | 0 | 0
2025-12-30 17:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 18:00 | 42.08 | 0 | 0 | 42.08 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 19:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 20:00 | 42.08 | 0 | 0 | 42.08 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 21:00 | 40.55 | 0 | 0 | 40.55 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 22:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 0.68 | 0 | 0
2025-12-30 23:00 | 39.86 | 0 | 0 | 39.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 01:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 02:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 04:00 | 37.61 | 0 | 0 | 37.61 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 05:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 06:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 07:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 08:00 | 39.98 | 3.92 | 3.92 | 36.06 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 09:00 | 41.27 | 39.39 | 39.39 | 1.88 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 10:00 | 42.37 | 44.25 | 44.25 | 0 | 1.88 | 0 | 2.46 | 0 | 0
2025-12-31 11:00 | 43.07 | 48.76 | 46.47 | 0 | 3.4 | 0 | 5.69 | 2.29 | 0
2025-12-31 12:00 | 43.43 | 42.22 | 42.22 | 0 | 0 | 1.22 | 4.41 | 0 | 0
2025-12-31 13:00 | 44.63 | 57.55 | 46.42 | 0 | 1.8 | 0 | 6.12 | 11.13 | 0
2025-12-31 14:00 | 44.08 | 69.02 | 44.08 | 0 | 0 | 0 | 6.12 | 24.94 | 0
2025-12-31 15:00 | 43.98 | 68.72 | 43.98 | 0 | 0 | 0 | 6.12 | 24.74 | 0
2025-12-31 16:00 | 42.92 | 6.19 | 6.19 | 33.33 | 0 | 3.4 | 2.54 | 0 | 0
2025-12-31 17:00 | 44.12 | 0 | 0 | 42.36 | 0 | 1.77 | 0.68 | 0 | 0
2025-12-31 18:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 19:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 20:00 | 40.97 | 0 | 0 | 40.97 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 21:00 | 40.68 | 0 | 0 | 40.68 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 22:00 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 0.68 | 0 | 0
2025-12-31 23:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 0.68 | 0 | 0

## Sim_SSR45pct
Timestamp | Load (MW) | PV available (MW) | PV used on-site (MW) | Grid import (MW) | BESS charge (MW) | BESS discharge (MW) | BESS state of charge (MWh) | PV curtailed (MW) | Unmet load (MW)
2025-01-01 | 39.07 | 0 | 0 | 0 | 0 | 39.07 | 21.43 | 0 | 0
2025-01-01 01:00 | 37.35 | 0 | 0 | 28.88 | 0 | 8.47 | 12.51 | 0 | 0
2025-01-01 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 03:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 04:00 | 37.77 | 0 | 0 | 37.77 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 05:00 | 37.73 | 0 | 0 | 37.73 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 06:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 07:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 08:00 | 40.47 | 0.35 | 0.35 | 40.12 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 09:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 10:00 | 43.25 | 39.6 | 39.6 | 3.65 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 11:00 | 42.95 | 51.11 | 51.11 | 0 | 8.16 | 0 | 20.26 | 0 | 0
2025-01-01 12:00 | 42.89 | 47.41 | 47.41 | 0 | 4.52 | 0 | 24.55 | 0 | 0
2025-01-01 13:00 | 45.35 | 15.24 | 15.24 | 18.67 | 0 | 11.44 | 12.51 | 0 | 0
2025-01-01 14:00 | 44.73 | 17.49 | 17.49 | 27.24 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 15:00 | 45.16 | 7.79 | 7.79 | 37.36 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 16:00 | 45.62 | 0.73 | 0.73 | 44.89 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 17:00 | 43.75 | 0 | 0 | 43.75 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 18:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 19:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 20:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 21:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 22:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 12.51 | 0 | 0
2025-01-01 23:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 01:00 | 36.51 | 0 | 0 | 36.51 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 02:00 | 37.33 | 0 | 0 | 37.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 04:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 05:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 06:00 | 38.3 | 0 | 0 | 38.3 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 07:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 08:00 | 39.84 | 3.35 | 3.35 | 36.49 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 09:00 | 40.79 | 0.73 | 0.73 | 40.07 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 10:00 | 40.93 | 11.93 | 11.93 | 29 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 11:00 | 41.86 | 40.23 | 40.23 | 1.63 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 12:00 | 42.58 | 49.61 | 49.61 | 0 | 7.03 | 0 | 19.19 | 0 | 0
2025-01-02 13:00 | 43.28 | 52.12 | 52.12 | 0 | 8.84 | 0 | 27.59 | 0 | 0
2025-01-02 14:00 | 42.91 | 35.75 | 35.75 | 0 | 0 | 7.17 | 20.04 | 0 | 0
2025-01-02 15:00 | 43.45 | 53.79 | 53.79 | 0 | 10.34 | 0 | 29.86 | 0 | 0
2025-01-02 16:00 | 42.98 | 6.95 | 6.95 | 19.54 | 0 | 16.49 | 12.51 | 0 | 0
2025-01-02 17:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 18:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 19:00 | 40.95 | 0 | 0 | 40.95 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 20:00 | 40.64 | 0 | 0 | 40.64 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 21:00 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 22:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 12.51 | 0 | 0
2025-01-02 23:00 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 01:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 02:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 03:00 | 37.67 | 0 | 0 | 37.67 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 04:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 05:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 06:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 07:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 08:00 | 39.56 | 5.56 | 5.56 | 34 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 09:00 | 40.75 | 58.94 | 58.94 | 0 | 18.19 | 0 | 29.79 | 0 | 0
2025-01-03 10:00 | 41.4 | 61.46 | 61.46 | 0 | 20.06 | 0 | 48.85 | 0 | 0
2025-01-03 11:00 | 42.74 | 45.74 | 45.74 | 0 | 3 | 0 | 51.7 | 0 | 0
2025-01-03 12:00 | 43.93 | 43.72 | 43.72 | 0 | 0 | 0.22 | 51.47 | 0 | 0
2025-01-03 13:00 | 45.24 | 53.25 | 53.25 | 0 | 8.01 | 0 | 59.08 | 0 | 0
2025-01-03 14:00 | 46.16 | 56.05 | 56.05 | 0 | 9.89 | 0 | 68.48 | 0 | 0
2025-01-03 15:00 | 44.76 | 59.27 | 59.27 | 0 | 14.51 | 0 | 82.27 | 0 | 0
2025-01-03 16:00 | 45.49 | 2.76 | 2.76 | 0 | 0 | 42.73 | 37.29 | 0 | 0
2025-01-03 17:00 | 44.31 | 0 | 0 | 20.77 | 0 | 23.54 | 12.51 | 0 | 0
2025-01-03 18:00 | 44.35 | 0 | 0 | 44.35 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 19:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 20:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 21:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 22:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 12.51 | 0 | 0
2025-01-03 23:00 | 38.76 | 0 | 0 | 38.76 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 | 37.64 | 0 | 0 | 37.64 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 01:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 02:00 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 03:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 04:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 05:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 06:00 | 38.84 | 0 | 0 | 38.84 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 07:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 08:00 | 39.21 | 5.61 | 5.61 | 33.61 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 09:00 | 41.56 | 63.95 | 63.95 | 0 | 22.38 | 0 | 33.77 | 0 | 0
2025-01-04 10:00 | 41.98 | 65.08 | 65.08 | 0 | 23.1 | 0 | 55.72 | 0 | 0
2025-01-04 11:00 | 43.79 | 50.17 | 50.17 | 0 | 6.38 | 0 | 61.78 | 0 | 0
2025-01-04 12:00 | 44.38 | 45.3 | 45.3 | 0 | 0.92 | 0 | 62.66 | 0 | 0
2025-01-04 13:00 | 44.88 | 44.2 | 44.2 | 0 | 0 | 0.68 | 61.94 | 0 | 0
2025-01-04 14:00 | 45.6 | 40.92 | 40.92 | 0 | 0 | 4.68 | 57.02 | 0 | 0
2025-01-04 15:00 | 46.56 | 17.8 | 17.8 | 0 | 0 | 28.77 | 26.74 | 0 | 0
2025-01-04 16:00 | 46.46 | 2.17 | 2.17 | 30.78 | 0 | 13.52 | 12.51 | 0 | 0
2025-01-04 17:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 18:00 | 44.27 | 0 | 0 | 44.27 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 19:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 20:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 21:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 22:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-04 23:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 01:00 | 36.72 | 0 | 0 | 36.72 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 02:00 | 36.13 | 0 | 0 | 36.13 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 03:00 | 36.48 | 0 | 0 | 36.48 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 04:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 05:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 06:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 07:00 | 39.24 | 0 | 0 | 39.24 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 08:00 | 38.89 | 5.6 | 5.6 | 33.29 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 09:00 | 40.19 | 69.74 | 69.74 | 0 | 29.55 | 0 | 40.58 | 0 | 0
2025-01-05 10:00 | 40.38 | 56.56 | 56.56 | 0 | 16.19 | 0 | 55.96 | 0 | 0
2025-01-05 11:00 | 40.89 | 41.29 | 41.29 | 0 | 0.4 | 0 | 56.34 | 0 | 0
2025-01-05 12:00 | 41.45 | 37.95 | 37.95 | 0 | 0 | 3.5 | 52.66 | 0 | 0
2025-01-05 13:00 | 41.88 | 35.68 | 35.68 | 0 | 0 | 6.2 | 46.14 | 0 | 0
2025-01-05 14:00 | 41.52 | 22.65 | 22.65 | 0 | 0 | 18.87 | 26.27 | 0 | 0
2025-01-05 15:00 | 42.25 | 33.53 | 33.53 | 0 | 0 | 8.72 | 17.1 | 0 | 0
2025-01-05 16:00 | 41.11 | 5.31 | 5.31 | 31.45 | 0 | 4.36 | 12.51 | 0 | 0
2025-01-05 17:00 | 41.57 | 0 | 0 | 41.57 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 18:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 19:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 20:00 | 41.3 | 0 | 0 | 41.3 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 21:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 22:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-05 23:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 01:00 | 37.09 | 0 | 0 | 37.09 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 02:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 03:00 | 36.58 | 0 | 0 | 36.58 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 04:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 05:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 06:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 07:00 | 38.54 | 0 | 0 | 38.54 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 08:00 | 39.65 | 1.65 | 1.65 | 38 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 09:00 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 10:00 | 41.31 | 31.52 | 31.52 | 9.79 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 11:00 | 40.51 | 40.66 | 40.66 | 0 | 0.15 | 0 | 12.65 | 0 | 0
2025-01-06 12:00 | 41.72 | 35.39 | 35.39 | 6.2 | 0 | 0.13 | 12.51 | 0 | 0
2025-01-06 13:00 | 41.22 | 32.44 | 32.44 | 8.78 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 14:00 | 41.67 | 25.68 | 25.68 | 15.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 15:00 | 43.16 | 4.26 | 4.26 | 38.91 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 16:00 | 42.86 | 1.43 | 1.43 | 41.44 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 17:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 18:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 19:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 20:00 | 40.57 | 0 | 0 | 40.57 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 21:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 22:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 12.51 | 0 | 0
2025-01-06 23:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 01:00 | 36.66 | 0 | 0 | 36.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 03:00 | 37.02 | 0 | 0 | 37.02 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 04:00 | 37.04 | 0 | 0 | 37.04 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 05:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 06:00 | 38.18 | 0 | 0 | 38.18 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 07:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 08:00 | 39.28 | 0 | 0 | 39.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 09:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 10:00 | 42.32 | 2.3 | 2.3 | 40.01 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 11:00 | 41.9 | 6.14 | 6.14 | 35.76 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 12:00 | 42.7 | 5.59 | 5.59 | 37.12 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 13:00 | 44.4 | 41.59 | 41.59 | 2.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 14:00 | 44.01 | 44.55 | 44.55 | 0 | 0.54 | 0 | 13.03 | 0 | 0
2025-01-07 15:00 | 44.93 | 49.89 | 49.89 | 0 | 4.96 | 0 | 17.74 | 0 | 0
2025-01-07 16:00 | 43.88 | 3.06 | 3.06 | 35.85 | 0 | 4.97 | 12.51 | 0 | 0
2025-01-07 17:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 18:00 | 43.21 | 0 | 0 | 43.21 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 19:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 20:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 21:00 | 40.38 | 0 | 0 | 40.38 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 22:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 12.51 | 0 | 0
2025-01-07 23:00 | 38.53 | 0 | 0 | 38.53 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 | 38.18 | 0 | 0 | 38.18 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 01:00 | 36.62 | 0 | 0 | 36.62 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 02:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 03:00 | 36.66 | 0 | 0 | 36.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 04:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 05:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 06:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 07:00 | 37.83 | 0 | 0 | 37.83 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 08:00 | 39.08 | 2.87 | 2.87 | 36.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 09:00 | 40.48 | 54.59 | 54.59 | 0 | 14.1 | 0 | 25.91 | 0 | 0
2025-01-08 10:00 | 41.12 | 46.52 | 46.52 | 0 | 5.4 | 0 | 31.04 | 0 | 0
2025-01-08 11:00 | 41.87 | 40.62 | 40.62 | 0 | 0 | 1.24 | 29.73 | 0 | 0
2025-01-08 12:00 | 42.58 | 30.81 | 30.81 | 0 | 0 | 11.77 | 17.34 | 0 | 0
2025-01-08 13:00 | 43.26 | 30.82 | 30.82 | 7.86 | 0 | 4.58 | 12.51 | 0 | 0
2025-01-08 14:00 | 42.97 | 21.02 | 21.02 | 21.95 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 15:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 16:00 | 43.81 | 0.49 | 0.49 | 43.31 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 17:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 18:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 19:00 | 42.14 | 0 | 0 | 42.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 20:00 | 42.23 | 0 | 0 | 42.23 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 21:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 22:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 12.51 | 0 | 0
2025-01-08 23:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 | 37.41 | 0 | 0 | 37.41 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 01:00 | 36.75 | 0 | 0 | 36.75 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 02:00 | 36.57 | 0 | 0 | 36.57 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 04:00 | 37.19 | 0 | 0 | 37.19 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 05:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 06:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 07:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 08:00 | 39.86 | 4.53 | 4.53 | 35.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 09:00 | 40.32 | 54.25 | 54.25 | 0 | 13.94 | 0 | 25.75 | 0 | 0
2025-01-09 10:00 | 40.97 | 63.39 | 63.39 | 0 | 22.42 | 0 | 47.04 | 0 | 0
2025-01-09 11:00 | 42.41 | 53.19 | 53.19 | 0 | 10.78 | 0 | 57.28 | 0 | 0
2025-01-09 12:00 | 42.95 | 50.69 | 50.69 | 0 | 7.74 | 0 | 64.64 | 0 | 0
2025-01-09 13:00 | 42.69 | 61.34 | 61.34 | 0 | 18.65 | 0 | 82.36 | 0 | 0
2025-01-09 14:00 | 43.73 | 72.15 | 72.15 | 0 | 28.42 | 0 | 109.35 | 0 | 0
2025-01-09 15:00 | 44.01 | 74.05 | 47.42 | 0 | 3.41 | 0 | 112.59 | 26.63 | 0
2025-01-09 16:00 | 43.31 | 11.39 | 11.39 | 0 | 0 | 31.92 | 78.99 | 0 | 0
2025-01-09 17:00 | 43.51 | 0 | 0 | 0 | 0 | 43.51 | 33.19 | 0 | 0
2025-01-09 18:00 | 42.13 | 0 | 0 | 22.48 | 0 | 19.65 | 12.51 | 0 | 0
2025-01-09 19:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 20:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 21:00 | 40.27 | 0 | 0 | 40.27 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 22:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 12.51 | 0 | 0
2025-01-09 23:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 | 37.29 | 0 | 0 | 37.29 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 01:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 02:00 | 36.45 | 0 | 0 | 36.45 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 03:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 04:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 05:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 06:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 07:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 08:00 | 40.11 | 1.65 | 1.65 | 38.46 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 09:00 | 39.47 | 23.38 | 23.38 | 16.09 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 10:00 | 40.95 | 35.23 | 35.23 | 5.72 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 11:00 | 42.4 | 16.56 | 16.56 | 25.83 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 12:00 | 41.2 | 23.28 | 23.28 | 17.92 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 13:00 | 41.79 | 36.62 | 36.62 | 5.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 14:00 | 42.46 | 10.28 | 10.28 | 32.18 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 15:00 | 42.5 | 0.06 | 0.06 | 42.44 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 16:00 | 43.08 | 0.33 | 0.33 | 42.75 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 17:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 18:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 19:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 20:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 21:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 22:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-10 23:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 01:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 02:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 03:00 | 36 | 0 | 0 | 36 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 04:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 05:00 | 36.79 | 0 | 0 | 36.79 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 07:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 08:00 | 39.78 | 5.3 | 5.3 | 34.47 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 09:00 | 40.17 | 72.35 | 72.35 | 0 | 32.18 | 0 | 43.08 | 0 | 0
2025-01-11 10:00 | 40.98 | 70.19 | 70.19 | 0 | 29.21 | 0 | 70.83 | 0 | 0
2025-01-11 11:00 | 43 | 58.87 | 58.87 | 0 | 15.87 | 0 | 85.9 | 0 | 0
2025-01-11 12:00 | 43.66 | 51.69 | 51.69 | 0 | 8.03 | 0 | 93.53 | 0 | 0
2025-01-11 13:00 | 43.94 | 56.66 | 56.66 | 0 | 12.72 | 0 | 105.62 | 0 | 0
2025-01-11 14:00 | 45.42 | 67.69 | 52.76 | 0 | 7.34 | 0 | 112.59 | 14.92 | 0
2025-01-11 15:00 | 44.63 | 69.51 | 44.63 | 0 | 0 | 0 | 112.59 | 24.88 | 0
2025-01-11 16:00 | 44.71 | 6.98 | 6.98 | 0 | 0 | 37.73 | 72.88 | 0 | 0
2025-01-11 17:00 | 44.38 | 0 | 0 | 0 | 0 | 44.38 | 26.16 | 0 | 0
2025-01-11 18:00 | 43.23 | 0 | 0 | 30.26 | 0 | 12.97 | 12.51 | 0 | 0
2025-01-11 19:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 20:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 21:00 | 40.37 | 0 | 0 | 40.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 12.51 | 0 | 0
2025-01-11 23:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 | 36.64 | 0 | 0 | 36.64 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 01:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 02:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 03:00 | 36.61 | 0 | 0 | 36.61 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 04:00 | 35.96 | 0 | 0 | 35.96 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 06:00 | 37.7 | 0 | 0 | 37.7 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 07:00 | 38.5 | 0 | 0 | 38.5 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 08:00 | 38.94 | 5.94 | 5.94 | 32.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 09:00 | 40.78 | 56.69 | 56.69 | 0 | 15.91 | 0 | 27.63 | 0 | 0
2025-01-12 10:00 | 41.79 | 54.06 | 54.06 | 0 | 12.27 | 0 | 39.29 | 0 | 0
2025-01-12 11:00 | 41.77 | 52.16 | 52.16 | 0 | 10.39 | 0 | 49.16 | 0 | 0
2025-01-12 12:00 | 43.74 | 56.79 | 56.79 | 0 | 13.05 | 0 | 61.55 | 0 | 0
2025-01-12 13:00 | 45.1 | 63.13 | 63.13 | 0 | 18.04 | 0 | 78.69 | 0 | 0
2025-01-12 14:00 | 44.59 | 74.02 | 74.02 | 0 | 29.43 | 0 | 106.65 | 0 | 0
2025-01-12 15:00 | 44.49 | 76.46 | 50.74 | 0 | 6.25 | 0 | 112.59 | 25.73 | 0
2025-01-12 16:00 | 44.43 | 14.19 | 14.19 | 0 | 0 | 30.24 | 80.76 | 0 | 0
2025-01-12 17:00 | 44.38 | 0 | 0 | 0 | 0 | 44.38 | 34.05 | 0 | 0
2025-01-12 18:00 | 42.52 | 0 | 0 | 22.06 | 0 | 20.46 | 12.51 | 0 | 0
2025-01-12 19:00 | 42.6 | 0 | 0 | 42.6 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 21:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 22:00 | 39.41 | 0 | 0 | 39.41 | 0 | 0 | 12.51 | 0 | 0
2025-01-12 23:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 | 37.24 | 0 | 0 | 37.24 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 01:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 02:00 | 37.07 | 0 | 0 | 37.07 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 03:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 04:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 05:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 06:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 07:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 08:00 | 39.33 | 3.52 | 3.52 | 35.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 09:00 | 39.78 | 36.98 | 36.98 | 2.8 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 10:00 | 40.96 | 30.12 | 30.12 | 10.84 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 11:00 | 41.93 | 21.09 | 21.09 | 20.84 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 12:00 | 41.84 | 13.28 | 13.28 | 28.56 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 13:00 | 42.44 | 38.06 | 38.06 | 4.38 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 14:00 | 43.83 | 61.2 | 61.2 | 0 | 17.37 | 0 | 29.01 | 0 | 0
2025-01-13 15:00 | 43.45 | 70.5 | 70.5 | 0 | 27.05 | 0 | 54.71 | 0 | 0
2025-01-13 16:00 | 42.31 | 15.81 | 15.81 | 0 | 0 | 26.5 | 26.81 | 0 | 0
2025-01-13 17:00 | 43.64 | 0 | 0 | 30.05 | 0 | 13.58 | 12.51 | 0 | 0
2025-01-13 18:00 | 42.82 | 0 | 0 | 42.82 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 19:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 20:00 | 40.47 | 0 | 0 | 40.47 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 21:00 | 40.65 | 0 | 0 | 40.65 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 22:00 | 39.51 | 0 | 0 | 39.51 | 0 | 0 | 12.51 | 0 | 0
2025-01-13 23:00 | 39.7 | 0 | 0 | 39.7 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 | 38 | 0 | 0 | 38 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 01:00 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 02:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 03:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 04:00 | 37.2 | 0 | 0 | 37.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 05:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 06:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 07:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 08:00 | 39.24 | 2.1 | 2.1 | 37.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 09:00 | 40.91 | 0 | 0 | 40.91 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 10:00 | 42.35 | 23.81 | 23.81 | 18.54 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 11:00 | 42.42 | 7.58 | 7.58 | 34.84 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 12:00 | 43.38 | 17.48 | 17.48 | 25.9 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 13:00 | 44.48 | 31.4 | 31.4 | 13.08 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 14:00 | 44.67 | 56.66 | 56.66 | 0 | 11.99 | 0 | 23.9 | 0 | 0
2025-01-14 15:00 | 45.44 | 67.78 | 67.78 | 0 | 22.35 | 0 | 45.13 | 0 | 0
2025-01-14 16:00 | 43.67 | 15.89 | 15.89 | 0 | 0 | 27.78 | 15.89 | 0 | 0
2025-01-14 17:00 | 43.91 | 0 | 0 | 40.7 | 0 | 3.21 | 12.51 | 0 | 0
2025-01-14 18:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 19:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 20:00 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 21:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 22:00 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 12.51 | 0 | 0
2025-01-14 23:00 | 39.11 | 0 | 0 | 39.11 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 01:00 | 36.69 | 0 | 0 | 36.69 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 02:00 | 36.83 | 0 | 0 | 36.83 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 03:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 04:00 | 36.37 | 0 | 0 | 36.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 05:00 | 36.75 | 0 | 0 | 36.75 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 06:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 07:00 | 38.37 | 0 | 0 | 38.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 08:00 | 39.66 | 5.23 | 5.23 | 34.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 09:00 | 40.27 | 59.3 | 59.3 | 0 | 19.03 | 0 | 30.59 | 0 | 0
2025-01-15 10:00 | 41.59 | 59.44 | 59.44 | 0 | 17.85 | 0 | 47.54 | 0 | 0
2025-01-15 11:00 | 41.64 | 52.05 | 52.05 | 0 | 10.41 | 0 | 57.43 | 0 | 0
2025-01-15 12:00 | 42.95 | 44.11 | 44.11 | 0 | 1.16 | 0 | 58.54 | 0 | 0
2025-01-15 13:00 | 43.47 | 52.23 | 52.23 | 0 | 8.77 | 0 | 66.86 | 0 | 0
2025-01-15 14:00 | 43.36 | 36.92 | 36.92 | 0 | 0 | 6.44 | 60.08 | 0 | 0
2025-01-15 15:00 | 43.32 | 50.39 | 50.39 | 0 | 7.07 | 0 | 66.8 | 0 | 0
2025-01-15 16:00 | 44.31 | 9.01 | 9.01 | 0 | 0 | 35.3 | 29.64 | 0 | 0
2025-01-15 17:00 | 43.4 | 0 | 0 | 27.12 | 0 | 16.28 | 12.51 | 0 | 0
2025-01-15 18:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 19:00 | 42.11 | 0 | 0 | 42.11 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 20:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 21:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 22:00 | 38.59 | 0 | 0 | 38.59 | 0 | 0 | 12.51 | 0 | 0
2025-01-15 23:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 01:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 02:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 03:00 | 36.16 | 0 | 0 | 36.16 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 04:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 05:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 06:00 | 37.72 | 0 | 0 | 37.72 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 07:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 08:00 | 39 | 0 | 0 | 39 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 09:00 | 39.98 | 0.01 | 0.01 | 39.97 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 10:00 | 40.65 | 5.61 | 5.61 | 35.04 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 11:00 | 41.6 | 8.51 | 8.51 | 33.09 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 12:00 | 42.14 | 9.57 | 9.57 | 32.57 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 13:00 | 41.31 | 42.62 | 42.62 | 0 | 1.31 | 0 | 13.75 | 0 | 0
2025-01-16 14:00 | 41.24 | 53.03 | 53.03 | 0 | 11.79 | 0 | 24.95 | 0 | 0
2025-01-16 15:00 | 42.94 | 35.77 | 35.77 | 0 | 0 | 7.18 | 17.4 | 0 | 0
2025-01-16 16:00 | 42.96 | 10.06 | 10.06 | 28.25 | 0 | 4.64 | 12.51 | 0 | 0
2025-01-16 17:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 18:00 | 40.8 | 0 | 0 | 40.8 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 19:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 20:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 21:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 22:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 12.51 | 0 | 0
2025-01-16 23:00 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 01:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 02:00 | 36.68 | 0 | 0 | 36.68 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 03:00 | 36.21 | 0 | 0 | 36.21 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 04:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 05:00 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 06:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 07:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 08:00 | 39.7 | 0.79 | 0.79 | 38.91 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 09:00 | 40.51 | 0.09 | 0.09 | 40.42 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 10:00 | 41.35 | 9.46 | 9.46 | 31.89 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 11:00 | 42.64 | 23.66 | 23.66 | 18.98 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 12:00 | 43.1 | 26.35 | 26.35 | 16.76 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 13:00 | 43.76 | 25.24 | 25.24 | 18.52 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 14:00 | 44.08 | 26.75 | 26.75 | 17.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 15:00 | 44.06 | 15.7 | 15.7 | 28.36 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 16:00 | 42.87 | 3.54 | 3.54 | 39.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 17:00 | 43.43 | 0 | 0 | 43.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 18:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 19:00 | 41.38 | 0 | 0 | 41.38 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 20:00 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 21:00 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 22:00 | 39.95 | 0 | 0 | 39.95 | 0 | 0 | 12.51 | 0 | 0
2025-01-17 23:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 01:00 | 37.15 | 0 | 0 | 37.15 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 02:00 | 36.92 | 0 | 0 | 36.92 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 03:00 | 36.15 | 0 | 0 | 36.15 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 04:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 05:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 06:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 07:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 08:00 | 38.99 | 0.3 | 0.3 | 38.69 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 09:00 | 40.67 | 3.59 | 3.59 | 37.08 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 10:00 | 40.92 | 7.21 | 7.21 | 33.7 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 11:00 | 41.09 | 8.96 | 8.96 | 32.13 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 12:00 | 41.71 | 10.82 | 10.82 | 30.9 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 13:00 | 41.98 | 11.55 | 11.55 | 30.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 14:00 | 42.08 | 8.37 | 8.37 | 33.71 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 15:00 | 41.72 | 4.23 | 4.23 | 37.48 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 16:00 | 42.11 | 0.33 | 0.33 | 41.78 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 17:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 18:00 | 40.96 | 0 | 0 | 40.96 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 19:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 20:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 21:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 22:00 | 38.97 | 0 | 0 | 38.97 | 0 | 0 | 12.51 | 0 | 0
2025-01-18 23:00 | 38.8 | 0 | 0 | 38.8 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 01:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 02:00 | 36.82 | 0 | 0 | 36.82 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 03:00 | 36.27 | 0 | 0 | 36.27 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 04:00 | 36.26 | 0 | 0 | 36.26 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 05:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 06:00 | 37.88 | 0 | 0 | 37.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 07:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 08:00 | 39.87 | 0 | 0 | 39.87 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 09:00 | 40.24 | 2.24 | 2.24 | 38 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 10:00 | 40.7 | 4.22 | 4.22 | 36.49 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 11:00 | 42.15 | 5.37 | 5.37 | 36.78 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 12:00 | 43.29 | 6.56 | 6.56 | 36.73 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 13:00 | 43.76 | 6.23 | 6.23 | 37.53 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 14:00 | 44.01 | 5.3 | 5.3 | 38.71 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 15:00 | 44.57 | 2.67 | 2.67 | 41.9 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 16:00 | 44.05 | 0.15 | 0.15 | 43.9 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 17:00 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 18:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 19:00 | 42.11 | 0 | 0 | 42.11 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 20:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 21:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 22:00 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 12.51 | 0 | 0
2025-01-19 23:00 | 38.19 | 0 | 0 | 38.19 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 01:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 02:00 | 35.74 | 0 | 0 | 35.74 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 03:00 | 35.75 | 0 | 0 | 35.75 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 04:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 05:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 06:00 | 37.6 | 0 | 0 | 37.6 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 07:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 08:00 | 37.81 | 9.17 | 9.17 | 28.65 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 09:00 | 40.21 | 69.34 | 69.34 | 0 | 29.14 | 0 | 40.19 | 0 | 0
2025-01-20 10:00 | 41.65 | 61.8 | 61.8 | 0 | 20.16 | 0 | 59.34 | 0 | 0
2025-01-20 11:00 | 41.1 | 52.27 | 52.27 | 0 | 11.17 | 0 | 69.95 | 0 | 0
2025-01-20 12:00 | 42.15 | 46.79 | 46.79 | 0 | 4.64 | 0 | 74.36 | 0 | 0
2025-01-20 13:00 | 42.49 | 53.41 | 53.41 | 0 | 10.92 | 0 | 84.74 | 0 | 0
2025-01-20 14:00 | 42.75 | 67.67 | 67.67 | 0 | 24.93 | 0 | 108.42 | 0 | 0
2025-01-20 15:00 | 43.14 | 74.01 | 47.54 | 0 | 4.39 | 0 | 112.59 | 26.47 | 0
2025-01-20 16:00 | 43.91 | 27.56 | 27.56 | 0 | 0 | 16.35 | 95.38 | 0 | 0
2025-01-20 17:00 | 43.78 | 0 | 0 | 0 | 0 | 43.78 | 49.29 | 0 | 0
2025-01-20 18:00 | 42.18 | 0 | 0 | 7.23 | 0 | 34.95 | 12.51 | 0 | 0
2025-01-20 19:00 | 42.61 | 0 | 0 | 42.61 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 20:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 21:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 22:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 12.51 | 0 | 0
2025-01-20 23:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 | 37.83 | 0 | 0 | 37.83 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 01:00 | 38.71 | 0 | 0 | 38.71 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 02:00 | 37.21 | 0 | 0 | 37.21 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 03:00 | 36.32 | 0 | 0 | 36.32 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 04:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 05:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 06:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 07:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 08:00 | 39.13 | 9.68 | 9.68 | 29.45 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 09:00 | 40.1 | 58.65 | 58.65 | 0 | 18.55 | 0 | 30.14 | 0 | 0
2025-01-21 10:00 | 40.79 | 67.45 | 67.45 | 0 | 26.65 | 0 | 55.45 | 0 | 0
2025-01-21 11:00 | 41.72 | 56.06 | 56.06 | 0 | 14.34 | 0 | 69.07 | 0 | 0
2025-01-21 12:00 | 42.42 | 49.51 | 49.51 | 0 | 7.09 | 0 | 75.81 | 0 | 0
2025-01-21 13:00 | 41.74 | 57.79 | 57.79 | 0 | 16.04 | 0 | 91.05 | 0 | 0
2025-01-21 14:00 | 43.36 | 65.14 | 65.14 | 0 | 21.78 | 0 | 111.74 | 0 | 0
2025-01-21 15:00 | 42.64 | 69.7 | 43.53 | 0 | 0.89 | 0 | 112.59 | 26.18 | 0
2025-01-21 16:00 | 42.3 | 24.93 | 24.93 | 0 | 0 | 17.37 | 94.31 | 0 | 0
2025-01-21 17:00 | 42.68 | 0 | 0 | 0 | 0 | 42.68 | 49.38 | 0 | 0
2025-01-21 18:00 | 42.25 | 0 | 0 | 7.22 | 0 | 35.03 | 12.51 | 0 | 0
2025-01-21 19:00 | 41.21 | 0 | 0 | 41.21 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 20:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 21:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 22:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 12.51 | 0 | 0
2025-01-21 23:00 | 38.04 | 0 | 0 | 38.04 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 | 37.6 | 0 | 0 | 37.6 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 01:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 02:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 03:00 | 37.03 | 0 | 0 | 37.03 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 04:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 05:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 06:00 | 36.65 | 0 | 0 | 36.65 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 07:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 08:00 | 38.92 | 10.55 | 10.55 | 28.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 09:00 | 39.75 | 52.26 | 52.26 | 0 | 12.51 | 0 | 24.4 | 0 | 0
2025-01-22 10:00 | 40.53 | 40.74 | 40.74 | 0 | 0.21 | 0 | 24.6 | 0 | 0
2025-01-22 11:00 | 41.32 | 32.04 | 32.04 | 0 | 0 | 9.28 | 14.83 | 0 | 0
2025-01-22 12:00 | 42.24 | 52.65 | 52.65 | 0 | 10.41 | 0 | 24.71 | 0 | 0
2025-01-22 13:00 | 41.62 | 55.13 | 55.13 | 0 | 13.51 | 0 | 37.54 | 0 | 0
2025-01-22 14:00 | 41.85 | 40.08 | 40.08 | 0 | 0 | 1.77 | 35.68 | 0 | 0
2025-01-22 15:00 | 41.97 | 53.58 | 53.58 | 0 | 11.6 | 0 | 46.7 | 0 | 0
2025-01-22 16:00 | 42.58 | 0 | 0 | 10.1 | 0 | 32.48 | 12.51 | 0 | 0
2025-01-22 17:00 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 18:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 19:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 20:00 | 39.69 | 0 | 0 | 39.69 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 21:00 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 22:00 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 12.51 | 0 | 0
2025-01-22 23:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 01:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 02:00 | 37.31 | 0 | 0 | 37.31 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 03:00 | 36.33 | 0 | 0 | 36.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 04:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 05:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 06:00 | 36.91 | 0 | 0 | 36.91 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 07:00 | 38.62 | 0 | 0 | 38.62 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 08:00 | 39.39 | 9.01 | 9.01 | 30.38 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 09:00 | 40.29 | 23.77 | 23.77 | 16.52 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 10:00 | 42.24 | 43 | 43 | 0 | 0.77 | 0 | 13.24 | 0 | 0
2025-01-23 11:00 | 42.18 | 57.82 | 57.82 | 0 | 15.64 | 0 | 28.09 | 0 | 0
2025-01-23 12:00 | 44.46 | 53.02 | 53.02 | 0 | 8.56 | 0 | 36.23 | 0 | 0
2025-01-23 13:00 | 44.05 | 61.04 | 61.04 | 0 | 16.99 | 0 | 52.36 | 0 | 0
2025-01-23 14:00 | 44 | 36.19 | 36.19 | 0 | 0 | 7.81 | 44.14 | 0 | 0
2025-01-23 15:00 | 44.84 | 35.58 | 35.58 | 0 | 0 | 9.26 | 34.39 | 0 | 0
2025-01-23 16:00 | 44.1 | 0 | 0 | 23.31 | 0 | 20.79 | 12.51 | 0 | 0
2025-01-23 17:00 | 43.79 | 0 | 0 | 43.79 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 18:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 19:00 | 42.77 | 0 | 0 | 42.77 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 20:00 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 21:00 | 40.86 | 0 | 0 | 40.86 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 22:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 12.51 | 0 | 0
2025-01-23 23:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 | 37.9 | 0 | 0 | 37.9 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 01:00 | 37.79 | 0 | 0 | 37.79 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 02:00 | 35.84 | 0 | 0 | 35.84 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 03:00 | 36.51 | 0 | 0 | 36.51 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 04:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 05:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 06:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 07:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 08:00 | 40.05 | 1.02 | 1.02 | 39.03 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 09:00 | 39.87 | 5.67 | 5.67 | 34.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 10:00 | 41 | 22.28 | 22.28 | 18.72 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 11:00 | 41.45 | 36.59 | 36.59 | 4.85 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 12:00 | 42.26 | 30.02 | 30.02 | 12.24 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 13:00 | 42.73 | 17.07 | 17.07 | 25.66 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 14:00 | 43.26 | 16.56 | 16.56 | 26.7 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 15:00 | 43.73 | 0.72 | 0.72 | 43.01 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 16:00 | 43.86 | 2 | 2 | 41.87 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 17:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 19:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 20:00 | 40.75 | 0 | 0 | 40.75 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 21:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 22:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 12.51 | 0 | 0
2025-01-24 23:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 01:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 02:00 | 37.38 | 0 | 0 | 37.38 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 03:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 04:00 | 36.61 | 0 | 0 | 36.61 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 05:00 | 37.28 | 0 | 0 | 37.28 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 06:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 07:00 | 38.5 | 0 | 0 | 38.5 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 08:00 | 37.25 | 5.03 | 5.03 | 32.21 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 09:00 | 39.01 | 57.95 | 57.95 | 0 | 18.94 | 0 | 30.5 | 0 | 0
2025-01-25 10:00 | 40.89 | 49.89 | 49.89 | 0 | 9 | 0 | 39.05 | 0 | 0
2025-01-25 11:00 | 41.62 | 38.85 | 38.85 | 0 | 0 | 2.77 | 36.13 | 0 | 0
2025-01-25 12:00 | 41.41 | 42.63 | 42.63 | 0 | 1.23 | 0 | 37.3 | 0 | 0
2025-01-25 13:00 | 42.09 | 57.38 | 57.38 | 0 | 15.29 | 0 | 51.82 | 0 | 0
2025-01-25 14:00 | 43.41 | 37.26 | 37.26 | 0 | 0 | 6.15 | 45.34 | 0 | 0
2025-01-25 15:00 | 42.58 | 5.07 | 5.07 | 6.32 | 0 | 31.19 | 12.51 | 0 | 0
2025-01-25 16:00 | 43.85 | 0 | 0 | 43.85 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 17:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 18:00 | 42.19 | 0 | 0 | 42.19 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 19:00 | 42.19 | 0 | 0 | 42.19 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 20:00 | 40.73 | 0 | 0 | 40.73 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 21:00 | 39.37 | 0 | 0 | 39.37 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 22:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 12.51 | 0 | 0
2025-01-25 23:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 01:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 02:00 | 36.42 | 0 | 0 | 36.42 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 03:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 04:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 05:00 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 06:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 07:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 08:00 | 39.4 | 3.54 | 3.54 | 35.85 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 09:00 | 39.41 | 11.53 | 11.53 | 27.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 10:00 | 40.19 | 12.3 | 12.3 | 27.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 11:00 | 42 | 25.7 | 25.7 | 16.29 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 12:00 | 41.86 | 34.22 | 34.22 | 7.64 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 13:00 | 41.83 | 44.39 | 44.39 | 0 | 2.56 | 0 | 14.94 | 0 | 0
2025-01-26 14:00 | 43.05 | 69.02 | 69.02 | 0 | 25.97 | 0 | 39.62 | 0 | 0
2025-01-26 15:00 | 43.16 | 72.81 | 72.81 | 0 | 29.65 | 0 | 67.79 | 0 | 0
2025-01-26 16:00 | 42.06 | 33.43 | 33.43 | 0 | 0 | 8.64 | 58.7 | 0 | 0
2025-01-26 17:00 | 42.65 | 0 | 0 | 0 | 0 | 42.65 | 13.8 | 0 | 0
2025-01-26 18:00 | 42.43 | 0 | 0 | 41.2 | 0 | 1.23 | 12.51 | 0 | 0
2025-01-26 19:00 | 41.63 | 0 | 0 | 41.63 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 20:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 21:00 | 39.2 | 0 | 0 | 39.2 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 22:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 12.51 | 0 | 0
2025-01-26 23:00 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 | 37.43 | 0 | 0 | 37.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 01:00 | 37.57 | 0 | 0 | 37.57 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 02:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 03:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 04:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 05:00 | 37.08 | 0 | 0 | 37.08 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 06:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 07:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 08:00 | 39.31 | 2.52 | 2.52 | 36.79 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 09:00 | 40.25 | 36.71 | 36.71 | 3.54 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 10:00 | 41.55 | 71.4 | 71.4 | 0 | 29.85 | 0 | 40.87 | 0 | 0
2025-01-27 11:00 | 42.03 | 48.64 | 48.64 | 0 | 6.62 | 0 | 47.15 | 0 | 0
2025-01-27 12:00 | 42.49 | 31.4 | 31.4 | 0 | 0 | 11.09 | 35.48 | 0 | 0
2025-01-27 13:00 | 43.27 | 14.53 | 14.53 | 6.91 | 0 | 21.83 | 12.51 | 0 | 0
2025-01-27 14:00 | 44.19 | 8.6 | 8.6 | 35.59 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 15:00 | 44.01 | 6.22 | 6.22 | 37.79 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 16:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 17:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 18:00 | 42.67 | 0 | 0 | 42.67 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 19:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 22:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 12.51 | 0 | 0
2025-01-27 23:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 | 36.85 | 0 | 0 | 36.85 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 01:00 | 36.62 | 0 | 0 | 36.62 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 02:00 | 36.29 | 0 | 0 | 36.29 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 03:00 | 36.71 | 0 | 0 | 36.71 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 04:00 | 36.67 | 0 | 0 | 36.67 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 05:00 | 36.97 | 0 | 0 | 36.97 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 07:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 08:00 | 39.39 | 24.32 | 24.32 | 15.07 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 09:00 | 40.35 | 69.08 | 69.08 | 0 | 28.72 | 0 | 39.79 | 0 | 0
2025-01-28 10:00 | 41.39 | 33.94 | 33.94 | 0 | 0 | 7.45 | 31.96 | 0 | 0
2025-01-28 11:00 | 40.91 | 24.24 | 24.24 | 0 | 0 | 16.67 | 14.41 | 0 | 0
2025-01-28 12:00 | 42.55 | 28.78 | 28.78 | 11.96 | 0 | 1.81 | 12.51 | 0 | 0
2025-01-28 13:00 | 42.23 | 21.07 | 21.07 | 21.16 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 14:00 | 43.72 | 25.41 | 25.41 | 18.31 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 15:00 | 43.83 | 45.56 | 45.56 | 0 | 1.74 | 0 | 14.16 | 0 | 0
2025-01-28 16:00 | 44.22 | 14.25 | 14.25 | 28.4 | 0 | 1.57 | 12.51 | 0 | 0
2025-01-28 17:00 | 43.92 | 0 | 0 | 43.92 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 18:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 19:00 | 41.71 | 0 | 0 | 41.71 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 20:00 | 41.32 | 0 | 0 | 41.32 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 21:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 22:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 12.51 | 0 | 0
2025-01-28 23:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 01:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 02:00 | 37.15 | 0 | 0 | 37.15 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 03:00 | 36.22 | 0 | 0 | 36.22 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 04:00 | 37.3 | 0 | 0 | 37.3 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 05:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 06:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 07:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 08:00 | 38.83 | 21.81 | 21.81 | 17.02 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 09:00 | 39.91 | 72.61 | 72.61 | 0 | 32.7 | 0 | 43.57 | 0 | 0
2025-01-29 10:00 | 41.4 | 61.64 | 61.64 | 0 | 20.24 | 0 | 62.8 | 0 | 0
2025-01-29 11:00 | 41.54 | 59.08 | 59.08 | 0 | 17.54 | 0 | 79.47 | 0 | 0
2025-01-29 12:00 | 43.01 | 52.21 | 52.21 | 0 | 9.2 | 0 | 88.21 | 0 | 0
2025-01-29 13:00 | 42.78 | 57.38 | 57.38 | 0 | 14.6 | 0 | 102.08 | 0 | 0
2025-01-29 14:00 | 43.68 | 41.32 | 41.32 | 0 | 0 | 2.36 | 99.59 | 0 | 0
2025-01-29 15:00 | 43.97 | 40.72 | 40.72 | 0 | 0 | 3.25 | 96.18 | 0 | 0
2025-01-29 16:00 | 45.01 | 12.53 | 12.53 | 0 | 0 | 32.47 | 61.99 | 0 | 0
2025-01-29 17:00 | 42.71 | 0 | 0 | 0 | 0 | 42.71 | 17.03 | 0 | 0
2025-01-29 18:00 | 43.53 | 0 | 0 | 39.23 | 0 | 4.3 | 12.51 | 0 | 0
2025-01-29 19:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 21:00 | 40.24 | 0 | 0 | 40.24 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 22:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 12.51 | 0 | 0
2025-01-29 23:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 01:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 02:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 03:00 | 36.39 | 0 | 0 | 36.39 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 04:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 05:00 | 36.63 | 0 | 0 | 36.63 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 06:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 07:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 08:00 | 39.24 | 14.56 | 14.56 | 24.69 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 09:00 | 40.11 | 25.94 | 25.94 | 14.17 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 10:00 | 40.6 | 49.76 | 49.76 | 0 | 9.15 | 0 | 21.21 | 0 | 0
2025-01-30 11:00 | 41.94 | 49.77 | 49.77 | 0 | 7.82 | 0 | 28.64 | 0 | 0
2025-01-30 12:00 | 42.05 | 44.9 | 44.9 | 0 | 2.85 | 0 | 31.34 | 0 | 0
2025-01-30 13:00 | 43 | 53.23 | 53.23 | 0 | 10.24 | 0 | 41.07 | 0 | 0
2025-01-30 14:00 | 43.95 | 53.8 | 53.8 | 0 | 9.85 | 0 | 50.43 | 0 | 0
2025-01-30 15:00 | 44.63 | 65.15 | 65.15 | 0 | 20.52 | 0 | 69.93 | 0 | 0
2025-01-30 16:00 | 45.24 | 36.99 | 36.99 | 0 | 0 | 8.26 | 61.24 | 0 | 0
2025-01-30 17:00 | 43.16 | 0 | 0 | 0 | 0 | 43.16 | 15.81 | 0 | 0
2025-01-30 18:00 | 43.56 | 0 | 0 | 40.43 | 0 | 3.13 | 12.51 | 0 | 0
2025-01-30 19:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 20:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 21:00 | 40.43 | 0 | 0 | 40.43 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 22:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 12.51 | 0 | 0
2025-01-30 23:00 | 38.48 | 0 | 0 | 38.48 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 | 37.57 | 0 | 0 | 37.57 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 01:00 | 36.49 | 0 | 0 | 36.49 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 02:00 | 36.07 | 0 | 0 | 36.07 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 03:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 04:00 | 36.71 | 0 | 0 | 36.71 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 05:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 06:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 07:00 | 38.98 | 0 | 0 | 38.98 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 08:00 | 39.68 | 27.73 | 27.73 | 11.95 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 09:00 | 40.43 | 79.33 | 79.33 | 0 | 38.9 | 0 | 49.47 | 0 | 0
2025-01-31 10:00 | 42.63 | 77.95 | 77.95 | 0 | 35.32 | 0 | 83.02 | 0 | 0
2025-01-31 11:00 | 44.05 | 68.62 | 68.62 | 0 | 24.57 | 0 | 106.37 | 0 | 0
2025-01-31 12:00 | 44.64 | 61.77 | 51.19 | 0 | 6.55 | 0 | 112.59 | 10.57 | 0
2025-01-31 13:00 | 45.79 | 57.65 | 45.79 | 0 | 0 | 0 | 112.59 | 11.87 | 0
2025-01-31 14:00 | 46.51 | 41.5 | 41.5 | 0 | 0 | 5.01 | 107.32 | 0 | 0
2025-01-31 15:00 | 46.66 | 17.34 | 17.34 | 0 | 0 | 29.32 | 76.46 | 0 | 0
2025-01-31 16:00 | 46.2 | 19.84 | 19.84 | 0 | 0 | 26.35 | 48.72 | 0 | 0
2025-01-31 17:00 | 45.6 | 0 | 0 | 11.2 | 0 | 34.4 | 12.51 | 0 | 0
2025-01-31 18:00 | 44.65 | 0 | 0 | 44.65 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 19:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 20:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 21:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 22:00 | 39.19 | 0 | 0 | 39.19 | 0 | 0 | 12.51 | 0 | 0
2025-01-31 23:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 01:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 02:00 | 36.73 | 0 | 0 | 36.73 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 03:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 04:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 05:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 06:00 | 37.77 | 0 | 0 | 37.77 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 07:00 | 38.98 | 0 | 0 | 38.98 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 08:00 | 39.01 | 23.06 | 23.06 | 15.96 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 09:00 | 40.19 | 68.7 | 68.7 | 0 | 28.51 | 0 | 39.59 | 0 | 0
2025-02-01 10:00 | 40.33 | 69.47 | 69.47 | 0 | 29.15 | 0 | 67.28 | 0 | 0
2025-02-01 11:00 | 41.78 | 48.34 | 48.34 | 0 | 6.56 | 0 | 73.51 | 0 | 0
2025-02-01 12:00 | 42.18 | 44.42 | 44.42 | 0 | 2.25 | 0 | 75.65 | 0 | 0
2025-02-01 13:00 | 42.27 | 53.73 | 53.73 | 0 | 11.46 | 0 | 86.54 | 0 | 0
2025-02-01 14:00 | 42.82 | 62.52 | 62.52 | 0 | 19.7 | 0 | 105.25 | 0 | 0
2025-02-01 15:00 | 42.94 | 74.18 | 50.66 | 0 | 7.72 | 0 | 112.59 | 23.51 | 0
2025-02-01 16:00 | 42.8 | 40.83 | 40.83 | 0 | 0 | 1.97 | 110.52 | 0 | 0
2025-02-01 17:00 | 43.53 | 0 | 0 | 0 | 0 | 43.53 | 64.7 | 0 | 0
2025-02-01 18:00 | 42.12 | 0 | 0 | 0 | 0 | 42.12 | 20.36 | 0 | 0
2025-02-01 19:00 | 41.43 | 0 | 0 | 33.98 | 0 | 7.46 | 12.51 | 0 | 0
2025-02-01 20:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 22:00 | 39.06 | 0 | 0 | 39.06 | 0 | 0 | 12.51 | 0 | 0
2025-02-01 23:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 01:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 02:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 03:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 04:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 05:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 06:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 08:00 | 38.04 | 36.21 | 36.21 | 1.83 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 09:00 | 39.01 | 85.37 | 85.37 | 0 | 46.36 | 0 | 56.55 | 0 | 0
2025-02-02 10:00 | 40.53 | 79.06 | 79.06 | 0 | 38.52 | 0 | 93.15 | 0 | 0
2025-02-02 11:00 | 41.53 | 15.34 | 15.34 | 0 | 0 | 26.19 | 65.58 | 0 | 0
2025-02-02 12:00 | 42.47 | 38.81 | 38.81 | 0 | 0 | 3.66 | 61.73 | 0 | 0
2025-02-02 13:00 | 42.81 | 62.9 | 62.9 | 0 | 20.09 | 0 | 80.81 | 0 | 0
2025-02-02 14:00 | 42.66 | 72.15 | 72.15 | 0 | 29.48 | 0 | 108.82 | 0 | 0
2025-02-02 15:00 | 43.46 | 56.47 | 47.42 | 0 | 3.97 | 0 | 112.59 | 9.04 | 0
2025-02-02 16:00 | 43.37 | 45.51 | 43.37 | 0 | 0 | 0 | 112.59 | 2.14 | 0
2025-02-02 17:00 | 42.67 | 0 | 0 | 0 | 0 | 42.67 | 67.68 | 0 | 0
2025-02-02 18:00 | 42.6 | 0 | 0 | 0 | 0 | 42.6 | 22.83 | 0 | 0
2025-02-02 19:00 | 41.66 | 0 | 0 | 31.85 | 0 | 9.81 | 12.51 | 0 | 0
2025-02-02 20:00 | 40.52 | 0 | 0 | 40.52 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 21:00 | 40.36 | 0 | 0 | 40.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 22:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 12.51 | 0 | 0
2025-02-02 23:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 01:00 | 36.02 | 0 | 0 | 36.02 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 02:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 03:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 04:00 | 36.72 | 0 | 0 | 36.72 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 06:00 | 37.02 | 0 | 0 | 37.02 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 07:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 08:00 | 38.76 | 1.4 | 1.4 | 37.35 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 09:00 | 41.19 | 8.34 | 8.34 | 32.85 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 10:00 | 41.6 | 11.46 | 11.46 | 30.14 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 11:00 | 41.15 | 28.92 | 28.92 | 12.23 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 12:00 | 41.72 | 31.18 | 31.18 | 10.54 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 13:00 | 41.73 | 38.39 | 38.39 | 3.34 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 14:00 | 41.59 | 28.73 | 28.73 | 12.86 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 15:00 | 42.57 | 22.59 | 22.59 | 19.98 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 16:00 | 42.05 | 44.68 | 44.68 | 0 | 2.63 | 0 | 15.01 | 0 | 0
2025-02-03 17:00 | 42.26 | 0.56 | 0.56 | 39.33 | 0 | 2.37 | 12.51 | 0 | 0
2025-02-03 18:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 19:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 20:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 21:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 22:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 12.51 | 0 | 0
2025-02-03 23:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 01:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 02:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 03:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 04:00 | 36.24 | 0 | 0 | 36.24 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 06:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 07:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 08:00 | 39.4 | 4.79 | 4.79 | 34.61 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 09:00 | 41.21 | 25.48 | 25.48 | 15.73 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 10:00 | 41.95 | 40.94 | 40.94 | 1.01 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 11:00 | 42.27 | 15.3 | 15.3 | 26.98 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 12:00 | 43.61 | 27.48 | 27.48 | 16.14 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 13:00 | 44.86 | 20.15 | 20.15 | 24.71 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 14:00 | 45.29 | 22.48 | 22.48 | 22.81 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 15:00 | 43.84 | 12.55 | 12.55 | 31.29 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 16:00 | 43.85 | 9.39 | 9.39 | 34.46 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 17:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 18:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 19:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 20:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 21:00 | 40.65 | 0 | 0 | 40.65 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 22:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 12.51 | 0 | 0
2025-02-04 23:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 | 37.55 | 0 | 0 | 37.55 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 01:00 | 36.95 | 0 | 0 | 36.95 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 02:00 | 36.52 | 0 | 0 | 36.52 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 03:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 04:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 05:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 06:00 | 37.64 | 0 | 0 | 37.64 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 07:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 08:00 | 39.24 | 12.08 | 12.08 | 27.16 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 09:00 | 39.32 | 13.84 | 13.84 | 25.48 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 10:00 | 41.06 | 36.55 | 36.55 | 4.51 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 11:00 | 41.91 | 36.66 | 36.66 | 5.25 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 12:00 | 42.64 | 43.01 | 43.01 | 0 | 0.37 | 0 | 12.86 | 0 | 0
2025-02-05 13:00 | 43.92 | 42.44 | 42.44 | 1.14 | 0 | 0.33 | 12.51 | 0 | 0
2025-02-05 14:00 | 45.66 | 37.58 | 37.58 | 8.08 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 15:00 | 45.14 | 29.01 | 29.01 | 16.13 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 16:00 | 45.64 | 40.98 | 40.98 | 4.67 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 17:00 | 44.72 | 1.01 | 1.01 | 43.71 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 18:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 19:00 | 42.37 | 0 | 0 | 42.37 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 20:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 21:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 22:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 12.51 | 0 | 0
2025-02-05 23:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 01:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 02:00 | 36.43 | 0 | 0 | 36.43 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 03:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 04:00 | 37.03 | 0 | 0 | 37.03 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 05:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 06:00 | 37.49 | 0 | 0 | 37.49 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 07:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 08:00 | 39.71 | 41.09 | 41.09 | 0 | 1.38 | 0 | 13.82 | 0 | 0
2025-02-06 09:00 | 40.62 | 89.38 | 89.38 | 0 | 48.76 | 0 | 60.14 | 0 | 0
2025-02-06 10:00 | 41.97 | 84.52 | 84.52 | 0 | 42.55 | 0 | 100.57 | 0 | 0
2025-02-06 11:00 | 42.64 | 75.48 | 55.3 | 0 | 12.66 | 0 | 112.59 | 20.18 | 0
2025-02-06 12:00 | 42.2 | 67.93 | 42.2 | 0 | 0 | 0 | 112.59 | 25.73 | 0
2025-02-06 13:00 | 44.08 | 72.02 | 44.08 | 0 | 0 | 0 | 112.59 | 27.94 | 0
2025-02-06 14:00 | 43.3 | 81.8 | 43.3 | 0 | 0 | 0 | 112.59 | 38.49 | 0
2025-02-06 15:00 | 44.21 | 88.01 | 44.21 | 0 | 0 | 0 | 112.59 | 43.81 | 0
2025-02-06 16:00 | 43.6 | 62.85 | 43.6 | 0 | 0 | 0 | 112.59 | 19.25 | 0
2025-02-06 17:00 | 43.03 | 0.62 | 0.62 | 0 | 0 | 42.41 | 67.95 | 0 | 0
2025-02-06 18:00 | 41.8 | 0 | 0 | 0 | 0 | 41.8 | 23.95 | 0 | 0
2025-02-06 19:00 | 41.92 | 0 | 0 | 31.05 | 0 | 10.87 | 12.51 | 0 | 0
2025-02-06 20:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 21:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 22:00 | 40.19 | 0 | 0 | 40.19 | 0 | 0 | 12.51 | 0 | 0
2025-02-06 23:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 | 38.05 | 0 | 0 | 38.05 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 01:00 | 37 | 0 | 0 | 37 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 02:00 | 36.7 | 0 | 0 | 36.7 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 03:00 | 37.29 | 0 | 0 | 37.29 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 04:00 | 37 | 0 | 0 | 37 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 05:00 | 38.23 | 0 | 0 | 38.23 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 06:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 07:00 | 39.08 | 0 | 0 | 39.08 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 08:00 | 39.4 | 40.97 | 40.97 | 0 | 1.58 | 0 | 14.01 | 0 | 0
2025-02-07 09:00 | 40.53 | 68.45 | 68.45 | 0 | 27.91 | 0 | 40.53 | 0 | 0
2025-02-07 10:00 | 40.66 | 15.93 | 15.93 | 0 | 0 | 24.73 | 14.5 | 0 | 0
2025-02-07 11:00 | 41.53 | 48.48 | 48.48 | 0 | 6.95 | 0 | 21.1 | 0 | 0
2025-02-07 12:00 | 42.05 | 63 | 63 | 0 | 20.95 | 0 | 41 | 0 | 0
2025-02-07 13:00 | 42.09 | 79.24 | 79.24 | 0 | 37.14 | 0 | 76.29 | 0 | 0
2025-02-07 14:00 | 43.09 | 78.03 | 78.03 | 0 | 34.94 | 0 | 109.49 | 0 | 0
2025-02-07 15:00 | 43.17 | 55.39 | 46.44 | 0 | 3.27 | 0 | 112.59 | 8.95 | 0
2025-02-07 16:00 | 43.06 | 0.15 | 0.15 | 0 | 0 | 42.91 | 67.42 | 0 | 0
2025-02-07 17:00 | 43.28 | 0 | 0 | 0 | 0 | 43.28 | 21.87 | 0 | 0
2025-02-07 18:00 | 42.83 | 0 | 0 | 33.94 | 0 | 8.89 | 12.51 | 0 | 0
2025-02-07 19:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 20:00 | 41.07 | 0 | 0 | 41.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 21:00 | 39.82 | 0 | 0 | 39.82 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 22:00 | 39.36 | 0 | 0 | 39.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-07 23:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 01:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 03:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 04:00 | 35.97 | 0 | 0 | 35.97 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 05:00 | 36.39 | 0 | 0 | 36.39 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 06:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 07:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 08:00 | 39.53 | 26.24 | 26.24 | 13.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 09:00 | 39.53 | 62.76 | 62.76 | 0 | 23.23 | 0 | 34.58 | 0 | 0
2025-02-08 10:00 | 40.94 | 69.38 | 69.38 | 0 | 28.44 | 0 | 61.6 | 0 | 0
2025-02-08 11:00 | 42.63 | 64.2 | 64.2 | 0 | 21.57 | 0 | 82.08 | 0 | 0
2025-02-08 12:00 | 42.6 | 58.78 | 58.78 | 0 | 16.18 | 0 | 97.45 | 0 | 0
2025-02-08 13:00 | 42.68 | 68.03 | 58.62 | 0 | 15.93 | 0 | 112.59 | 9.41 | 0
2025-02-08 14:00 | 42.63 | 68.69 | 42.63 | 0 | 0 | 0 | 112.59 | 26.06 | 0
2025-02-08 15:00 | 42.74 | 76.88 | 42.74 | 0 | 0 | 0 | 112.59 | 34.14 | 0
2025-02-08 16:00 | 41.79 | 59.93 | 41.79 | 0 | 0 | 0 | 112.59 | 18.14 | 0
2025-02-08 17:00 | 42.73 | 0.95 | 0.95 | 0 | 0 | 41.77 | 68.62 | 0 | 0
2025-02-08 18:00 | 42.61 | 0 | 0 | 0 | 0 | 42.61 | 23.77 | 0 | 0
2025-02-08 19:00 | 40.84 | 0 | 0 | 30.15 | 0 | 10.69 | 12.51 | 0 | 0
2025-02-08 20:00 | 40.62 | 0 | 0 | 40.62 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 21:00 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 22:00 | 38.92 | 0 | 0 | 38.92 | 0 | 0 | 12.51 | 0 | 0
2025-02-08 23:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 01:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 02:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 03:00 | 36.84 | 0 | 0 | 36.84 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 04:00 | 35.85 | 0 | 0 | 35.85 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 05:00 | 36.95 | 0 | 0 | 36.95 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 06:00 | 38.64 | 0 | 0 | 38.64 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 07:00 | 37.41 | 0 | 0 | 37.41 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 08:00 | 39.54 | 5.15 | 5.15 | 34.38 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 09:00 | 40.14 | 46.9 | 46.9 | 0 | 6.76 | 0 | 18.94 | 0 | 0
2025-02-09 10:00 | 42.17 | 63.94 | 63.94 | 0 | 21.77 | 0 | 39.62 | 0 | 0
2025-02-09 11:00 | 42.42 | 80.13 | 80.13 | 0 | 37.71 | 0 | 75.44 | 0 | 0
2025-02-09 12:00 | 43.84 | 68.89 | 68.89 | 0 | 25.05 | 0 | 99.24 | 0 | 0
2025-02-09 13:00 | 44.6 | 37.37 | 37.37 | 0 | 0 | 7.23 | 91.64 | 0 | 0
2025-02-09 14:00 | 45.67 | 11.68 | 11.68 | 0 | 0 | 33.99 | 55.86 | 0 | 0
2025-02-09 15:00 | 44.8 | 13.07 | 13.07 | 0 | 0 | 31.73 | 22.46 | 0 | 0
2025-02-09 16:00 | 44.94 | 0.1 | 0.1 | 35.38 | 0 | 9.46 | 12.51 | 0 | 0
2025-02-09 17:00 | 43.57 | 0.4 | 0.4 | 43.17 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 18:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 19:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 20:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 21:00 | 40.71 | 0 | 0 | 40.71 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 22:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 12.51 | 0 | 0
2025-02-09 23:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 01:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 02:00 | 36.33 | 0 | 0 | 36.33 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 04:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 05:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 06:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 08:00 | 39.92 | 46.69 | 46.69 | 0 | 6.77 | 0 | 18.94 | 0 | 0
2025-02-10 09:00 | 41.03 | 87.4 | 87.4 | 0 | 46.38 | 0 | 63 | 0 | 0
2025-02-10 10:00 | 42.82 | 83.84 | 83.84 | 0 | 41.02 | 0 | 101.96 | 0 | 0
2025-02-10 11:00 | 43.14 | 73.06 | 54.33 | 0 | 11.19 | 0 | 112.59 | 18.73 | 0
2025-02-10 12:00 | 44.14 | 67.79 | 44.14 | 0 | 0 | 0 | 112.59 | 23.65 | 0
2025-02-10 13:00 | 45.87 | 71.3 | 45.87 | 0 | 0 | 0 | 112.59 | 25.43 | 0
2025-02-10 14:00 | 44.86 | 79.67 | 44.86 | 0 | 0 | 0 | 112.59 | 34.82 | 0
2025-02-10 15:00 | 44.72 | 84.97 | 44.72 | 0 | 0 | 0 | 112.59 | 40.25 | 0
2025-02-10 16:00 | 45.18 | 63.83 | 45.18 | 0 | 0 | 0 | 112.59 | 18.65 | 0
2025-02-10 17:00 | 44.73 | 1.37 | 1.37 | 0 | 0 | 43.36 | 66.95 | 0 | 0
2025-02-10 18:00 | 43.54 | 0 | 0 | 0 | 0 | 43.54 | 21.11 | 0 | 0
2025-02-10 19:00 | 42.39 | 0 | 0 | 34.22 | 0 | 8.17 | 12.51 | 0 | 0
2025-02-10 20:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 21:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 22:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 12.51 | 0 | 0
2025-02-10 23:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 01:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 02:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 03:00 | 36.4 | 0 | 0 | 36.4 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 04:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 05:00 | 38.49 | 0 | 0 | 38.49 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 06:00 | 38.35 | 0 | 0 | 38.35 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 07:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 08:00 | 39.56 | 27.92 | 27.92 | 11.64 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 09:00 | 40.62 | 20.51 | 20.51 | 20.11 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 10:00 | 41.74 | 38.6 | 38.6 | 3.14 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 11:00 | 42.66 | 44.1 | 44.1 | 0 | 1.44 | 0 | 13.88 | 0 | 0
2025-02-11 12:00 | 44.17 | 33.39 | 33.39 | 9.48 | 0 | 1.3 | 12.51 | 0 | 0
2025-02-11 13:00 | 43.52 | 54.17 | 54.17 | 0 | 10.65 | 0 | 22.62 | 0 | 0
2025-02-11 14:00 | 45.24 | 73.51 | 73.51 | 0 | 28.27 | 0 | 49.48 | 0 | 0
2025-02-11 15:00 | 44.77 | 96.26 | 96.26 | 0 | 51.49 | 0 | 98.4 | 0 | 0
2025-02-11 16:00 | 45 | 71.46 | 59.94 | 0 | 14.94 | 0 | 112.59 | 11.52 | 0
2025-02-11 17:00 | 43.82 | 4.65 | 4.65 | 0 | 0 | 39.17 | 71.36 | 0 | 0
2025-02-11 18:00 | 44.38 | 0 | 0 | 0 | 0 | 44.38 | 24.65 | 0 | 0
2025-02-11 19:00 | 43.47 | 0 | 0 | 31.94 | 0 | 11.53 | 12.51 | 0 | 0
2025-02-11 20:00 | 42.34 | 0 | 0 | 42.34 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 21:00 | 40.07 | 0 | 0 | 40.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 12.51 | 0 | 0
2025-02-11 23:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 | 37.33 | 0 | 0 | 37.33 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 01:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 02:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 03:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 04:00 | 37.3 | 0 | 0 | 37.3 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 05:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 06:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 07:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 08:00 | 38.23 | 20.27 | 20.27 | 17.96 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 09:00 | 40.34 | 44.77 | 44.77 | 0 | 4.43 | 0 | 16.71 | 0 | 0
2025-02-12 10:00 | 41.23 | 20.02 | 20.02 | 17.22 | 0 | 3.99 | 12.51 | 0 | 0
2025-02-12 11:00 | 41.17 | 29.6 | 29.6 | 11.58 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 12:00 | 42.7 | 16.46 | 16.46 | 26.24 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 13:00 | 43.74 | 49.2 | 49.2 | 0 | 5.47 | 0 | 17.7 | 0 | 0
2025-02-12 14:00 | 42.85 | 92.14 | 92.14 | 0 | 49.29 | 0 | 64.53 | 0 | 0
2025-02-12 15:00 | 43.65 | 100.86 | 94.24 | 0 | 50.59 | 0 | 112.59 | 6.62 | 0
2025-02-12 16:00 | 42.93 | 83.76 | 42.93 | 0 | 0 | 0 | 112.59 | 40.83 | 0
2025-02-12 17:00 | 42.78 | 5.42 | 5.42 | 0 | 0 | 37.36 | 73.27 | 0 | 0
2025-02-12 18:00 | 43.4 | 0 | 0 | 0 | 0 | 43.4 | 27.59 | 0 | 0
2025-02-12 19:00 | 41.78 | 0 | 0 | 27.45 | 0 | 14.32 | 12.51 | 0 | 0
2025-02-12 20:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 22:00 | 40.59 | 0 | 0 | 40.59 | 0 | 0 | 12.51 | 0 | 0
2025-02-12 23:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 01:00 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 02:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 03:00 | 37.72 | 0 | 0 | 37.72 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 04:00 | 37.09 | 0 | 0 | 37.09 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 05:00 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 06:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 07:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 08:00 | 40.24 | 8.21 | 8.21 | 32.02 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 09:00 | 41 | 16.36 | 16.36 | 24.64 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 10:00 | 42.19 | 6.13 | 6.13 | 36.06 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 11:00 | 42.8 | 51.45 | 51.45 | 0 | 8.65 | 0 | 20.73 | 0 | 0
2025-02-13 12:00 | 43.87 | 68.26 | 68.26 | 0 | 24.39 | 0 | 43.9 | 0 | 0
2025-02-13 13:00 | 44.03 | 64.78 | 64.78 | 0 | 20.75 | 0 | 63.61 | 0 | 0
2025-02-13 14:00 | 45.75 | 59.18 | 59.18 | 0 | 13.43 | 0 | 76.37 | 0 | 0
2025-02-13 15:00 | 43.99 | 25.63 | 25.63 | 0 | 0 | 18.36 | 57.04 | 0 | 0
2025-02-13 16:00 | 45.26 | 54.09 | 54.09 | 0 | 8.82 | 0 | 65.42 | 0 | 0
2025-02-13 17:00 | 44.92 | 1.17 | 1.17 | 0 | 0 | 43.76 | 19.37 | 0 | 0
2025-02-13 18:00 | 43.19 | 0 | 0 | 36.67 | 0 | 6.51 | 12.51 | 0 | 0
2025-02-13 19:00 | 43.92 | 0 | 0 | 43.92 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 20:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 21:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 22:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 12.51 | 0 | 0
2025-02-13 23:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 01:00 | 37.87 | 0 | 0 | 37.87 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 02:00 | 38 | 0 | 0 | 38 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 03:00 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 04:00 | 36.84 | 0 | 0 | 36.84 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 05:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 06:00 | 38.72 | 0 | 0 | 38.72 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 07:00 | 39.36 | 0 | 0 | 39.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 08:00 | 40.31 | 13.51 | 13.51 | 26.8 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 09:00 | 40.78 | 1.76 | 1.76 | 39.02 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 10:00 | 41.43 | 45.83 | 45.83 | 0 | 4.41 | 0 | 16.7 | 0 | 0
2025-02-14 11:00 | 42.38 | 31.82 | 31.82 | 6.59 | 0 | 3.98 | 12.51 | 0 | 0
2025-02-14 12:00 | 42.79 | 34.43 | 34.43 | 8.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 13:00 | 44.33 | 34.05 | 34.05 | 10.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 14:00 | 44.56 | 22.54 | 22.54 | 22.02 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 15:00 | 44.51 | 53.08 | 53.08 | 0 | 8.57 | 0 | 20.65 | 0 | 0
2025-02-14 16:00 | 43.12 | 59.61 | 59.61 | 0 | 16.49 | 0 | 36.32 | 0 | 0
2025-02-14 17:00 | 43.59 | 0.97 | 0.97 | 20 | 0 | 22.62 | 12.51 | 0 | 0
2025-02-14 18:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 19:00 | 42.48 | 0 | 0 | 42.48 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 20:00 | 42.07 | 0 | 0 | 42.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 21:00 | 40.22 | 0 | 0 | 40.22 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 22:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 12.51 | 0 | 0
2025-02-14 23:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 | 38.47 | 0 | 0 | 38.47 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 01:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 02:00 | 38.11 | 0 | 0 | 38.11 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 03:00 | 37.07 | 0 | 0 | 37.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 04:00 | 37.05 | 0 | 0 | 37.05 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 05:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 06:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 07:00 | 39.06 | 0.02 | 0.02 | 39.03 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 08:00 | 39.83 | 23.32 | 23.32 | 16.51 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 09:00 | 41.76 | 68.23 | 68.23 | 0 | 26.46 | 0 | 37.65 | 0 | 0
2025-02-15 10:00 | 41.98 | 71.9 | 71.9 | 0 | 29.91 | 0 | 66.07 | 0 | 0
2025-02-15 11:00 | 44.14 | 53.27 | 53.27 | 0 | 9.13 | 0 | 74.74 | 0 | 0
2025-02-15 12:00 | 43.86 | 54.72 | 54.72 | 0 | 10.86 | 0 | 85.06 | 0 | 0
2025-02-15 13:00 | 45.34 | 31.92 | 31.92 | 0 | 0 | 13.42 | 70.93 | 0 | 0
2025-02-15 14:00 | 45.03 | 49 | 49 | 0 | 3.97 | 0 | 74.71 | 0 | 0
2025-02-15 15:00 | 45.47 | 73.4 | 73.4 | 0 | 27.94 | 0 | 101.24 | 0 | 0
2025-02-15 16:00 | 44.49 | 61.85 | 56.43 | 0 | 11.94 | 0 | 112.59 | 5.42 | 0
2025-02-15 17:00 | 44.02 | 0.75 | 0.75 | 0 | 0 | 43.27 | 67.04 | 0 | 0
2025-02-15 18:00 | 44.04 | 0 | 0 | 0 | 0 | 44.04 | 20.69 | 0 | 0
2025-02-15 19:00 | 43.48 | 0 | 0 | 35.72 | 0 | 7.77 | 12.51 | 0 | 0
2025-02-15 20:00 | 42.06 | 0 | 0 | 42.06 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 21:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 22:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 12.51 | 0 | 0
2025-02-15 23:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 01:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 02:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 03:00 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 04:00 | 36.27 | 0 | 0 | 36.27 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 05:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 06:00 | 38.32 | 0 | 0 | 38.32 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 07:00 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 08:00 | 39.5 | 1.21 | 1.21 | 38.3 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 09:00 | 41.14 | 2.78 | 2.78 | 38.37 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 10:00 | 43.34 | 6.08 | 6.08 | 37.26 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 11:00 | 43.82 | 5.75 | 5.75 | 38.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 12:00 | 44.85 | 9.5 | 9.5 | 35.35 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 13:00 | 45.4 | 51.23 | 51.23 | 0 | 5.83 | 0 | 18.05 | 0 | 0
2025-02-16 14:00 | 45.99 | 45.33 | 45.33 | 0 | 0 | 0.66 | 17.35 | 0 | 0
2025-02-16 15:00 | 46.38 | 36.31 | 36.31 | 5.48 | 0 | 4.6 | 12.51 | 0 | 0
2025-02-16 16:00 | 45.42 | 29.12 | 29.12 | 16.3 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 17:00 | 45.78 | 2.11 | 2.11 | 43.66 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 18:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 19:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 20:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 21:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 22:00 | 40.22 | 0 | 0 | 40.22 | 0 | 0 | 12.51 | 0 | 0
2025-02-16 23:00 | 38.92 | 0 | 0 | 38.92 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 01:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 02:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 03:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 04:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 05:00 | 38.19 | 0 | 0 | 38.19 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 06:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 07:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 08:00 | 39.88 | 0.09 | 0.09 | 39.79 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 09:00 | 41.87 | 1.72 | 1.72 | 40.15 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 10:00 | 42.4 | 3.04 | 3.04 | 39.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 11:00 | 43.1 | 4.06 | 4.06 | 39.04 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 12:00 | 44.3 | 4.48 | 4.48 | 39.82 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 13:00 | 43.64 | 47.2 | 47.2 | 0 | 3.56 | 0 | 15.89 | 0 | 0
2025-02-17 14:00 | 45.08 | 46.46 | 46.46 | 0 | 1.37 | 0 | 17.2 | 0 | 0
2025-02-17 15:00 | 46.24 | 35.17 | 35.17 | 6.62 | 0 | 4.45 | 12.51 | 0 | 0
2025-02-17 16:00 | 45.17 | 34.89 | 34.89 | 10.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 17:00 | 44.73 | 1.98 | 1.98 | 42.75 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 18:00 | 44.32 | 0 | 0 | 44.32 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 19:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 20:00 | 41.24 | 0 | 0 | 41.24 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 21:00 | 40.37 | 0 | 0 | 40.37 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 22:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 12.51 | 0 | 0
2025-02-17 23:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 01:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 02:00 | 36.54 | 0 | 0 | 36.54 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 03:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 04:00 | 36.13 | 0 | 0 | 36.13 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 05:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 06:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 07:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 08:00 | 40.9 | 5.26 | 5.26 | 35.64 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 09:00 | 42.06 | 7.33 | 7.33 | 34.73 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 10:00 | 42.51 | 17.9 | 17.9 | 24.61 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 11:00 | 42.61 | 28.85 | 28.85 | 13.75 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 12:00 | 44.94 | 23.36 | 23.36 | 21.58 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 13:00 | 45.65 | 18.86 | 18.86 | 26.8 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 14:00 | 46 | 14.62 | 14.62 | 31.38 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 15:00 | 46.5 | 9.8 | 9.8 | 36.7 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 16:00 | 45.27 | 2.02 | 2.02 | 43.25 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 17:00 | 46.38 | 0.05 | 0.05 | 46.33 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 18:00 | 44.15 | 0 | 0 | 44.15 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 19:00 | 44.05 | 0 | 0 | 44.05 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 20:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 21:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 22:00 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 12.51 | 0 | 0
2025-02-18 23:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 01:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 02:00 | 37.51 | 0 | 0 | 37.51 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 03:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 04:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 05:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 06:00 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 07:00 | 39.66 | 0.6 | 0.6 | 39.06 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 08:00 | 40.53 | 25.45 | 25.45 | 15.08 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 09:00 | 40.56 | 65.5 | 65.5 | 0 | 24.94 | 0 | 36.2 | 0 | 0
2025-02-19 10:00 | 42 | 71 | 71 | 0 | 28.99 | 0 | 63.75 | 0 | 0
2025-02-19 11:00 | 43.03 | 73.02 | 73.02 | 0 | 29.99 | 0 | 92.24 | 0 | 0
2025-02-19 12:00 | 43.96 | 68.64 | 65.38 | 0 | 21.42 | 0 | 112.59 | 3.26 | 0
2025-02-19 13:00 | 44.08 | 71.86 | 44.08 | 0 | 0 | 0 | 112.59 | 27.78 | 0
2025-02-19 14:00 | 44.85 | 68.45 | 44.85 | 0 | 0 | 0 | 112.59 | 23.6 | 0
2025-02-19 15:00 | 44.94 | 65.61 | 44.94 | 0 | 0 | 0 | 112.59 | 20.67 | 0
2025-02-19 16:00 | 45.55 | 32.82 | 32.82 | 0 | 0 | 12.74 | 99.18 | 0 | 0
2025-02-19 17:00 | 45.17 | 4.9 | 4.9 | 0 | 0 | 40.28 | 56.79 | 0 | 0
2025-02-19 18:00 | 44.07 | 0 | 0 | 2 | 0 | 42.06 | 12.51 | 0 | 0
2025-02-19 19:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 20:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 21:00 | 40.94 | 0 | 0 | 40.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 22:00 | 39.75 | 0 | 0 | 39.75 | 0 | 0 | 12.51 | 0 | 0
2025-02-19 23:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 01:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 02:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 03:00 | 37.86 | 0 | 0 | 37.86 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 04:00 | 36.83 | 0 | 0 | 36.83 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 05:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 06:00 | 38.54 | 0 | 0 | 38.54 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 07:00 | 39.65 | 1.23 | 1.23 | 38.43 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 08:00 | 40.45 | 58.24 | 58.24 | 0 | 17.79 | 0 | 29.41 | 0 | 0
2025-02-20 09:00 | 40.8 | 77.64 | 77.64 | 0 | 36.84 | 0 | 64.41 | 0 | 0
2025-02-20 10:00 | 41.97 | 80 | 80 | 0 | 38.03 | 0 | 100.54 | 0 | 0
2025-02-20 11:00 | 43.63 | 70.88 | 56.31 | 0 | 12.68 | 0 | 112.59 | 14.57 | 0
2025-02-20 12:00 | 45.01 | 66.4 | 45.01 | 0 | 0 | 0 | 112.59 | 21.39 | 0
2025-02-20 13:00 | 44.07 | 70.19 | 44.07 | 0 | 0 | 0 | 112.59 | 26.12 | 0
2025-02-20 14:00 | 45.78 | 79.21 | 45.78 | 0 | 0 | 0 | 112.59 | 33.42 | 0
2025-02-20 15:00 | 46.35 | 70.73 | 46.35 | 0 | 0 | 0 | 112.59 | 24.38 | 0
2025-02-20 16:00 | 45.53 | 57.18 | 45.53 | 0 | 0 | 0 | 112.59 | 11.65 | 0
2025-02-20 17:00 | 45.45 | 7.96 | 7.96 | 0 | 0 | 37.49 | 73.12 | 0 | 0
2025-02-20 18:00 | 44.14 | 0 | 0 | 0 | 0 | 44.14 | 26.65 | 0 | 0
2025-02-20 19:00 | 43.56 | 0 | 0 | 30.12 | 0 | 13.44 | 12.51 | 0 | 0
2025-02-20 20:00 | 41.79 | 0 | 0 | 41.79 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 21:00 | 40.35 | 0 | 0 | 40.35 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 22:00 | 40.93 | 0 | 0 | 40.93 | 0 | 0 | 12.51 | 0 | 0
2025-02-20 23:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 01:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 02:00 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 03:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 04:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 06:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 07:00 | 39.75 | 0.33 | 0.33 | 39.43 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 08:00 | 40.74 | 19.2 | 19.2 | 21.53 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 09:00 | 42.54 | 49.15 | 49.15 | 0 | 6.61 | 0 | 18.79 | 0 | 0
2025-02-21 10:00 | 42.38 | 72.83 | 72.83 | 0 | 30.45 | 0 | 47.72 | 0 | 0
2025-02-21 11:00 | 43.99 | 83.86 | 83.86 | 0 | 39.87 | 0 | 85.6 | 0 | 0
2025-02-21 12:00 | 45.56 | 40.3 | 40.3 | 0 | 0 | 5.26 | 80.06 | 0 | 0
2025-02-21 13:00 | 46.38 | 23.61 | 23.61 | 0 | 0 | 22.77 | 56.09 | 0 | 0
2025-02-21 14:00 | 45.52 | 6.16 | 6.16 | 0 | 0 | 39.36 | 14.67 | 0 | 0
2025-02-21 15:00 | 46.24 | 4.11 | 4.11 | 40.09 | 0 | 2.05 | 12.51 | 0 | 0
2025-02-21 16:00 | 46.91 | 1.23 | 1.23 | 45.68 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 17:00 | 46 | 0.54 | 0.54 | 45.46 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 18:00 | 45.09 | 0 | 0 | 45.09 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 19:00 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 20:00 | 42.72 | 0 | 0 | 42.72 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 21:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 22:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 12.51 | 0 | 0
2025-02-21 23:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 01:00 | 37.8 | 0 | 0 | 37.8 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 02:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 04:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 05:00 | 38.3 | 0 | 0 | 38.3 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 06:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 07:00 | 39.78 | 1.94 | 1.94 | 37.84 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 08:00 | 40.32 | 62.8 | 62.8 | 0 | 22.48 | 0 | 33.87 | 0 | 0
2025-02-22 09:00 | 41.48 | 81.93 | 81.93 | 0 | 40.45 | 0 | 72.29 | 0 | 0
2025-02-22 10:00 | 42.42 | 64.32 | 64.32 | 0 | 21.9 | 0 | 93.09 | 0 | 0
2025-02-22 11:00 | 42.55 | 75.36 | 63.07 | 0 | 20.53 | 0 | 112.59 | 12.29 | 0
2025-02-22 12:00 | 43.5 | 78.18 | 43.5 | 0 | 0 | 0 | 112.59 | 34.68 | 0
2025-02-22 13:00 | 42.1 | 54.19 | 42.1 | 0 | 0 | 0 | 112.59 | 12.09 | 0
2025-02-22 14:00 | 44.27 | 41.51 | 41.51 | 0 | 0 | 2.76 | 109.69 | 0 | 0
2025-02-22 15:00 | 43.73 | 26.19 | 26.19 | 0 | 0 | 17.54 | 91.22 | 0 | 0
2025-02-22 16:00 | 44.01 | 5.74 | 5.74 | 0 | 0 | 38.28 | 50.93 | 0 | 0
2025-02-22 17:00 | 42.66 | 0.95 | 0.95 | 5.22 | 0 | 36.5 | 12.51 | 0 | 0
2025-02-22 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 19:00 | 42.53 | 0 | 0 | 42.53 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 20:00 | 41.83 | 0 | 0 | 41.83 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 21:00 | 41.24 | 0 | 0 | 41.24 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 22:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 12.51 | 0 | 0
2025-02-22 23:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 01:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 02:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 04:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 05:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 06:00 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 07:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 08:00 | 40.65 | 9 | 9 | 31.65 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 09:00 | 41.56 | 9.29 | 9.29 | 32.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 10:00 | 43.19 | 3.13 | 3.13 | 40.07 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 11:00 | 43.42 | 85.53 | 85.53 | 0 | 42.11 | 0 | 52.52 | 0 | 0
2025-02-23 12:00 | 43.92 | 65.48 | 65.48 | 0 | 21.55 | 0 | 72.99 | 0 | 0
2025-02-23 13:00 | 44.6 | 44.84 | 44.84 | 0 | 0.24 | 0 | 73.22 | 0 | 0
2025-02-23 14:00 | 45.85 | 42.71 | 42.71 | 0 | 0 | 3.14 | 69.91 | 0 | 0
2025-02-23 15:00 | 45.6 | 89.97 | 89.97 | 0 | 44.37 | 0 | 112.06 | 0 | 0
2025-02-23 16:00 | 45.02 | 81.84 | 45.58 | 0 | 0.56 | 0 | 112.59 | 36.26 | 0
2025-02-23 17:00 | 44.73 | 16.11 | 16.11 | 0 | 0 | 28.62 | 82.46 | 0 | 0
2025-02-23 18:00 | 43.49 | 0 | 0 | 0 | 0 | 43.49 | 36.69 | 0 | 0
2025-02-23 19:00 | 43.7 | 0 | 0 | 20.74 | 0 | 22.97 | 12.51 | 0 | 0
2025-02-23 20:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 21:00 | 42 | 0 | 0 | 42 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 22:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 12.51 | 0 | 0
2025-02-23 23:00 | 40.87 | 0 | 0 | 40.87 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 01:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 02:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 03:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 04:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 05:00 | 38.4 | 0 | 0 | 38.4 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 06:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 07:00 | 39.9 | 6.12 | 6.12 | 33.78 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 08:00 | 40.34 | 77.32 | 77.32 | 0 | 36.98 | 0 | 47.64 | 0 | 0
2025-02-24 09:00 | 41.63 | 75.75 | 75.75 | 0 | 34.12 | 0 | 80.05 | 0 | 0
2025-02-24 10:00 | 41.84 | 85.13 | 76.09 | 0 | 34.25 | 0 | 112.59 | 9.04 | 0
2025-02-24 11:00 | 43.58 | 91.48 | 43.58 | 0 | 0 | 0 | 112.59 | 47.89 | 0
2025-02-24 12:00 | 44.48 | 85.72 | 44.48 | 0 | 0 | 0 | 112.59 | 41.24 | 0
2025-02-24 13:00 | 44.69 | 61.01 | 44.69 | 0 | 0 | 0 | 112.59 | 16.32 | 0
2025-02-24 14:00 | 44.34 | 59.19 | 44.34 | 0 | 0 | 0 | 112.59 | 14.85 | 0
2025-02-24 15:00 | 45.76 | 9.79 | 9.79 | 0 | 0 | 35.97 | 74.72 | 0 | 0
2025-02-24 16:00 | 45.33 | 1.1 | 1.1 | 0 | 0 | 44.23 | 28.17 | 0 | 0
2025-02-24 17:00 | 44.44 | 0 | 0 | 29.57 | 0 | 14.87 | 12.51 | 0 | 0
2025-02-24 18:00 | 44.11 | 0 | 0 | 44.11 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 19:00 | 42.77 | 0 | 0 | 42.77 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 20:00 | 42.13 | 0 | 0 | 42.13 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 21:00 | 41.41 | 0 | 0 | 41.41 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 22:00 | 41.31 | 0 | 0 | 41.31 | 0 | 0 | 12.51 | 0 | 0
2025-02-24 23:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 | 39.33 | 0 | 0 | 39.33 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 01:00 | 38.09 | 0 | 0 | 38.09 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 02:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 03:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 04:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 05:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 06:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 07:00 | 39.14 | 2.1 | 2.1 | 37.04 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 08:00 | 40.5 | 58.95 | 58.95 | 0 | 18.45 | 0 | 30.04 | 0 | 0
2025-02-25 09:00 | 41.11 | 79 | 79 | 0 | 37.89 | 0 | 66.04 | 0 | 0
2025-02-25 10:00 | 42.87 | 82.37 | 82.37 | 0 | 39.5 | 0 | 103.56 | 0 | 0
2025-02-25 11:00 | 43.28 | 72.09 | 52.78 | 0 | 9.5 | 0 | 112.59 | 19.32 | 0
2025-02-25 12:00 | 45.4 | 71.06 | 45.4 | 0 | 0 | 0 | 112.59 | 25.66 | 0
2025-02-25 13:00 | 43.87 | 77.21 | 43.87 | 0 | 0 | 0 | 112.59 | 33.34 | 0
2025-02-25 14:00 | 45.16 | 76.33 | 45.16 | 0 | 0 | 0 | 112.59 | 31.16 | 0
2025-02-25 15:00 | 44.61 | 64.23 | 44.61 | 0 | 0 | 0 | 112.59 | 19.62 | 0
2025-02-25 16:00 | 44.82 | 65.45 | 44.82 | 0 | 0 | 0 | 112.59 | 20.64 | 0
2025-02-25 17:00 | 44.81 | 11.01 | 11.01 | 0 | 0 | 33.8 | 77.01 | 0 | 0
2025-02-25 18:00 | 43.05 | 0 | 0 | 0 | 0 | 43.05 | 31.69 | 0 | 0
2025-02-25 19:00 | 43.63 | 0 | 0 | 25.41 | 0 | 18.22 | 12.51 | 0 | 0
2025-02-25 20:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 21:00 | 41.5 | 0 | 0 | 41.5 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 22:00 | 40.89 | 0 | 0 | 40.89 | 0 | 0 | 12.51 | 0 | 0
2025-02-25 23:00 | 40.34 | 0 | 0 | 40.34 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 01:00 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 02:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 03:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 04:00 | 37.97 | 0 | 0 | 37.97 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 05:00 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 06:00 | 39.17 | 0 | 0 | 39.17 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 07:00 | 39.67 | 2.84 | 2.84 | 36.82 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 08:00 | 40.68 | 24.75 | 24.75 | 15.92 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 09:00 | 42.29 | 78.92 | 78.92 | 0 | 36.64 | 0 | 47.31 | 0 | 0
2025-02-26 10:00 | 42.34 | 87.6 | 87.6 | 0 | 45.26 | 0 | 90.31 | 0 | 0
2025-02-26 11:00 | 44.48 | 78.02 | 67.94 | 0 | 23.46 | 0 | 112.59 | 10.08 | 0
2025-02-26 12:00 | 44.06 | 78.32 | 44.06 | 0 | 0 | 0 | 112.59 | 34.25 | 0
2025-02-26 13:00 | 45.04 | 63.27 | 45.04 | 0 | 0 | 0 | 112.59 | 18.23 | 0
2025-02-26 14:00 | 46.71 | 39.39 | 39.39 | 0 | 0 | 7.32 | 104.88 | 0 | 0
2025-02-26 15:00 | 46.44 | 19.29 | 19.29 | 0 | 0 | 27.15 | 76.3 | 0 | 0
2025-02-26 16:00 | 45.8 | 4.99 | 4.99 | 0 | 0 | 40.81 | 33.34 | 0 | 0
2025-02-26 17:00 | 44.9 | 0 | 0 | 25.11 | 0 | 19.79 | 12.51 | 0 | 0
2025-02-26 18:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 19:00 | 44 | 0 | 0 | 44 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 20:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 21:00 | 41.94 | 0 | 0 | 41.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 22:00 | 40.93 | 0 | 0 | 40.93 | 0 | 0 | 12.51 | 0 | 0
2025-02-26 23:00 | 39.85 | 0 | 0 | 39.85 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 | 38.53 | 0 | 0 | 38.53 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 01:00 | 38.27 | 0 | 0 | 38.27 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 02:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 03:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 04:00 | 38 | 0 | 0 | 38 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 05:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 06:00 | 39.3 | 0 | 0 | 39.3 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 07:00 | 40.03 | 4.97 | 4.97 | 35.06 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 08:00 | 42.16 | 77.21 | 77.21 | 0 | 35.05 | 0 | 45.81 | 0 | 0
2025-02-27 09:00 | 43.04 | 91.12 | 91.12 | 0 | 48.09 | 0 | 91.49 | 0 | 0
2025-02-27 10:00 | 43.57 | 89.2 | 65.78 | 0 | 22.21 | 0 | 112.59 | 23.42 | 0
2025-02-27 11:00 | 45.97 | 83.43 | 45.97 | 0 | 0 | 0 | 112.59 | 37.46 | 0
2025-02-27 12:00 | 46.51 | 76.75 | 46.51 | 0 | 0 | 0 | 112.59 | 30.24 | 0
2025-02-27 13:00 | 47.61 | 80.25 | 47.61 | 0 | 0 | 0 | 112.59 | 32.64 | 0
2025-02-27 14:00 | 48.7 | 87.23 | 48.7 | 0 | 0 | 0 | 112.59 | 38.53 | 0
2025-02-27 15:00 | 48.52 | 94.02 | 48.52 | 0 | 0 | 0 | 112.59 | 45.5 | 0
2025-02-27 16:00 | 48.99 | 85.24 | 48.99 | 0 | 0 | 0 | 112.59 | 36.25 | 0
2025-02-27 17:00 | 47.51 | 20.07 | 20.07 | 0 | 0 | 27.44 | 83.7 | 0 | 0
2025-02-27 18:00 | 46.59 | 0 | 0 | 0 | 0 | 46.59 | 34.67 | 0 | 0
2025-02-27 19:00 | 45.3 | 0 | 0 | 24.26 | 0 | 21.05 | 12.51 | 0 | 0
2025-02-27 20:00 | 43.94 | 0 | 0 | 43.94 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 21:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 22:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 12.51 | 0 | 0
2025-02-27 23:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 01:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 02:00 | 38.21 | 0 | 0 | 38.21 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 03:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 04:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 06:00 | 38.73 | 0 | 0 | 38.73 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 07:00 | 39.57 | 5.75 | 5.75 | 33.83 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 08:00 | 40.96 | 86.96 | 86.96 | 0 | 46 | 0 | 56.21 | 0 | 0
2025-02-28 09:00 | 41.39 | 98.33 | 98.33 | 0 | 56.94 | 0 | 110.3 | 0 | 0
2025-02-28 10:00 | 43.34 | 94.42 | 45.75 | 0 | 2.41 | 0 | 112.59 | 48.67 | 0
2025-02-28 11:00 | 43.28 | 86.89 | 43.28 | 0 | 0 | 0 | 112.59 | 43.62 | 0
2025-02-28 12:00 | 45.81 | 81.98 | 45.81 | 0 | 0 | 0 | 112.59 | 36.17 | 0
2025-02-28 13:00 | 44.68 | 84.82 | 44.68 | 0 | 0 | 0 | 112.59 | 40.15 | 0
2025-02-28 14:00 | 45.24 | 91.46 | 45.24 | 0 | 0 | 0 | 112.59 | 46.22 | 0
2025-02-28 15:00 | 44.66 | 97.1 | 44.66 | 0 | 0 | 0 | 112.59 | 52.44 | 0
2025-02-28 16:00 | 46.06 | 91.6 | 46.06 | 0 | 0 | 0 | 112.59 | 45.55 | 0
2025-02-28 17:00 | 45.46 | 25.19 | 25.19 | 0 | 0 | 20.28 | 91.25 | 0 | 0
2025-02-28 18:00 | 44.56 | 0 | 0 | 0 | 0 | 44.56 | 44.35 | 0 | 0
2025-02-28 19:00 | 43.06 | 0 | 0 | 12.82 | 0 | 30.24 | 12.51 | 0 | 0
2025-02-28 20:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 21:00 | 41.44 | 0 | 0 | 41.44 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 22:00 | 41.77 | 0 | 0 | 41.77 | 0 | 0 | 12.51 | 0 | 0
2025-02-28 23:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 01:00 | 37.47 | 0 | 0 | 37.47 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 03:00 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 04:00 | 38.86 | 0 | 0 | 38.86 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 05:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 06:00 | 38.62 | 0 | 0 | 38.62 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 07:00 | 40.53 | 4.6 | 4.6 | 35.93 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 08:00 | 42.05 | 60.17 | 60.17 | 0 | 18.12 | 0 | 29.72 | 0 | 0
2025-03-01 09:00 | 42.02 | 45.65 | 45.65 | 0 | 3.63 | 0 | 33.17 | 0 | 0
2025-03-01 10:00 | 44.2 | 70.62 | 70.62 | 0 | 26.42 | 0 | 58.28 | 0 | 0
2025-03-01 11:00 | 45.64 | 60.91 | 60.91 | 0 | 15.27 | 0 | 72.78 | 0 | 0
2025-03-01 12:00 | 46.51 | 69.53 | 69.53 | 0 | 23.02 | 0 | 94.65 | 0 | 0
2025-03-01 13:00 | 46.65 | 68.62 | 65.53 | 0 | 18.88 | 0 | 112.59 | 3.09 | 0
2025-03-01 14:00 | 47.99 | 71.77 | 47.99 | 0 | 0 | 0 | 112.59 | 23.78 | 0
2025-03-01 15:00 | 48.19 | 74.43 | 48.19 | 0 | 0 | 0 | 112.59 | 26.24 | 0
2025-03-01 16:00 | 48.08 | 78.28 | 48.08 | 0 | 0 | 0 | 112.59 | 30.19 | 0
2025-03-01 17:00 | 47.29 | 21.25 | 21.25 | 0 | 0 | 26.04 | 85.18 | 0 | 0
2025-03-01 18:00 | 46.44 | 0 | 0 | 0 | 0 | 46.44 | 36.29 | 0 | 0
2025-03-01 19:00 | 45.49 | 0 | 0 | 22.9 | 0 | 22.59 | 12.51 | 0 | 0
2025-03-01 20:00 | 44.42 | 0 | 0 | 44.42 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 21:00 | 42.7 | 0 | 0 | 42.7 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 22:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 12.51 | 0 | 0
2025-03-01 23:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 | 38.45 | 0 | 0 | 38.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 01:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 02:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 03:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 04:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 05:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 06:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 07:00 | 40.36 | 8.56 | 8.56 | 31.8 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 08:00 | 41.08 | 81.17 | 81.17 | 0 | 40.08 | 0 | 50.59 | 0 | 0
2025-03-02 09:00 | 42.01 | 96.6 | 96.6 | 0 | 54.59 | 0 | 102.44 | 0 | 0
2025-03-02 10:00 | 42.45 | 93.91 | 53.13 | 0 | 10.68 | 0 | 112.59 | 40.78 | 0
2025-03-02 11:00 | 43.64 | 86.93 | 43.64 | 0 | 0 | 0 | 112.59 | 43.3 | 0
2025-03-02 12:00 | 44.24 | 82.38 | 44.24 | 0 | 0 | 0 | 112.59 | 38.14 | 0
2025-03-02 13:00 | 44.34 | 86.12 | 44.34 | 0 | 0 | 0 | 112.59 | 41.78 | 0
2025-03-02 14:00 | 44.15 | 92.51 | 44.15 | 0 | 0 | 0 | 112.59 | 48.35 | 0
2025-03-02 15:00 | 43.29 | 95.99 | 43.29 | 0 | 0 | 0 | 112.59 | 52.7 | 0
2025-03-02 16:00 | 44.67 | 85.82 | 44.67 | 0 | 0 | 0 | 112.59 | 41.16 | 0
2025-03-02 17:00 | 44.71 | 25.89 | 25.89 | 0 | 0 | 18.82 | 92.78 | 0 | 0
2025-03-02 18:00 | 44.1 | 0 | 0 | 0 | 0 | 44.1 | 46.36 | 0 | 0
2025-03-02 19:00 | 42.86 | 0 | 0 | 10.71 | 0 | 32.16 | 12.51 | 0 | 0
2025-03-02 20:00 | 43.02 | 0 | 0 | 43.02 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 21:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 22:00 | 41.87 | 0 | 0 | 41.87 | 0 | 0 | 12.51 | 0 | 0
2025-03-02 23:00 | 39.78 | 0 | 0 | 39.78 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 | 39.44 | 0 | 0 | 39.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 01:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 02:00 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 03:00 | 37.7 | 0 | 0 | 37.7 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 04:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 06:00 | 39.6 | 0 | 0 | 39.6 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 07:00 | 40.57 | 0.13 | 0.13 | 40.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 08:00 | 41.37 | 19.83 | 19.83 | 21.55 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 09:00 | 43.34 | 2.59 | 2.59 | 40.74 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 10:00 | 43.23 | 33.59 | 33.59 | 9.64 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 11:00 | 44.38 | 62.55 | 62.55 | 0 | 18.17 | 0 | 29.77 | 0 | 0
2025-03-03 12:00 | 45.51 | 44.69 | 44.69 | 0 | 0 | 0.83 | 28.9 | 0 | 0
2025-03-03 13:00 | 46.58 | 25.12 | 25.12 | 5.9 | 0 | 15.57 | 12.51 | 0 | 0
2025-03-03 14:00 | 45.79 | 37.92 | 37.92 | 7.87 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 15:00 | 46.02 | 24.56 | 24.56 | 21.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 16:00 | 45.52 | 54.9 | 54.9 | 0 | 9.38 | 0 | 21.42 | 0 | 0
2025-03-03 17:00 | 46.16 | 15.77 | 15.77 | 21.93 | 0 | 8.47 | 12.51 | 0 | 0
2025-03-03 18:00 | 44.95 | 0 | 0 | 44.95 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 19:00 | 44.48 | 0 | 0 | 44.48 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 20:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 21:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 22:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 12.51 | 0 | 0
2025-03-03 23:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 01:00 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 02:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 03:00 | 38.25 | 0 | 0 | 38.25 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 04:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 06:00 | 38.97 | 0 | 0 | 38.97 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 07:00 | 40.95 | 7.99 | 7.99 | 32.96 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 08:00 | 41.19 | 39.13 | 39.13 | 2.07 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 09:00 | 43.65 | 85.24 | 85.24 | 0 | 41.59 | 0 | 52.02 | 0 | 0
2025-03-04 10:00 | 44.66 | 40.85 | 40.85 | 0 | 0 | 3.82 | 48 | 0 | 0
2025-03-04 11:00 | 45.44 | 50.67 | 50.67 | 0 | 5.24 | 0 | 52.98 | 0 | 0
2025-03-04 12:00 | 46.35 | 53.82 | 53.82 | 0 | 7.46 | 0 | 60.07 | 0 | 0
2025-03-04 13:00 | 46.93 | 61.45 | 61.45 | 0 | 14.52 | 0 | 73.86 | 0 | 0
2025-03-04 14:00 | 47.85 | 97.16 | 88.62 | 0 | 40.77 | 0 | 112.59 | 8.53 | 0
2025-03-04 15:00 | 47.49 | 76.36 | 47.49 | 0 | 0 | 0 | 112.59 | 28.87 | 0
2025-03-04 16:00 | 47.63 | 47.32 | 47.32 | 0 | 0 | 0.31 | 112.26 | 0 | 0
2025-03-04 17:00 | 47.47 | 10.34 | 10.34 | 0 | 0 | 37.13 | 73.18 | 0 | 0
2025-03-04 18:00 | 45.99 | 0 | 0 | 0 | 0 | 45.99 | 24.76 | 0 | 0
2025-03-04 19:00 | 44.98 | 0 | 0 | 33.34 | 0 | 11.64 | 12.51 | 0 | 0
2025-03-04 20:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 21:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 22:00 | 40.82 | 0 | 0 | 40.82 | 0 | 0 | 12.51 | 0 | 0
2025-03-04 23:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 01:00 | 39.75 | 0 | 0 | 39.75 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 03:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 04:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 05:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 06:00 | 39.84 | 0 | 0 | 39.84 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 07:00 | 39.77 | 9.62 | 9.62 | 30.16 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 08:00 | 42.09 | 97.11 | 97.11 | 0 | 55.02 | 0 | 64.78 | 0 | 0
2025-03-05 09:00 | 42.72 | 100.21 | 93.05 | 0 | 50.33 | 0 | 112.59 | 7.15 | 0
2025-03-05 10:00 | 44.69 | 87.68 | 44.69 | 0 | 0 | 0 | 112.59 | 42.99 | 0
2025-03-05 11:00 | 45.08 | 71.89 | 45.08 | 0 | 0 | 0 | 112.59 | 26.81 | 0
2025-03-05 12:00 | 47.24 | 54.23 | 47.24 | 0 | 0 | 0 | 112.59 | 6.99 | 0
2025-03-05 13:00 | 48.35 | 45.76 | 45.76 | 0 | 0 | 2.59 | 109.87 | 0 | 0
2025-03-05 14:00 | 48 | 42.47 | 42.47 | 0 | 0 | 5.53 | 104.05 | 0 | 0
2025-03-05 15:00 | 48.01 | 38.32 | 38.32 | 0 | 0 | 9.69 | 93.85 | 0 | 0
2025-03-05 16:00 | 47.31 | 25.29 | 25.29 | 0 | 0 | 22.03 | 70.66 | 0 | 0
2025-03-05 17:00 | 47.71 | 3.62 | 3.62 | 0 | 0 | 44.09 | 24.25 | 0 | 0
2025-03-05 18:00 | 46.68 | 0 | 0 | 35.52 | 0 | 11.16 | 12.51 | 0 | 0
2025-03-05 19:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 20:00 | 44.82 | 0 | 0 | 44.82 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 21:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 22:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 12.51 | 0 | 0
2025-03-05 23:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 | 40.43 | 0 | 0 | 40.43 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 01:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 02:00 | 38.59 | 0 | 0 | 38.59 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 03:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 04:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 06:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 07:00 | 40.67 | 12.98 | 12.98 | 27.69 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 08:00 | 42.33 | 74.38 | 74.38 | 0 | 32.04 | 0 | 42.95 | 0 | 0
2025-03-06 09:00 | 43.07 | 88.67 | 88.67 | 0 | 45.61 | 0 | 86.28 | 0 | 0
2025-03-06 10:00 | 45.09 | 86.36 | 72.79 | 0 | 27.7 | 0 | 112.59 | 13.57 | 0
2025-03-06 11:00 | 46.43 | 84.74 | 46.43 | 0 | 0 | 0 | 112.59 | 38.3 | 0
2025-03-06 12:00 | 45.86 | 81.76 | 45.86 | 0 | 0 | 0 | 112.59 | 35.9 | 0
2025-03-06 13:00 | 48.82 | 86.9 | 48.82 | 0 | 0 | 0 | 112.59 | 38.08 | 0
2025-03-06 14:00 | 47.29 | 95.31 | 47.29 | 0 | 0 | 0 | 112.59 | 48.02 | 0
2025-03-06 15:00 | 48.7 | 94.48 | 48.7 | 0 | 0 | 0 | 112.59 | 45.78 | 0
2025-03-06 16:00 | 49.32 | 83.23 | 49.32 | 0 | 0 | 0 | 112.59 | 33.91 | 0
2025-03-06 17:00 | 48.07 | 31.2 | 31.2 | 0 | 0 | 16.87 | 94.83 | 0 | 0
2025-03-06 18:00 | 46.59 | 0 | 0 | 0 | 0 | 46.59 | 45.79 | 0 | 0
2025-03-06 19:00 | 45.61 | 0 | 0 | 13.99 | 0 | 31.62 | 12.51 | 0 | 0
2025-03-06 20:00 | 45.35 | 0 | 0 | 45.35 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 21:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 22:00 | 42.68 | 0 | 0 | 42.68 | 0 | 0 | 12.51 | 0 | 0
2025-03-06 23:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 01:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 02:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 03:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 04:00 | 39.11 | 0 | 0 | 39.11 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 05:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 06:00 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 07:00 | 40.6 | 19.12 | 19.12 | 21.48 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 08:00 | 42.92 | 85.22 | 85.22 | 0 | 42.31 | 0 | 52.7 | 0 | 0
2025-03-07 09:00 | 42.97 | 92.76 | 92.76 | 0 | 49.79 | 0 | 100 | 0 | 0
2025-03-07 10:00 | 45.86 | 92.32 | 59.11 | 0 | 13.25 | 0 | 112.59 | 33.21 | 0
2025-03-07 11:00 | 46.41 | 85.91 | 46.41 | 0 | 0 | 0 | 112.59 | 39.51 | 0
2025-03-07 12:00 | 47.04 | 77.75 | 47.04 | 0 | 0 | 0 | 112.59 | 30.71 | 0
2025-03-07 13:00 | 48.23 | 79.15 | 48.23 | 0 | 0 | 0 | 112.59 | 30.92 | 0
2025-03-07 14:00 | 48.77 | 80 | 48.77 | 0 | 0 | 0 | 112.59 | 31.23 | 0
2025-03-07 15:00 | 48.74 | 80.55 | 48.74 | 0 | 0 | 0 | 112.59 | 31.82 | 0
2025-03-07 16:00 | 49.21 | 82.72 | 49.21 | 0 | 0 | 0 | 112.59 | 33.51 | 0
2025-03-07 17:00 | 47.95 | 32.93 | 32.93 | 0 | 0 | 15.02 | 96.78 | 0 | 0
2025-03-07 18:00 | 46.53 | 0 | 0 | 0 | 0 | 46.53 | 47.79 | 0 | 0
2025-03-07 19:00 | 46.23 | 0 | 0 | 12.72 | 0 | 33.52 | 12.51 | 0 | 0
2025-03-07 20:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 21:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 22:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 12.51 | 0 | 0
2025-03-07 23:00 | 40.59 | 0 | 0 | 40.59 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 01:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 02:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 03:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 04:00 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 05:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 06:00 | 39.55 | 0 | 0 | 39.55 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 07:00 | 41.48 | 20.12 | 20.12 | 21.36 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 08:00 | 41.53 | 75.45 | 75.45 | 0 | 33.92 | 0 | 44.73 | 0 | 0
2025-03-08 09:00 | 43.16 | 89.27 | 89.27 | 0 | 46.11 | 0 | 88.54 | 0 | 0
2025-03-08 10:00 | 44.16 | 87.98 | 69.48 | 0 | 25.32 | 0 | 112.59 | 18.5 | 0
2025-03-08 11:00 | 45.59 | 83.92 | 45.59 | 0 | 0 | 0 | 112.59 | 38.33 | 0
2025-03-08 12:00 | 46.08 | 82.02 | 46.08 | 0 | 0 | 0 | 112.59 | 35.94 | 0
2025-03-08 13:00 | 46.94 | 83.58 | 46.94 | 0 | 0 | 0 | 112.59 | 36.64 | 0
2025-03-08 14:00 | 47.38 | 84.11 | 47.38 | 0 | 0 | 0 | 112.59 | 36.74 | 0
2025-03-08 15:00 | 47.27 | 89.17 | 47.27 | 0 | 0 | 0 | 112.59 | 41.9 | 0
2025-03-08 16:00 | 47.74 | 86.84 | 47.74 | 0 | 0 | 0 | 112.59 | 39.1 | 0
2025-03-08 17:00 | 47.19 | 34.87 | 34.87 | 0 | 0 | 12.33 | 99.61 | 0 | 0
2025-03-08 18:00 | 46.36 | 0 | 0 | 0 | 0 | 46.36 | 50.82 | 0 | 0
2025-03-08 19:00 | 45.29 | 0 | 0 | 8.9 | 0 | 36.39 | 12.51 | 0 | 0
2025-03-08 20:00 | 44.85 | 0 | 0 | 44.85 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 21:00 | 43.19 | 0 | 0 | 43.19 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 22:00 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 12.51 | 0 | 0
2025-03-08 23:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 01:00 | 38.74 | 0 | 0 | 38.74 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 02:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 03:00 | 37.82 | 0 | 0 | 37.82 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 04:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 05:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 06:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 07:00 | 41.22 | 22.18 | 22.18 | 19.03 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 08:00 | 41.96 | 80.47 | 80.47 | 0 | 38.51 | 0 | 49.09 | 0 | 0
2025-03-09 09:00 | 43.42 | 94.87 | 94.87 | 0 | 51.45 | 0 | 97.97 | 0 | 0
2025-03-09 10:00 | 44.42 | 91.81 | 59.81 | 0 | 15.39 | 0 | 112.59 | 32 | 0
2025-03-09 11:00 | 45.18 | 86.48 | 45.18 | 0 | 0 | 0 | 112.59 | 41.29 | 0
2025-03-09 12:00 | 46.3 | 83.19 | 46.3 | 0 | 0 | 0 | 112.59 | 36.89 | 0
2025-03-09 13:00 | 47.2 | 84.31 | 47.2 | 0 | 0 | 0 | 112.59 | 37.1 | 0
2025-03-09 14:00 | 47.13 | 85.11 | 47.13 | 0 | 0 | 0 | 112.59 | 37.98 | 0
2025-03-09 15:00 | 47.24 | 86.96 | 47.24 | 0 | 0 | 0 | 112.59 | 39.72 | 0
2025-03-09 16:00 | 46.83 | 72.75 | 46.83 | 0 | 0 | 0 | 112.59 | 25.92 | 0
2025-03-09 17:00 | 47.3 | 34.04 | 34.04 | 0 | 0 | 13.25 | 98.64 | 0 | 0
2025-03-09 18:00 | 46.72 | 0 | 0 | 0 | 0 | 46.72 | 49.46 | 0 | 0
2025-03-09 19:00 | 45.69 | 0 | 0 | 10.59 | 0 | 35.1 | 12.51 | 0 | 0
2025-03-09 20:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 21:00 | 43.45 | 0 | 0 | 43.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 22:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-09 23:00 | 41.29 | 0 | 0 | 41.29 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 01:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 02:00 | 40.13 | 0 | 0 | 40.13 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 03:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 04:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 05:00 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 06:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 07:00 | 40.7 | 23.9 | 23.9 | 16.8 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 08:00 | 43.26 | 75.89 | 75.89 | 0 | 32.63 | 0 | 43.51 | 0 | 0
2025-03-10 09:00 | 44.1 | 81.14 | 81.14 | 0 | 37.05 | 0 | 78.7 | 0 | 0
2025-03-10 10:00 | 45.08 | 96.37 | 80.75 | 0 | 35.67 | 0 | 112.59 | 15.62 | 0
2025-03-10 11:00 | 47.67 | 86.26 | 47.67 | 0 | 0 | 0 | 112.59 | 38.59 | 0
2025-03-10 12:00 | 48.66 | 76.34 | 48.66 | 0 | 0 | 0 | 112.59 | 27.68 | 0
2025-03-10 13:00 | 48.71 | 79.31 | 48.71 | 0 | 0 | 0 | 112.59 | 30.61 | 0
2025-03-10 14:00 | 50.86 | 77.72 | 50.86 | 0 | 0 | 0 | 112.59 | 26.85 | 0
2025-03-10 15:00 | 50.52 | 63.51 | 50.52 | 0 | 0 | 0 | 112.59 | 12.99 | 0
2025-03-10 16:00 | 49.97 | 33.47 | 33.47 | 0 | 0 | 16.5 | 95.22 | 0 | 0
2025-03-10 17:00 | 50.13 | 5.56 | 5.56 | 0 | 0 | 44.58 | 48.3 | 0 | 0
2025-03-10 18:00 | 48.42 | 0 | 0 | 14.42 | 0 | 34 | 12.51 | 0 | 0
2025-03-10 19:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 20:00 | 45.31 | 0 | 0 | 45.31 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 21:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 12.51 | 0 | 0
2025-03-10 23:00 | 41.41 | 0 | 0 | 41.41 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 | 40 | 0 | 0 | 40 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 01:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 02:00 | 39.08 | 0 | 0 | 39.08 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 03:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 04:00 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 05:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 06:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 07:00 | 41.51 | 8.45 | 8.45 | 33.07 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 08:00 | 42.35 | 16.52 | 16.52 | 25.83 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 09:00 | 44.49 | 46.23 | 46.23 | 0 | 1.74 | 0 | 14.16 | 0 | 0
2025-03-11 10:00 | 44.83 | 70.45 | 70.45 | 0 | 25.62 | 0 | 38.5 | 0 | 0
2025-03-11 11:00 | 46.55 | 69.4 | 69.4 | 0 | 22.85 | 0 | 60.22 | 0 | 0
2025-03-11 12:00 | 46.99 | 79.68 | 79.68 | 0 | 32.69 | 0 | 91.27 | 0 | 0
2025-03-11 13:00 | 47.99 | 83.11 | 70.43 | 0 | 22.44 | 0 | 112.59 | 12.67 | 0
2025-03-11 14:00 | 48.77 | 87.94 | 48.77 | 0 | 0 | 0 | 112.59 | 39.18 | 0
2025-03-11 15:00 | 48.33 | 78.28 | 48.33 | 0 | 0 | 0 | 112.59 | 29.95 | 0
2025-03-11 16:00 | 48.9 | 63.85 | 48.9 | 0 | 0 | 0 | 112.59 | 14.95 | 0
2025-03-11 17:00 | 47.44 | 34.13 | 34.13 | 0 | 0 | 13.31 | 98.58 | 0 | 0
2025-03-11 18:00 | 47.34 | 0 | 0 | 0 | 0 | 47.34 | 48.75 | 0 | 0
2025-03-11 19:00 | 46.68 | 0 | 0 | 12.25 | 0 | 34.43 | 12.51 | 0 | 0
2025-03-11 20:00 | 45.4 | 0 | 0 | 45.4 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 21:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 22:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 12.51 | 0 | 0
2025-03-11 23:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 01:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 02:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 03:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 04:00 | 38.65 | 0 | 0 | 38.65 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 05:00 | 40.09 | 0 | 0 | 40.09 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 06:00 | 39.85 | 0 | 0 | 39.85 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 07:00 | 42 | 18.83 | 18.83 | 23.16 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 08:00 | 43.89 | 65.3 | 65.3 | 0 | 21.41 | 0 | 32.85 | 0 | 0
2025-03-12 09:00 | 43.69 | 85.82 | 85.82 | 0 | 42.14 | 0 | 72.88 | 0 | 0
2025-03-12 10:00 | 44.76 | 59.03 | 59.03 | 0 | 14.26 | 0 | 86.43 | 0 | 0
2025-03-12 11:00 | 45.06 | 70 | 70 | 0 | 24.94 | 0 | 110.12 | 0 | 0
2025-03-12 12:00 | 45.06 | 60.39 | 47.65 | 0 | 2.6 | 0 | 112.59 | 12.74 | 0
2025-03-12 13:00 | 46.13 | 74.88 | 46.13 | 0 | 0 | 0 | 112.59 | 28.75 | 0
2025-03-12 14:00 | 46.17 | 68.25 | 46.17 | 0 | 0 | 0 | 112.59 | 22.08 | 0
2025-03-12 15:00 | 46.09 | 61.31 | 46.09 | 0 | 0 | 0 | 112.59 | 15.23 | 0
2025-03-12 16:00 | 47.58 | 66.9 | 47.58 | 0 | 0 | 0 | 112.59 | 19.32 | 0
2025-03-12 17:00 | 46.57 | 36.2 | 36.2 | 0 | 0 | 10.38 | 101.67 | 0 | 0
2025-03-12 18:00 | 46.15 | 0 | 0 | 0 | 0 | 46.15 | 53.09 | 0 | 0
2025-03-12 19:00 | 45.15 | 0 | 0 | 6.6 | 0 | 38.55 | 12.51 | 0 | 0
2025-03-12 20:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 21:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 22:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-12 23:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 01:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 02:00 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 03:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 04:00 | 39.17 | 0 | 0 | 39.17 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 05:00 | 39.84 | 0 | 0 | 39.84 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 06:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 07:00 | 41.54 | 1.76 | 1.76 | 39.78 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 08:00 | 42.66 | 11.73 | 11.73 | 30.94 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 09:00 | 42.65 | 17.85 | 17.85 | 24.8 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 10:00 | 44.29 | 33.1 | 33.1 | 11.19 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 11:00 | 45.83 | 46.65 | 46.65 | 0 | 0.82 | 0 | 13.29 | 0 | 0
2025-03-13 12:00 | 46.54 | 62.44 | 62.44 | 0 | 15.91 | 0 | 28.4 | 0 | 0
2025-03-13 13:00 | 46.28 | 70.32 | 70.32 | 0 | 24.04 | 0 | 51.23 | 0 | 0
2025-03-13 14:00 | 47.25 | 69.23 | 69.23 | 0 | 21.98 | 0 | 72.11 | 0 | 0
2025-03-13 15:00 | 47.78 | 86.84 | 86.84 | 0 | 39.06 | 0 | 109.22 | 0 | 0
2025-03-13 16:00 | 47.56 | 103.26 | 51.11 | 0 | 3.55 | 0 | 112.59 | 52.15 | 0
2025-03-13 17:00 | 46.81 | 38.09 | 38.09 | 0 | 0 | 8.72 | 103.41 | 0 | 0
2025-03-13 18:00 | 46.11 | 0 | 0 | 0 | 0 | 46.11 | 54.87 | 0 | 0
2025-03-13 19:00 | 45.32 | 0 | 0 | 5.07 | 0 | 40.24 | 12.51 | 0 | 0
2025-03-13 20:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 21:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 22:00 | 42.95 | 0 | 0 | 42.95 | 0 | 0 | 12.51 | 0 | 0
2025-03-13 23:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 01:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 02:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 03:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 04:00 | 39 | 0 | 0 | 39 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 05:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 06:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 07:00 | 41.84 | 44.95 | 44.95 | 0 | 3.1 | 0 | 15.46 | 0 | 0
2025-03-14 08:00 | 41.98 | 103.66 | 103.66 | 0 | 61.68 | 0 | 74.06 | 0 | 0
2025-03-14 09:00 | 43.63 | 75.11 | 75.11 | 0 | 31.49 | 0 | 103.97 | 0 | 0
2025-03-14 10:00 | 45.46 | 59.69 | 54.54 | 0 | 9.08 | 0 | 112.59 | 5.15 | 0
2025-03-14 11:00 | 45.9 | 78.51 | 45.9 | 0 | 0 | 0 | 112.59 | 32.61 | 0
2025-03-14 12:00 | 46.57 | 102.98 | 46.57 | 0 | 0 | 0 | 112.59 | 56.4 | 0
2025-03-14 13:00 | 48.11 | 92.12 | 48.11 | 0 | 0 | 0 | 112.59 | 44.01 | 0
2025-03-14 14:00 | 47.24 | 48.56 | 47.24 | 0 | 0 | 0 | 112.59 | 1.32 | 0
2025-03-14 15:00 | 47.48 | 3.65 | 3.65 | 0 | 0 | 43.83 | 66.45 | 0 | 0
2025-03-14 16:00 | 47.87 | 20.84 | 20.84 | 0 | 0 | 27.03 | 38 | 0 | 0
2025-03-14 17:00 | 47.6 | 2.91 | 2.91 | 20.48 | 0 | 24.21 | 12.51 | 0 | 0
2025-03-14 18:00 | 47.08 | 0 | 0 | 47.08 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 19:00 | 46.5 | 0 | 0 | 46.5 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 20:00 | 45.17 | 0 | 0 | 45.17 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 21:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 22:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 12.51 | 0 | 0
2025-03-14 23:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 | 40.94 | 0 | 0 | 40.94 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 01:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 02:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 03:00 | 39.6 | 0 | 0 | 39.6 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 04:00 | 39.53 | 0 | 0 | 39.53 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 05:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 06:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 07:00 | 42 | 3.34 | 3.34 | 38.65 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 08:00 | 43.45 | 8.38 | 8.38 | 35.06 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 09:00 | 45.92 | 12.94 | 12.94 | 32.98 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 10:00 | 46.05 | 12.96 | 12.96 | 33.1 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 11:00 | 47.95 | 6.48 | 6.48 | 41.47 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 12:00 | 49.52 | 24.1 | 24.1 | 25.42 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 13:00 | 50 | 32.89 | 32.89 | 17.11 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 14:00 | 51.73 | 42.88 | 42.88 | 8.86 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 15:00 | 50.59 | 38.92 | 38.92 | 11.66 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 16:00 | 50.73 | 56.03 | 56.03 | 0 | 5.31 | 0 | 17.55 | 0 | 0
2025-03-15 17:00 | 49.55 | 35.18 | 35.18 | 9.59 | 0 | 4.79 | 12.51 | 0 | 0
2025-03-15 18:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 19:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 20:00 | 46.74 | 0 | 0 | 46.74 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 21:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 22:00 | 43.98 | 0 | 0 | 43.98 | 0 | 0 | 12.51 | 0 | 0
2025-03-15 23:00 | 41.96 | 0 | 0 | 41.96 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 | 40.83 | 0 | 0 | 40.83 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 01:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 02:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 04:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 05:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 06:00 | 41.46 | 0 | 0 | 41.46 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 07:00 | 41.92 | 14.95 | 14.95 | 26.97 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 08:00 | 43.48 | 21.45 | 21.45 | 22.03 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 09:00 | 44.79 | 32.26 | 32.26 | 12.53 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 10:00 | 46.6 | 31.93 | 31.93 | 14.67 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 11:00 | 47.14 | 38.63 | 38.63 | 8.52 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 12:00 | 48.18 | 31.11 | 31.11 | 17.07 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 13:00 | 49.71 | 19.71 | 19.71 | 30.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 14:00 | 50.46 | 13.27 | 13.27 | 37.19 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 15:00 | 50.52 | 15.26 | 15.26 | 35.26 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 16:00 | 49.76 | 10.85 | 10.85 | 38.9 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 17:00 | 49.94 | 4.07 | 4.07 | 45.87 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 18:00 | 48.35 | 0 | 0 | 48.35 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 19:00 | 47.31 | 0 | 0 | 47.31 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 20:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 21:00 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 22:00 | 43.73 | 0 | 0 | 43.73 | 0 | 0 | 12.51 | 0 | 0
2025-03-16 23:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 | 41.76 | 0 | 0 | 41.76 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 01:00 | 41.66 | 0 | 0 | 41.66 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 02:00 | 38.86 | 0 | 0 | 38.86 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 03:00 | 39.16 | 0 | 0 | 39.16 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 04:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 05:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 06:00 | 40.6 | 0 | 0 | 40.6 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 07:00 | 42.16 | 0 | 0 | 42.16 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 08:00 | 43.1 | 2.45 | 2.45 | 40.65 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 09:00 | 45.43 | 4.31 | 4.31 | 41.12 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 10:00 | 46.88 | 5.16 | 5.16 | 41.72 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 11:00 | 48.62 | 7.18 | 7.18 | 41.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 12:00 | 49.97 | 7.39 | 7.39 | 42.59 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 13:00 | 51.07 | 62.54 | 62.54 | 0 | 11.47 | 0 | 23.4 | 0 | 0
2025-03-17 14:00 | 51.25 | 57.12 | 57.12 | 0 | 5.87 | 0 | 28.98 | 0 | 0
2025-03-17 15:00 | 52.73 | 51.99 | 51.99 | 0 | 0 | 0.74 | 28.21 | 0 | 0
2025-03-17 16:00 | 51.55 | 40.06 | 40.06 | 0 | 0 | 11.49 | 16.11 | 0 | 0
2025-03-17 17:00 | 49.84 | 19.98 | 19.98 | 26.44 | 0 | 3.42 | 12.51 | 0 | 0
2025-03-17 18:00 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 19:00 | 47.51 | 0 | 0 | 47.51 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 20:00 | 46.86 | 0 | 0 | 46.86 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 21:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 22:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 12.51 | 0 | 0
2025-03-17 23:00 | 43.32 | 0 | 0 | 43.32 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 01:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 02:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 03:00 | 39.13 | 0 | 0 | 39.13 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 04:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 05:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 06:00 | 40.29 | 0.04 | 0.04 | 40.24 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 07:00 | 42.22 | 0.01 | 0.01 | 42.22 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 08:00 | 43.58 | 41.14 | 41.14 | 2.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 09:00 | 44.78 | 104.28 | 104.28 | 0 | 59.5 | 0 | 69.03 | 0 | 0
2025-03-18 10:00 | 45.78 | 109.1 | 91.63 | 0 | 45.85 | 0 | 112.59 | 17.47 | 0
2025-03-18 11:00 | 47.09 | 99.65 | 47.09 | 0 | 0 | 0 | 112.59 | 52.56 | 0
2025-03-18 12:00 | 48.27 | 100.48 | 48.27 | 0 | 0 | 0 | 112.59 | 52.21 | 0
2025-03-18 13:00 | 49.15 | 61.6 | 49.15 | 0 | 0 | 0 | 112.59 | 12.44 | 0
2025-03-18 14:00 | 49.88 | 25.46 | 25.46 | 0 | 0 | 24.41 | 86.89 | 0 | 0
2025-03-18 15:00 | 50.27 | 3.68 | 3.68 | 0 | 0 | 46.59 | 37.85 | 0 | 0
2025-03-18 16:00 | 49.43 | 1.98 | 1.98 | 23.38 | 0 | 24.07 | 12.51 | 0 | 0
2025-03-18 17:00 | 48.88 | 25.22 | 25.22 | 23.66 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 18:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 19:00 | 47.67 | 0 | 0 | 47.67 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 20:00 | 45.97 | 0 | 0 | 45.97 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 21:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 22:00 | 44.06 | 0 | 0 | 44.06 | 0 | 0 | 12.51 | 0 | 0
2025-03-18 23:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 01:00 | 40.04 | 0 | 0 | 40.04 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 02:00 | 39.93 | 0 | 0 | 39.93 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 03:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 04:00 | 39.87 | 0 | 0 | 39.87 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 05:00 | 40.15 | 0 | 0 | 40.15 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 06:00 | 40.62 | 0 | 0 | 40.62 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 07:00 | 42.57 | 15.79 | 15.79 | 26.78 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 08:00 | 43.5 | 40 | 40 | 3.5 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 09:00 | 45.4 | 48.8 | 48.8 | 0 | 3.39 | 0 | 15.73 | 0 | 0
2025-03-19 10:00 | 46.44 | 80.53 | 80.53 | 0 | 34.08 | 0 | 48.11 | 0 | 0
2025-03-19 11:00 | 47.68 | 71.06 | 71.06 | 0 | 23.38 | 0 | 70.32 | 0 | 0
2025-03-19 12:00 | 49.55 | 66.07 | 66.07 | 0 | 16.52 | 0 | 86.01 | 0 | 0
2025-03-19 13:00 | 50.43 | 90.94 | 78.41 | 0 | 27.98 | 0 | 112.59 | 12.53 | 0
2025-03-19 14:00 | 51.23 | 94.6 | 51.23 | 0 | 0 | 0 | 112.59 | 43.36 | 0
2025-03-19 15:00 | 52.24 | 70.83 | 52.24 | 0 | 0 | 0 | 112.59 | 18.6 | 0
2025-03-19 16:00 | 51.08 | 65.82 | 51.08 | 0 | 0 | 0 | 112.59 | 14.74 | 0
2025-03-19 17:00 | 50.6 | 27.73 | 27.73 | 0 | 0 | 22.88 | 88.51 | 0 | 0
2025-03-19 18:00 | 48.89 | 0.33 | 0.33 | 0 | 0 | 48.57 | 37.39 | 0 | 0
2025-03-19 19:00 | 47.59 | 0 | 0 | 23.96 | 0 | 23.63 | 12.51 | 0 | 0
2025-03-19 20:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 21:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 22:00 | 43.36 | 0 | 0 | 43.36 | 0 | 0 | 12.51 | 0 | 0
2025-03-19 23:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 01:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 02:00 | 39.88 | 0 | 0 | 39.88 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 03:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 04:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 05:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 06:00 | 41.98 | 0.01 | 0.01 | 41.97 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 07:00 | 42.97 | 21.23 | 21.23 | 21.75 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 08:00 | 43.87 | 44.86 | 44.86 | 0 | 0.99 | 0 | 13.45 | 0 | 0
2025-03-20 09:00 | 44.99 | 70.98 | 70.98 | 0 | 26 | 0 | 38.15 | 0 | 0
2025-03-20 10:00 | 47.04 | 67.15 | 67.15 | 0 | 20.11 | 0 | 57.25 | 0 | 0
2025-03-20 11:00 | 48.96 | 70.78 | 70.78 | 0 | 21.82 | 0 | 77.98 | 0 | 0
2025-03-20 12:00 | 50.94 | 79.82 | 79.82 | 0 | 28.88 | 0 | 105.42 | 0 | 0
2025-03-20 13:00 | 50.91 | 84.15 | 58.46 | 0 | 7.55 | 0 | 112.59 | 25.69 | 0
2025-03-20 14:00 | 52.07 | 85.22 | 52.07 | 0 | 0 | 0 | 112.59 | 33.15 | 0
2025-03-20 15:00 | 52.69 | 79.71 | 52.69 | 0 | 0 | 0 | 112.59 | 27.02 | 0
2025-03-20 16:00 | 50.92 | 97.17 | 50.92 | 0 | 0 | 0 | 112.59 | 46.25 | 0
2025-03-20 17:00 | 51.95 | 71.64 | 51.95 | 0 | 0 | 0 | 112.59 | 19.69 | 0
2025-03-20 18:00 | 49.77 | 1.24 | 1.24 | 0 | 0 | 48.53 | 61.51 | 0 | 0
2025-03-20 19:00 | 49.15 | 0 | 0 | 2.6 | 0 | 46.55 | 12.51 | 0 | 0
2025-03-20 20:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 21:00 | 46.32 | 0 | 0 | 46.32 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 22:00 | 44.45 | 0 | 0 | 44.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-20 23:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 | 41.21 | 0 | 0 | 41.21 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 01:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 02:00 | 40.04 | 0 | 0 | 40.04 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 03:00 | 40.18 | 0 | 0 | 40.18 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 04:00 | 40.53 | 0 | 0 | 40.53 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 05:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 06:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 07:00 | 41.83 | 6.39 | 6.39 | 35.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 08:00 | 43.85 | 17.78 | 17.78 | 26.07 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 09:00 | 45.69 | 39.53 | 39.53 | 6.17 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 10:00 | 46.32 | 39.7 | 39.7 | 6.62 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 11:00 | 48.45 | 50.93 | 50.93 | 0 | 2.48 | 0 | 14.86 | 0 | 0
2025-03-21 12:00 | 49.66 | 49.98 | 49.98 | 0 | 0.32 | 0 | 15.17 | 0 | 0
2025-03-21 13:00 | 50.09 | 34.83 | 34.83 | 12.73 | 0 | 2.53 | 12.51 | 0 | 0
2025-03-21 14:00 | 49 | 23.98 | 23.98 | 25.02 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 15:00 | 50.07 | 12.79 | 12.79 | 37.28 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 16:00 | 51.48 | 9.36 | 9.36 | 42.12 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 17:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 18:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 19:00 | 48.75 | 0 | 0 | 48.75 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 20:00 | 46.87 | 0 | 0 | 46.87 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 21:00 | 46.04 | 0 | 0 | 46.04 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 22:00 | 44.22 | 0 | 0 | 44.22 | 0 | 0 | 12.51 | 0 | 0
2025-03-21 23:00 | 42.98 | 0 | 0 | 42.98 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 | 41.94 | 0 | 0 | 41.94 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 01:00 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 02:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 03:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 04:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 05:00 | 41.05 | 0 | 0 | 41.05 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 06:00 | 42.33 | 0.13 | 0.13 | 42.2 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 07:00 | 43.6 | 4.36 | 4.36 | 39.24 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 08:00 | 44.25 | 41.83 | 41.83 | 2.41 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 09:00 | 46.65 | 61.56 | 61.56 | 0 | 14.91 | 0 | 26.67 | 0 | 0
2025-03-22 10:00 | 48.16 | 56.68 | 56.68 | 0 | 8.52 | 0 | 34.77 | 0 | 0
2025-03-22 11:00 | 50.54 | 55.04 | 55.04 | 0 | 4.5 | 0 | 39.04 | 0 | 0
2025-03-22 12:00 | 50.23 | 70.72 | 70.72 | 0 | 20.49 | 0 | 58.51 | 0 | 0
2025-03-22 13:00 | 51.4 | 52.75 | 52.75 | 0 | 1.34 | 0 | 59.78 | 0 | 0
2025-03-22 14:00 | 52.17 | 69.78 | 69.78 | 0 | 17.61 | 0 | 76.51 | 0 | 0
2025-03-22 15:00 | 52.31 | 110.66 | 90.29 | 0 | 37.98 | 0 | 112.59 | 20.37 | 0
2025-03-22 16:00 | 51.88 | 75.8 | 51.88 | 0 | 0 | 0 | 112.59 | 23.92 | 0
2025-03-22 17:00 | 50.28 | 53.58 | 50.28 | 0 | 0 | 0 | 112.59 | 3.3 | 0
2025-03-22 18:00 | 50.39 | 0.52 | 0.52 | 0 | 0 | 49.87 | 60.1 | 0 | 0
2025-03-22 19:00 | 49.44 | 0 | 0 | 4.23 | 0 | 45.21 | 12.51 | 0 | 0
2025-03-22 20:00 | 47.45 | 0 | 0 | 47.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 21:00 | 47.03 | 0 | 0 | 47.03 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 22:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 12.51 | 0 | 0
2025-03-22 23:00 | 43.64 | 0 | 0 | 43.64 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 01:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 02:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 04:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 05:00 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 06:00 | 42.03 | 0.62 | 0.62 | 41.4 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 07:00 | 42.86 | 47.26 | 47.26 | 0 | 4.4 | 0 | 16.69 | 0 | 0
2025-03-23 08:00 | 44.51 | 88.35 | 88.35 | 0 | 43.84 | 0 | 58.34 | 0 | 0
2025-03-23 09:00 | 46.78 | 101.35 | 101.35 | 0 | 54.56 | 0 | 110.18 | 0 | 0
2025-03-23 10:00 | 46.84 | 96.08 | 49.38 | 0 | 2.54 | 0 | 112.59 | 46.7 | 0
2025-03-23 11:00 | 48.37 | 91.41 | 48.37 | 0 | 0 | 0 | 112.59 | 43.04 | 0
2025-03-23 12:00 | 49.77 | 90.52 | 49.77 | 0 | 0 | 0 | 112.59 | 40.76 | 0
2025-03-23 13:00 | 50.44 | 91.85 | 50.44 | 0 | 0 | 0 | 112.59 | 41.41 | 0
2025-03-23 14:00 | 50.33 | 97.14 | 50.33 | 0 | 0 | 0 | 112.59 | 46.81 | 0
2025-03-23 15:00 | 49.28 | 96.71 | 49.28 | 0 | 0 | 0 | 112.59 | 47.43 | 0
2025-03-23 16:00 | 50.58 | 79.24 | 50.58 | 0 | 0 | 0 | 112.59 | 28.66 | 0
2025-03-23 17:00 | 48.76 | 44.7 | 44.7 | 0 | 0 | 4.06 | 108.32 | 0 | 0
2025-03-23 18:00 | 49.87 | 0.91 | 0.91 | 0 | 0 | 48.96 | 56.78 | 0 | 0
2025-03-23 19:00 | 48.24 | 0 | 0 | 6.19 | 0 | 42.06 | 12.51 | 0 | 0
2025-03-23 20:00 | 47.48 | 0 | 0 | 47.48 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 21:00 | 45.21 | 0 | 0 | 45.21 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 22:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 12.51 | 0 | 0
2025-03-23 23:00 | 43.13 | 0 | 0 | 43.13 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 01:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 02:00 | 40.51 | 0 | 0 | 40.51 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 03:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 04:00 | 40.89 | 0 | 0 | 40.89 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 05:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 06:00 | 42.41 | 0.89 | 0.89 | 41.52 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 07:00 | 43.93 | 70.1 | 70.1 | 0 | 26.17 | 0 | 37.37 | 0 | 0
2025-03-24 08:00 | 44.47 | 96.17 | 96.17 | 0 | 51.71 | 0 | 86.49 | 0 | 0
2025-03-24 09:00 | 44.98 | 6.15 | 6.15 | 0 | 0 | 38.83 | 45.62 | 0 | 0
2025-03-24 10:00 | 47.34 | 29.44 | 29.44 | 0 | 0 | 17.9 | 26.78 | 0 | 0
2025-03-24 11:00 | 49.14 | 22.52 | 22.52 | 13.07 | 0 | 13.55 | 12.51 | 0 | 0
2025-03-24 12:00 | 49.35 | 53.96 | 53.96 | 0 | 4.61 | 0 | 16.89 | 0 | 0
2025-03-24 13:00 | 50.58 | 107.36 | 107.36 | 0 | 56.78 | 0 | 70.83 | 0 | 0
2025-03-24 14:00 | 50.84 | 112.43 | 94.79 | 0 | 43.95 | 0 | 112.59 | 17.64 | 0
2025-03-24 15:00 | 52.11 | 116.21 | 52.11 | 0 | 0 | 0 | 112.59 | 64.1 | 0
2025-03-24 16:00 | 51.56 | 112.42 | 51.56 | 0 | 0 | 0 | 112.59 | 60.86 | 0
2025-03-24 17:00 | 50.99 | 75.48 | 50.99 | 0 | 0 | 0 | 112.59 | 24.49 | 0
2025-03-24 18:00 | 50.15 | 2.42 | 2.42 | 0 | 0 | 47.72 | 62.36 | 0 | 0
2025-03-24 19:00 | 48.72 | 0 | 0 | 1.36 | 0 | 47.35 | 12.51 | 0 | 0
2025-03-24 20:00 | 47.53 | 0 | 0 | 47.53 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 21:00 | 45.42 | 0 | 0 | 45.42 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 22:00 | 43.47 | 0 | 0 | 43.47 | 0 | 0 | 12.51 | 0 | 0
2025-03-24 23:00 | 43.26 | 0 | 0 | 43.26 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 | 42.29 | 0 | 0 | 42.29 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 01:00 | 41.79 | 0 | 0 | 41.79 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 02:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 03:00 | 41.16 | 0 | 0 | 41.16 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 04:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 05:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 06:00 | 42.36 | 0.89 | 0.89 | 41.47 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 07:00 | 44.6 | 56.07 | 56.07 | 0 | 11.47 | 0 | 23.41 | 0 | 0
2025-03-25 08:00 | 45.46 | 81.64 | 81.64 | 0 | 36.17 | 0 | 57.77 | 0 | 0
2025-03-25 09:00 | 46.75 | 100.18 | 100.18 | 0 | 53.43 | 0 | 108.53 | 0 | 0
2025-03-25 10:00 | 47.43 | 95.28 | 51.7 | 0 | 4.27 | 0 | 112.59 | 43.58 | 0
2025-03-25 11:00 | 48.5 | 91.9 | 48.5 | 0 | 0 | 0 | 112.59 | 43.41 | 0
2025-03-25 12:00 | 50.44 | 93.31 | 50.44 | 0 | 0 | 0 | 112.59 | 42.87 | 0
2025-03-25 13:00 | 50.33 | 70.1 | 50.33 | 0 | 0 | 0 | 112.59 | 19.77 | 0
2025-03-25 14:00 | 51.29 | 75.5 | 51.29 | 0 | 0 | 0 | 112.59 | 24.22 | 0
2025-03-25 15:00 | 51.52 | 68.59 | 51.52 | 0 | 0 | 0 | 112.59 | 17.06 | 0
2025-03-25 16:00 | 52.2 | 49.36 | 49.36 | 0 | 0 | 2.84 | 109.6 | 0 | 0
2025-03-25 17:00 | 50.71 | 23.19 | 23.19 | 0 | 0 | 27.51 | 80.64 | 0 | 0
2025-03-25 18:00 | 48.83 | 1.04 | 1.04 | 0 | 0 | 47.78 | 30.34 | 0 | 0
2025-03-25 19:00 | 49.19 | 0 | 0 | 32.25 | 0 | 16.94 | 12.51 | 0 | 0
2025-03-25 20:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 21:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 22:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 12.51 | 0 | 0
2025-03-25 23:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 01:00 | 40.53 | 0 | 0 | 40.53 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 02:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 03:00 | 40.83 | 0 | 0 | 40.83 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 04:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 05:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 06:00 | 42.56 | 1.32 | 1.32 | 41.23 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 07:00 | 43.94 | 56.25 | 56.25 | 0 | 12.32 | 0 | 24.21 | 0 | 0
2025-03-26 08:00 | 44.63 | 89.86 | 89.86 | 0 | 45.23 | 0 | 67.18 | 0 | 0
2025-03-26 09:00 | 44.95 | 100.72 | 92.75 | 0 | 47.8 | 0 | 112.59 | 7.97 | 0
2025-03-26 10:00 | 47.48 | 99.55 | 47.48 | 0 | 0 | 0 | 112.59 | 52.07 | 0
2025-03-26 11:00 | 47.33 | 95.17 | 47.33 | 0 | 0 | 0 | 112.59 | 47.84 | 0
2025-03-26 12:00 | 49.14 | 91.87 | 49.14 | 0 | 0 | 0 | 112.59 | 42.73 | 0
2025-03-26 13:00 | 49.14 | 95.36 | 49.14 | 0 | 0 | 0 | 112.59 | 46.22 | 0
2025-03-26 14:00 | 49.36 | 97.22 | 49.36 | 0 | 0 | 0 | 112.59 | 47.86 | 0
2025-03-26 15:00 | 49.84 | 100.8 | 49.84 | 0 | 0 | 0 | 112.59 | 50.96 | 0
2025-03-26 16:00 | 49.85 | 90.11 | 49.85 | 0 | 0 | 0 | 112.59 | 40.26 | 0
2025-03-26 17:00 | 49.26 | 59.1 | 49.26 | 0 | 0 | 0 | 112.59 | 9.84 | 0
2025-03-26 18:00 | 49.28 | 1.43 | 1.43 | 0 | 0 | 47.85 | 62.22 | 0 | 0
2025-03-26 19:00 | 47.94 | 0 | 0 | 0.71 | 0 | 47.23 | 12.51 | 0 | 0
2025-03-26 20:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 21:00 | 46.07 | 0 | 0 | 46.07 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 22:00 | 44.3 | 0 | 0 | 44.3 | 0 | 0 | 12.51 | 0 | 0
2025-03-26 23:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 01:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 02:00 | 40.64 | 0 | 0 | 40.64 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 03:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 04:00 | 40.55 | 0 | 0 | 40.55 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 05:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 06:00 | 43.22 | 1.32 | 1.32 | 41.91 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 07:00 | 42.91 | 55.68 | 55.68 | 0 | 12.77 | 0 | 24.64 | 0 | 0
2025-03-27 08:00 | 44.61 | 93.66 | 93.66 | 0 | 49.05 | 0 | 71.24 | 0 | 0
2025-03-27 09:00 | 47.61 | 106.18 | 91.14 | 0 | 43.53 | 0 | 112.59 | 15.05 | 0
2025-03-27 10:00 | 49.49 | 107.81 | 49.49 | 0 | 0 | 0 | 112.59 | 58.32 | 0
2025-03-27 11:00 | 50.11 | 87.49 | 50.11 | 0 | 0 | 0 | 112.59 | 37.38 | 0
2025-03-27 12:00 | 51.62 | 76.58 | 51.62 | 0 | 0 | 0 | 112.59 | 24.96 | 0
2025-03-27 13:00 | 53.38 | 80.81 | 53.38 | 0 | 0 | 0 | 112.59 | 27.42 | 0
2025-03-27 14:00 | 52.63 | 93.62 | 52.63 | 0 | 0 | 0 | 112.59 | 40.98 | 0
2025-03-27 15:00 | 53.11 | 75.08 | 53.11 | 0 | 0 | 0 | 112.59 | 21.97 | 0
2025-03-27 16:00 | 53.65 | 37.82 | 37.82 | 0 | 0 | 15.84 | 95.92 | 0 | 0
2025-03-27 17:00 | 53.85 | 25.65 | 25.65 | 0 | 0 | 28.2 | 66.24 | 0 | 0
2025-03-27 18:00 | 51.72 | 1.4 | 1.4 | 0 | 0 | 50.32 | 13.27 | 0 | 0
2025-03-27 19:00 | 50.53 | 0 | 0 | 49.81 | 0 | 0.72 | 12.51 | 0 | 0
2025-03-27 20:00 | 49.38 | 0 | 0 | 49.38 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 21:00 | 48.11 | 0 | 0 | 48.11 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 22:00 | 45.04 | 0 | 0 | 45.04 | 0 | 0 | 12.51 | 0 | 0
2025-03-27 23:00 | 43.75 | 0 | 0 | 43.75 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 | 43.44 | 0 | 0 | 43.44 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 01:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 02:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 03:00 | 40.21 | 0 | 0 | 40.21 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 04:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 05:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 06:00 | 42.05 | 2.6 | 2.6 | 39.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 07:00 | 43.29 | 79.14 | 79.14 | 0 | 35.85 | 0 | 46.57 | 0 | 0
2025-03-28 08:00 | 45.35 | 111.12 | 107.85 | 0 | 62.5 | 0 | 105.94 | 3.27 | 0
2025-03-28 09:00 | 47.21 | 114.7 | 54.21 | 0 | 7 | 0 | 112.59 | 60.49 | 0
2025-03-28 10:00 | 48.12 | 111.79 | 48.12 | 0 | 0 | 0 | 112.59 | 63.67 | 0
2025-03-28 11:00 | 49.55 | 106.32 | 49.55 | 0 | 0 | 0 | 112.59 | 56.77 | 0
2025-03-28 12:00 | 50.92 | 102.67 | 50.92 | 0 | 0 | 0 | 112.59 | 51.75 | 0
2025-03-28 13:00 | 50.99 | 105.08 | 50.99 | 0 | 0 | 0 | 112.59 | 54.08 | 0
2025-03-28 14:00 | 52.37 | 109.65 | 52.37 | 0 | 0 | 0 | 112.59 | 57.28 | 0
2025-03-28 15:00 | 52.59 | 111.58 | 52.59 | 0 | 0 | 0 | 112.59 | 58.99 | 0
2025-03-28 16:00 | 53.3 | 106.52 | 53.3 | 0 | 0 | 0 | 112.59 | 53.22 | 0
2025-03-28 17:00 | 51.29 | 73.15 | 51.29 | 0 | 0 | 0 | 112.59 | 21.86 | 0
2025-03-28 18:00 | 50.4 | 2.01 | 2.01 | 0 | 0 | 48.39 | 61.65 | 0 | 0
2025-03-28 19:00 | 49.9 | 0 | 0 | 3.21 | 0 | 46.68 | 12.51 | 0 | 0
2025-03-28 20:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 21:00 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 22:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 12.51 | 0 | 0
2025-03-28 23:00 | 44.05 | 0 | 0 | 44.05 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 01:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 02:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 03:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 04:00 | 40.75 | 0 | 0 | 40.75 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 05:00 | 40.76 | 0 | 0 | 40.76 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 06:00 | 41.73 | 3.26 | 3.26 | 38.47 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 07:00 | 43.38 | 85.91 | 85.91 | 0 | 42.53 | 0 | 52.91 | 0 | 0
2025-03-29 08:00 | 44.88 | 114.49 | 107.38 | 0 | 62.5 | 0 | 112.29 | 7.11 | 0
2025-03-29 09:00 | 47.11 | 117.2 | 47.43 | 0 | 0.32 | 0 | 112.59 | 69.77 | 0
2025-03-29 10:00 | 48.24 | 112.6 | 48.24 | 0 | 0 | 0 | 112.59 | 64.37 | 0
2025-03-29 11:00 | 50.01 | 106.35 | 50.01 | 0 | 0 | 0 | 112.59 | 56.34 | 0
2025-03-29 12:00 | 51.3 | 103.21 | 51.3 | 0 | 0 | 0 | 112.59 | 51.91 | 0
2025-03-29 13:00 | 52.47 | 105.29 | 52.47 | 0 | 0 | 0 | 112.59 | 52.82 | 0
2025-03-29 14:00 | 53.99 | 109.28 | 53.99 | 0 | 0 | 0 | 112.59 | 55.29 | 0
2025-03-29 15:00 | 53.88 | 111.62 | 53.88 | 0 | 0 | 0 | 112.59 | 57.74 | 0
2025-03-29 16:00 | 53.34 | 108.92 | 53.34 | 0 | 0 | 0 | 112.59 | 55.58 | 0
2025-03-29 17:00 | 52.46 | 80.28 | 52.46 | 0 | 0 | 0 | 112.59 | 27.82 | 0
2025-03-29 18:00 | 51.47 | 2.78 | 2.78 | 0 | 0 | 48.68 | 61.35 | 0 | 0
2025-03-29 19:00 | 50.53 | 0 | 0 | 4.13 | 0 | 46.39 | 12.51 | 0 | 0
2025-03-29 20:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 21:00 | 46.73 | 0 | 0 | 46.73 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 22:00 | 45.56 | 0 | 0 | 45.56 | 0 | 0 | 12.51 | 0 | 0
2025-03-29 23:00 | 42.99 | 0 | 0 | 42.99 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 01:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 02:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 03:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 04:00 | 40.73 | 0 | 0 | 40.73 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 05:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 06:00 | 42.84 | 4.6 | 4.6 | 38.23 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 07:00 | 44.18 | 85.45 | 85.45 | 0 | 41.27 | 0 | 51.71 | 0 | 0
2025-03-30 08:00 | 45.81 | 112.38 | 108.31 | 0 | 62.5 | 0 | 111.09 | 4.07 | 0
2025-03-30 09:00 | 47.71 | 114.91 | 49.29 | 0 | 1.58 | 0 | 112.59 | 65.62 | 0
2025-03-30 10:00 | 49.91 | 111.14 | 49.91 | 0 | 0 | 0 | 112.59 | 61.24 | 0
2025-03-30 11:00 | 51.9 | 105.13 | 51.9 | 0 | 0 | 0 | 112.59 | 53.22 | 0
2025-03-30 12:00 | 52.73 | 102.74 | 52.73 | 0 | 0 | 0 | 112.59 | 50.01 | 0
2025-03-30 13:00 | 54.32 | 103.79 | 54.32 | 0 | 0 | 0 | 112.59 | 49.47 | 0
2025-03-30 14:00 | 54.31 | 107.48 | 54.31 | 0 | 0 | 0 | 112.59 | 53.17 | 0
2025-03-30 15:00 | 55.3 | 110.5 | 55.3 | 0 | 0 | 0 | 112.59 | 55.2 | 0
2025-03-30 16:00 | 54.28 | 104.55 | 54.28 | 0 | 0 | 0 | 112.59 | 50.27 | 0
2025-03-30 17:00 | 54.46 | 75.48 | 54.46 | 0 | 0 | 0 | 112.59 | 21.02 | 0
2025-03-30 18:00 | 53.84 | 3.03 | 3.03 | 0 | 0 | 50.81 | 59.11 | 0 | 0
2025-03-30 19:00 | 51.16 | 0 | 0 | 6.88 | 0 | 44.27 | 12.51 | 0 | 0
2025-03-30 20:00 | 48.38 | 0 | 0 | 48.38 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 21:00 | 47.38 | 0 | 0 | 47.38 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 22:00 | 46.48 | 0 | 0 | 46.48 | 0 | 0 | 12.51 | 0 | 0
2025-03-30 23:00 | 44.51 | 0 | 0 | 44.51 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 01:00 | 42.45 | 0 | 0 | 42.45 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 02:00 | 41.53 | 0 | 0 | 41.53 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 03:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 04:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 05:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 06:00 | 43.18 | 4.54 | 4.54 | 38.63 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 07:00 | 44.84 | 88.76 | 88.76 | 0 | 43.92 | 0 | 54.24 | 0 | 0
2025-03-31 08:00 | 45.88 | 113.26 | 107.31 | 0 | 61.43 | 0 | 112.59 | 5.96 | 0
2025-03-31 09:00 | 47.54 | 115.56 | 47.54 | 0 | 0 | 0 | 112.59 | 68.02 | 0
2025-03-31 10:00 | 50.53 | 112.89 | 50.53 | 0 | 0 | 0 | 112.59 | 62.36 | 0
2025-03-31 11:00 | 51.53 | 107.98 | 51.53 | 0 | 0 | 0 | 112.59 | 56.45 | 0
2025-03-31 12:00 | 53.35 | 104.82 | 53.35 | 0 | 0 | 0 | 112.59 | 51.47 | 0
2025-03-31 13:00 | 54.19 | 106.99 | 54.19 | 0 | 0 | 0 | 112.59 | 52.8 | 0
2025-03-31 14:00 | 54.59 | 111.66 | 54.59 | 0 | 0 | 0 | 112.59 | 57.07 | 0
2025-03-31 15:00 | 55.14 | 114.66 | 55.14 | 0 | 0 | 0 | 112.59 | 59.52 | 0
2025-03-31 16:00 | 55.6 | 112.13 | 55.6 | 0 | 0 | 0 | 112.59 | 56.54 | 0
2025-03-31 17:00 | 54.41 | 85.18 | 54.41 | 0 | 0 | 0 | 112.59 | 30.77 | 0
2025-03-31 18:00 | 52.09 | 4.07 | 4.07 | 0 | 0 | 48.02 | 62.04 | 0 | 0
2025-03-31 19:00 | 51.32 | 0 | 0 | 4.26 | 0 | 47.05 | 12.51 | 0 | 0
2025-03-31 20:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 21:00 | 47.73 | 0 | 0 | 47.73 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 22:00 | 45.14 | 0 | 0 | 45.14 | 0 | 0 | 12.51 | 0 | 0
2025-03-31 23:00 | 45.34 | 0 | 0 | 45.34 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 | 43.49 | 0 | 0 | 43.49 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 01:00 | 42.04 | 0 | 0 | 42.04 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 02:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 03:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 04:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 05:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 06:00 | 43.42 | 3.11 | 3.11 | 40.31 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 07:00 | 44.7 | 12.61 | 12.61 | 32.09 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 08:00 | 46.36 | 49.59 | 49.59 | 0 | 3.23 | 0 | 15.57 | 0 | 0
2025-04-01 09:00 | 48.09 | 55.41 | 55.41 | 0 | 7.32 | 0 | 22.53 | 0 | 0
2025-04-01 10:00 | 50.64 | 52.99 | 52.99 | 0 | 2.35 | 0 | 24.76 | 0 | 0
2025-04-01 11:00 | 51.54 | 70.33 | 70.33 | 0 | 18.79 | 0 | 42.62 | 0 | 0
2025-04-01 12:00 | 52.79 | 34.85 | 34.85 | 0 | 0 | 17.94 | 23.74 | 0 | 0
2025-04-01 13:00 | 55.18 | 68.41 | 68.41 | 0 | 13.23 | 0 | 36.3 | 0 | 0
2025-04-01 14:00 | 56 | 34.98 | 34.98 | 0 | 0 | 21.01 | 14.19 | 0 | 0
2025-04-01 15:00 | 56.2 | 49.87 | 49.87 | 4.74 | 0 | 1.59 | 12.51 | 0 | 0
2025-04-01 16:00 | 55.88 | 19.1 | 19.1 | 36.78 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 17:00 | 54.71 | 4.46 | 4.46 | 50.25 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 18:00 | 53.99 | 0 | 0 | 53.99 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 19:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 20:00 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 21:00 | 48.02 | 0 | 0 | 48.02 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 22:00 | 47.3 | 0 | 0 | 47.3 | 0 | 0 | 12.51 | 0 | 0
2025-04-01 23:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 | 43.51 | 0 | 0 | 43.51 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 01:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 02:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 03:00 | 41.09 | 0 | 0 | 41.09 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 04:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 05:00 | 42.39 | 0 | 0 | 42.39 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 06:00 | 43.07 | 0.52 | 0.52 | 42.55 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 07:00 | 43.58 | 4.07 | 4.07 | 39.51 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 08:00 | 46.64 | 9.3 | 9.3 | 37.34 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 09:00 | 48.64 | 14.88 | 14.88 | 33.76 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 10:00 | 50.37 | 23.3 | 23.3 | 27.06 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 11:00 | 51.37 | 26.41 | 26.41 | 24.96 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 12:00 | 52.56 | 25.56 | 25.56 | 27 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 13:00 | 54.23 | 21.26 | 21.26 | 32.97 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 14:00 | 55.05 | 19.85 | 19.85 | 35.2 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 15:00 | 55 | 17.83 | 17.83 | 37.17 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 16:00 | 53.74 | 11.22 | 11.22 | 42.53 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 17:00 | 53.67 | 5.12 | 5.12 | 48.55 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 18:00 | 52.76 | 0.27 | 0.27 | 52.49 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 19:00 | 50.29 | 0 | 0 | 50.29 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 20:00 | 49.86 | 0 | 0 | 49.86 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 21:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 22:00 | 46.54 | 0 | 0 | 46.54 | 0 | 0 | 12.51 | 0 | 0
2025-04-02 23:00 | 45.37 | 0 | 0 | 45.37 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 01:00 | 42.29 | 0 | 0 | 42.29 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 02:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 03:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 04:00 | 41.17 | 0 | 0 | 41.17 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 05:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 06:00 | 44.07 | 1.17 | 1.17 | 42.9 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 07:00 | 44.25 | 6.13 | 6.13 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 08:00 | 46.78 | 16.34 | 16.34 | 30.44 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 09:00 | 47.89 | 19.67 | 19.67 | 28.22 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 10:00 | 49.71 | 26.73 | 26.73 | 22.97 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 11:00 | 51.23 | 21.46 | 21.46 | 29.77 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 12:00 | 52.72 | 28.87 | 28.87 | 23.85 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 13:00 | 53.2 | 32.61 | 32.61 | 20.59 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 14:00 | 54.44 | 28.94 | 28.94 | 25.5 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 15:00 | 54.09 | 25.94 | 25.94 | 28.14 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 16:00 | 54.05 | 14.72 | 14.72 | 39.33 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 17:00 | 52.74 | 4.65 | 4.65 | 48.09 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 18:00 | 53.31 | 0.27 | 0.27 | 53.04 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 19:00 | 51.23 | 0 | 0 | 51.23 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 20:00 | 49.89 | 0 | 0 | 49.89 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 21:00 | 47.13 | 0 | 0 | 47.13 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 22:00 | 45.89 | 0 | 0 | 45.89 | 0 | 0 | 12.51 | 0 | 0
2025-04-03 23:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 01:00 | 41.5 | 0 | 0 | 41.5 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 02:00 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 03:00 | 41.27 | 0 | 0 | 41.27 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 04:00 | 42.48 | 0 | 0 | 42.48 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 05:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 06:00 | 43.65 | 9.78 | 9.78 | 33.87 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 07:00 | 45.55 | 102.33 | 102.33 | 0 | 56.78 | 0 | 66.45 | 0 | 0
2025-04-04 08:00 | 46.15 | 124.05 | 94.72 | 0 | 48.57 | 0 | 112.59 | 29.33 | 0
2025-04-04 09:00 | 47.86 | 121.2 | 47.86 | 0 | 0 | 0 | 112.59 | 73.34 | 0
2025-04-04 10:00 | 50 | 123.82 | 50 | 0 | 0 | 0 | 112.59 | 73.83 | 0
2025-04-04 11:00 | 52.13 | 88.13 | 52.13 | 0 | 0 | 0 | 112.59 | 36 | 0
2025-04-04 12:00 | 52.44 | 52.44 | 52.44 | 0 | 0 | 0 | 112.59 | 0 | 0
2025-04-04 13:00 | 53.33 | 22.17 | 22.17 | 0 | 0 | 31.16 | 79.79 | 0 | 0
2025-04-04 14:00 | 55.24 | 36.57 | 36.57 | 0 | 0 | 18.68 | 60.13 | 0 | 0
2025-04-04 15:00 | 54.76 | 28.49 | 28.49 | 0 | 0 | 26.27 | 32.48 | 0 | 0
2025-04-04 16:00 | 54.64 | 30.1 | 30.1 | 5.57 | 0 | 18.97 | 12.51 | 0 | 0
2025-04-04 17:00 | 53.24 | 12.32 | 12.32 | 40.92 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 18:00 | 52.77 | 5.39 | 5.39 | 47.38 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 19:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 20:00 | 50.56 | 0 | 0 | 50.56 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 21:00 | 47.97 | 0 | 0 | 47.97 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 22:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 12.51 | 0 | 0
2025-04-04 23:00 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 01:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 02:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 03:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 04:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 05:00 | 43.25 | 0 | 0 | 43.25 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 06:00 | 44.34 | 3.66 | 3.66 | 40.68 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 07:00 | 44.47 | 69.96 | 69.96 | 0 | 25.5 | 0 | 36.73 | 0 | 0
2025-04-05 08:00 | 46.21 | 93.95 | 93.95 | 0 | 47.74 | 0 | 82.09 | 0 | 0
2025-04-05 09:00 | 47.6 | 49.3 | 49.3 | 0 | 1.7 | 0 | 83.7 | 0 | 0
2025-04-05 10:00 | 48.24 | 73.96 | 73.96 | 0 | 25.72 | 0 | 108.13 | 0 | 0
2025-04-05 11:00 | 49.68 | 87.07 | 54.37 | 0 | 4.69 | 0 | 112.59 | 32.7 | 0
2025-04-05 12:00 | 50.45 | 56.86 | 50.45 | 0 | 0 | 0 | 112.59 | 6.41 | 0
2025-04-05 13:00 | 51.52 | 49.81 | 49.81 | 0 | 0 | 1.71 | 110.79 | 0 | 0
2025-04-05 14:00 | 51.84 | 18.98 | 18.98 | 0 | 0 | 32.86 | 76.19 | 0 | 0
2025-04-05 15:00 | 51.17 | 53.64 | 53.64 | 0 | 2.47 | 0 | 78.54 | 0 | 0
2025-04-05 16:00 | 51.13 | 82.27 | 82.27 | 0 | 31.13 | 0 | 108.11 | 0 | 0
2025-04-05 17:00 | 51.28 | 61.51 | 56 | 0 | 4.71 | 0 | 112.59 | 5.51 | 0
2025-04-05 18:00 | 50.15 | 4.54 | 4.54 | 0 | 0 | 45.62 | 64.57 | 0 | 0
2025-04-05 19:00 | 50 | 0 | 0 | 0.54 | 0 | 49.46 | 12.51 | 0 | 0
2025-04-05 20:00 | 48.69 | 0 | 0 | 48.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 21:00 | 47.07 | 0 | 0 | 47.07 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 22:00 | 45.75 | 0 | 0 | 45.75 | 0 | 0 | 12.51 | 0 | 0
2025-04-05 23:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 01:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 02:00 | 41.77 | 0 | 0 | 41.77 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 03:00 | 41.93 | 0 | 0 | 41.93 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 04:00 | 43.22 | 0 | 0 | 43.22 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 05:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 06:00 | 42.82 | 4.61 | 4.61 | 38.21 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 07:00 | 45.72 | 20.71 | 20.71 | 25.01 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 08:00 | 46.08 | 50.81 | 50.81 | 0 | 4.73 | 0 | 17 | 0 | 0
2025-04-06 09:00 | 47.89 | 57.76 | 57.76 | 0 | 9.87 | 0 | 26.37 | 0 | 0
2025-04-06 10:00 | 48.9 | 64.28 | 64.28 | 0 | 15.38 | 0 | 40.99 | 0 | 0
2025-04-06 11:00 | 50.41 | 67.98 | 67.98 | 0 | 17.57 | 0 | 57.68 | 0 | 0
2025-04-06 12:00 | 50.65 | 49.64 | 49.64 | 0 | 0 | 1.01 | 56.62 | 0 | 0
2025-04-06 13:00 | 51.63 | 48.22 | 48.22 | 0 | 0 | 3.42 | 53.02 | 0 | 0
2025-04-06 14:00 | 52.3 | 47.36 | 47.36 | 0 | 0 | 4.94 | 47.83 | 0 | 0
2025-04-06 15:00 | 51.68 | 100.98 | 100.98 | 0 | 49.3 | 0 | 94.66 | 0 | 0
2025-04-06 16:00 | 51.72 | 78.76 | 70.6 | 0 | 18.88 | 0 | 112.59 | 8.16 | 0
2025-04-06 17:00 | 51.55 | 79.15 | 51.55 | 0 | 0 | 0 | 112.59 | 27.6 | 0
2025-04-06 18:00 | 50.41 | 11.1 | 11.1 | 0 | 0 | 39.31 | 71.21 | 0 | 0
2025-04-06 19:00 | 50.06 | 0 | 0 | 0 | 0 | 50.06 | 18.52 | 0 | 0
2025-04-06 20:00 | 49.25 | 0 | 0 | 43.54 | 0 | 5.71 | 12.51 | 0 | 0
2025-04-06 21:00 | 47.7 | 0 | 0 | 47.7 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 22:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 12.51 | 0 | 0
2025-04-06 23:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 01:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 02:00 | 42.87 | 0 | 0 | 42.87 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 03:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 04:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 05:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 06:00 | 44.11 | 3.28 | 3.28 | 40.82 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 07:00 | 46.04 | 17.34 | 17.34 | 28.7 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 08:00 | 46.98 | 39.72 | 39.72 | 7.26 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 09:00 | 47.3 | 13.38 | 13.38 | 33.91 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 10:00 | 49.76 | 14.62 | 14.62 | 35.14 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 11:00 | 51.3 | 44.81 | 44.81 | 6.49 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 12:00 | 51.48 | 56.77 | 56.77 | 0 | 5.28 | 0 | 17.53 | 0 | 0
2025-04-07 13:00 | 52.74 | 99.85 | 99.85 | 0 | 47.1 | 0 | 62.28 | 0 | 0
2025-04-07 14:00 | 52.29 | 114.26 | 105.25 | 0 | 52.96 | 0 | 112.59 | 9.01 | 0
2025-04-07 15:00 | 52.02 | 52.45 | 52.02 | 0 | 0 | 0 | 112.59 | 0.44 | 0
2025-04-07 16:00 | 52.7 | 103.3 | 52.7 | 0 | 0 | 0 | 112.59 | 50.6 | 0
2025-04-07 17:00 | 51.37 | 76.92 | 51.37 | 0 | 0 | 0 | 112.59 | 25.55 | 0
2025-04-07 18:00 | 51.48 | 6.85 | 6.85 | 0 | 0 | 44.62 | 65.62 | 0 | 0
2025-04-07 19:00 | 51.33 | 0 | 0 | 0.87 | 0 | 50.45 | 12.51 | 0 | 0
2025-04-07 20:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 21:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 22:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 12.51 | 0 | 0
2025-04-07 23:00 | 45.23 | 0 | 0 | 45.23 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 01:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 02:00 | 42.76 | 0 | 0 | 42.76 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 03:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 04:00 | 42.35 | 0 | 0 | 42.35 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 05:00 | 43.18 | 0 | 0 | 43.18 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 06:00 | 43.66 | 14.91 | 14.91 | 28.74 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 07:00 | 45.91 | 74.11 | 74.11 | 0 | 28.2 | 0 | 39.3 | 0 | 0
2025-04-08 08:00 | 46.47 | 96.98 | 96.98 | 0 | 50.51 | 0 | 87.29 | 0 | 0
2025-04-08 09:00 | 49.01 | 105.24 | 75.65 | 0 | 26.64 | 0 | 112.59 | 29.59 | 0
2025-04-08 10:00 | 50.68 | 101.39 | 50.68 | 0 | 0 | 0 | 112.59 | 50.72 | 0
2025-04-08 11:00 | 51.5 | 102.42 | 51.5 | 0 | 0 | 0 | 112.59 | 50.92 | 0
2025-04-08 12:00 | 52.37 | 102.53 | 52.37 | 0 | 0 | 0 | 112.59 | 50.16 | 0
2025-04-08 13:00 | 53.43 | 98.12 | 53.43 | 0 | 0 | 0 | 112.59 | 44.68 | 0
2025-04-08 14:00 | 52.28 | 96.16 | 52.28 | 0 | 0 | 0 | 112.59 | 43.88 | 0
2025-04-08 15:00 | 54.02 | 101.12 | 54.02 | 0 | 0 | 0 | 112.59 | 47.11 | 0
2025-04-08 16:00 | 53.65 | 92.8 | 53.65 | 0 | 0 | 0 | 112.59 | 39.15 | 0
2025-04-08 17:00 | 53.21 | 64.85 | 53.21 | 0 | 0 | 0 | 112.59 | 11.64 | 0
2025-04-08 18:00 | 52.81 | 10.05 | 10.05 | 0 | 0 | 42.76 | 67.58 | 0 | 0
2025-04-08 19:00 | 51.36 | 0 | 0 | 0 | 0 | 51.36 | 13.52 | 0 | 0
2025-04-08 20:00 | 49.51 | 0 | 0 | 48.55 | 0 | 0.96 | 12.51 | 0 | 0
2025-04-08 21:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 22:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 12.51 | 0 | 0
2025-04-08 23:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 | 44.4 | 0 | 0 | 44.4 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 01:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 02:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 03:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 04:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 05:00 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 06:00 | 44.41 | 18.68 | 18.68 | 25.73 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 07:00 | 45.58 | 81.76 | 81.76 | 0 | 36.18 | 0 | 46.88 | 0 | 0
2025-04-09 08:00 | 47.53 | 92.74 | 92.74 | 0 | 45.22 | 0 | 89.83 | 0 | 0
2025-04-09 09:00 | 49.27 | 100.13 | 73.22 | 0 | 23.95 | 0 | 112.59 | 26.91 | 0
2025-04-09 10:00 | 51.68 | 98.85 | 51.68 | 0 | 0 | 0 | 112.59 | 47.17 | 0
2025-04-09 11:00 | 54.62 | 97.36 | 54.62 | 0 | 0 | 0 | 112.59 | 42.75 | 0
2025-04-09 12:00 | 54.75 | 98.62 | 54.75 | 0 | 0 | 0 | 112.59 | 43.87 | 0
2025-04-09 13:00 | 56.11 | 98.85 | 56.11 | 0 | 0 | 0 | 112.59 | 42.74 | 0
2025-04-09 14:00 | 56.87 | 103.87 | 56.87 | 0 | 0 | 0 | 112.59 | 47 | 0
2025-04-09 15:00 | 58.67 | 103.3 | 58.67 | 0 | 0 | 0 | 112.59 | 44.63 | 0
2025-04-09 16:00 | 57.29 | 95.73 | 57.29 | 0 | 0 | 0 | 112.59 | 38.44 | 0
2025-04-09 17:00 | 56.68 | 78.52 | 56.68 | 0 | 0 | 0 | 112.59 | 21.84 | 0
2025-04-09 18:00 | 55.18 | 11.82 | 11.82 | 0 | 0 | 43.36 | 66.95 | 0 | 0
2025-04-09 19:00 | 53.23 | 0 | 0 | 1.51 | 0 | 51.71 | 12.51 | 0 | 0
2025-04-09 20:00 | 51.64 | 0 | 0 | 51.64 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 21:00 | 50.95 | 0 | 0 | 50.95 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 22:00 | 48.41 | 0 | 0 | 48.41 | 0 | 0 | 12.51 | 0 | 0
2025-04-09 23:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 | 44.72 | 0 | 0 | 44.72 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 01:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 02:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 03:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 04:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 05:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 06:00 | 44.16 | 4.4 | 4.4 | 39.76 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 07:00 | 45.74 | 1.1 | 1.1 | 44.64 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 08:00 | 47.8 | 3.89 | 3.89 | 43.92 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 09:00 | 49.27 | 25.95 | 25.95 | 23.31 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 10:00 | 50.43 | 110.24 | 110.24 | 0 | 59.81 | 0 | 69.33 | 0 | 0
2025-04-10 11:00 | 51.2 | 115.78 | 96.74 | 0 | 45.54 | 0 | 112.59 | 19.04 | 0
2025-04-10 12:00 | 53.2 | 112.86 | 53.2 | 0 | 0 | 0 | 112.59 | 59.66 | 0
2025-04-10 13:00 | 54.51 | 72.39 | 54.51 | 0 | 0 | 0 | 112.59 | 17.88 | 0
2025-04-10 14:00 | 53.88 | 56.82 | 53.88 | 0 | 0 | 0 | 112.59 | 2.94 | 0
2025-04-10 15:00 | 54.97 | 117.8 | 54.97 | 0 | 0 | 0 | 112.59 | 62.82 | 0
2025-04-10 16:00 | 54.65 | 84.24 | 54.65 | 0 | 0 | 0 | 112.59 | 29.59 | 0
2025-04-10 17:00 | 54.35 | 88.71 | 54.35 | 0 | 0 | 0 | 112.59 | 34.36 | 0
2025-04-10 18:00 | 53.58 | 16.08 | 16.08 | 0 | 0 | 37.5 | 73.11 | 0 | 0
2025-04-10 19:00 | 51.66 | 0 | 0 | 0 | 0 | 51.66 | 18.73 | 0 | 0
2025-04-10 20:00 | 49.82 | 0 | 0 | 43.91 | 0 | 5.91 | 12.51 | 0 | 0
2025-04-10 21:00 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 22:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 12.51 | 0 | 0
2025-04-10 23:00 | 45.56 | 0 | 0 | 45.56 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 01:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 02:00 | 43.54 | 0 | 0 | 43.54 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 03:00 | 42.82 | 0 | 0 | 42.82 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 04:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 05:00 | 43.89 | 0 | 0 | 43.89 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 06:00 | 44.86 | 24.54 | 24.54 | 20.33 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 07:00 | 45.96 | 79.42 | 79.42 | 0 | 33.46 | 0 | 44.3 | 0 | 0
2025-04-11 08:00 | 47.73 | 105.97 | 105.97 | 0 | 58.24 | 0 | 99.62 | 0 | 0
2025-04-11 09:00 | 49.42 | 115.39 | 63.07 | 0 | 13.65 | 0 | 112.59 | 52.32 | 0
2025-04-11 10:00 | 52.74 | 101.85 | 52.74 | 0 | 0 | 0 | 112.59 | 49.11 | 0
2025-04-11 11:00 | 53.33 | 77.36 | 53.33 | 0 | 0 | 0 | 112.59 | 24.03 | 0
2025-04-11 12:00 | 54.2 | 82.59 | 54.2 | 0 | 0 | 0 | 112.59 | 28.39 | 0
2025-04-11 13:00 | 55.71 | 97.07 | 55.71 | 0 | 0 | 0 | 112.59 | 41.36 | 0
2025-04-11 14:00 | 55.62 | 80.71 | 55.62 | 0 | 0 | 0 | 112.59 | 25.08 | 0
2025-04-11 15:00 | 57.1 | 75.14 | 57.1 | 0 | 0 | 0 | 112.59 | 18.04 | 0
2025-04-11 16:00 | 55.8 | 56.58 | 55.8 | 0 | 0 | 0 | 112.59 | 0.79 | 0
2025-04-11 17:00 | 55.73 | 59.13 | 55.73 | 0 | 0 | 0 | 112.59 | 3.4 | 0
2025-04-11 18:00 | 54.97 | 11.73 | 11.73 | 0 | 0 | 43.24 | 67.07 | 0 | 0
2025-04-11 19:00 | 53.25 | 0 | 0 | 1.41 | 0 | 51.83 | 12.51 | 0 | 0
2025-04-11 20:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 21:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 22:00 | 47.78 | 0 | 0 | 47.78 | 0 | 0 | 12.51 | 0 | 0
2025-04-11 23:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 01:00 | 44.3 | 0 | 0 | 44.3 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 02:00 | 42.74 | 0 | 0 | 42.74 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 03:00 | 42.14 | 0 | 0 | 42.14 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 04:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 05:00 | 44.11 | 0 | 0 | 44.11 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 06:00 | 45.16 | 20.01 | 20.01 | 25.16 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 07:00 | 46.82 | 75.02 | 75.02 | 0 | 28.2 | 0 | 39.3 | 0 | 0
2025-04-12 08:00 | 48.5 | 119.78 | 111 | 0 | 62.5 | 0 | 98.68 | 8.77 | 0
2025-04-12 09:00 | 51.28 | 124.64 | 65.92 | 0 | 14.65 | 0 | 112.59 | 58.71 | 0
2025-04-12 10:00 | 53.14 | 122.32 | 53.14 | 0 | 0 | 0 | 112.59 | 69.17 | 0
2025-04-12 11:00 | 55.75 | 118.16 | 55.75 | 0 | 0 | 0 | 112.59 | 62.4 | 0
2025-04-12 12:00 | 58.52 | 115.65 | 58.52 | 0 | 0 | 0 | 112.59 | 57.13 | 0
2025-04-12 13:00 | 60.18 | 7.21 | 7.21 | 0 | 0 | 52.97 | 56.83 | 0 | 0
2025-04-12 14:00 | 60.35 | 53.97 | 53.97 | 0 | 0 | 6.37 | 50.12 | 0 | 0
2025-04-12 15:00 | 60.79 | 98.2 | 98.2 | 0 | 37.41 | 0 | 85.66 | 0 | 0
2025-04-12 16:00 | 60.89 | 118.28 | 89.24 | 0 | 28.35 | 0 | 112.59 | 29.04 | 0
2025-04-12 17:00 | 60.61 | 99.43 | 60.61 | 0 | 0 | 0 | 112.59 | 38.83 | 0
2025-04-12 18:00 | 57.08 | 20.2 | 20.2 | 0 | 0 | 36.88 | 73.76 | 0 | 0
2025-04-12 19:00 | 56.02 | 0 | 0 | 0 | 0 | 56.02 | 14.79 | 0 | 0
2025-04-12 20:00 | 52.78 | 0 | 0 | 50.61 | 0 | 2.17 | 12.51 | 0 | 0
2025-04-12 21:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 22:00 | 48.45 | 0 | 0 | 48.45 | 0 | 0 | 12.51 | 0 | 0
2025-04-12 23:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 01:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 02:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 03:00 | 41.93 | 0 | 0 | 41.93 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 04:00 | 43.31 | 0 | 0 | 43.31 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 05:00 | 44.06 | 0 | 0 | 44.06 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 06:00 | 45.3 | 30.47 | 30.47 | 14.84 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 07:00 | 45.66 | 91.46 | 91.46 | 0 | 45.8 | 0 | 56.02 | 0 | 0
2025-04-13 08:00 | 48.35 | 108.65 | 107.9 | 0 | 59.55 | 0 | 112.59 | 0.75 | 0
2025-04-13 09:00 | 50.41 | 111.39 | 50.41 | 0 | 0 | 0 | 112.59 | 60.98 | 0
2025-04-13 10:00 | 51.4 | 108.26 | 51.4 | 0 | 0 | 0 | 112.59 | 56.86 | 0
2025-04-13 11:00 | 53.6 | 104.16 | 53.6 | 0 | 0 | 0 | 112.59 | 50.56 | 0
2025-04-13 12:00 | 54.97 | 104.1 | 54.97 | 0 | 0 | 0 | 112.59 | 49.13 | 0
2025-04-13 13:00 | 57.02 | 109 | 57.02 | 0 | 0 | 0 | 112.59 | 51.98 | 0
2025-04-13 14:00 | 57.73 | 112.54 | 57.73 | 0 | 0 | 0 | 112.59 | 54.8 | 0
2025-04-13 15:00 | 56.17 | 112.52 | 56.17 | 0 | 0 | 0 | 112.59 | 56.35 | 0
2025-04-13 16:00 | 58.02 | 109.05 | 58.02 | 0 | 0 | 0 | 112.59 | 51.03 | 0
2025-04-13 17:00 | 55.64 | 91.81 | 55.64 | 0 | 0 | 0 | 112.59 | 36.16 | 0
2025-04-13 18:00 | 55.51 | 18.04 | 18.04 | 0 | 0 | 37.47 | 73.15 | 0 | 0
2025-04-13 19:00 | 54.09 | 0 | 0 | 0 | 0 | 54.09 | 16.22 | 0 | 0
2025-04-13 20:00 | 51.42 | 0 | 0 | 47.9 | 0 | 3.52 | 12.51 | 0 | 0
2025-04-13 21:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 22:00 | 48.15 | 0 | 0 | 48.15 | 0 | 0 | 12.51 | 0 | 0
2025-04-13 23:00 | 46.71 | 0 | 0 | 46.71 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 | 45.22 | 0 | 0 | 45.22 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 01:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 02:00 | 43.09 | 0 | 0 | 43.09 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 03:00 | 42.7 | 0 | 0 | 42.7 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 04:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 05:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 06:00 | 45.47 | 16.71 | 16.71 | 28.75 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 07:00 | 46.46 | 66.96 | 66.96 | 0 | 20.5 | 0 | 31.98 | 0 | 0
2025-04-14 08:00 | 48.29 | 82.55 | 82.55 | 0 | 34.26 | 0 | 64.53 | 0 | 0
2025-04-14 09:00 | 50.77 | 98.27 | 98.27 | 0 | 47.5 | 0 | 109.66 | 0 | 0
2025-04-14 10:00 | 53.05 | 105.36 | 56.14 | 0 | 3.09 | 0 | 112.59 | 49.22 | 0
2025-04-14 11:00 | 55.97 | 99.99 | 55.97 | 0 | 0 | 0 | 112.59 | 44.02 | 0
2025-04-14 12:00 | 58.01 | 96.77 | 58.01 | 0 | 0 | 0 | 112.59 | 38.76 | 0
2025-04-14 13:00 | 58.97 | 96.48 | 58.97 | 0 | 0 | 0 | 112.59 | 37.51 | 0
2025-04-14 14:00 | 60.73 | 80.36 | 60.73 | 0 | 0 | 0 | 112.59 | 19.63 | 0
2025-04-14 15:00 | 61.04 | 88.06 | 61.04 | 0 | 0 | 0 | 112.59 | 27.02 | 0
2025-04-14 16:00 | 60.14 | 63.55 | 60.14 | 0 | 0 | 0 | 112.59 | 3.41 | 0
2025-04-14 17:00 | 58.64 | 74.27 | 58.64 | 0 | 0 | 0 | 112.59 | 15.64 | 0
2025-04-14 18:00 | 58.31 | 17.53 | 17.53 | 0 | 0 | 40.78 | 69.66 | 0 | 0
2025-04-14 19:00 | 55.54 | 0 | 0 | 1.25 | 0 | 54.3 | 12.51 | 0 | 0
2025-04-14 20:00 | 53.42 | 0 | 0 | 53.42 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 21:00 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 22:00 | 48.37 | 0 | 0 | 48.37 | 0 | 0 | 12.51 | 0 | 0
2025-04-14 23:00 | 46.06 | 0 | 0 | 46.06 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 01:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 02:00 | 44.71 | 0 | 0 | 44.71 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 03:00 | 42.37 | 0 | 0 | 42.37 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 04:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 05:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 06:00 | 45.92 | 32.3 | 32.3 | 13.62 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 07:00 | 46.7 | 82.6 | 82.6 | 0 | 35.89 | 0 | 46.61 | 0 | 0
2025-04-15 08:00 | 48.65 | 97.7 | 97.7 | 0 | 49.05 | 0 | 93.21 | 0 | 0
2025-04-15 09:00 | 49.18 | 104.08 | 69.58 | 0 | 20.4 | 0 | 112.59 | 34.5 | 0
2025-04-15 10:00 | 51.41 | 101.77 | 51.41 | 0 | 0 | 0 | 112.59 | 50.36 | 0
2025-04-15 11:00 | 52.66 | 99.76 | 52.66 | 0 | 0 | 0 | 112.59 | 47.1 | 0
2025-04-15 12:00 | 53.44 | 100.93 | 53.44 | 0 | 0 | 0 | 112.59 | 47.49 | 0
2025-04-15 13:00 | 55.32 | 104.05 | 55.32 | 0 | 0 | 0 | 112.59 | 48.73 | 0
2025-04-15 14:00 | 54.67 | 106.25 | 54.67 | 0 | 0 | 0 | 112.59 | 51.59 | 0
2025-04-15 15:00 | 55.31 | 104.12 | 55.31 | 0 | 0 | 0 | 112.59 | 48.81 | 0
2025-04-15 16:00 | 55.52 | 100.34 | 55.52 | 0 | 0 | 0 | 112.59 | 44.81 | 0
2025-04-15 17:00 | 54.84 | 85.95 | 54.84 | 0 | 0 | 0 | 112.59 | 31.11 | 0
2025-04-15 18:00 | 54.58 | 19.53 | 19.53 | 0 | 0 | 35.05 | 75.69 | 0 | 0
2025-04-15 19:00 | 53.35 | 0 | 0 | 0 | 0 | 53.35 | 19.54 | 0 | 0
2025-04-15 20:00 | 52.19 | 0 | 0 | 45.52 | 0 | 6.67 | 12.51 | 0 | 0
2025-04-15 21:00 | 50.48 | 0 | 0 | 50.48 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 22:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 12.51 | 0 | 0
2025-04-15 23:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 01:00 | 44.36 | 0 | 0 | 44.36 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 02:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 03:00 | 42.84 | 0 | 0 | 42.84 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 04:00 | 43.14 | 0 | 0 | 43.14 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 05:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 06:00 | 45.56 | 9.12 | 9.12 | 36.44 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 07:00 | 46.93 | 19.7 | 19.7 | 27.22 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 08:00 | 48.51 | 30.65 | 30.65 | 17.86 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 09:00 | 50.5 | 53.51 | 53.51 | 0 | 3.01 | 0 | 15.37 | 0 | 0
2025-04-16 10:00 | 52.2 | 58.5 | 58.5 | 0 | 6.3 | 0 | 21.36 | 0 | 0
2025-04-16 11:00 | 55.11 | 54.2 | 54.2 | 0 | 0 | 0.91 | 20.41 | 0 | 0
2025-04-16 12:00 | 56.2 | 42.96 | 42.96 | 5.74 | 0 | 7.5 | 12.51 | 0 | 0
2025-04-16 13:00 | 56.91 | 48.5 | 48.5 | 8.41 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 14:00 | 58.48 | 46.21 | 46.21 | 12.27 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 15:00 | 58.05 | 32.68 | 32.68 | 25.37 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 16:00 | 57.38 | 17.82 | 17.82 | 39.55 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 17:00 | 57.85 | 7.45 | 7.45 | 50.4 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 18:00 | 55.9 | 0 | 0 | 55.9 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 19:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 20:00 | 52.82 | 0 | 0 | 52.82 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 21:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 22:00 | 48.85 | 0 | 0 | 48.85 | 0 | 0 | 12.51 | 0 | 0
2025-04-16 23:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 | 45.73 | 0 | 0 | 45.73 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 01:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 02:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 03:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 04:00 | 42.32 | 0 | 0 | 42.32 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 05:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 06:00 | 46.43 | 45.29 | 45.29 | 1.15 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 07:00 | 47.8 | 109.23 | 109.23 | 0 | 61.43 | 0 | 70.87 | 0 | 0
2025-04-17 08:00 | 49.66 | 121.48 | 93.58 | 0 | 43.92 | 0 | 112.59 | 27.91 | 0
2025-04-17 09:00 | 50 | 122.78 | 50 | 0 | 0 | 0 | 112.59 | 72.77 | 0
2025-04-17 10:00 | 52.64 | 120.02 | 52.64 | 0 | 0 | 0 | 112.59 | 67.37 | 0
2025-04-17 11:00 | 53.31 | 115.97 | 53.31 | 0 | 0 | 0 | 112.59 | 62.66 | 0
2025-04-17 12:00 | 54.99 | 113.86 | 54.99 | 0 | 0 | 0 | 112.59 | 58.87 | 0
2025-04-17 13:00 | 55.12 | 116.57 | 55.12 | 0 | 0 | 0 | 112.59 | 61.45 | 0
2025-04-17 14:00 | 55.98 | 119.92 | 55.98 | 0 | 0 | 0 | 112.59 | 63.94 | 0
2025-04-17 15:00 | 56.14 | 122.41 | 56.14 | 0 | 0 | 0 | 112.59 | 66.26 | 0
2025-04-17 16:00 | 56.75 | 119.24 | 56.75 | 0 | 0 | 0 | 112.59 | 62.49 | 0
2025-04-17 17:00 | 56.16 | 104.54 | 56.16 | 0 | 0 | 0 | 112.59 | 48.38 | 0
2025-04-17 18:00 | 55.01 | 28.57 | 28.57 | 0 | 0 | 26.44 | 84.76 | 0 | 0
2025-04-17 19:00 | 52.99 | 0 | 0 | 0 | 0 | 52.99 | 28.98 | 0 | 0
2025-04-17 20:00 | 52.03 | 0 | 0 | 36.39 | 0 | 15.64 | 12.51 | 0 | 0
2025-04-17 21:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 22:00 | 49.18 | 0 | 0 | 49.18 | 0 | 0 | 12.51 | 0 | 0
2025-04-17 23:00 | 47.6 | 0 | 0 | 47.6 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 01:00 | 44 | 0 | 0 | 44 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 02:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 03:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 04:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 05:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 06:00 | 45.28 | 43.09 | 43.09 | 2.19 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 07:00 | 48.12 | 100.64 | 100.64 | 0 | 52.52 | 0 | 62.4 | 0 | 0
2025-04-18 08:00 | 49.81 | 114.46 | 102.64 | 0 | 52.83 | 0 | 112.59 | 11.82 | 0
2025-04-18 09:00 | 51.18 | 116.71 | 51.18 | 0 | 0 | 0 | 112.59 | 65.52 | 0
2025-04-18 10:00 | 52.98 | 114.77 | 52.98 | 0 | 0 | 0 | 112.59 | 61.79 | 0
2025-04-18 11:00 | 54.86 | 111.24 | 54.86 | 0 | 0 | 0 | 112.59 | 56.38 | 0
2025-04-18 12:00 | 56.55 | 107.8 | 56.55 | 0 | 0 | 0 | 112.59 | 51.24 | 0
2025-04-18 13:00 | 58.39 | 109.37 | 58.39 | 0 | 0 | 0 | 112.59 | 50.98 | 0
2025-04-18 14:00 | 58.52 | 112.67 | 58.52 | 0 | 0 | 0 | 112.59 | 54.16 | 0
2025-04-18 15:00 | 58.91 | 114.32 | 58.91 | 0 | 0 | 0 | 112.59 | 55.4 | 0
2025-04-18 16:00 | 58.89 | 107.97 | 58.89 | 0 | 0 | 0 | 112.59 | 49.08 | 0
2025-04-18 17:00 | 57 | 90.16 | 57 | 0 | 0 | 0 | 112.59 | 33.15 | 0
2025-04-18 18:00 | 56.82 | 25.3 | 25.3 | 0 | 0 | 31.52 | 79.41 | 0 | 0
2025-04-18 19:00 | 54.78 | 0 | 0 | 0 | 0 | 54.78 | 21.75 | 0 | 0
2025-04-18 20:00 | 51.87 | 0 | 0 | 43.09 | 0 | 8.78 | 12.51 | 0 | 0
2025-04-18 21:00 | 50.11 | 0 | 0 | 50.11 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 22:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 12.51 | 0 | 0
2025-04-18 23:00 | 47.56 | 0 | 0 | 47.56 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 | 45.94 | 0 | 0 | 45.94 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 01:00 | 44.63 | 0 | 0 | 44.63 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 02:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 03:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 04:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 05:00 | 44.69 | 0 | 0 | 44.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 06:00 | 45.52 | 16.34 | 16.34 | 29.17 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 07:00 | 47.7 | 37.04 | 37.04 | 10.66 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 08:00 | 49.06 | 49.3 | 49.3 | 0 | 0.24 | 0 | 12.74 | 0 | 0
2025-04-19 09:00 | 52.97 | 56.09 | 56.09 | 0 | 3.12 | 0 | 15.7 | 0 | 0
2025-04-19 10:00 | 54.41 | 86.83 | 86.83 | 0 | 32.42 | 0 | 46.5 | 0 | 0
2025-04-19 11:00 | 58.16 | 78.73 | 78.73 | 0 | 20.57 | 0 | 66.04 | 0 | 0
2025-04-19 12:00 | 59.24 | 88.4 | 88.4 | 0 | 29.16 | 0 | 93.74 | 0 | 0
2025-04-19 13:00 | 61.43 | 104.92 | 81.28 | 0 | 19.84 | 0 | 112.59 | 23.64 | 0
2025-04-19 14:00 | 61.95 | 108.09 | 61.95 | 0 | 0 | 0 | 112.59 | 46.14 | 0
2025-04-19 15:00 | 62.33 | 108.74 | 62.33 | 0 | 0 | 0 | 112.59 | 46.42 | 0
2025-04-19 16:00 | 61.68 | 125.09 | 61.68 | 0 | 0 | 0 | 112.59 | 63.41 | 0
2025-04-19 17:00 | 60.98 | 114.33 | 60.98 | 0 | 0 | 0 | 112.59 | 53.35 | 0
2025-04-19 18:00 | 59.42 | 37.37 | 37.37 | 0 | 0 | 22.05 | 89.38 | 0 | 0
2025-04-19 19:00 | 56.75 | 0 | 0 | 0 | 0 | 56.75 | 29.64 | 0 | 0
2025-04-19 20:00 | 54.69 | 0 | 0 | 38.42 | 0 | 16.27 | 12.51 | 0 | 0
2025-04-19 21:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 22:00 | 51 | 0 | 0 | 51 | 0 | 0 | 12.51 | 0 | 0
2025-04-19 23:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 | 46.65 | 0 | 0 | 46.65 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 01:00 | 44.55 | 0 | 0 | 44.55 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 02:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 03:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 04:00 | 43.61 | 0 | 0 | 43.61 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 05:00 | 44.75 | 0.3 | 0.3 | 44.45 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 06:00 | 46.67 | 4.54 | 4.54 | 42.12 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 07:00 | 47.5 | 74.82 | 74.82 | 0 | 27.33 | 0 | 38.47 | 0 | 0
2025-04-20 08:00 | 49.69 | 123.97 | 112.19 | 0 | 62.5 | 0 | 97.85 | 11.77 | 0
2025-04-20 09:00 | 50.89 | 108.04 | 66.41 | 0 | 15.52 | 0 | 112.59 | 41.63 | 0
2025-04-20 10:00 | 52.78 | 104.14 | 52.78 | 0 | 0 | 0 | 112.59 | 51.37 | 0
2025-04-20 11:00 | 53.08 | 38.85 | 38.85 | 0 | 0 | 14.23 | 97.61 | 0 | 0
2025-04-20 12:00 | 55.17 | 74.9 | 70.94 | 0 | 15.77 | 0 | 112.59 | 3.97 | 0
2025-04-20 13:00 | 54.32 | 130.93 | 54.32 | 0 | 0 | 0 | 112.59 | 76.61 | 0
2025-04-20 14:00 | 54.51 | 45.84 | 45.84 | 0 | 0 | 8.67 | 103.46 | 0 | 0
2025-04-20 15:00 | 54.4 | 5.91 | 5.91 | 0 | 0 | 48.49 | 52.42 | 0 | 0
2025-04-20 16:00 | 56.06 | 3.85 | 3.85 | 14.29 | 0 | 37.91 | 12.51 | 0 | 0
2025-04-20 17:00 | 54.97 | 1.73 | 1.73 | 53.24 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 18:00 | 53.8 | 0 | 0 | 53.8 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 19:00 | 53.73 | 0 | 0 | 53.73 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 20:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 21:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 22:00 | 48.23 | 0 | 0 | 48.23 | 0 | 0 | 12.51 | 0 | 0
2025-04-20 23:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 | 45.94 | 0 | 0 | 45.94 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 01:00 | 43.83 | 0 | 0 | 43.83 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 02:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 03:00 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 04:00 | 44.34 | 0 | 0 | 44.34 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 05:00 | 45.99 | 0.12 | 0.12 | 45.88 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 06:00 | 46 | 47.49 | 47.49 | 0 | 1.49 | 0 | 13.93 | 0 | 0
2025-04-21 07:00 | 47.76 | 100.95 | 100.95 | 0 | 53.2 | 0 | 64.46 | 0 | 0
2025-04-21 08:00 | 50.15 | 113.68 | 100.81 | 0 | 50.66 | 0 | 112.59 | 12.88 | 0
2025-04-21 09:00 | 52.91 | 118.91 | 52.91 | 0 | 0 | 0 | 112.59 | 66 | 0
2025-04-21 10:00 | 54.5 | 114.88 | 54.5 | 0 | 0 | 0 | 112.59 | 60.38 | 0
2025-04-21 11:00 | 56.71 | 111.38 | 56.71 | 0 | 0 | 0 | 112.59 | 54.67 | 0
2025-04-21 12:00 | 59.51 | 109.34 | 59.51 | 0 | 0 | 0 | 112.59 | 49.83 | 0
2025-04-21 13:00 | 60.69 | 110.78 | 60.69 | 0 | 0 | 0 | 112.59 | 50.09 | 0
2025-04-21 14:00 | 60.45 | 113.69 | 60.45 | 0 | 0 | 0 | 112.59 | 53.25 | 0
2025-04-21 15:00 | 61.18 | 116.1 | 61.18 | 0 | 0 | 0 | 112.59 | 54.92 | 0
2025-04-21 16:00 | 62.22 | 110.88 | 62.22 | 0 | 0 | 0 | 112.59 | 48.66 | 0
2025-04-21 17:00 | 60.7 | 95.24 | 60.7 | 0 | 0 | 0 | 112.59 | 34.54 | 0
2025-04-21 18:00 | 58.6 | 31.33 | 31.33 | 0 | 0 | 27.27 | 83.88 | 0 | 0
2025-04-21 19:00 | 56.94 | 0 | 0 | 0 | 0 | 56.94 | 23.95 | 0 | 0
2025-04-21 20:00 | 54.78 | 0 | 0 | 43.92 | 0 | 10.87 | 12.51 | 0 | 0
2025-04-21 21:00 | 52.78 | 0 | 0 | 52.78 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 22:00 | 49.41 | 0 | 0 | 49.41 | 0 | 0 | 12.51 | 0 | 0
2025-04-21 23:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 01:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 02:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 03:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 04:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 05:00 | 45.5 | 0.22 | 0.22 | 45.28 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 06:00 | 46.56 | 45.42 | 45.42 | 1.14 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 07:00 | 48.17 | 91.78 | 91.78 | 0 | 43.6 | 0 | 53.93 | 0 | 0
2025-04-22 08:00 | 50.16 | 106.11 | 106.11 | 0 | 55.95 | 0 | 107.09 | 0 | 0
2025-04-22 09:00 | 52.07 | 112.73 | 57.86 | 0 | 5.79 | 0 | 112.59 | 54.87 | 0
2025-04-22 10:00 | 54.76 | 111.17 | 54.76 | 0 | 0 | 0 | 112.59 | 56.42 | 0
2025-04-22 11:00 | 57.59 | 102.94 | 57.59 | 0 | 0 | 0 | 112.59 | 45.35 | 0
2025-04-22 12:00 | 58.78 | 101.28 | 58.78 | 0 | 0 | 0 | 112.59 | 42.5 | 0
2025-04-22 13:00 | 59.85 | 97.88 | 59.85 | 0 | 0 | 0 | 112.59 | 38.03 | 0
2025-04-22 14:00 | 60.97 | 100.24 | 60.97 | 0 | 0 | 0 | 112.59 | 39.28 | 0
2025-04-22 15:00 | 61.63 | 96.38 | 61.63 | 0 | 0 | 0 | 112.59 | 34.76 | 0
2025-04-22 16:00 | 61.03 | 87.69 | 61.03 | 0 | 0 | 0 | 112.59 | 26.66 | 0
2025-04-22 17:00 | 60.54 | 70.73 | 60.54 | 0 | 0 | 0 | 112.59 | 10.19 | 0
2025-04-22 18:00 | 59.1 | 26.9 | 26.9 | 0 | 0 | 32.2 | 78.69 | 0 | 0
2025-04-22 19:00 | 57.41 | 0 | 0 | 0 | 0 | 57.41 | 18.26 | 0 | 0
2025-04-22 20:00 | 55.5 | 0 | 0 | 50.04 | 0 | 5.47 | 12.51 | 0 | 0
2025-04-22 21:00 | 52.99 | 0 | 0 | 52.99 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 22:00 | 49.74 | 0 | 0 | 49.74 | 0 | 0 | 12.51 | 0 | 0
2025-04-22 23:00 | 47.65 | 0 | 0 | 47.65 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 01:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 02:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 03:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 04:00 | 44 | 0 | 0 | 44 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 05:00 | 44.75 | 0.55 | 0.55 | 44.2 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 06:00 | 46.26 | 49.69 | 49.69 | 0 | 3.43 | 0 | 15.77 | 0 | 0
2025-04-23 07:00 | 48.71 | 79.56 | 79.56 | 0 | 30.85 | 0 | 45.08 | 0 | 0
2025-04-23 08:00 | 50.15 | 92.56 | 92.56 | 0 | 42.4 | 0 | 85.37 | 0 | 0
2025-04-23 09:00 | 53.3 | 75.06 | 75.06 | 0 | 21.76 | 0 | 106.03 | 0 | 0
2025-04-23 10:00 | 54.11 | 85.03 | 61.01 | 0 | 6.9 | 0 | 112.59 | 24.02 | 0
2025-04-23 11:00 | 55.64 | 98.81 | 55.64 | 0 | 0 | 0 | 112.59 | 43.17 | 0
2025-04-23 12:00 | 57.26 | 96.7 | 57.26 | 0 | 0 | 0 | 112.59 | 39.43 | 0
2025-04-23 13:00 | 58.49 | 99.07 | 58.49 | 0 | 0 | 0 | 112.59 | 40.57 | 0
2025-04-23 14:00 | 59.26 | 108.41 | 59.26 | 0 | 0 | 0 | 112.59 | 49.15 | 0
2025-04-23 15:00 | 60.32 | 110.96 | 60.32 | 0 | 0 | 0 | 112.59 | 50.64 | 0
2025-04-23 16:00 | 58.62 | 111.21 | 58.62 | 0 | 0 | 0 | 112.59 | 52.58 | 0
2025-04-23 17:00 | 58.79 | 81.47 | 58.79 | 0 | 0 | 0 | 112.59 | 22.68 | 0
2025-04-23 18:00 | 57.36 | 21.24 | 21.24 | 0 | 0 | 36.13 | 74.56 | 0 | 0
2025-04-23 19:00 | 55 | 0 | 0 | 0 | 0 | 55 | 16.66 | 0 | 0
2025-04-23 20:00 | 54.41 | 0 | 0 | 50.46 | 0 | 3.95 | 12.51 | 0 | 0
2025-04-23 21:00 | 52.7 | 0 | 0 | 52.7 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 22:00 | 49.62 | 0 | 0 | 49.62 | 0 | 0 | 12.51 | 0 | 0
2025-04-23 23:00 | 48.12 | 0 | 0 | 48.12 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 | 45.65 | 0 | 0 | 45.65 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 01:00 | 44.58 | 0 | 0 | 44.58 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 02:00 | 44.89 | 0 | 0 | 44.89 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 03:00 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 04:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 05:00 | 45.33 | 0 | 0 | 45.33 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 06:00 | 46.25 | 13.97 | 13.97 | 32.29 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 07:00 | 47.89 | 74.62 | 74.62 | 0 | 26.72 | 0 | 37.9 | 0 | 0
2025-04-24 08:00 | 50.25 | 77.86 | 77.86 | 0 | 27.6 | 0 | 64.12 | 0 | 0
2025-04-24 09:00 | 51.04 | 48.69 | 48.69 | 0 | 0 | 2.34 | 61.65 | 0 | 0
2025-04-24 10:00 | 52.75 | 53.23 | 53.23 | 0 | 0.48 | 0 | 62.11 | 0 | 0
2025-04-24 11:00 | 54.62 | 34.9 | 34.9 | 0 | 0 | 19.72 | 41.35 | 0 | 0
2025-04-24 12:00 | 56.08 | 33.08 | 33.08 | 0 | 0 | 23 | 17.14 | 0 | 0
2025-04-24 13:00 | 56.95 | 21.18 | 21.18 | 31.37 | 0 | 4.4 | 12.51 | 0 | 0
2025-04-24 14:00 | 56.44 | 43.72 | 43.72 | 12.71 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 15:00 | 57.38 | 36.54 | 36.54 | 20.84 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 16:00 | 56.38 | 27.1 | 27.1 | 29.27 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 17:00 | 57.25 | 5.02 | 5.02 | 52.23 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 18:00 | 55.03 | 0 | 0 | 55.03 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 19:00 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 20:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 21:00 | 52.63 | 0 | 0 | 52.63 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 22:00 | 50.18 | 0 | 0 | 50.18 | 0 | 0 | 12.51 | 0 | 0
2025-04-24 23:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 | 46.51 | 0 | 0 | 46.51 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 01:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 02:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 03:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 04:00 | 44.52 | 0 | 0 | 44.52 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 05:00 | 45.75 | 0.08 | 0.08 | 45.67 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 06:00 | 46.84 | 8.5 | 8.5 | 38.34 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 07:00 | 47.95 | 52.54 | 52.54 | 0 | 4.58 | 0 | 16.86 | 0 | 0
2025-04-25 08:00 | 50.33 | 51.1 | 51.1 | 0 | 0.77 | 0 | 17.6 | 0 | 0
2025-04-25 09:00 | 53.15 | 29.38 | 29.38 | 18.93 | 0 | 4.83 | 12.51 | 0 | 0
2025-04-25 10:00 | 55.94 | 40.62 | 40.62 | 15.32 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 11:00 | 58.29 | 91.98 | 91.98 | 0 | 33.69 | 0 | 44.51 | 0 | 0
2025-04-25 12:00 | 59.73 | 95.89 | 95.89 | 0 | 36.16 | 0 | 78.86 | 0 | 0
2025-04-25 13:00 | 60.91 | 122.74 | 96.42 | 0 | 35.51 | 0 | 112.59 | 26.33 | 0
2025-04-25 14:00 | 62.04 | 125.1 | 62.04 | 0 | 0 | 0 | 112.59 | 63.06 | 0
2025-04-25 15:00 | 61.64 | 125.04 | 61.64 | 0 | 0 | 0 | 112.59 | 63.4 | 0
2025-04-25 16:00 | 61.59 | 99.31 | 61.59 | 0 | 0 | 0 | 112.59 | 37.72 | 0
2025-04-25 17:00 | 60.36 | 101.78 | 60.36 | 0 | 0 | 0 | 112.59 | 41.42 | 0
2025-04-25 18:00 | 58.72 | 37.49 | 37.49 | 0 | 0 | 21.23 | 90.24 | 0 | 0
2025-04-25 19:00 | 57.65 | 0 | 0 | 0 | 0 | 57.65 | 29.55 | 0 | 0
2025-04-25 20:00 | 55.43 | 0 | 0 | 39.23 | 0 | 16.19 | 12.51 | 0 | 0
2025-04-25 21:00 | 53.37 | 0 | 0 | 53.37 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 22:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 12.51 | 0 | 0
2025-04-25 23:00 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 | 47.17 | 0 | 0 | 47.17 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 01:00 | 45.49 | 0 | 0 | 45.49 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 02:00 | 44.84 | 0 | 0 | 44.84 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 03:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 04:00 | 44.81 | 0 | 0 | 44.81 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 05:00 | 45.84 | 0.78 | 0.78 | 45.06 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 06:00 | 46.55 | 8.81 | 8.81 | 37.74 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 07:00 | 48.68 | 11.62 | 11.62 | 37.06 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 08:00 | 50.36 | 38.69 | 38.69 | 11.67 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 09:00 | 52.51 | 47.36 | 47.36 | 5.15 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 10:00 | 54.26 | 68.33 | 68.33 | 0 | 14.07 | 0 | 25.88 | 0 | 0
2025-04-26 11:00 | 57.31 | 101.8 | 101.8 | 0 | 44.5 | 0 | 68.15 | 0 | 0
2025-04-26 12:00 | 58.77 | 101 | 101 | 0 | 42.23 | 0 | 108.26 | 0 | 0
2025-04-26 13:00 | 59.67 | 84.31 | 64.22 | 0 | 4.55 | 0 | 112.59 | 20.08 | 0
2025-04-26 14:00 | 61.11 | 94.76 | 61.11 | 0 | 0 | 0 | 112.59 | 33.64 | 0
2025-04-26 15:00 | 60.28 | 86.27 | 60.28 | 0 | 0 | 0 | 112.59 | 25.99 | 0
2025-04-26 16:00 | 61.64 | 57.22 | 57.22 | 0 | 0 | 4.43 | 107.93 | 0 | 0
2025-04-26 17:00 | 59.29 | 20.34 | 20.34 | 0 | 0 | 38.95 | 66.93 | 0 | 0
2025-04-26 18:00 | 58.36 | 4.79 | 4.79 | 1.87 | 0 | 51.7 | 12.51 | 0 | 0
2025-04-26 19:00 | 56.48 | 0 | 0 | 56.48 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 20:00 | 55.01 | 0 | 0 | 55.01 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 21:00 | 53.19 | 0 | 0 | 53.19 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 22:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 12.51 | 0 | 0
2025-04-26 23:00 | 49.54 | 0 | 0 | 49.54 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 01:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 02:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 03:00 | 44.67 | 0 | 0 | 44.67 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 04:00 | 44.7 | 0 | 0 | 44.7 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 05:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 06:00 | 46.71 | 0.14 | 0.14 | 46.57 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 07:00 | 50.32 | 25.36 | 25.36 | 24.96 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 08:00 | 51.07 | 44.59 | 44.59 | 6.48 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 09:00 | 52.88 | 98.32 | 98.32 | 0 | 45.45 | 0 | 55.69 | 0 | 0
2025-04-27 10:00 | 55.68 | 65.37 | 65.37 | 0 | 9.69 | 0 | 64.89 | 0 | 0
2025-04-27 11:00 | 58.29 | 82.57 | 82.57 | 0 | 24.27 | 0 | 87.95 | 0 | 0
2025-04-27 12:00 | 60.57 | 59.87 | 59.87 | 0 | 0 | 0.7 | 87.21 | 0 | 0
2025-04-27 13:00 | 62.11 | 52.63 | 52.63 | 0 | 0 | 9.48 | 77.24 | 0 | 0
2025-04-27 14:00 | 63.14 | 38.83 | 38.83 | 0 | 0 | 24.3 | 51.66 | 0 | 0
2025-04-27 15:00 | 62.8 | 55.97 | 55.97 | 0 | 0 | 6.83 | 44.47 | 0 | 0
2025-04-27 16:00 | 62.97 | 57.33 | 57.33 | 0 | 0 | 5.63 | 38.54 | 0 | 0
2025-04-27 17:00 | 61.39 | 86.82 | 86.82 | 0 | 25.43 | 0 | 62.69 | 0 | 0
2025-04-27 18:00 | 59.99 | 34.56 | 34.56 | 0 | 0 | 25.43 | 35.93 | 0 | 0
2025-04-27 19:00 | 57.86 | 0 | 0 | 35.61 | 0 | 22.25 | 12.51 | 0 | 0
2025-04-27 20:00 | 55.44 | 0 | 0 | 55.44 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 21:00 | 54.14 | 0 | 0 | 54.14 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 22:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 12.51 | 0 | 0
2025-04-27 23:00 | 49.47 | 0 | 0 | 49.47 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 | 47.26 | 0 | 0 | 47.26 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 01:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 02:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 03:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 04:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 05:00 | 46.11 | 0.67 | 0.67 | 45.44 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 06:00 | 47.43 | 17.9 | 17.9 | 29.53 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 07:00 | 48.62 | 37.07 | 37.07 | 11.55 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 08:00 | 50.56 | 59.88 | 59.88 | 0 | 9.32 | 0 | 21.37 | 0 | 0
2025-04-28 09:00 | 53.3 | 100.35 | 100.35 | 0 | 47.05 | 0 | 66.07 | 0 | 0
2025-04-28 10:00 | 56.29 | 115.48 | 105.27 | 0 | 48.97 | 0 | 112.59 | 10.22 | 0
2025-04-28 11:00 | 58.55 | 98.48 | 58.55 | 0 | 0 | 0 | 112.59 | 39.93 | 0
2025-04-28 12:00 | 59.41 | 64.34 | 59.41 | 0 | 0 | 0 | 112.59 | 4.93 | 0
2025-04-28 13:00 | 61.05 | 60.28 | 60.28 | 0 | 0 | 0.77 | 111.78 | 0 | 0
2025-04-28 14:00 | 62.09 | 61.82 | 61.82 | 0 | 0 | 0.27 | 111.5 | 0 | 0
2025-04-28 15:00 | 62.58 | 33.16 | 33.16 | 0 | 0 | 29.43 | 80.53 | 0 | 0
2025-04-28 16:00 | 61.77 | 21.09 | 21.09 | 0 | 0 | 40.68 | 37.7 | 0 | 0
2025-04-28 17:00 | 60.83 | 1.11 | 1.11 | 35.78 | 0 | 23.93 | 12.51 | 0 | 0
2025-04-28 18:00 | 59.68 | 0 | 0 | 59.68 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 19:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 20:00 | 55.42 | 0 | 0 | 55.42 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 21:00 | 53.6 | 0 | 0 | 53.6 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 22:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 12.51 | 0 | 0
2025-04-28 23:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 01:00 | 46.48 | 0 | 0 | 46.48 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 02:00 | 44.82 | 0 | 0 | 44.82 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 03:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 04:00 | 45.61 | 0 | 0 | 45.61 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 05:00 | 45.81 | 1.33 | 1.33 | 44.48 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 06:00 | 48.06 | 28.37 | 28.37 | 19.69 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 07:00 | 49.83 | 84.62 | 84.62 | 0 | 34.79 | 0 | 45.56 | 0 | 0
2025-04-29 08:00 | 52.05 | 46.47 | 46.47 | 0 | 0 | 5.58 | 39.69 | 0 | 0
2025-04-29 09:00 | 55.42 | 65.39 | 65.39 | 0 | 9.98 | 0 | 49.17 | 0 | 0
2025-04-29 10:00 | 58.48 | 107.99 | 107.99 | 0 | 49.52 | 0 | 96.21 | 0 | 0
2025-04-29 11:00 | 61.91 | 71.76 | 71.76 | 0 | 9.85 | 0 | 105.56 | 0 | 0
2025-04-29 12:00 | 63.9 | 96.4 | 71.29 | 0 | 7.4 | 0 | 112.59 | 25.11 | 0
2025-04-29 13:00 | 66.39 | 107.24 | 66.39 | 0 | 0 | 0 | 112.59 | 40.84 | 0
2025-04-29 14:00 | 67.76 | 122.04 | 67.76 | 0 | 0 | 0 | 112.59 | 54.28 | 0
2025-04-29 15:00 | 68.63 | 121.78 | 68.63 | 0 | 0 | 0 | 112.59 | 53.15 | 0
2025-04-29 16:00 | 67.28 | 118.85 | 67.28 | 0 | 0 | 0 | 112.59 | 51.57 | 0
2025-04-29 17:00 | 66.88 | 100.12 | 66.88 | 0 | 0 | 0 | 112.59 | 33.24 | 0
2025-04-29 18:00 | 64.4 | 40.38 | 40.38 | 0 | 0 | 24.02 | 87.3 | 0 | 0
2025-04-29 19:00 | 60.74 | 0 | 0 | 0 | 0 | 60.74 | 23.36 | 0 | 0
2025-04-29 20:00 | 58.92 | 0 | 0 | 48.61 | 0 | 10.31 | 12.51 | 0 | 0
2025-04-29 21:00 | 56.3 | 0 | 0 | 56.3 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 22:00 | 52.72 | 0 | 0 | 52.72 | 0 | 0 | 12.51 | 0 | 0
2025-04-29 23:00 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 | 47.58 | 0 | 0 | 47.58 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 01:00 | 45.25 | 0 | 0 | 45.25 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 02:00 | 44.24 | 0 | 0 | 44.24 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 03:00 | 44.97 | 0 | 0 | 44.97 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 04:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 05:00 | 45.62 | 1.38 | 1.38 | 44.24 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 06:00 | 47.5 | 30.1 | 30.1 | 17.4 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 07:00 | 49.72 | 59.36 | 59.36 | 0 | 9.64 | 0 | 21.67 | 0 | 0
2025-04-30 08:00 | 50.86 | 94.24 | 94.24 | 0 | 43.38 | 0 | 62.88 | 0 | 0
2025-04-30 09:00 | 53.66 | 96.66 | 96.66 | 0 | 43 | 0 | 103.73 | 0 | 0
2025-04-30 10:00 | 56.91 | 98.46 | 66.24 | 0 | 9.32 | 0 | 112.59 | 32.22 | 0
2025-04-30 11:00 | 57.72 | 99.82 | 57.72 | 0 | 0 | 0 | 112.59 | 42.1 | 0
2025-04-30 12:00 | 60.47 | 101.89 | 60.47 | 0 | 0 | 0 | 112.59 | 41.42 | 0
2025-04-30 13:00 | 61.15 | 104.15 | 61.15 | 0 | 0 | 0 | 112.59 | 43 | 0
2025-04-30 14:00 | 62.51 | 97.84 | 62.51 | 0 | 0 | 0 | 112.59 | 35.34 | 0
2025-04-30 15:00 | 63.07 | 91.86 | 63.07 | 0 | 0 | 0 | 112.59 | 28.79 | 0
2025-04-30 16:00 | 62.61 | 62.54 | 62.54 | 0 | 0 | 0.07 | 112.51 | 0 | 0
2025-04-30 17:00 | 61.84 | 64.11 | 61.92 | 0 | 0.08 | 0 | 112.59 | 2.18 | 0
2025-04-30 18:00 | 59.46 | 35.69 | 35.69 | 0 | 0 | 23.77 | 87.57 | 0 | 0
2025-04-30 19:00 | 58.81 | 0 | 0 | 0 | 0 | 58.81 | 25.66 | 0 | 0
2025-04-30 20:00 | 55.73 | 0 | 0 | 43.24 | 0 | 12.5 | 12.51 | 0 | 0
2025-04-30 21:00 | 54.01 | 0 | 0 | 54.01 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 22:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 12.51 | 0 | 0
2025-04-30 23:00 | 49.66 | 0 | 0 | 49.66 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 | 47.8 | 0 | 0 | 47.8 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 01:00 | 45.78 | 0 | 0 | 45.78 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 02:00 | 44.61 | 0 | 0 | 44.61 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 03:00 | 45.41 | 0 | 0 | 45.41 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 04:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 05:00 | 46.78 | 0 | 0 | 46.78 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 06:00 | 47.61 | 4.29 | 4.29 | 43.32 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 07:00 | 48.72 | 5.86 | 5.86 | 42.86 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 08:00 | 51.9 | 7.5 | 7.5 | 44.4 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 09:00 | 53.26 | 16.01 | 16.01 | 37.25 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 10:00 | 55.53 | 17.46 | 17.46 | 38.07 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 11:00 | 56.71 | 22.8 | 22.8 | 33.91 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 12:00 | 59.22 | 30.33 | 30.33 | 28.89 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 13:00 | 58.95 | 39.8 | 39.8 | 19.16 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 14:00 | 59.83 | 43.18 | 43.18 | 16.65 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 15:00 | 60.25 | 59.31 | 59.31 | 0.95 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 16:00 | 59.45 | 32.24 | 32.24 | 27.21 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 17:00 | 59.56 | 33.98 | 33.98 | 25.58 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 18:00 | 59.2 | 35.76 | 35.76 | 23.45 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 19:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 20:00 | 55.55 | 0 | 0 | 55.55 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 21:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 22:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-05-01 23:00 | 49.27 | 0 | 0 | 49.27 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 | 47.46 | 0 | 0 | 47.46 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 01:00 | 46.91 | 0 | 0 | 46.91 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 02:00 | 45.26 | 0 | 0 | 45.26 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 03:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 04:00 | 45.23 | 0 | 0 | 45.23 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 05:00 | 45.41 | 0.56 | 0.56 | 44.84 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 06:00 | 47.31 | 14.56 | 14.56 | 32.75 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 07:00 | 50.33 | 14.81 | 14.81 | 35.52 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 08:00 | 51.11 | 18.51 | 18.51 | 32.61 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 09:00 | 54.29 | 6.41 | 6.41 | 47.89 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 10:00 | 57 | 26.03 | 26.03 | 30.98 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 11:00 | 60.45 | 57 | 57 | 3.45 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 12:00 | 62.02 | 69.07 | 69.07 | 0 | 7.06 | 0 | 19.22 | 0 | 0
2025-05-02 13:00 | 62.94 | 73.25 | 73.25 | 0 | 10.32 | 0 | 29.02 | 0 | 0
2025-05-02 14:00 | 64.87 | 52.82 | 52.82 | 0 | 0 | 12.05 | 16.33 | 0 | 0
2025-05-02 15:00 | 64.19 | 69.83 | 69.83 | 0 | 5.64 | 0 | 21.69 | 0 | 0
2025-05-02 16:00 | 64.72 | 43.46 | 43.46 | 12.54 | 0 | 8.72 | 12.51 | 0 | 0
2025-05-02 17:00 | 62.54 | 21.72 | 21.72 | 40.81 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 18:00 | 62.17 | 2.69 | 2.69 | 59.47 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 19:00 | 59.38 | 0 | 0 | 59.38 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 20:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 21:00 | 54.57 | 0 | 0 | 54.57 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 22:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 12.51 | 0 | 0
2025-05-02 23:00 | 49.6 | 0 | 0 | 49.6 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 | 48.31 | 0 | 0 | 48.31 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 01:00 | 46.22 | 0 | 0 | 46.22 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 02:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 03:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 04:00 | 45.52 | 0 | 0 | 45.52 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 05:00 | 46.29 | 2.88 | 2.88 | 43.41 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 06:00 | 48.11 | 59.25 | 59.25 | 0 | 11.14 | 0 | 23.1 | 0 | 0
2025-05-03 07:00 | 50.31 | 113.74 | 112.81 | 0 | 62.5 | 0 | 82.47 | 0.94 | 0
2025-05-03 08:00 | 53.42 | 119.36 | 85.12 | 0 | 31.7 | 0 | 112.59 | 34.24 | 0
2025-05-03 09:00 | 55.4 | 121.35 | 55.4 | 0 | 0 | 0 | 112.59 | 65.95 | 0
2025-05-03 10:00 | 57.99 | 121.72 | 57.99 | 0 | 0 | 0 | 112.59 | 63.72 | 0
2025-05-03 11:00 | 61.47 | 51.45 | 51.45 | 0 | 0 | 10.02 | 102.04 | 0 | 0
2025-05-03 12:00 | 62.28 | 46.45 | 46.45 | 0 | 0 | 15.83 | 85.38 | 0 | 0
2025-05-03 13:00 | 63.89 | 49.85 | 49.85 | 0 | 0 | 14.04 | 70.6 | 0 | 0
2025-05-03 14:00 | 65.02 | 52.21 | 52.21 | 0 | 0 | 12.8 | 57.12 | 0 | 0
2025-05-03 15:00 | 64.51 | 59.55 | 59.55 | 0 | 0 | 4.96 | 51.91 | 0 | 0
2025-05-03 16:00 | 64.44 | 50.54 | 50.54 | 0 | 0 | 13.91 | 37.27 | 0 | 0
2025-05-03 17:00 | 63.39 | 27.13 | 27.13 | 12.74 | 0 | 23.52 | 12.51 | 0 | 0
2025-05-03 18:00 | 62.35 | 10.43 | 10.43 | 51.92 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 19:00 | 59.84 | 0 | 0 | 59.84 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 20:00 | 57.58 | 0 | 0 | 57.58 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 21:00 | 55.48 | 0 | 0 | 55.48 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 22:00 | 52.82 | 0 | 0 | 52.82 | 0 | 0 | 12.51 | 0 | 0
2025-05-03 23:00 | 49.95 | 0 | 0 | 49.95 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 01:00 | 47.23 | 0 | 0 | 47.23 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 02:00 | 46.07 | 0 | 0 | 46.07 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 03:00 | 44.55 | 0 | 0 | 44.55 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 04:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 05:00 | 46.75 | 3.76 | 3.76 | 42.99 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 06:00 | 48.66 | 65.58 | 65.58 | 0 | 16.92 | 0 | 28.58 | 0 | 0
2025-05-04 07:00 | 50.91 | 83.25 | 83.25 | 0 | 32.34 | 0 | 59.3 | 0 | 0
2025-05-04 08:00 | 53.27 | 88.89 | 88.89 | 0 | 35.62 | 0 | 93.15 | 0 | 0
2025-05-04 09:00 | 56.43 | 99.04 | 76.9 | 0 | 20.47 | 0 | 112.59 | 22.15 | 0
2025-05-04 10:00 | 59.35 | 108.22 | 59.35 | 0 | 0 | 0 | 112.59 | 48.87 | 0
2025-05-04 11:00 | 62.08 | 106.64 | 62.08 | 0 | 0 | 0 | 112.59 | 44.57 | 0
2025-05-04 12:00 | 65.05 | 103.03 | 65.05 | 0 | 0 | 0 | 112.59 | 37.97 | 0
2025-05-04 13:00 | 67.39 | 103.76 | 67.39 | 0 | 0 | 0 | 112.59 | 36.37 | 0
2025-05-04 14:00 | 68.77 | 103.5 | 68.77 | 0 | 0 | 0 | 112.59 | 34.73 | 0
2025-05-04 15:00 | 68.33 | 105.2 | 68.33 | 0 | 0 | 0 | 112.59 | 36.87 | 0
2025-05-04 16:00 | 68.59 | 104.09 | 68.59 | 0 | 0 | 0 | 112.59 | 35.5 | 0
2025-05-04 17:00 | 67.41 | 67.57 | 67.41 | 0 | 0 | 0 | 112.59 | 0.17 | 0
2025-05-04 18:00 | 65.04 | 27.76 | 27.76 | 0 | 0 | 37.28 | 73.35 | 0 | 0
2025-05-04 19:00 | 62.29 | 0.08 | 0.08 | 4.42 | 0 | 57.8 | 12.51 | 0 | 0
2025-05-04 20:00 | 59.56 | 0 | 0 | 59.56 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 21:00 | 55.6 | 0 | 0 | 55.6 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 22:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 12.51 | 0 | 0
2025-05-04 23:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 01:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 02:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 03:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 04:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 05:00 | 46.92 | 8.83 | 8.83 | 38.09 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 06:00 | 48.48 | 86.85 | 86.85 | 0 | 38.37 | 0 | 48.97 | 0 | 0
2025-05-05 07:00 | 50.79 | 124.72 | 113.29 | 0 | 62.5 | 0 | 108.34 | 11.43 | 0
2025-05-05 08:00 | 52.62 | 134.3 | 57.09 | 0 | 4.47 | 0 | 112.59 | 77.21 | 0
2025-05-05 09:00 | 55.95 | 135.94 | 55.95 | 0 | 0 | 0 | 112.59 | 80 | 0
2025-05-05 10:00 | 59.06 | 132.78 | 59.06 | 0 | 0 | 0 | 112.59 | 73.72 | 0
2025-05-05 11:00 | 62.09 | 77.95 | 62.09 | 0 | 0 | 0 | 112.59 | 15.86 | 0
2025-05-05 12:00 | 63.77 | 68.64 | 63.77 | 0 | 0 | 0 | 112.59 | 4.87 | 0
2025-05-05 13:00 | 65.95 | 46.54 | 46.54 | 0 | 0 | 19.41 | 92.15 | 0 | 0
2025-05-05 14:00 | 66.02 | 42.22 | 42.22 | 0 | 0 | 23.8 | 67.11 | 0 | 0
2025-05-05 15:00 | 67.49 | 46.39 | 46.39 | 0 | 0 | 21.1 | 44.89 | 0 | 0
2025-05-05 16:00 | 67.11 | 36.35 | 36.35 | 0 | 0 | 30.76 | 12.51 | 0 | 0
2025-05-05 17:00 | 65.61 | 21.21 | 21.21 | 44.4 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 18:00 | 64.25 | 0.11 | 0.11 | 64.14 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 19:00 | 61.65 | 0 | 0 | 61.65 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 20:00 | 57.72 | 0 | 0 | 57.72 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 21:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 22:00 | 52.61 | 0 | 0 | 52.61 | 0 | 0 | 12.51 | 0 | 0
2025-05-05 23:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 01:00 | 46.94 | 0 | 0 | 46.94 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 02:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 03:00 | 45.76 | 0 | 0 | 45.76 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 04:00 | 46.01 | 0 | 0 | 46.01 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 05:00 | 46.8 | 4.93 | 4.93 | 41.87 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 06:00 | 47.74 | 65.33 | 65.33 | 0 | 17.59 | 0 | 29.22 | 0 | 0
2025-05-06 07:00 | 49.85 | 99.88 | 99.88 | 0 | 50.03 | 0 | 76.75 | 0 | 0
2025-05-06 08:00 | 52.75 | 112.09 | 90.47 | 0 | 37.73 | 0 | 112.59 | 21.61 | 0
2025-05-06 09:00 | 55.71 | 113.12 | 55.71 | 0 | 0 | 0 | 112.59 | 57.41 | 0
2025-05-06 10:00 | 58.13 | 112.01 | 58.13 | 0 | 0 | 0 | 112.59 | 53.87 | 0
2025-05-06 11:00 | 61.32 | 109.31 | 61.32 | 0 | 0 | 0 | 112.59 | 47.99 | 0
2025-05-06 12:00 | 63.1 | 108.34 | 63.1 | 0 | 0 | 0 | 112.59 | 45.24 | 0
2025-05-06 13:00 | 64.5 | 107.74 | 64.5 | 0 | 0 | 0 | 112.59 | 43.24 | 0
2025-05-06 14:00 | 65.94 | 108.46 | 65.94 | 0 | 0 | 0 | 112.59 | 42.52 | 0
2025-05-06 15:00 | 66.57 | 103.78 | 66.57 | 0 | 0 | 0 | 112.59 | 37.22 | 0
2025-05-06 16:00 | 66.24 | 93.92 | 66.24 | 0 | 0 | 0 | 112.59 | 27.68 | 0
2025-05-06 17:00 | 65.92 | 76.57 | 65.92 | 0 | 0 | 0 | 112.59 | 10.66 | 0
2025-05-06 18:00 | 62.91 | 35.38 | 35.38 | 0 | 0 | 27.53 | 83.61 | 0 | 0
2025-05-06 19:00 | 60.97 | 0.3 | 0.3 | 0 | 0 | 60.67 | 19.75 | 0 | 0
2025-05-06 20:00 | 58.65 | 0 | 0 | 51.77 | 0 | 6.87 | 12.51 | 0 | 0
2025-05-06 21:00 | 55.71 | 0 | 0 | 55.71 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 22:00 | 52.79 | 0 | 0 | 52.79 | 0 | 0 | 12.51 | 0 | 0
2025-05-06 23:00 | 49.81 | 0 | 0 | 49.81 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 | 48.49 | 0 | 0 | 48.49 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 01:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 02:00 | 45.21 | 0 | 0 | 45.21 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 03:00 | 45.34 | 0 | 0 | 45.34 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 04:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 05:00 | 47.38 | 0.49 | 0.49 | 46.89 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 06:00 | 49.04 | 12.37 | 12.37 | 36.67 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 07:00 | 50.55 | 31.61 | 31.61 | 18.94 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 08:00 | 53.65 | 50.42 | 50.42 | 3.22 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 09:00 | 55.99 | 54.23 | 54.23 | 1.76 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 10:00 | 59.99 | 44.31 | 44.31 | 15.68 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 11:00 | 63.69 | 29.25 | 29.25 | 34.44 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 12:00 | 66.82 | 33.43 | 33.43 | 33.38 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 13:00 | 68.36 | 28.17 | 28.17 | 40.19 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 14:00 | 70.72 | 12.91 | 12.91 | 57.82 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 15:00 | 69.95 | 11.82 | 11.82 | 58.14 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 16:00 | 69.57 | 16.55 | 16.55 | 53.03 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 17:00 | 69.07 | 8.19 | 8.19 | 60.88 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 18:00 | 67.24 | 2.2 | 2.2 | 65.04 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 19:00 | 63.74 | 0 | 0 | 63.74 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 20:00 | 60.22 | 0 | 0 | 60.22 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 21:00 | 55.82 | 0 | 0 | 55.82 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 22:00 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 12.51 | 0 | 0
2025-05-07 23:00 | 51.07 | 0 | 0 | 51.07 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 | 48.51 | 0 | 0 | 48.51 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 01:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 02:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 03:00 | 45.92 | 0 | 0 | 45.92 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 04:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 05:00 | 47.25 | 0.17 | 0.17 | 47.08 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 06:00 | 49.31 | 3.97 | 3.97 | 45.34 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 07:00 | 50.59 | 11.5 | 11.5 | 39.09 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 08:00 | 52.61 | 17.42 | 17.42 | 35.19 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 09:00 | 55.3 | 18.51 | 18.51 | 36.79 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 10:00 | 56.24 | 36.22 | 36.22 | 20.02 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 11:00 | 59.83 | 26.55 | 26.55 | 33.28 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 12:00 | 59.97 | 29.16 | 29.16 | 30.81 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 13:00 | 60.95 | 23.11 | 23.11 | 37.84 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 14:00 | 61.61 | 43.06 | 43.06 | 18.55 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 15:00 | 62.48 | 43.45 | 43.45 | 19.04 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 16:00 | 61.74 | 42.22 | 42.22 | 19.53 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 17:00 | 59.96 | 24.57 | 24.57 | 35.39 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 18:00 | 60.48 | 5.43 | 5.43 | 55.05 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 19:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 20:00 | 56.78 | 0 | 0 | 56.78 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 21:00 | 54.13 | 0 | 0 | 54.13 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 22:00 | 52.93 | 0 | 0 | 52.93 | 0 | 0 | 12.51 | 0 | 0
2025-05-08 23:00 | 50.26 | 0 | 0 | 50.26 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 01:00 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 02:00 | 47.29 | 0 | 0 | 47.29 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 03:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 04:00 | 46.35 | 0 | 0 | 46.35 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 05:00 | 47.36 | 0.46 | 0.46 | 46.9 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 06:00 | 48.7 | 1.71 | 1.71 | 46.99 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 07:00 | 51.43 | 7.43 | 7.43 | 44 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 08:00 | 52.97 | 31.22 | 31.22 | 21.74 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 09:00 | 55.26 | 44.82 | 44.82 | 10.44 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 10:00 | 58.23 | 52.75 | 52.75 | 5.48 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 11:00 | 59.51 | 62.79 | 62.79 | 0 | 3.27 | 0 | 15.62 | 0 | 0
2025-05-09 12:00 | 61.46 | 47.49 | 47.49 | 11.02 | 0 | 2.95 | 12.51 | 0 | 0
2025-05-09 13:00 | 61.96 | 41.94 | 41.94 | 20.03 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 14:00 | 63.89 | 30.57 | 30.57 | 33.32 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 15:00 | 64.77 | 21.13 | 21.13 | 43.64 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 16:00 | 63.9 | 3.18 | 3.18 | 60.72 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 17:00 | 63.48 | 4.8 | 4.8 | 58.69 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 18:00 | 61.06 | 2.81 | 2.81 | 58.25 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 19:00 | 59.9 | 0 | 0 | 59.9 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 20:00 | 57.27 | 0 | 0 | 57.27 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 21:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 22:00 | 53.52 | 0 | 0 | 53.52 | 0 | 0 | 12.51 | 0 | 0
2025-05-09 23:00 | 50.93 | 0 | 0 | 50.93 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 | 48.31 | 0 | 0 | 48.31 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 01:00 | 46.8 | 0 | 0 | 46.8 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 02:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 03:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 04:00 | 47.49 | 0 | 0 | 47.49 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 05:00 | 48.14 | 2.42 | 2.42 | 45.72 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 06:00 | 48.07 | 68.65 | 68.65 | 0 | 20.59 | 0 | 32.07 | 0 | 0
2025-05-10 07:00 | 51.69 | 101.92 | 101.92 | 0 | 50.23 | 0 | 79.79 | 0 | 0
2025-05-10 08:00 | 53.64 | 104.06 | 88.17 | 0 | 34.52 | 0 | 112.59 | 15.89 | 0
2025-05-10 09:00 | 54.65 | 112.35 | 54.65 | 0 | 0 | 0 | 112.59 | 57.7 | 0
2025-05-10 10:00 | 57.4 | 121.88 | 57.4 | 0 | 0 | 0 | 112.59 | 64.47 | 0
2025-05-10 11:00 | 59.99 | 90.73 | 59.99 | 0 | 0 | 0 | 112.59 | 30.74 | 0
2025-05-10 12:00 | 61.26 | 91.74 | 61.26 | 0 | 0 | 0 | 112.59 | 30.48 | 0
2025-05-10 13:00 | 61.46 | 45.75 | 45.75 | 0 | 0 | 15.71 | 96.05 | 0 | 0
2025-05-10 14:00 | 63.11 | 28.27 | 28.27 | 0 | 0 | 34.84 | 59.38 | 0 | 0
2025-05-10 15:00 | 61.97 | 5.1 | 5.1 | 12.35 | 0 | 44.52 | 12.51 | 0 | 0
2025-05-10 16:00 | 62.69 | 21.06 | 21.06 | 41.63 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 17:00 | 62.68 | 12.62 | 12.62 | 50.06 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 18:00 | 60.99 | 6.42 | 6.42 | 54.57 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 19:00 | 59.19 | 0 | 0 | 59.19 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 20:00 | 58 | 0 | 0 | 58 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 21:00 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 22:00 | 53.83 | 0 | 0 | 53.83 | 0 | 0 | 12.51 | 0 | 0
2025-05-10 23:00 | 51.42 | 0 | 0 | 51.42 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 01:00 | 47.97 | 0 | 0 | 47.97 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 02:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 03:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 04:00 | 46.47 | 0 | 0 | 46.47 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 05:00 | 47 | 4.27 | 4.27 | 42.73 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 06:00 | 48.73 | 50.51 | 50.51 | 0 | 1.78 | 0 | 14.2 | 0 | 0
2025-05-11 07:00 | 51.13 | 49.13 | 49.13 | 0.39 | 0 | 1.61 | 12.51 | 0 | 0
2025-05-11 08:00 | 53.75 | 63.3 | 63.3 | 0 | 9.54 | 0 | 21.57 | 0 | 0
2025-05-11 09:00 | 56.84 | 96.07 | 96.07 | 0 | 39.23 | 0 | 58.84 | 0 | 0
2025-05-11 10:00 | 58.54 | 91.37 | 91.37 | 0 | 32.83 | 0 | 90.03 | 0 | 0
2025-05-11 11:00 | 61.3 | 95.43 | 85.05 | 0 | 23.75 | 0 | 112.59 | 10.38 | 0
2025-05-11 12:00 | 63.22 | 86.43 | 63.22 | 0 | 0 | 0 | 112.59 | 23.21 | 0
2025-05-11 13:00 | 63.99 | 73.42 | 63.99 | 0 | 0 | 0 | 112.59 | 9.43 | 0
2025-05-11 14:00 | 65.29 | 99.07 | 65.29 | 0 | 0 | 0 | 112.59 | 33.78 | 0
2025-05-11 15:00 | 65.17 | 110.83 | 65.17 | 0 | 0 | 0 | 112.59 | 45.66 | 0
2025-05-11 16:00 | 65.65 | 105.94 | 65.65 | 0 | 0 | 0 | 112.59 | 40.29 | 0
2025-05-11 17:00 | 64.42 | 100.78 | 64.42 | 0 | 0 | 0 | 112.59 | 36.36 | 0
2025-05-11 18:00 | 62.08 | 58.68 | 58.68 | 0 | 0 | 3.4 | 109.01 | 0 | 0
2025-05-11 19:00 | 60.88 | 1.62 | 1.62 | 0 | 0 | 59.26 | 46.63 | 0 | 0
2025-05-11 20:00 | 59.39 | 0 | 0 | 26.97 | 0 | 32.42 | 12.51 | 0 | 0
2025-05-11 21:00 | 56.03 | 0 | 0 | 56.03 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 22:00 | 53.86 | 0 | 0 | 53.86 | 0 | 0 | 12.51 | 0 | 0
2025-05-11 23:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 | 48.76 | 0 | 0 | 48.76 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 01:00 | 47.98 | 0 | 0 | 47.98 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 02:00 | 46.02 | 0 | 0 | 46.02 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 03:00 | 46.05 | 0 | 0 | 46.05 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 04:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 05:00 | 47.9 | 10.28 | 10.28 | 37.62 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 06:00 | 49.13 | 78.62 | 78.62 | 0 | 29.5 | 0 | 40.53 | 0 | 0
2025-05-12 07:00 | 51.43 | 102.71 | 102.71 | 0 | 51.28 | 0 | 89.25 | 0 | 0
2025-05-12 08:00 | 53.29 | 116.09 | 77.86 | 0 | 24.57 | 0 | 112.59 | 38.24 | 0
2025-05-12 09:00 | 55.42 | 120.08 | 55.42 | 0 | 0 | 0 | 112.59 | 64.65 | 0
2025-05-12 10:00 | 57.67 | 117.34 | 57.67 | 0 | 0 | 0 | 112.59 | 59.67 | 0
2025-05-12 11:00 | 58.62 | 115.37 | 58.62 | 0 | 0 | 0 | 112.59 | 56.75 | 0
2025-05-12 12:00 | 60.29 | 113.03 | 60.29 | 0 | 0 | 0 | 112.59 | 52.74 | 0
2025-05-12 13:00 | 61.03 | 114.58 | 61.03 | 0 | 0 | 0 | 112.59 | 53.55 | 0
2025-05-12 14:00 | 60.94 | 115.3 | 60.94 | 0 | 0 | 0 | 112.59 | 54.36 | 0
2025-05-12 15:00 | 61.45 | 111.32 | 61.45 | 0 | 0 | 0 | 112.59 | 49.87 | 0
2025-05-12 16:00 | 62.51 | 105.9 | 62.51 | 0 | 0 | 0 | 112.59 | 43.39 | 0
2025-05-12 17:00 | 61.38 | 91.54 | 61.38 | 0 | 0 | 0 | 112.59 | 30.16 | 0
2025-05-12 18:00 | 59.61 | 48.47 | 48.47 | 0 | 0 | 11.14 | 100.86 | 0 | 0
2025-05-12 19:00 | 58.21 | 1.11 | 1.11 | 0 | 0 | 57.1 | 40.75 | 0 | 0
2025-05-12 20:00 | 57.29 | 0 | 0 | 30.45 | 0 | 26.83 | 12.51 | 0 | 0
2025-05-12 21:00 | 56.2 | 0 | 0 | 56.2 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 22:00 | 53.22 | 0 | 0 | 53.22 | 0 | 0 | 12.51 | 0 | 0
2025-05-12 23:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 | 49.76 | 0 | 0 | 49.76 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 01:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 02:00 | 46.17 | 0 | 0 | 46.17 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 03:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 04:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 05:00 | 48.32 | 10.33 | 10.33 | 38 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 06:00 | 49.18 | 67.57 | 67.57 | 0 | 18.39 | 0 | 29.98 | 0 | 0
2025-05-13 07:00 | 51.93 | 94.3 | 94.3 | 0 | 42.36 | 0 | 70.23 | 0 | 0
2025-05-13 08:00 | 54.71 | 109.3 | 99.31 | 0 | 44.59 | 0 | 112.59 | 9.99 | 0
2025-05-13 09:00 | 57.43 | 114.62 | 57.43 | 0 | 0 | 0 | 112.59 | 57.19 | 0
2025-05-13 10:00 | 60.75 | 113.63 | 60.75 | 0 | 0 | 0 | 112.59 | 52.88 | 0
2025-05-13 11:00 | 63.33 | 110.24 | 63.33 | 0 | 0 | 0 | 112.59 | 46.91 | 0
2025-05-13 12:00 | 65.69 | 108.44 | 65.69 | 0 | 0 | 0 | 112.59 | 42.74 | 0
2025-05-13 13:00 | 68.81 | 108.74 | 68.81 | 0 | 0 | 0 | 112.59 | 39.92 | 0
2025-05-13 14:00 | 69.8 | 110.24 | 69.8 | 0 | 0 | 0 | 112.59 | 40.43 | 0
2025-05-13 15:00 | 69.34 | 107.89 | 69.34 | 0 | 0 | 0 | 112.59 | 38.55 | 0
2025-05-13 16:00 | 69.56 | 93.92 | 69.56 | 0 | 0 | 0 | 112.59 | 24.35 | 0
2025-05-13 17:00 | 67.64 | 76.83 | 67.64 | 0 | 0 | 0 | 112.59 | 9.19 | 0
2025-05-13 18:00 | 65.42 | 43.16 | 43.16 | 0 | 0 | 22.26 | 89.15 | 0 | 0
2025-05-13 19:00 | 63.98 | 1.18 | 1.18 | 0.3 | 0 | 62.5 | 23.36 | 0 | 0
2025-05-13 20:00 | 59.7 | 0 | 0 | 49.39 | 0 | 10.31 | 12.51 | 0 | 0
2025-05-13 21:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 22:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 12.51 | 0 | 0
2025-05-13 23:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 01:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 02:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 03:00 | 46.97 | 0 | 0 | 46.97 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 04:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 05:00 | 47.38 | 12.95 | 12.95 | 34.43 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 06:00 | 49.58 | 78.6 | 78.6 | 0 | 29.02 | 0 | 40.08 | 0 | 0
2025-05-14 07:00 | 52.5 | 99.04 | 99.04 | 0 | 46.54 | 0 | 84.29 | 0 | 0
2025-05-14 08:00 | 55.12 | 9.92 | 9.92 | 0 | 0 | 45.2 | 36.71 | 0 | 0
2025-05-14 09:00 | 57.27 | 29.56 | 29.56 | 4.72 | 0 | 22.99 | 12.51 | 0 | 0
2025-05-14 10:00 | 58.91 | 91.47 | 91.47 | 0 | 32.56 | 0 | 43.44 | 0 | 0
2025-05-14 11:00 | 62.15 | 117.51 | 117.51 | 0 | 55.36 | 0 | 96.03 | 0 | 0
2025-05-14 12:00 | 64.36 | 122.97 | 81.79 | 0 | 17.43 | 0 | 112.59 | 41.18 | 0
2025-05-14 13:00 | 65.85 | 100.71 | 65.85 | 0 | 0 | 0 | 112.59 | 34.86 | 0
2025-05-14 14:00 | 66.85 | 84.33 | 66.85 | 0 | 0 | 0 | 112.59 | 17.48 | 0
2025-05-14 15:00 | 66.97 | 96.84 | 66.97 | 0 | 0 | 0 | 112.59 | 29.87 | 0
2025-05-14 16:00 | 66.42 | 40.14 | 40.14 | 0 | 0 | 26.28 | 84.93 | 0 | 0
2025-05-14 17:00 | 65.19 | 11.13 | 11.13 | 0 | 0 | 54.06 | 28.02 | 0 | 0
2025-05-14 18:00 | 62.99 | 0 | 0 | 48.25 | 0 | 14.74 | 12.51 | 0 | 0
2025-05-14 19:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 20:00 | 59.6 | 0 | 0 | 59.6 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 21:00 | 57.19 | 0 | 0 | 57.19 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 22:00 | 53.61 | 0 | 0 | 53.61 | 0 | 0 | 12.51 | 0 | 0
2025-05-14 23:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 | 50.74 | 0 | 0 | 50.74 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 01:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 02:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 03:00 | 46.88 | 0 | 0 | 46.88 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 04:00 | 48.1 | 0 | 0 | 48.1 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 05:00 | 47.61 | 11.78 | 11.78 | 35.83 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 06:00 | 49.81 | 67.46 | 67.46 | 0 | 17.65 | 0 | 29.28 | 0 | 0
2025-05-15 07:00 | 51.28 | 93.85 | 93.85 | 0 | 42.57 | 0 | 69.72 | 0 | 0
2025-05-15 08:00 | 53.54 | 109.56 | 98.67 | 0 | 45.13 | 0 | 112.59 | 10.89 | 0
2025-05-15 09:00 | 55.9 | 113.37 | 55.9 | 0 | 0 | 0 | 112.59 | 57.47 | 0
2025-05-15 10:00 | 58.52 | 114.44 | 58.52 | 0 | 0 | 0 | 112.59 | 55.91 | 0
2025-05-15 11:00 | 60.37 | 113.44 | 60.37 | 0 | 0 | 0 | 112.59 | 53.07 | 0
2025-05-15 12:00 | 60.96 | 112.81 | 60.96 | 0 | 0 | 0 | 112.59 | 51.85 | 0
2025-05-15 13:00 | 61.43 | 112.11 | 61.43 | 0 | 0 | 0 | 112.59 | 50.68 | 0
2025-05-15 14:00 | 63.39 | 109.64 | 63.39 | 0 | 0 | 0 | 112.59 | 46.24 | 0
2025-05-15 15:00 | 62.1 | 105.09 | 62.1 | 0 | 0 | 0 | 112.59 | 42.99 | 0
2025-05-15 16:00 | 61.86 | 92.54 | 61.86 | 0 | 0 | 0 | 112.59 | 30.68 | 0
2025-05-15 17:00 | 60.74 | 80.82 | 60.74 | 0 | 0 | 0 | 112.59 | 20.08 | 0
2025-05-15 18:00 | 61.43 | 44.28 | 44.28 | 0 | 0 | 17.16 | 94.53 | 0 | 0
2025-05-15 19:00 | 59.96 | 1.72 | 1.72 | 0 | 0 | 58.23 | 33.23 | 0 | 0
2025-05-15 20:00 | 59.06 | 0 | 0 | 39.37 | 0 | 19.69 | 12.51 | 0 | 0
2025-05-15 21:00 | 55.23 | 0 | 0 | 55.23 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 22:00 | 54.54 | 0 | 0 | 54.54 | 0 | 0 | 12.51 | 0 | 0
2025-05-15 23:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 | 50.3 | 0 | 0 | 50.3 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 01:00 | 47.44 | 0 | 0 | 47.44 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 02:00 | 47.95 | 0 | 0 | 47.95 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 03:00 | 47.24 | 0 | 0 | 47.24 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 04:00 | 47.19 | 0 | 0 | 47.19 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 05:00 | 48.59 | 13.94 | 13.94 | 34.65 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 06:00 | 49.51 | 73.42 | 73.42 | 0 | 23.91 | 0 | 35.22 | 0 | 0
2025-05-16 07:00 | 51.66 | 101.1 | 101.1 | 0 | 49.44 | 0 | 82.19 | 0 | 0
2025-05-16 08:00 | 54 | 98.29 | 86 | 0 | 32 | 0 | 112.59 | 12.29 | 0
2025-05-16 09:00 | 55.63 | 113.55 | 55.63 | 0 | 0 | 0 | 112.59 | 57.92 | 0
2025-05-16 10:00 | 59.19 | 109.66 | 59.19 | 0 | 0 | 0 | 112.59 | 50.47 | 0
2025-05-16 11:00 | 61.28 | 107.52 | 61.28 | 0 | 0 | 0 | 112.59 | 46.24 | 0
2025-05-16 12:00 | 61.9 | 106.83 | 61.9 | 0 | 0 | 0 | 112.59 | 44.93 | 0
2025-05-16 13:00 | 63.57 | 106.46 | 63.57 | 0 | 0 | 0 | 112.59 | 42.89 | 0
2025-05-16 14:00 | 63.95 | 105.6 | 63.95 | 0 | 0 | 0 | 112.59 | 41.65 | 0
2025-05-16 15:00 | 64.48 | 96.4 | 64.48 | 0 | 0 | 0 | 112.59 | 31.92 | 0
2025-05-16 16:00 | 63.77 | 80.12 | 63.77 | 0 | 0 | 0 | 112.59 | 16.34 | 0
2025-05-16 17:00 | 62.95 | 49.74 | 49.74 | 0 | 0 | 13.21 | 98.68 | 0 | 0
2025-05-16 18:00 | 62.77 | 28.88 | 28.88 | 0 | 0 | 33.9 | 63 | 0 | 0
2025-05-16 19:00 | 60.65 | 1.47 | 1.47 | 11.22 | 0 | 47.97 | 12.51 | 0 | 0
2025-05-16 20:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 21:00 | 56.58 | 0 | 0 | 56.58 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 22:00 | 53.77 | 0 | 0 | 53.77 | 0 | 0 | 12.51 | 0 | 0
2025-05-16 23:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 | 50.47 | 0 | 0 | 50.47 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 01:00 | 48.78 | 0 | 0 | 48.78 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 02:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 03:00 | 46.64 | 0 | 0 | 46.64 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 04:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 05:00 | 48.33 | 12.21 | 12.21 | 36.12 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 06:00 | 49.51 | 52.04 | 52.04 | 0 | 2.53 | 0 | 14.92 | 0 | 0
2025-05-17 07:00 | 52.3 | 77.34 | 77.34 | 0 | 25.04 | 0 | 38.7 | 0 | 0
2025-05-17 08:00 | 55.79 | 89.68 | 89.68 | 0 | 33.89 | 0 | 70.9 | 0 | 0
2025-05-17 09:00 | 58.17 | 87.16 | 87.16 | 0 | 28.99 | 0 | 98.44 | 0 | 0
2025-05-17 10:00 | 60.34 | 89.8 | 75.23 | 0 | 14.89 | 0 | 112.59 | 14.57 | 0
2025-05-17 11:00 | 63.04 | 95 | 63.04 | 0 | 0 | 0 | 112.59 | 31.96 | 0
2025-05-17 12:00 | 67.08 | 103.07 | 67.08 | 0 | 0 | 0 | 112.59 | 35.98 | 0
2025-05-17 13:00 | 68.09 | 112.3 | 68.09 | 0 | 0 | 0 | 112.59 | 44.21 | 0
2025-05-17 14:00 | 69 | 113.89 | 69 | 0 | 0 | 0 | 112.59 | 44.89 | 0
2025-05-17 15:00 | 69.6 | 120.85 | 69.6 | 0 | 0 | 0 | 112.59 | 51.25 | 0
2025-05-17 16:00 | 68.59 | 112.29 | 68.59 | 0 | 0 | 0 | 112.59 | 43.7 | 0
2025-05-17 17:00 | 68.84 | 99.52 | 68.84 | 0 | 0 | 0 | 112.59 | 30.67 | 0
2025-05-17 18:00 | 66.05 | 61.6 | 61.6 | 0 | 0 | 4.45 | 107.9 | 0 | 0
2025-05-17 19:00 | 64.5 | 2.74 | 2.74 | 0 | 0 | 61.76 | 42.9 | 0 | 0
2025-05-17 20:00 | 61.04 | 0 | 0 | 32.17 | 0 | 28.87 | 12.51 | 0 | 0
2025-05-17 21:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 22:00 | 55.25 | 0 | 0 | 55.25 | 0 | 0 | 12.51 | 0 | 0
2025-05-17 23:00 | 52.86 | 0 | 0 | 52.86 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 01:00 | 48.87 | 0 | 0 | 48.87 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 02:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 03:00 | 46.97 | 0 | 0 | 46.97 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 04:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 05:00 | 48.1 | 17.08 | 17.08 | 31.02 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 06:00 | 50.34 | 88.99 | 88.99 | 0 | 38.65 | 0 | 49.23 | 0 | 0
2025-05-18 07:00 | 52.73 | 115.02 | 115.02 | 0 | 62.29 | 0 | 108.4 | 0 | 0
2025-05-18 08:00 | 55.79 | 123.53 | 60.2 | 0 | 4.41 | 0 | 112.59 | 63.34 | 0
2025-05-18 09:00 | 58.55 | 125.64 | 58.55 | 0 | 0 | 0 | 112.59 | 67.09 | 0
2025-05-18 10:00 | 62.22 | 124.88 | 62.22 | 0 | 0 | 0 | 112.59 | 62.66 | 0
2025-05-18 11:00 | 65.14 | 123.2 | 65.14 | 0 | 0 | 0 | 112.59 | 58.06 | 0
2025-05-18 12:00 | 67.22 | 121.93 | 67.22 | 0 | 0 | 0 | 112.59 | 54.71 | 0
2025-05-18 13:00 | 70.21 | 123.68 | 70.21 | 0 | 0 | 0 | 112.59 | 53.47 | 0
2025-05-18 14:00 | 71.06 | 125.51 | 71.06 | 0 | 0 | 0 | 112.59 | 54.46 | 0
2025-05-18 15:00 | 71.22 | 124.72 | 71.22 | 0 | 0 | 0 | 112.59 | 53.5 | 0
2025-05-18 16:00 | 71.67 | 120.58 | 71.67 | 0 | 0 | 0 | 112.59 | 48.91 | 0
2025-05-18 17:00 | 70.45 | 106.53 | 70.45 | 0 | 0 | 0 | 112.59 | 36.08 | 0
2025-05-18 18:00 | 68.28 | 68.43 | 68.28 | 0 | 0 | 0 | 112.59 | 0.15 | 0
2025-05-18 19:00 | 65.51 | 2.63 | 2.63 | 0.37 | 0 | 62.5 | 46.8 | 0 | 0
2025-05-18 20:00 | 61.09 | 0 | 0 | 28.52 | 0 | 32.58 | 12.51 | 0 | 0
2025-05-18 21:00 | 58.09 | 0 | 0 | 58.09 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 22:00 | 56.58 | 0 | 0 | 56.58 | 0 | 0 | 12.51 | 0 | 0
2025-05-18 23:00 | 52.2 | 0 | 0 | 52.2 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 01:00 | 48.37 | 0 | 0 | 48.37 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 02:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 03:00 | 46.89 | 0 | 0 | 46.89 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 04:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 05:00 | 48.78 | 16.09 | 16.09 | 32.69 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 06:00 | 50.36 | 71.2 | 71.2 | 0 | 20.85 | 0 | 32.31 | 0 | 0
2025-05-19 07:00 | 52.65 | 91.5 | 91.5 | 0 | 38.85 | 0 | 69.22 | 0 | 0
2025-05-19 08:00 | 56.54 | 102.38 | 102.18 | 0 | 45.65 | 0 | 112.59 | 0.19 | 0
2025-05-19 09:00 | 59.51 | 111.27 | 59.51 | 0 | 0 | 0 | 112.59 | 51.76 | 0
2025-05-19 10:00 | 64.32 | 113.55 | 64.32 | 0 | 0 | 0 | 112.59 | 49.23 | 0
2025-05-19 11:00 | 69.37 | 110.24 | 69.37 | 0 | 0 | 0 | 112.59 | 40.87 | 0
2025-05-19 12:00 | 72.3 | 101.37 | 72.3 | 0 | 0 | 0 | 112.59 | 29.07 | 0
2025-05-19 13:00 | 74.84 | 101.02 | 74.84 | 0 | 0 | 0 | 112.59 | 26.18 | 0
2025-05-19 14:00 | 76.29 | 101.36 | 76.29 | 0 | 0 | 0 | 112.59 | 25.08 | 0
2025-05-19 15:00 | 76 | 98.12 | 76 | 0 | 0 | 0 | 112.59 | 22.12 | 0
2025-05-19 16:00 | 75.67 | 77.74 | 75.67 | 0 | 0 | 0 | 112.59 | 2.08 | 0
2025-05-19 17:00 | 75.12 | 63.85 | 63.85 | 0 | 0 | 11.28 | 100.72 | 0 | 0
2025-05-19 18:00 | 71.23 | 23.14 | 23.14 | 0 | 0 | 48.09 | 50.1 | 0 | 0
2025-05-19 19:00 | 67.7 | 1.84 | 1.84 | 30.15 | 0 | 35.71 | 12.51 | 0 | 0
2025-05-19 20:00 | 64.02 | 0 | 0 | 64.02 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 21:00 | 59.59 | 0 | 0 | 59.59 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 22:00 | 55.79 | 0 | 0 | 55.79 | 0 | 0 | 12.51 | 0 | 0
2025-05-19 23:00 | 53.15 | 0 | 0 | 53.15 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 | 50.36 | 0 | 0 | 50.36 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 01:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 02:00 | 47.31 | 0 | 0 | 47.31 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 03:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 04:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 05:00 | 48.77 | 20.83 | 20.83 | 27.93 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 06:00 | 51.1 | 68.71 | 68.71 | 0 | 17.6 | 0 | 29.23 | 0 | 0
2025-05-20 07:00 | 53.49 | 103.75 | 103.75 | 0 | 50.26 | 0 | 76.98 | 0 | 0
2025-05-20 08:00 | 56.95 | 133.3 | 94.44 | 0 | 37.49 | 0 | 112.59 | 38.87 | 0
2025-05-20 09:00 | 61.48 | 92.86 | 61.48 | 0 | 0 | 0 | 112.59 | 31.37 | 0
2025-05-20 10:00 | 66.13 | 8.78 | 8.78 | 0 | 0 | 57.35 | 52.22 | 0 | 0
2025-05-20 11:00 | 70.31 | 20.68 | 20.68 | 11.9 | 0 | 37.72 | 12.51 | 0 | 0
2025-05-20 12:00 | 74.63 | 9.5 | 9.5 | 65.12 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 13:00 | 77.59 | 22.58 | 22.58 | 55.01 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 14:00 | 79.76 | 8.1 | 8.1 | 71.66 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 15:00 | 81.34 | 87.11 | 87.11 | 0 | 5.77 | 0 | 17.99 | 0 | 0
2025-05-20 16:00 | 80.41 | 115.03 | 115.03 | 0 | 34.61 | 0 | 50.87 | 0 | 0
2025-05-20 17:00 | 78.21 | 29.54 | 29.54 | 12.22 | 0 | 36.45 | 12.51 | 0 | 0
2025-05-20 18:00 | 74.73 | 39.15 | 39.15 | 35.57 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 19:00 | 70.4 | 0.71 | 0.71 | 69.69 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 20:00 | 66.14 | 0 | 0 | 66.14 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 21:00 | 61.72 | 0 | 0 | 61.72 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 22:00 | 57.55 | 0 | 0 | 57.55 | 0 | 0 | 12.51 | 0 | 0
2025-05-20 23:00 | 53.51 | 0 | 0 | 53.51 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 | 51.43 | 0 | 0 | 51.43 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 01:00 | 49.05 | 0 | 0 | 49.05 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 02:00 | 48.14 | 0 | 0 | 48.14 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 03:00 | 47.58 | 0 | 0 | 47.58 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 04:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 05:00 | 48.57 | 7.9 | 7.9 | 40.67 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 06:00 | 51.08 | 43.37 | 43.37 | 7.72 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 07:00 | 54.53 | 106.15 | 106.15 | 0 | 51.62 | 0 | 61.55 | 0 | 0
2025-05-21 08:00 | 55.72 | 100.1 | 100.1 | 0 | 44.37 | 0 | 103.71 | 0 | 0
2025-05-21 09:00 | 59.01 | 117.61 | 68.36 | 0 | 9.35 | 0 | 112.59 | 49.25 | 0
2025-05-21 10:00 | 61.87 | 104.91 | 61.87 | 0 | 0 | 0 | 112.59 | 43.04 | 0
2025-05-21 11:00 | 64.8 | 92.48 | 64.8 | 0 | 0 | 0 | 112.59 | 27.68 | 0
2025-05-21 12:00 | 68.4 | 76.43 | 68.4 | 0 | 0 | 0 | 112.59 | 8.04 | 0
2025-05-21 13:00 | 69.29 | 69.8 | 69.29 | 0 | 0 | 0 | 112.59 | 0.51 | 0
2025-05-21 14:00 | 70.66 | 64.83 | 64.83 | 0 | 0 | 5.82 | 106.46 | 0 | 0
2025-05-21 15:00 | 70.54 | 92.07 | 76.99 | 0 | 6.45 | 0 | 112.59 | 15.08 | 0
2025-05-21 16:00 | 70.52 | 100.47 | 70.52 | 0 | 0 | 0 | 112.59 | 29.95 | 0
2025-05-21 17:00 | 68.77 | 109.57 | 68.77 | 0 | 0 | 0 | 112.59 | 40.8 | 0
2025-05-21 18:00 | 67.94 | 70.44 | 67.94 | 0 | 0 | 0 | 112.59 | 2.5 | 0
2025-05-21 19:00 | 66.45 | 2.83 | 2.83 | 1.12 | 0 | 62.5 | 46.8 | 0 | 0
2025-05-21 20:00 | 61.91 | 0 | 0 | 29.33 | 0 | 32.58 | 12.51 | 0 | 0
2025-05-21 21:00 | 58.14 | 0 | 0 | 58.14 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 22:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 12.51 | 0 | 0
2025-05-21 23:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 01:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 02:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 03:00 | 47.47 | 0 | 0 | 47.47 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 04:00 | 48.32 | 0 | 0 | 48.32 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 05:00 | 48.93 | 9.76 | 9.76 | 39.17 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 06:00 | 50.5 | 56.87 | 56.87 | 0 | 6.36 | 0 | 18.56 | 0 | 0
2025-05-22 07:00 | 52.81 | 19.86 | 19.86 | 27.21 | 0 | 5.74 | 12.51 | 0 | 0
2025-05-22 08:00 | 54.67 | 54.59 | 54.59 | 0.08 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 09:00 | 57.96 | 51.47 | 51.47 | 6.49 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 10:00 | 59.18 | 105.04 | 105.04 | 0 | 45.86 | 0 | 56.08 | 0 | 0
2025-05-22 11:00 | 61.89 | 77.21 | 77.21 | 0 | 15.32 | 0 | 70.64 | 0 | 0
2025-05-22 12:00 | 64.15 | 67.51 | 67.51 | 0 | 3.36 | 0 | 73.83 | 0 | 0
2025-05-22 13:00 | 65.13 | 85.86 | 85.86 | 0 | 20.73 | 0 | 93.52 | 0 | 0
2025-05-22 14:00 | 66.01 | 91.88 | 86.08 | 0 | 20.07 | 0 | 112.59 | 5.8 | 0
2025-05-22 15:00 | 65.93 | 106.27 | 65.93 | 0 | 0 | 0 | 112.59 | 40.33 | 0
2025-05-22 16:00 | 66.3 | 124.45 | 66.3 | 0 | 0 | 0 | 112.59 | 58.14 | 0
2025-05-22 17:00 | 65.44 | 115.69 | 65.44 | 0 | 0 | 0 | 112.59 | 50.24 | 0
2025-05-22 18:00 | 63.99 | 82.69 | 63.99 | 0 | 0 | 0 | 112.59 | 18.7 | 0
2025-05-22 19:00 | 62.58 | 7.67 | 7.67 | 0 | 0 | 54.91 | 54.79 | 0 | 0
2025-05-22 20:00 | 60.45 | 0 | 0 | 20.28 | 0 | 40.17 | 12.51 | 0 | 0
2025-05-22 21:00 | 57.54 | 0 | 0 | 57.54 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 22:00 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 12.51 | 0 | 0
2025-05-22 23:00 | 53.12 | 0 | 0 | 53.12 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 01:00 | 49.69 | 0 | 0 | 49.69 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 02:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 03:00 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 04:00 | 48.28 | 0 | 0 | 48.28 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 05:00 | 49.11 | 17.61 | 17.61 | 31.49 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 06:00 | 49.85 | 72.37 | 72.37 | 0 | 22.53 | 0 | 33.91 | 0 | 0
2025-05-23 07:00 | 52.96 | 101.99 | 101.99 | 0 | 49.03 | 0 | 80.49 | 0 | 0
2025-05-23 08:00 | 53.92 | 110.66 | 87.71 | 0 | 33.79 | 0 | 112.59 | 22.95 | 0
2025-05-23 09:00 | 56.32 | 114.9 | 56.32 | 0 | 0 | 0 | 112.59 | 58.58 | 0
2025-05-23 10:00 | 59.12 | 111.7 | 59.12 | 0 | 0 | 0 | 112.59 | 52.58 | 0
2025-05-23 11:00 | 60.64 | 109.87 | 60.64 | 0 | 0 | 0 | 112.59 | 49.23 | 0
2025-05-23 12:00 | 60.01 | 110.26 | 60.01 | 0 | 0 | 0 | 112.59 | 50.25 | 0
2025-05-23 13:00 | 61.02 | 110.96 | 61.02 | 0 | 0 | 0 | 112.59 | 49.93 | 0
2025-05-23 14:00 | 61.5 | 110.74 | 61.5 | 0 | 0 | 0 | 112.59 | 49.23 | 0
2025-05-23 15:00 | 62.47 | 105.77 | 62.47 | 0 | 0 | 0 | 112.59 | 43.31 | 0
2025-05-23 16:00 | 61.24 | 100.43 | 61.24 | 0 | 0 | 0 | 112.59 | 39.19 | 0
2025-05-23 17:00 | 60.95 | 80.51 | 60.95 | 0 | 0 | 0 | 112.59 | 19.56 | 0
2025-05-23 18:00 | 61.4 | 53.14 | 53.14 | 0 | 0 | 8.26 | 103.9 | 0 | 0
2025-05-23 19:00 | 59.54 | 4.35 | 4.35 | 0 | 0 | 55.19 | 45.81 | 0 | 0
2025-05-23 20:00 | 58.8 | 0 | 0 | 27.17 | 0 | 31.63 | 12.51 | 0 | 0
2025-05-23 21:00 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 22:00 | 54.76 | 0 | 0 | 54.76 | 0 | 0 | 12.51 | 0 | 0
2025-05-23 23:00 | 51.94 | 0 | 0 | 51.94 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 01:00 | 49.73 | 0 | 0 | 49.73 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 02:00 | 48.15 | 0 | 0 | 48.15 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 03:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 04:00 | 47.8 | 0 | 0 | 47.8 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 05:00 | 49.2 | 15.06 | 15.06 | 34.14 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 06:00 | 51.29 | 39.98 | 39.98 | 11.31 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 07:00 | 54.03 | 72.18 | 72.18 | 0 | 18.16 | 0 | 29.76 | 0 | 0
2025-05-24 08:00 | 55.05 | 93.46 | 93.46 | 0 | 38.42 | 0 | 66.26 | 0 | 0
2025-05-24 09:00 | 59.01 | 98.08 | 98.08 | 0 | 39.07 | 0 | 103.37 | 0 | 0
2025-05-24 10:00 | 62.6 | 110.62 | 72.31 | 0 | 9.7 | 0 | 112.59 | 38.32 | 0
2025-05-24 11:00 | 65.4 | 102.63 | 65.4 | 0 | 0 | 0 | 112.59 | 37.23 | 0
2025-05-24 12:00 | 68.18 | 106.46 | 68.18 | 0 | 0 | 0 | 112.59 | 38.28 | 0
2025-05-24 13:00 | 70.08 | 106.29 | 70.08 | 0 | 0 | 0 | 112.59 | 36.21 | 0
2025-05-24 14:00 | 71.03 | 111.18 | 71.03 | 0 | 0 | 0 | 112.59 | 40.15 | 0
2025-05-24 15:00 | 71.34 | 110.24 | 71.34 | 0 | 0 | 0 | 112.59 | 38.9 | 0
2025-05-24 16:00 | 71.06 | 94.32 | 71.06 | 0 | 0 | 0 | 112.59 | 23.26 | 0
2025-05-24 17:00 | 70.52 | 79.48 | 70.52 | 0 | 0 | 0 | 112.59 | 8.96 | 0
2025-05-24 18:00 | 67.62 | 48.39 | 48.39 | 0 | 0 | 19.22 | 92.35 | 0 | 0
2025-05-24 19:00 | 65.42 | 4.42 | 4.42 | 0 | 0 | 61 | 28.14 | 0 | 0
2025-05-24 20:00 | 62.62 | 0 | 0 | 47.76 | 0 | 14.85 | 12.51 | 0 | 0
2025-05-24 21:00 | 60.2 | 0 | 0 | 60.2 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 22:00 | 56.21 | 0 | 0 | 56.21 | 0 | 0 | 12.51 | 0 | 0
2025-05-24 23:00 | 54.02 | 0 | 0 | 54.02 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 | 51.79 | 0 | 0 | 51.79 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 01:00 | 49.38 | 0 | 0 | 49.38 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 02:00 | 48.18 | 0 | 0 | 48.18 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 03:00 | 47.73 | 0 | 0 | 47.73 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 04:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 05:00 | 49.84 | 1.55 | 1.55 | 48.29 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 06:00 | 51.29 | 9.06 | 9.06 | 42.23 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 07:00 | 53.53 | 19.33 | 19.33 | 34.2 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 08:00 | 55.36 | 34 | 34 | 21.36 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 09:00 | 58.02 | 42.1 | 42.1 | 15.93 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 10:00 | 62.05 | 52.29 | 52.29 | 9.76 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 11:00 | 63.09 | 56.05 | 56.05 | 7.04 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 12:00 | 64.61 | 49.25 | 49.25 | 15.36 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 13:00 | 67.05 | 55.92 | 55.92 | 11.13 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 14:00 | 67.3 | 49.55 | 49.55 | 17.75 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 15:00 | 67.73 | 27.4 | 27.4 | 40.32 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 16:00 | 67.09 | 17.77 | 17.77 | 49.33 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 17:00 | 66.18 | 9.87 | 9.87 | 56.31 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 18:00 | 64.91 | 0 | 0 | 64.91 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 19:00 | 62.49 | 0 | 0 | 62.49 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 20:00 | 60.93 | 0 | 0 | 60.93 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 21:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 22:00 | 56.85 | 0 | 0 | 56.85 | 0 | 0 | 12.51 | 0 | 0
2025-05-25 23:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 | 50.18 | 0 | 0 | 50.18 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 01:00 | 49.5 | 0 | 0 | 49.5 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 02:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 03:00 | 48.44 | 0 | 0 | 48.44 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 04:00 | 48 | 0 | 0 | 48 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 05:00 | 49.84 | 20.12 | 20.12 | 29.72 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 06:00 | 50.98 | 55.47 | 55.47 | 0 | 4.49 | 0 | 16.77 | 0 | 0
2025-05-26 07:00 | 52.99 | 109.28 | 109.28 | 0 | 56.29 | 0 | 70.25 | 0 | 0
2025-05-26 08:00 | 56.14 | 123.77 | 100.71 | 0 | 44.56 | 0 | 112.59 | 23.07 | 0
2025-05-26 09:00 | 59.15 | 121.63 | 59.15 | 0 | 0 | 0 | 112.59 | 62.48 | 0
2025-05-26 10:00 | 60.9 | 56.11 | 56.11 | 0 | 0 | 4.79 | 107.55 | 0 | 0
2025-05-26 11:00 | 63.75 | 76.42 | 69.06 | 0 | 5.31 | 0 | 112.59 | 7.36 | 0
2025-05-26 12:00 | 66.43 | 101.34 | 66.43 | 0 | 0 | 0 | 112.59 | 34.91 | 0
2025-05-26 13:00 | 67.81 | 125.96 | 67.81 | 0 | 0 | 0 | 112.59 | 58.14 | 0
2025-05-26 14:00 | 69.2 | 102.72 | 69.2 | 0 | 0 | 0 | 112.59 | 33.52 | 0
2025-05-26 15:00 | 68.73 | 125.3 | 68.73 | 0 | 0 | 0 | 112.59 | 56.57 | 0
2025-05-26 16:00 | 69.36 | 119.71 | 69.36 | 0 | 0 | 0 | 112.59 | 50.35 | 0
2025-05-26 17:00 | 67.42 | 104.21 | 67.42 | 0 | 0 | 0 | 112.59 | 36.79 | 0
2025-05-26 18:00 | 67.25 | 70.25 | 67.25 | 0 | 0 | 0 | 112.59 | 3 | 0
2025-05-26 19:00 | 63.47 | 7.79 | 7.79 | 0 | 0 | 55.68 | 53.98 | 0 | 0
2025-05-26 20:00 | 61.29 | 0 | 0 | 21.89 | 0 | 39.39 | 12.51 | 0 | 0
2025-05-26 21:00 | 59.31 | 0 | 0 | 59.31 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 22:00 | 57.15 | 0 | 0 | 57.15 | 0 | 0 | 12.51 | 0 | 0
2025-05-26 23:00 | 53.82 | 0 | 0 | 53.82 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 01:00 | 49.67 | 0 | 0 | 49.67 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 02:00 | 48 | 0 | 0 | 48 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 03:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 04:00 | 47.91 | 0 | 0 | 47.91 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 05:00 | 49.02 | 22.89 | 22.89 | 26.13 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 06:00 | 51.66 | 87.41 | 87.41 | 0 | 35.75 | 0 | 46.47 | 0 | 0
2025-05-27 07:00 | 53.2 | 104.75 | 104.75 | 0 | 51.55 | 0 | 95.44 | 0 | 0
2025-05-27 08:00 | 56.53 | 116.91 | 74.58 | 0 | 18.05 | 0 | 112.59 | 42.33 | 0
2025-05-27 09:00 | 58.43 | 110.39 | 58.43 | 0 | 0 | 0 | 112.59 | 51.96 | 0
2025-05-27 10:00 | 61.86 | 108.58 | 61.86 | 0 | 0 | 0 | 112.59 | 46.71 | 0
2025-05-27 11:00 | 63.84 | 97.62 | 63.84 | 0 | 0 | 0 | 112.59 | 33.78 | 0
2025-05-27 12:00 | 66.77 | 79.32 | 66.77 | 0 | 0 | 0 | 112.59 | 12.55 | 0
2025-05-27 13:00 | 67.71 | 103.04 | 67.71 | 0 | 0 | 0 | 112.59 | 35.33 | 0
2025-05-27 14:00 | 69.08 | 89.07 | 69.08 | 0 | 0 | 0 | 112.59 | 19.99 | 0
2025-05-27 15:00 | 68.4 | 60.62 | 60.62 | 0 | 0 | 7.77 | 104.41 | 0 | 0
2025-05-27 16:00 | 68.49 | 56.28 | 56.28 | 0 | 0 | 12.21 | 91.55 | 0 | 0
2025-05-27 17:00 | 67.06 | 32.8 | 32.8 | 0 | 0 | 34.25 | 55.49 | 0 | 0
2025-05-27 18:00 | 65.86 | 19.16 | 19.16 | 5.86 | 0 | 40.84 | 12.51 | 0 | 0
2025-05-27 19:00 | 63.96 | 1.93 | 1.93 | 62.03 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 20:00 | 61.35 | 0 | 0 | 61.35 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 21:00 | 58.48 | 0 | 0 | 58.48 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 22:00 | 55.66 | 0 | 0 | 55.66 | 0 | 0 | 12.51 | 0 | 0
2025-05-27 23:00 | 52.59 | 0 | 0 | 52.59 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 | 51.11 | 0 | 0 | 51.11 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 01:00 | 50.1 | 0 | 0 | 50.1 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 02:00 | 47.83 | 0 | 0 | 47.83 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 03:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 04:00 | 49.52 | 0 | 0 | 49.52 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 05:00 | 49.47 | 0.66 | 0.66 | 48.82 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 06:00 | 51.8 | 32.98 | 32.98 | 18.82 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 07:00 | 54.36 | 28.37 | 28.37 | 25.99 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 08:00 | 57.14 | 37.02 | 37.02 | 20.12 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 09:00 | 59 | 83.94 | 83.94 | 0 | 24.94 | 0 | 36.2 | 0 | 0
2025-05-28 10:00 | 62.59 | 89.2 | 89.2 | 0 | 26.61 | 0 | 61.48 | 0 | 0
2025-05-28 11:00 | 64.61 | 106.7 | 106.7 | 0 | 42.09 | 0 | 101.47 | 0 | 0
2025-05-28 12:00 | 68.97 | 97.14 | 80.68 | 0 | 11.71 | 0 | 112.59 | 16.46 | 0
2025-05-28 13:00 | 68.72 | 116.42 | 68.72 | 0 | 0 | 0 | 112.59 | 47.7 | 0
2025-05-28 14:00 | 70.1 | 61.31 | 61.31 | 0 | 0 | 8.8 | 103.33 | 0 | 0
2025-05-28 15:00 | 70.48 | 64.78 | 64.78 | 0 | 0 | 5.71 | 97.33 | 0 | 0
2025-05-28 16:00 | 69.88 | 64.64 | 64.64 | 0 | 0 | 5.24 | 91.81 | 0 | 0
2025-05-28 17:00 | 70.19 | 63.42 | 63.42 | 0 | 0 | 6.77 | 84.69 | 0 | 0
2025-05-28 18:00 | 68.95 | 52.32 | 52.32 | 0 | 0 | 16.63 | 67.18 | 0 | 0
2025-05-28 19:00 | 65.18 | 2.46 | 2.46 | 10.79 | 0 | 51.94 | 12.51 | 0 | 0
2025-05-28 20:00 | 62.04 | 0 | 0 | 62.04 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 21:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 22:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 12.51 | 0 | 0
2025-05-28 23:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 01:00 | 50.04 | 0 | 0 | 50.04 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 02:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 03:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 04:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 05:00 | 49.38 | 17.48 | 17.48 | 31.9 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 06:00 | 52.21 | 69.15 | 69.15 | 0 | 16.94 | 0 | 28.6 | 0 | 0
2025-05-29 07:00 | 54.51 | 96.07 | 96.07 | 0 | 41.56 | 0 | 68.09 | 0 | 0
2025-05-29 08:00 | 58.12 | 108.84 | 104.96 | 0 | 46.84 | 0 | 112.59 | 3.88 | 0
2025-05-29 09:00 | 61.62 | 110.7 | 61.62 | 0 | 0 | 0 | 112.59 | 49.08 | 0
2025-05-29 10:00 | 64.22 | 112.65 | 64.22 | 0 | 0 | 0 | 112.59 | 48.43 | 0
2025-05-29 11:00 | 67.8 | 108.46 | 67.8 | 0 | 0 | 0 | 112.59 | 40.66 | 0
2025-05-29 12:00 | 71.33 | 102.98 | 71.33 | 0 | 0 | 0 | 112.59 | 31.65 | 0
2025-05-29 13:00 | 73.69 | 103.99 | 73.69 | 0 | 0 | 0 | 112.59 | 30.31 | 0
2025-05-29 14:00 | 76.2 | 98.78 | 76.2 | 0 | 0 | 0 | 112.59 | 22.58 | 0
2025-05-29 15:00 | 76.55 | 100.74 | 76.55 | 0 | 0 | 0 | 112.59 | 24.19 | 0
2025-05-29 16:00 | 76.37 | 72.29 | 72.29 | 0 | 0 | 4.08 | 108.29 | 0 | 0
2025-05-29 17:00 | 74.41 | 46.93 | 46.93 | 0 | 0 | 27.49 | 79.36 | 0 | 0
2025-05-29 18:00 | 71.81 | 24.65 | 24.65 | 0 | 0 | 47.15 | 29.72 | 0 | 0
2025-05-29 19:00 | 69.12 | 4.33 | 4.33 | 48.43 | 0 | 16.35 | 12.51 | 0 | 0
2025-05-29 20:00 | 65.17 | 0 | 0 | 65.17 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 21:00 | 61.26 | 0 | 0 | 61.26 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 22:00 | 58.41 | 0 | 0 | 58.41 | 0 | 0 | 12.51 | 0 | 0
2025-05-29 23:00 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 01:00 | 49.61 | 0 | 0 | 49.61 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 02:00 | 49.2 | 0 | 0 | 49.2 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 03:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 04:00 | 48.82 | 0 | 0 | 48.82 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 05:00 | 50.69 | 22.44 | 22.44 | 28.25 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 06:00 | 50.94 | 75.76 | 75.76 | 0 | 24.82 | 0 | 36.09 | 0 | 0
2025-05-30 07:00 | 54.38 | 98.35 | 98.35 | 0 | 43.97 | 0 | 77.86 | 0 | 0
2025-05-30 08:00 | 57.29 | 111.32 | 93.85 | 0 | 36.56 | 0 | 112.59 | 17.47 | 0
2025-05-30 09:00 | 60.09 | 110.94 | 60.09 | 0 | 0 | 0 | 112.59 | 50.85 | 0
2025-05-30 10:00 | 64.8 | 112.08 | 64.8 | 0 | 0 | 0 | 112.59 | 47.28 | 0
2025-05-30 11:00 | 66.54 | 110.41 | 66.54 | 0 | 0 | 0 | 112.59 | 43.86 | 0
2025-05-30 12:00 | 68.94 | 110.79 | 68.94 | 0 | 0 | 0 | 112.59 | 41.85 | 0
2025-05-30 13:00 | 71.13 | 109.49 | 71.13 | 0 | 0 | 0 | 112.59 | 38.36 | 0
2025-05-30 14:00 | 71.36 | 110.84 | 71.36 | 0 | 0 | 0 | 112.59 | 39.47 | 0
2025-05-30 15:00 | 72.41 | 107.76 | 72.41 | 0 | 0 | 0 | 112.59 | 35.35 | 0
2025-05-30 16:00 | 72.86 | 104.57 | 72.86 | 0 | 0 | 0 | 112.59 | 31.72 | 0
2025-05-30 17:00 | 70.8 | 93.81 | 70.8 | 0 | 0 | 0 | 112.59 | 23.01 | 0
2025-05-30 18:00 | 68.73 | 68.75 | 68.73 | 0 | 0 | 0 | 112.59 | 0.03 | 0
2025-05-30 19:00 | 67.23 | 8.97 | 8.97 | 0 | 0 | 58.27 | 51.26 | 0 | 0
2025-05-30 20:00 | 64.28 | 0 | 0 | 27.47 | 0 | 36.81 | 12.51 | 0 | 0
2025-05-30 21:00 | 60.71 | 0 | 0 | 60.71 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 22:00 | 57.08 | 0 | 0 | 57.08 | 0 | 0 | 12.51 | 0 | 0
2025-05-30 23:00 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 01:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 02:00 | 48.43 | 0 | 0 | 48.43 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 03:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 04:00 | 48.44 | 0 | 0 | 48.44 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 05:00 | 49.36 | 29.23 | 29.23 | 20.13 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 06:00 | 52.13 | 92.67 | 92.67 | 0 | 40.54 | 0 | 51.02 | 0 | 0
2025-05-31 07:00 | 54.58 | 113.34 | 113.34 | 0 | 58.76 | 0 | 106.84 | 0 | 0
2025-05-31 08:00 | 58.14 | 121.03 | 64.19 | 0 | 6.05 | 0 | 112.59 | 56.84 | 0
2025-05-31 09:00 | 59.96 | 122.72 | 59.96 | 0 | 0 | 0 | 112.59 | 62.76 | 0
2025-05-31 10:00 | 63.43 | 121.34 | 63.43 | 0 | 0 | 0 | 112.59 | 57.92 | 0
2025-05-31 11:00 | 66.19 | 119.25 | 66.19 | 0 | 0 | 0 | 112.59 | 53.06 | 0
2025-05-31 12:00 | 68.27 | 117.5 | 68.27 | 0 | 0 | 0 | 112.59 | 49.24 | 0
2025-05-31 13:00 | 70.56 | 119.28 | 70.56 | 0 | 0 | 0 | 112.59 | 48.72 | 0
2025-05-31 14:00 | 71.7 | 120.63 | 71.7 | 0 | 0 | 0 | 112.59 | 48.93 | 0
2025-05-31 15:00 | 71.86 | 119.35 | 71.86 | 0 | 0 | 0 | 112.59 | 47.49 | 0
2025-05-31 16:00 | 71.19 | 115.02 | 71.19 | 0 | 0 | 0 | 112.59 | 43.83 | 0
2025-05-31 17:00 | 70.01 | 100.58 | 70.01 | 0 | 0 | 0 | 112.59 | 30.56 | 0
2025-05-31 18:00 | 67.71 | 74.6 | 67.71 | 0 | 0 | 0 | 112.59 | 6.89 | 0
2025-05-31 19:00 | 65.64 | 8.12 | 8.12 | 0 | 0 | 57.51 | 52.05 | 0 | 0
2025-05-31 20:00 | 62.97 | 0 | 0 | 25.4 | 0 | 37.56 | 12.51 | 0 | 0
2025-05-31 21:00 | 59.73 | 0 | 0 | 59.73 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 22:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 12.51 | 0 | 0
2025-05-31 23:00 | 55.06 | 0 | 0 | 55.06 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 01:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 02:00 | 48.54 | 0 | 0 | 48.54 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 03:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 04:00 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 05:00 | 50.54 | 30.5 | 30.5 | 20.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 06:00 | 51.73 | 93.28 | 93.28 | 0 | 41.56 | 0 | 51.99 | 0 | 0
2025-06-01 07:00 | 54.87 | 113.48 | 113.48 | 0 | 58.6 | 0 | 107.66 | 0 | 0
2025-06-01 08:00 | 56.8 | 121.91 | 61.99 | 0 | 5.19 | 0 | 112.59 | 59.92 | 0
2025-06-01 09:00 | 59.2 | 124.1 | 59.2 | 0 | 0 | 0 | 112.59 | 64.9 | 0
2025-06-01 10:00 | 61.35 | 122.98 | 61.35 | 0 | 0 | 0 | 112.59 | 61.63 | 0
2025-06-01 11:00 | 64.25 | 121 | 64.25 | 0 | 0 | 0 | 112.59 | 56.75 | 0
2025-06-01 12:00 | 66.31 | 119.56 | 66.31 | 0 | 0 | 0 | 112.59 | 53.25 | 0
2025-06-01 13:00 | 67.27 | 120.29 | 67.27 | 0 | 0 | 0 | 112.59 | 53.02 | 0
2025-06-01 14:00 | 69.03 | 120.92 | 69.03 | 0 | 0 | 0 | 112.59 | 51.9 | 0
2025-06-01 15:00 | 68.88 | 120.48 | 68.88 | 0 | 0 | 0 | 112.59 | 51.6 | 0
2025-06-01 16:00 | 67.75 | 115.21 | 67.75 | 0 | 0 | 0 | 112.59 | 47.46 | 0
2025-06-01 17:00 | 66.98 | 104.89 | 66.98 | 0 | 0 | 0 | 112.59 | 37.91 | 0
2025-06-01 18:00 | 66.1 | 79.57 | 66.1 | 0 | 0 | 0 | 112.59 | 13.47 | 0
2025-06-01 19:00 | 63.7 | 8.44 | 8.44 | 0 | 0 | 55.26 | 54.42 | 0 | 0
2025-06-01 20:00 | 62.56 | 0 | 0 | 22.74 | 0 | 39.82 | 12.51 | 0 | 0
2025-06-01 21:00 | 59.71 | 0 | 0 | 59.71 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 22:00 | 57.05 | 0 | 0 | 57.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-01 23:00 | 54.71 | 0 | 0 | 54.71 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 | 53 | 0 | 0 | 53 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 01:00 | 50.42 | 0 | 0 | 50.42 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 02:00 | 49.11 | 0 | 0 | 49.11 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 03:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 04:00 | 49.65 | 0 | 0 | 49.65 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 05:00 | 50.18 | 28.22 | 28.22 | 21.96 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 06:00 | 52.14 | 85.54 | 85.54 | 0 | 33.41 | 0 | 44.25 | 0 | 0
2025-06-02 07:00 | 54.43 | 105.29 | 105.29 | 0 | 50.86 | 0 | 92.57 | 0 | 0
2025-06-02 08:00 | 56.88 | 114.17 | 77.96 | 0 | 21.08 | 0 | 112.59 | 36.22 | 0
2025-06-02 09:00 | 58.32 | 116.57 | 58.32 | 0 | 0 | 0 | 112.59 | 58.25 | 0
2025-06-02 10:00 | 60.29 | 117.43 | 60.29 | 0 | 0 | 0 | 112.59 | 57.14 | 0
2025-06-02 11:00 | 62.32 | 115.6 | 62.32 | 0 | 0 | 0 | 112.59 | 53.29 | 0
2025-06-02 12:00 | 63.57 | 113.86 | 63.57 | 0 | 0 | 0 | 112.59 | 50.3 | 0
2025-06-02 13:00 | 64.61 | 113.78 | 64.61 | 0 | 0 | 0 | 112.59 | 49.16 | 0
2025-06-02 14:00 | 65.76 | 114.74 | 65.76 | 0 | 0 | 0 | 112.59 | 48.97 | 0
2025-06-02 15:00 | 65.53 | 112.94 | 65.53 | 0 | 0 | 0 | 112.59 | 47.41 | 0
2025-06-02 16:00 | 65.54 | 108.82 | 65.54 | 0 | 0 | 0 | 112.59 | 43.27 | 0
2025-06-02 17:00 | 64.32 | 97.42 | 64.32 | 0 | 0 | 0 | 112.59 | 33.09 | 0
2025-06-02 18:00 | 63.82 | 72.76 | 63.82 | 0 | 0 | 0 | 112.59 | 8.94 | 0
2025-06-02 19:00 | 63.05 | 8.52 | 8.52 | 0 | 0 | 54.53 | 55.19 | 0 | 0
2025-06-02 20:00 | 61.36 | 0 | 0 | 20.81 | 0 | 40.54 | 12.51 | 0 | 0
2025-06-02 21:00 | 58.64 | 0 | 0 | 58.64 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 22:00 | 56.78 | 0 | 0 | 56.78 | 0 | 0 | 12.51 | 0 | 0
2025-06-02 23:00 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 02:00 | 49.18 | 0 | 0 | 49.18 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 03:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 04:00 | 49.2 | 0 | 0 | 49.2 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 05:00 | 50.46 | 26.46 | 26.46 | 24 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 06:00 | 51.64 | 85.99 | 85.99 | 0 | 34.34 | 0 | 45.14 | 0 | 0
2025-06-03 07:00 | 54.31 | 109.48 | 109.48 | 0 | 55.17 | 0 | 97.54 | 0 | 0
2025-06-03 08:00 | 57.49 | 119.12 | 73.33 | 0 | 15.84 | 0 | 112.59 | 45.8 | 0
2025-06-03 09:00 | 60.38 | 121.73 | 60.38 | 0 | 0 | 0 | 112.59 | 61.35 | 0
2025-06-03 10:00 | 63.01 | 120.87 | 63.01 | 0 | 0 | 0 | 112.59 | 57.86 | 0
2025-06-03 11:00 | 65.78 | 118.83 | 65.78 | 0 | 0 | 0 | 112.59 | 53.05 | 0
2025-06-03 12:00 | 68.06 | 117.59 | 68.06 | 0 | 0 | 0 | 112.59 | 49.53 | 0
2025-06-03 13:00 | 70.1 | 118.27 | 70.1 | 0 | 0 | 0 | 112.59 | 48.17 | 0
2025-06-03 14:00 | 70.62 | 119.1 | 70.62 | 0 | 0 | 0 | 112.59 | 48.48 | 0
2025-06-03 15:00 | 71.21 | 117.31 | 71.21 | 0 | 0 | 0 | 112.59 | 46.1 | 0
2025-06-03 16:00 | 70.4 | 111.01 | 70.4 | 0 | 0 | 0 | 112.59 | 40.61 | 0
2025-06-03 17:00 | 69.94 | 97.52 | 69.94 | 0 | 0 | 0 | 112.59 | 27.57 | 0
2025-06-03 18:00 | 68.22 | 70.09 | 68.22 | 0 | 0 | 0 | 112.59 | 1.87 | 0
2025-06-03 19:00 | 66.3 | 9.96 | 9.96 | 0 | 0 | 56.35 | 53.28 | 0 | 0
2025-06-03 20:00 | 63.65 | 0 | 0 | 24.92 | 0 | 38.73 | 12.51 | 0 | 0
2025-06-03 21:00 | 60.76 | 0 | 0 | 60.76 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 22:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 12.51 | 0 | 0
2025-06-03 23:00 | 54.92 | 0 | 0 | 54.92 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 | 53.06 | 0 | 0 | 53.06 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 01:00 | 50.27 | 0 | 0 | 50.27 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 02:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 03:00 | 49.05 | 0 | 0 | 49.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 04:00 | 49.58 | 0 | 0 | 49.58 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 05:00 | 50.18 | 23.1 | 23.1 | 27.08 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 06:00 | 52.49 | 77.45 | 77.45 | 0 | 24.96 | 0 | 36.22 | 0 | 0
2025-06-04 07:00 | 55 | 100.88 | 100.88 | 0 | 45.87 | 0 | 79.8 | 0 | 0
2025-06-04 08:00 | 56.87 | 111.86 | 91.38 | 0 | 34.51 | 0 | 112.59 | 20.48 | 0
2025-06-04 09:00 | 61 | 118.01 | 61 | 0 | 0 | 0 | 112.59 | 57.01 | 0
2025-06-04 10:00 | 64.16 | 117.83 | 64.16 | 0 | 0 | 0 | 112.59 | 53.68 | 0
2025-06-04 11:00 | 67.06 | 116.17 | 67.06 | 0 | 0 | 0 | 112.59 | 49.11 | 0
2025-06-04 12:00 | 70.34 | 115.41 | 70.34 | 0 | 0 | 0 | 112.59 | 45.07 | 0
2025-06-04 13:00 | 70.93 | 116.16 | 70.93 | 0 | 0 | 0 | 112.59 | 45.23 | 0
2025-06-04 14:00 | 72.32 | 116.11 | 72.32 | 0 | 0 | 0 | 112.59 | 43.79 | 0
2025-06-04 15:00 | 71.83 | 114.52 | 71.83 | 0 | 0 | 0 | 112.59 | 42.68 | 0
2025-06-04 16:00 | 72.49 | 107.36 | 72.49 | 0 | 0 | 0 | 112.59 | 34.86 | 0
2025-06-04 17:00 | 71.34 | 93.03 | 71.34 | 0 | 0 | 0 | 112.59 | 21.69 | 0
2025-06-04 18:00 | 69.37 | 64.81 | 64.81 | 0 | 0 | 4.56 | 107.79 | 0 | 0
2025-06-04 19:00 | 67.69 | 9.78 | 9.78 | 0 | 0 | 57.91 | 46.83 | 0 | 0
2025-06-04 20:00 | 64.66 | 0 | 0 | 32.06 | 0 | 32.6 | 12.51 | 0 | 0
2025-06-04 21:00 | 61.15 | 0 | 0 | 61.15 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 22:00 | 57.79 | 0 | 0 | 57.79 | 0 | 0 | 12.51 | 0 | 0
2025-06-04 23:00 | 55.56 | 0 | 0 | 55.56 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 | 52.81 | 0 | 0 | 52.81 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 01:00 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 02:00 | 48.62 | 0 | 0 | 48.62 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 04:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 05:00 | 51.88 | 18.75 | 18.75 | 33.13 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 06:00 | 52.85 | 64.49 | 64.49 | 0 | 11.64 | 0 | 23.57 | 0 | 0
2025-06-05 07:00 | 55.3 | 84.83 | 84.83 | 0 | 29.53 | 0 | 51.62 | 0 | 0
2025-06-05 08:00 | 58.64 | 106.6 | 106.6 | 0 | 47.96 | 0 | 97.18 | 0 | 0
2025-06-05 09:00 | 63.57 | 103.18 | 79.78 | 0 | 16.22 | 0 | 112.59 | 23.39 | 0
2025-06-05 10:00 | 66.73 | 102.33 | 66.73 | 0 | 0 | 0 | 112.59 | 35.6 | 0
2025-06-05 11:00 | 72.15 | 106.94 | 72.15 | 0 | 0 | 0 | 112.59 | 34.79 | 0
2025-06-05 12:00 | 76.12 | 103.54 | 76.12 | 0 | 0 | 0 | 112.59 | 27.42 | 0
2025-06-05 13:00 | 78.99 | 102.44 | 78.99 | 0 | 0 | 0 | 112.59 | 23.45 | 0
2025-06-05 14:00 | 80.64 | 106.76 | 80.64 | 0 | 0 | 0 | 112.59 | 26.12 | 0
2025-06-05 15:00 | 81.72 | 99.97 | 81.72 | 0 | 0 | 0 | 112.59 | 18.25 | 0
2025-06-05 16:00 | 80.84 | 89.19 | 80.84 | 0 | 0 | 0 | 112.59 | 8.35 | 0
2025-06-05 17:00 | 78.39 | 73.16 | 73.16 | 0 | 0 | 5.23 | 107.08 | 0 | 0
2025-06-05 18:00 | 76.64 | 52.25 | 52.25 | 0 | 0 | 24.4 | 81.4 | 0 | 0
2025-06-05 19:00 | 71.7 | 8.85 | 8.85 | 0.35 | 0 | 62.5 | 15.61 | 0 | 0
2025-06-05 20:00 | 68 | 0 | 0 | 65.05 | 0 | 2.95 | 12.51 | 0 | 0
2025-06-05 21:00 | 62.08 | 0 | 0 | 62.08 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 22:00 | 59.87 | 0 | 0 | 59.87 | 0 | 0 | 12.51 | 0 | 0
2025-06-05 23:00 | 56.42 | 0 | 0 | 56.42 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 | 52.8 | 0 | 0 | 52.8 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 01:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 02:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 04:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 05:00 | 50.41 | 3.27 | 3.27 | 47.14 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 06:00 | 52.48 | 6.99 | 6.99 | 45.49 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 07:00 | 55.93 | 17.27 | 17.27 | 38.65 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 08:00 | 58.87 | 33.84 | 33.84 | 25.03 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 09:00 | 61.3 | 80.72 | 80.72 | 0 | 19.43 | 0 | 30.97 | 0 | 0
2025-06-06 10:00 | 64.56 | 129.79 | 127.06 | 0 | 62.5 | 0 | 90.34 | 2.73 | 0
2025-06-06 11:00 | 67.68 | 90.35 | 90.35 | 0 | 22.67 | 0 | 111.88 | 0 | 0
2025-06-06 12:00 | 71.03 | 32.46 | 32.46 | 0 | 0 | 38.57 | 71.28 | 0 | 0
2025-06-06 13:00 | 72.2 | 34.49 | 34.49 | 0 | 0 | 37.71 | 31.58 | 0 | 0
2025-06-06 14:00 | 74.17 | 29.18 | 29.18 | 26.87 | 0 | 18.12 | 12.51 | 0 | 0
2025-06-06 15:00 | 74.81 | 35.39 | 35.39 | 39.42 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 16:00 | 73.95 | 3.85 | 3.85 | 70.1 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 17:00 | 73.21 | 2.16 | 2.16 | 71.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 18:00 | 70.51 | 0.63 | 0.63 | 69.87 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 19:00 | 67.9 | 0 | 0 | 67.9 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 20:00 | 64.44 | 0 | 0 | 64.44 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 21:00 | 62.16 | 0 | 0 | 62.16 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 22:00 | 58 | 0 | 0 | 58 | 0 | 0 | 12.51 | 0 | 0
2025-06-06 23:00 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 | 52.94 | 0 | 0 | 52.94 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 01:00 | 50.41 | 0 | 0 | 50.41 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 02:00 | 49.37 | 0 | 0 | 49.37 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 03:00 | 49.94 | 0 | 0 | 49.94 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 04:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 05:00 | 50.43 | 19.15 | 19.15 | 31.28 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 06:00 | 53.13 | 13.31 | 13.31 | 39.83 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 07:00 | 55.66 | 43.2 | 43.2 | 12.46 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 08:00 | 60.78 | 19.19 | 19.19 | 41.59 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 09:00 | 62.91 | 39.6 | 39.6 | 23.31 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 10:00 | 66.43 | 73.82 | 73.82 | 0 | 7.39 | 0 | 19.53 | 0 | 0
2025-06-07 11:00 | 71.06 | 87.76 | 87.76 | 0 | 16.7 | 0 | 35.39 | 0 | 0
2025-06-07 12:00 | 72.73 | 122.07 | 122.07 | 0 | 49.34 | 0 | 82.26 | 0 | 0
2025-06-07 13:00 | 76.3 | 99.16 | 99.16 | 0 | 22.87 | 0 | 103.98 | 0 | 0
2025-06-07 14:00 | 78.91 | 108.31 | 87.97 | 0 | 9.06 | 0 | 112.59 | 20.34 | 0
2025-06-07 15:00 | 78.43 | 101.03 | 78.43 | 0 | 0 | 0 | 112.59 | 22.61 | 0
2025-06-07 16:00 | 77.05 | 96.24 | 77.05 | 0 | 0 | 0 | 112.59 | 19.19 | 0
2025-06-07 17:00 | 76.05 | 32.92 | 32.92 | 0 | 0 | 43.13 | 67.19 | 0 | 0
2025-06-07 18:00 | 74.38 | 27.11 | 27.11 | 0 | 0 | 47.27 | 17.43 | 0 | 0
2025-06-07 19:00 | 70.54 | 4.56 | 4.56 | 61.31 | 0 | 4.67 | 12.51 | 0 | 0
2025-06-07 20:00 | 66.2 | 0 | 0 | 66.2 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 21:00 | 62.42 | 0 | 0 | 62.42 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 22:00 | 58.78 | 0 | 0 | 58.78 | 0 | 0 | 12.51 | 0 | 0
2025-06-07 23:00 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 | 53.62 | 0 | 0 | 53.62 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 01:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 02:00 | 50 | 0 | 0 | 50 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 03:00 | 48.68 | 0 | 0 | 48.68 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 04:00 | 49.1 | 0 | 0 | 49.1 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 05:00 | 51.27 | 18.5 | 18.5 | 32.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 06:00 | 52.28 | 18.04 | 18.04 | 34.24 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 07:00 | 55.33 | 75.48 | 75.48 | 0 | 20.15 | 0 | 31.65 | 0 | 0
2025-06-08 08:00 | 58.44 | 94.84 | 94.84 | 0 | 36.39 | 0 | 66.22 | 0 | 0
2025-06-08 09:00 | 60.7 | 98.08 | 98.08 | 0 | 37.38 | 0 | 101.74 | 0 | 0
2025-06-08 10:00 | 63.66 | 91.39 | 75.09 | 0 | 11.42 | 0 | 112.59 | 16.3 | 0
2025-06-08 11:00 | 66.77 | 73.79 | 66.77 | 0 | 0 | 0 | 112.59 | 7.03 | 0
2025-06-08 12:00 | 69.28 | 36.52 | 36.52 | 0 | 0 | 32.75 | 78.11 | 0 | 0
2025-06-08 13:00 | 71.22 | 60.03 | 60.03 | 0 | 0 | 11.19 | 66.33 | 0 | 0
2025-06-08 14:00 | 72.03 | 95.12 | 95.12 | 0 | 23.09 | 0 | 88.27 | 0 | 0
2025-06-08 15:00 | 72.11 | 82.69 | 82.69 | 0 | 10.58 | 0 | 98.31 | 0 | 0
2025-06-08 16:00 | 71.35 | 62.59 | 62.59 | 0 | 0 | 8.76 | 89.09 | 0 | 0
2025-06-08 17:00 | 70.16 | 52.11 | 52.11 | 0 | 0 | 18.04 | 70.1 | 0 | 0
2025-06-08 18:00 | 68.77 | 64.21 | 64.21 | 0 | 0 | 4.56 | 65.3 | 0 | 0
2025-06-08 19:00 | 67.02 | 9.76 | 9.76 | 7.11 | 0 | 50.15 | 12.51 | 0 | 0
2025-06-08 20:00 | 64.34 | 0 | 0 | 64.34 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 21:00 | 60.22 | 0 | 0 | 60.22 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 22:00 | 57.9 | 0 | 0 | 57.9 | 0 | 0 | 12.51 | 0 | 0
2025-06-08 23:00 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 01:00 | 50.39 | 0 | 0 | 50.39 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 02:00 | 51.04 | 0 | 0 | 51.04 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 03:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 04:00 | 50.05 | 0 | 0 | 50.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 05:00 | 51.29 | 24.58 | 24.58 | 26.72 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 06:00 | 52.81 | 79.03 | 79.03 | 0 | 26.22 | 0 | 37.42 | 0 | 0
2025-06-09 07:00 | 55.02 | 103.01 | 103.01 | 0 | 48 | 0 | 83.02 | 0 | 0
2025-06-09 08:00 | 59.07 | 112.22 | 90.2 | 0 | 31.13 | 0 | 112.59 | 22.02 | 0
2025-06-09 09:00 | 61.15 | 116.22 | 61.15 | 0 | 0 | 0 | 112.59 | 55.07 | 0
2025-06-09 10:00 | 63.53 | 118.83 | 63.53 | 0 | 0 | 0 | 112.59 | 55.3 | 0
2025-06-09 11:00 | 65.54 | 116.54 | 65.54 | 0 | 0 | 0 | 112.59 | 51 | 0
2025-06-09 12:00 | 66.46 | 115.36 | 66.46 | 0 | 0 | 0 | 112.59 | 48.89 | 0
2025-06-09 13:00 | 68.84 | 115.39 | 68.84 | 0 | 0 | 0 | 112.59 | 46.55 | 0
2025-06-09 14:00 | 68.52 | 114.89 | 68.52 | 0 | 0 | 0 | 112.59 | 46.37 | 0
2025-06-09 15:00 | 69.33 | 113.16 | 69.33 | 0 | 0 | 0 | 112.59 | 43.83 | 0
2025-06-09 16:00 | 68.12 | 107.98 | 68.12 | 0 | 0 | 0 | 112.59 | 39.85 | 0
2025-06-09 17:00 | 67.18 | 95.84 | 67.18 | 0 | 0 | 0 | 112.59 | 28.66 | 0
2025-06-09 18:00 | 67.13 | 70.03 | 67.13 | 0 | 0 | 0 | 112.59 | 2.9 | 0
2025-06-09 19:00 | 64.85 | 12.74 | 12.74 | 0 | 0 | 52.11 | 57.73 | 0 | 0
2025-06-09 20:00 | 62.12 | 0 | 0 | 19.16 | 0 | 42.96 | 12.51 | 0 | 0
2025-06-09 21:00 | 60.92 | 0 | 0 | 60.92 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 22:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 12.51 | 0 | 0
2025-06-09 23:00 | 56.07 | 0 | 0 | 56.07 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 | 53 | 0 | 0 | 53 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 01:00 | 51.2 | 0 | 0 | 51.2 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 02:00 | 50.4 | 0 | 0 | 50.4 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 03:00 | 50.09 | 0 | 0 | 50.09 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 04:00 | 49.78 | 0 | 0 | 49.78 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 05:00 | 51.22 | 20.67 | 20.67 | 30.55 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 06:00 | 53.28 | 65.83 | 65.83 | 0 | 12.55 | 0 | 24.43 | 0 | 0
2025-06-10 07:00 | 55.84 | 68.69 | 68.69 | 0 | 12.85 | 0 | 36.64 | 0 | 0
2025-06-10 08:00 | 58.21 | 91.61 | 91.61 | 0 | 33.4 | 0 | 68.37 | 0 | 0
2025-06-10 09:00 | 60.99 | 98.19 | 98.19 | 0 | 37.2 | 0 | 103.71 | 0 | 0
2025-06-10 10:00 | 64.37 | 104.41 | 73.72 | 0 | 9.35 | 0 | 112.59 | 30.69 | 0
2025-06-10 11:00 | 66.6 | 105.08 | 66.6 | 0 | 0 | 0 | 112.59 | 38.48 | 0
2025-06-10 12:00 | 68.12 | 106.76 | 68.12 | 0 | 0 | 0 | 112.59 | 38.64 | 0
2025-06-10 13:00 | 70.12 | 111.06 | 70.12 | 0 | 0 | 0 | 112.59 | 40.94 | 0
2025-06-10 14:00 | 69.91 | 111.34 | 69.91 | 0 | 0 | 0 | 112.59 | 41.43 | 0
2025-06-10 15:00 | 71.19 | 103.69 | 71.19 | 0 | 0 | 0 | 112.59 | 32.49 | 0
2025-06-10 16:00 | 70.37 | 106.29 | 70.37 | 0 | 0 | 0 | 112.59 | 35.92 | 0
2025-06-10 17:00 | 70.9 | 88.93 | 70.9 | 0 | 0 | 0 | 112.59 | 18.03 | 0
2025-06-10 18:00 | 67.28 | 58.76 | 58.76 | 0 | 0 | 8.53 | 103.61 | 0 | 0
2025-06-10 19:00 | 65.65 | 11.54 | 11.54 | 0 | 0 | 54.1 | 46.66 | 0 | 0
2025-06-10 20:00 | 63.89 | 0 | 0 | 31.44 | 0 | 32.44 | 12.51 | 0 | 0
2025-06-10 21:00 | 61.25 | 0 | 0 | 61.25 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 22:00 | 59.25 | 0 | 0 | 59.25 | 0 | 0 | 12.51 | 0 | 0
2025-06-10 23:00 | 55.23 | 0 | 0 | 55.23 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 | 53.71 | 0 | 0 | 53.71 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 01:00 | 51.88 | 0 | 0 | 51.88 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 02:00 | 50.4 | 0 | 0 | 50.4 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 03:00 | 49.14 | 0 | 0 | 49.14 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 04:00 | 50.75 | 0 | 0 | 50.75 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 05:00 | 51.92 | 25.02 | 25.02 | 26.89 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 06:00 | 53.56 | 67.06 | 67.06 | 0 | 13.5 | 0 | 25.34 | 0 | 0
2025-06-11 07:00 | 55.85 | 88.62 | 88.62 | 0 | 32.77 | 0 | 56.46 | 0 | 0
2025-06-11 08:00 | 58.68 | 119.08 | 117.76 | 0 | 59.08 | 0 | 112.59 | 1.33 | 0
2025-06-11 09:00 | 61.43 | 128.89 | 61.43 | 0 | 0 | 0 | 112.59 | 67.45 | 0
2025-06-11 10:00 | 64.59 | 129.16 | 64.59 | 0 | 0 | 0 | 112.59 | 64.57 | 0
2025-06-11 11:00 | 66.8 | 85.62 | 66.8 | 0 | 0 | 0 | 112.59 | 18.82 | 0
2025-06-11 12:00 | 68.44 | 65.97 | 65.97 | 0 | 0 | 2.46 | 110 | 0 | 0
2025-06-11 13:00 | 69.88 | 67.34 | 67.34 | 0 | 0 | 2.54 | 107.33 | 0 | 0
2025-06-11 14:00 | 70.98 | 47.51 | 47.51 | 0 | 0 | 23.47 | 82.63 | 0 | 0
2025-06-11 15:00 | 71.79 | 23.87 | 23.87 | 0 | 0 | 47.91 | 32.19 | 0 | 0
2025-06-11 16:00 | 71.34 | 17.39 | 17.39 | 35.26 | 0 | 18.7 | 12.51 | 0 | 0
2025-06-11 17:00 | 70.51 | 5.43 | 5.43 | 65.08 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 18:00 | 69.11 | 0.76 | 0.76 | 68.35 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 19:00 | 66.47 | 0 | 0 | 66.47 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 20:00 | 65.01 | 0 | 0 | 65.01 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 21:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 22:00 | 58.35 | 0 | 0 | 58.35 | 0 | 0 | 12.51 | 0 | 0
2025-06-11 23:00 | 55.99 | 0 | 0 | 55.99 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 | 52.73 | 0 | 0 | 52.73 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 01:00 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 04:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 05:00 | 52.21 | 23.48 | 23.48 | 28.73 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 06:00 | 53.46 | 71.72 | 71.72 | 0 | 18.25 | 0 | 29.85 | 0 | 0
2025-06-12 07:00 | 56.84 | 98.38 | 98.38 | 0 | 41.55 | 0 | 69.32 | 0 | 0
2025-06-12 08:00 | 61.06 | 106.83 | 106.6 | 0 | 45.54 | 0 | 112.59 | 0.23 | 0
2025-06-12 09:00 | 64.66 | 110.99 | 64.66 | 0 | 0 | 0 | 112.59 | 46.33 | 0
2025-06-12 10:00 | 70.06 | 115.39 | 70.06 | 0 | 0 | 0 | 112.59 | 45.33 | 0
2025-06-12 11:00 | 73.99 | 113.4 | 73.99 | 0 | 0 | 0 | 112.59 | 39.41 | 0
2025-06-12 12:00 | 78.35 | 113.32 | 78.35 | 0 | 0 | 0 | 112.59 | 34.97 | 0
2025-06-12 13:00 | 81.6 | 111.26 | 81.6 | 0 | 0 | 0 | 112.59 | 29.66 | 0
2025-06-12 14:00 | 84.38 | 111.27 | 84.38 | 0 | 0 | 0 | 112.59 | 26.89 | 0
2025-06-12 15:00 | 85.55 | 109.98 | 85.55 | 0 | 0 | 0 | 112.59 | 24.43 | 0
2025-06-12 16:00 | 84.12 | 108.16 | 84.12 | 0 | 0 | 0 | 112.59 | 24.05 | 0
2025-06-12 17:00 | 81.36 | 86.01 | 81.36 | 0 | 0 | 0 | 112.59 | 4.65 | 0
2025-06-12 18:00 | 78.04 | 60.74 | 60.74 | 0 | 0 | 17.3 | 94.38 | 0 | 0
2025-06-12 19:00 | 74.52 | 14.14 | 14.14 | 0 | 0 | 60.38 | 30.82 | 0 | 0
2025-06-12 20:00 | 70.54 | 0 | 0 | 53.15 | 0 | 17.39 | 12.51 | 0 | 0
2025-06-12 21:00 | 65.09 | 0 | 0 | 65.09 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 22:00 | 60.3 | 0 | 0 | 60.3 | 0 | 0 | 12.51 | 0 | 0
2025-06-12 23:00 | 57.07 | 0 | 0 | 57.07 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 01:00 | 51.3 | 0 | 0 | 51.3 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 02:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 03:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 04:00 | 48.96 | 0 | 0 | 48.96 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 05:00 | 51.89 | 22.46 | 22.46 | 29.43 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 06:00 | 53.23 | 19.46 | 19.46 | 33.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 07:00 | 55.75 | 53.32 | 53.32 | 2.44 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 08:00 | 59.61 | 23.47 | 23.47 | 36.14 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 09:00 | 61.3 | 63.45 | 63.45 | 0 | 2.15 | 0 | 14.55 | 0 | 0
2025-06-13 10:00 | 64.08 | 92.13 | 92.13 | 0 | 28.05 | 0 | 41.2 | 0 | 0
2025-06-13 11:00 | 66.81 | 86.6 | 86.6 | 0 | 19.79 | 0 | 60 | 0 | 0
2025-06-13 12:00 | 69.11 | 16.89 | 16.89 | 7.1 | 0 | 45.12 | 12.51 | 0 | 0
2025-06-13 13:00 | 70.18 | 76.48 | 76.48 | 0 | 6.31 | 0 | 18.5 | 0 | 0
2025-06-13 14:00 | 70.53 | 76.07 | 76.07 | 0 | 5.54 | 0 | 23.77 | 0 | 0
2025-06-13 15:00 | 71.19 | 41.92 | 41.92 | 18.58 | 0 | 10.69 | 12.51 | 0 | 0
2025-06-13 16:00 | 71.96 | 49.33 | 49.33 | 22.63 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 17:00 | 70.44 | 5.93 | 5.93 | 64.5 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 18:00 | 69.13 | 59.11 | 59.11 | 10.02 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 19:00 | 66.75 | 1.14 | 1.14 | 65.6 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 20:00 | 64.09 | 0 | 0 | 64.09 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 21:00 | 62.49 | 0 | 0 | 62.49 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 22:00 | 58.67 | 0 | 0 | 58.67 | 0 | 0 | 12.51 | 0 | 0
2025-06-13 23:00 | 55.74 | 0 | 0 | 55.74 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 01:00 | 51.26 | 0 | 0 | 51.26 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 02:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 03:00 | 49.88 | 0 | 0 | 49.88 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 04:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 05:00 | 51.75 | 27.39 | 27.39 | 24.35 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 06:00 | 54.77 | 65.14 | 65.14 | 0 | 10.36 | 0 | 22.36 | 0 | 0
2025-06-14 07:00 | 56.72 | 96.14 | 96.14 | 0 | 39.42 | 0 | 59.8 | 0 | 0
2025-06-14 08:00 | 58.76 | 86.57 | 86.57 | 0 | 27.8 | 0 | 86.22 | 0 | 0
2025-06-14 09:00 | 63.88 | 60.74 | 60.74 | 0 | 0 | 3.15 | 82.91 | 0 | 0
2025-06-14 10:00 | 67.64 | 71.66 | 71.66 | 0 | 4.02 | 0 | 86.73 | 0 | 0
2025-06-14 11:00 | 71.39 | 123.15 | 98.62 | 0 | 27.22 | 0 | 112.59 | 24.53 | 0
2025-06-14 12:00 | 74.8 | 104.69 | 74.8 | 0 | 0 | 0 | 112.59 | 29.89 | 0
2025-06-14 13:00 | 77.26 | 60.72 | 60.72 | 0 | 0 | 16.55 | 95.17 | 0 | 0
2025-06-14 14:00 | 78.91 | 63.53 | 63.53 | 0 | 0 | 15.38 | 78.99 | 0 | 0
2025-06-14 15:00 | 79.81 | 104.97 | 104.97 | 0 | 25.16 | 0 | 102.89 | 0 | 0
2025-06-14 16:00 | 78.66 | 122.41 | 88.88 | 0 | 10.22 | 0 | 112.59 | 33.53 | 0
2025-06-14 17:00 | 76.8 | 111.53 | 76.8 | 0 | 0 | 0 | 112.59 | 34.73 | 0
2025-06-14 18:00 | 76.19 | 85.52 | 76.19 | 0 | 0 | 0 | 112.59 | 9.32 | 0
2025-06-14 19:00 | 71.01 | 18.72 | 18.72 | 0 | 0 | 52.29 | 57.54 | 0 | 0
2025-06-14 20:00 | 67.67 | 0 | 0 | 24.89 | 0 | 42.78 | 12.51 | 0 | 0
2025-06-14 21:00 | 62.97 | 0 | 0 | 62.97 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 22:00 | 60.01 | 0 | 0 | 60.01 | 0 | 0 | 12.51 | 0 | 0
2025-06-14 23:00 | 56.09 | 0 | 0 | 56.09 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 | 53.43 | 0 | 0 | 53.43 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 01:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 03:00 | 50.24 | 0 | 0 | 50.24 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 04:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 05:00 | 52.59 | 24.19 | 24.19 | 28.4 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 06:00 | 53.06 | 47.97 | 47.97 | 5.09 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 07:00 | 56.93 | 94.91 | 94.91 | 0 | 37.99 | 0 | 48.6 | 0 | 0
2025-06-15 08:00 | 59.48 | 68.88 | 68.88 | 0 | 9.4 | 0 | 57.53 | 0 | 0
2025-06-15 09:00 | 62.13 | 105.04 | 105.04 | 0 | 42.91 | 0 | 98.29 | 0 | 0
2025-06-15 10:00 | 64.15 | 90.88 | 79.2 | 0 | 15.05 | 0 | 112.59 | 11.69 | 0
2025-06-15 11:00 | 67.07 | 103.41 | 67.07 | 0 | 0 | 0 | 112.59 | 36.34 | 0
2025-06-15 12:00 | 68.74 | 105.96 | 68.74 | 0 | 0 | 0 | 112.59 | 37.22 | 0
2025-06-15 13:00 | 70.45 | 112.26 | 70.45 | 0 | 0 | 0 | 112.59 | 41.81 | 0
2025-06-15 14:00 | 71.2 | 106.18 | 71.2 | 0 | 0 | 0 | 112.59 | 34.98 | 0
2025-06-15 15:00 | 70.6 | 81.22 | 70.6 | 0 | 0 | 0 | 112.59 | 10.62 | 0
2025-06-15 16:00 | 71.88 | 80.12 | 71.88 | 0 | 0 | 0 | 112.59 | 8.24 | 0
2025-06-15 17:00 | 70.39 | 67.17 | 67.17 | 0 | 0 | 3.22 | 109.2 | 0 | 0
2025-06-15 18:00 | 68.73 | 56.61 | 56.61 | 0 | 0 | 12.12 | 96.45 | 0 | 0
2025-06-15 19:00 | 66.71 | 20.37 | 20.37 | 0 | 0 | 46.34 | 47.67 | 0 | 0
2025-06-15 20:00 | 64.75 | 0 | 0 | 31.35 | 0 | 33.4 | 12.51 | 0 | 0
2025-06-15 21:00 | 61.39 | 0 | 0 | 61.39 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 22:00 | 57.84 | 0 | 0 | 57.84 | 0 | 0 | 12.51 | 0 | 0
2025-06-15 23:00 | 56.37 | 0 | 0 | 56.37 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 | 54.2 | 0 | 0 | 54.2 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 01:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 02:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 03:00 | 50.08 | 0 | 0 | 50.08 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 04:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 05:00 | 51.29 | 33.48 | 33.48 | 17.81 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 06:00 | 53.56 | 108.26 | 108.26 | 0 | 54.69 | 0 | 64.47 | 0 | 0
2025-06-16 07:00 | 57.23 | 128.84 | 107.88 | 0 | 50.65 | 0 | 112.59 | 20.96 | 0
2025-06-16 08:00 | 60.08 | 137.15 | 60.08 | 0 | 0 | 0 | 112.59 | 77.06 | 0
2025-06-16 09:00 | 63.9 | 134.32 | 63.9 | 0 | 0 | 0 | 112.59 | 70.42 | 0
2025-06-16 10:00 | 69.1 | 121.64 | 69.1 | 0 | 0 | 0 | 112.59 | 52.54 | 0
2025-06-16 11:00 | 72.15 | 99.58 | 72.15 | 0 | 0 | 0 | 112.59 | 27.43 | 0
2025-06-16 12:00 | 75.56 | 86.85 | 75.56 | 0 | 0 | 0 | 112.59 | 11.29 | 0
2025-06-16 13:00 | 77.89 | 81.28 | 77.89 | 0 | 0 | 0 | 112.59 | 3.39 | 0
2025-06-16 14:00 | 79.49 | 67.11 | 67.11 | 0 | 0 | 12.38 | 99.56 | 0 | 0
2025-06-16 15:00 | 79.28 | 38.57 | 38.57 | 0 | 0 | 40.72 | 56.7 | 0 | 0
2025-06-16 16:00 | 80.27 | 29.7 | 29.7 | 8.59 | 0 | 41.98 | 12.51 | 0 | 0
2025-06-16 17:00 | 78.3 | 16.19 | 16.19 | 62.11 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 18:00 | 75.3 | 7.39 | 7.39 | 67.91 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 19:00 | 71.91 | 0 | 0 | 71.9 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 20:00 | 68.49 | 0 | 0 | 68.49 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 21:00 | 63.34 | 0 | 0 | 63.34 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 22:00 | 59.97 | 0 | 0 | 59.97 | 0 | 0 | 12.51 | 0 | 0
2025-06-16 23:00 | 56.24 | 0 | 0 | 56.24 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 | 54.86 | 0 | 0 | 54.86 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 01:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 02:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 03:00 | 49.36 | 0 | 0 | 49.36 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 04:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 05:00 | 51.64 | 2.53 | 2.53 | 49.11 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 06:00 | 53.32 | 7.82 | 7.82 | 45.5 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 07:00 | 57.73 | 54.5 | 54.5 | 3.23 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 08:00 | 60.19 | 65.83 | 65.83 | 0 | 5.63 | 0 | 17.86 | 0 | 0
2025-06-17 09:00 | 63.86 | 91.73 | 91.73 | 0 | 27.88 | 0 | 44.35 | 0 | 0
2025-06-17 10:00 | 66.91 | 71.58 | 71.58 | 0 | 4.66 | 0 | 48.78 | 0 | 0
2025-06-17 11:00 | 71.07 | 61.89 | 61.89 | 0 | 0 | 9.18 | 39.11 | 0 | 0
2025-06-17 12:00 | 73.52 | 58.06 | 58.06 | 0 | 0 | 15.46 | 22.84 | 0 | 0
2025-06-17 13:00 | 75.9 | 36.21 | 36.21 | 29.87 | 0 | 9.81 | 12.51 | 0 | 0
2025-06-17 14:00 | 77.82 | 34.42 | 34.42 | 43.4 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 15:00 | 77.21 | 50.88 | 50.88 | 26.33 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 16:00 | 78.32 | 110.84 | 110.84 | 0 | 32.52 | 0 | 43.4 | 0 | 0
2025-06-17 17:00 | 76.13 | 58.92 | 58.92 | 0 | 0 | 17.21 | 25.29 | 0 | 0
2025-06-17 18:00 | 74.35 | 74.35 | 74.35 | 0 | 0 | 0 | 25.28 | 0 | 0
2025-06-17 19:00 | 70.17 | 20.47 | 20.47 | 37.56 | 0 | 12.14 | 12.51 | 0 | 0
2025-06-17 20:00 | 66.8 | 0 | 0 | 66.8 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 21:00 | 63.04 | 0 | 0 | 63.04 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 22:00 | 60.16 | 0 | 0 | 60.16 | 0 | 0 | 12.51 | 0 | 0
2025-06-17 23:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 | 53.79 | 0 | 0 | 53.79 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 01:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 02:00 | 50.01 | 0 | 0 | 50.01 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 03:00 | 50.17 | 0 | 0 | 50.17 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 04:00 | 50.41 | 0 | 0 | 50.41 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 05:00 | 51.61 | 24.19 | 24.19 | 27.42 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 06:00 | 54.79 | 82.69 | 82.69 | 0 | 27.9 | 0 | 39.01 | 0 | 0
2025-06-18 07:00 | 56.66 | 89.71 | 89.71 | 0 | 33.05 | 0 | 70.41 | 0 | 0
2025-06-18 08:00 | 60.44 | 76.48 | 76.48 | 0 | 16.03 | 0 | 85.64 | 0 | 0
2025-06-18 09:00 | 62.85 | 126.23 | 91.22 | 0 | 28.37 | 0 | 112.59 | 35.01 | 0
2025-06-18 10:00 | 66.52 | 114.39 | 66.52 | 0 | 0 | 0 | 112.59 | 47.87 | 0
2025-06-18 11:00 | 69.41 | 113.42 | 69.41 | 0 | 0 | 0 | 112.59 | 44 | 0
2025-06-18 12:00 | 71.18 | 91.99 | 71.18 | 0 | 0 | 0 | 112.59 | 20.82 | 0
2025-06-18 13:00 | 74.72 | 97.81 | 74.72 | 0 | 0 | 0 | 112.59 | 23.09 | 0
2025-06-18 14:00 | 75.18 | 74.44 | 74.44 | 0 | 0 | 0.74 | 111.82 | 0 | 0
2025-06-18 15:00 | 76.04 | 49.89 | 49.89 | 0 | 0 | 26.15 | 84.29 | 0 | 0
2025-06-18 16:00 | 74.87 | 35.37 | 35.37 | 0 | 0 | 39.5 | 42.71 | 0 | 0
2025-06-18 17:00 | 73.92 | 26.15 | 26.15 | 19.08 | 0 | 28.69 | 12.51 | 0 | 0
2025-06-18 18:00 | 71.6 | 1.53 | 1.53 | 70.07 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 19:00 | 70.06 | 0.26 | 0.26 | 69.8 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 20:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 21:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 22:00 | 60.49 | 0 | 0 | 60.49 | 0 | 0 | 12.51 | 0 | 0
2025-06-18 23:00 | 57.28 | 0 | 0 | 57.28 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 01:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 02:00 | 50.37 | 0 | 0 | 50.37 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 03:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 04:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 05:00 | 52.12 | 11.85 | 11.85 | 40.27 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 06:00 | 53.43 | 55.3 | 55.3 | 0 | 1.87 | 0 | 14.29 | 0 | 0
2025-06-19 07:00 | 56.74 | 90.86 | 90.86 | 0 | 34.11 | 0 | 46.69 | 0 | 0
2025-06-19 08:00 | 59.25 | 112.68 | 112.68 | 0 | 53.43 | 0 | 97.45 | 0 | 0
2025-06-19 09:00 | 63.36 | 113.8 | 79.29 | 0 | 15.94 | 0 | 112.59 | 34.5 | 0
2025-06-19 10:00 | 65.93 | 109.24 | 65.93 | 0 | 0 | 0 | 112.59 | 43.3 | 0
2025-06-19 11:00 | 70.17 | 103.82 | 70.17 | 0 | 0 | 0 | 112.59 | 33.65 | 0
2025-06-19 12:00 | 72.78 | 101.62 | 72.78 | 0 | 0 | 0 | 112.59 | 28.84 | 0
2025-06-19 13:00 | 75.61 | 103.29 | 75.61 | 0 | 0 | 0 | 112.59 | 27.68 | 0
2025-06-19 14:00 | 76.38 | 98.56 | 76.38 | 0 | 0 | 0 | 112.59 | 22.18 | 0
2025-06-19 15:00 | 76.19 | 90.87 | 76.19 | 0 | 0 | 0 | 112.59 | 14.68 | 0
2025-06-19 16:00 | 76.37 | 78.14 | 76.37 | 0 | 0 | 0 | 112.59 | 1.77 | 0
2025-06-19 17:00 | 73.96 | 54.17 | 54.17 | 0 | 0 | 19.79 | 91.76 | 0 | 0
2025-06-19 18:00 | 72.11 | 33.87 | 33.87 | 0 | 0 | 38.25 | 51.5 | 0 | 0
2025-06-19 19:00 | 70.07 | 8.45 | 8.45 | 24.59 | 0 | 37.04 | 12.51 | 0 | 0
2025-06-19 20:00 | 65.68 | 0 | 0 | 65.68 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 21:00 | 63.36 | 0 | 0 | 63.36 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 22:00 | 59.49 | 0 | 0 | 59.49 | 0 | 0 | 12.51 | 0 | 0
2025-06-19 23:00 | 56.89 | 0 | 0 | 56.89 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 | 53.61 | 0 | 0 | 53.61 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 01:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 02:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 03:00 | 51.05 | 0 | 0 | 51.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 04:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 05:00 | 51.72 | 25.01 | 25.01 | 26.71 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 06:00 | 54.03 | 81.65 | 81.65 | 0 | 27.63 | 0 | 38.76 | 0 | 0
2025-06-20 07:00 | 56.09 | 108.1 | 108.1 | 0 | 52.02 | 0 | 88.17 | 0 | 0
2025-06-20 08:00 | 59.91 | 120.57 | 85.62 | 0 | 25.7 | 0 | 112.59 | 34.95 | 0
2025-06-20 09:00 | 63.08 | 124.42 | 63.08 | 0 | 0 | 0 | 112.59 | 61.34 | 0
2025-06-20 10:00 | 66.98 | 124.96 | 66.98 | 0 | 0 | 0 | 112.59 | 57.98 | 0
2025-06-20 11:00 | 68.1 | 123.57 | 68.1 | 0 | 0 | 0 | 112.59 | 55.47 | 0
2025-06-20 12:00 | 70.5 | 122.57 | 70.5 | 0 | 0 | 0 | 112.59 | 52.07 | 0
2025-06-20 13:00 | 72 | 109.1 | 72 | 0 | 0 | 0 | 112.59 | 37.1 | 0
2025-06-20 14:00 | 73.42 | 42.5 | 42.5 | 0 | 0 | 30.92 | 80.04 | 0 | 0
2025-06-20 15:00 | 73.85 | 47.09 | 47.09 | 0 | 0 | 26.76 | 51.88 | 0 | 0
2025-06-20 16:00 | 73.29 | 41.03 | 41.03 | 0 | 0 | 32.25 | 17.93 | 0 | 0
2025-06-20 17:00 | 72.83 | 98.21 | 98.21 | 0 | 25.38 | 0 | 42.04 | 0 | 0
2025-06-20 18:00 | 70.32 | 74.96 | 74.96 | 0 | 4.64 | 0 | 46.44 | 0 | 0
2025-06-20 19:00 | 68.91 | 17.57 | 17.57 | 19.11 | 0 | 32.23 | 12.51 | 0 | 0
2025-06-20 20:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 21:00 | 62.77 | 0 | 0 | 62.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 22:00 | 59.55 | 0 | 0 | 59.55 | 0 | 0 | 12.51 | 0 | 0
2025-06-20 23:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 | 53.94 | 0 | 0 | 53.94 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 01:00 | 52.35 | 0 | 0 | 52.35 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 02:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 03:00 | 51.31 | 0 | 0 | 51.31 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 04:00 | 51.31 | 0 | 0 | 51.31 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 05:00 | 51.87 | 13.05 | 13.05 | 38.82 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 06:00 | 54.61 | 61.58 | 61.58 | 0 | 6.98 | 0 | 19.14 | 0 | 0
2025-06-21 07:00 | 57.31 | 96.5 | 96.5 | 0 | 39.18 | 0 | 56.36 | 0 | 0
2025-06-21 08:00 | 60.28 | 109.14 | 109.14 | 0 | 48.86 | 0 | 102.78 | 0 | 0
2025-06-21 09:00 | 64.59 | 119.79 | 74.93 | 0 | 10.33 | 0 | 112.59 | 44.86 | 0
2025-06-21 10:00 | 68.16 | 119.38 | 68.16 | 0 | 0 | 0 | 112.59 | 51.22 | 0
2025-06-21 11:00 | 71.62 | 109.79 | 71.62 | 0 | 0 | 0 | 112.59 | 38.17 | 0
2025-06-21 12:00 | 74.59 | 94.08 | 74.59 | 0 | 0 | 0 | 112.59 | 19.49 | 0
2025-06-21 13:00 | 77.24 | 106.55 | 77.24 | 0 | 0 | 0 | 112.59 | 29.31 | 0
2025-06-21 14:00 | 78.67 | 122.68 | 78.67 | 0 | 0 | 0 | 112.59 | 44.02 | 0
2025-06-21 15:00 | 79.11 | 126.38 | 79.11 | 0 | 0 | 0 | 112.59 | 47.27 | 0
2025-06-21 16:00 | 78.23 | 121.83 | 78.23 | 0 | 0 | 0 | 112.59 | 43.6 | 0
2025-06-21 17:00 | 77.87 | 110.23 | 77.87 | 0 | 0 | 0 | 112.59 | 32.36 | 0
2025-06-21 18:00 | 74.09 | 84.98 | 74.09 | 0 | 0 | 0 | 112.59 | 10.88 | 0
2025-06-21 19:00 | 71.73 | 20.53 | 20.53 | 0 | 0 | 51.2 | 58.7 | 0 | 0
2025-06-21 20:00 | 67.8 | 0 | 0 | 23.92 | 0 | 43.88 | 12.51 | 0 | 0
2025-06-21 21:00 | 65.1 | 0 | 0 | 65.1 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 22:00 | 60.09 | 0 | 0 | 60.09 | 0 | 0 | 12.51 | 0 | 0
2025-06-21 23:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 | 53.86 | 0 | 0 | 53.86 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 01:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 02:00 | 50.26 | 0 | 0 | 50.26 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 03:00 | 50.25 | 0 | 0 | 50.25 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 04:00 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 05:00 | 52.38 | 8.82 | 8.82 | 43.56 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 06:00 | 54.09 | 49.29 | 49.29 | 4.81 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 07:00 | 56.27 | 27.74 | 27.74 | 28.53 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 08:00 | 60.6 | 62.99 | 62.99 | 0 | 2.39 | 0 | 14.78 | 0 | 0
2025-06-22 09:00 | 62.61 | 92.17 | 92.17 | 0 | 29.56 | 0 | 42.87 | 0 | 0
2025-06-22 10:00 | 66.79 | 91.21 | 91.21 | 0 | 24.42 | 0 | 66.07 | 0 | 0
2025-06-22 11:00 | 68.89 | 97.39 | 97.39 | 0 | 28.5 | 0 | 93.14 | 0 | 0
2025-06-22 12:00 | 72.43 | 92.7 | 92.7 | 0 | 20.27 | 0 | 112.4 | 0 | 0
2025-06-22 13:00 | 73.81 | 96.58 | 74.01 | 0 | 0.2 | 0 | 112.59 | 22.57 | 0
2025-06-22 14:00 | 74.06 | 108.73 | 74.06 | 0 | 0 | 0 | 112.59 | 34.67 | 0
2025-06-22 15:00 | 74.48 | 79.6 | 74.48 | 0 | 0 | 0 | 112.59 | 5.12 | 0
2025-06-22 16:00 | 74.86 | 88.4 | 74.86 | 0 | 0 | 0 | 112.59 | 13.54 | 0
2025-06-22 17:00 | 73.31 | 63.14 | 63.14 | 0 | 0 | 10.17 | 101.89 | 0 | 0
2025-06-22 18:00 | 71.55 | 11.07 | 11.07 | 0 | 0 | 60.47 | 38.23 | 0 | 0
2025-06-22 19:00 | 69.87 | 2.67 | 2.67 | 42.77 | 0 | 24.44 | 12.51 | 0 | 0
2025-06-22 20:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 21:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 22:00 | 60.54 | 0 | 0 | 60.54 | 0 | 0 | 12.51 | 0 | 0
2025-06-22 23:00 | 57.41 | 0 | 0 | 57.41 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 | 54.27 | 0 | 0 | 54.27 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 01:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 02:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 03:00 | 50.03 | 0 | 0 | 50.03 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 04:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 05:00 | 52.25 | 8.74 | 8.74 | 43.52 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 06:00 | 54.38 | 39.08 | 39.08 | 15.3 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 07:00 | 57.39 | 57.81 | 57.81 | 0 | 0.42 | 0 | 12.91 | 0 | 0
2025-06-23 08:00 | 59.06 | 61.35 | 61.35 | 0 | 2.29 | 0 | 15.08 | 0 | 0
2025-06-23 09:00 | 62.33 | 74.41 | 74.41 | 0 | 12.08 | 0 | 26.56 | 0 | 0
2025-06-23 10:00 | 65.14 | 108.2 | 108.2 | 0 | 43.05 | 0 | 67.46 | 0 | 0
2025-06-23 11:00 | 66.94 | 115.94 | 114.44 | 0 | 47.51 | 0 | 112.59 | 1.49 | 0
2025-06-23 12:00 | 69.79 | 116.05 | 69.79 | 0 | 0 | 0 | 112.59 | 46.25 | 0
2025-06-23 13:00 | 70.82 | 99.38 | 70.82 | 0 | 0 | 0 | 112.59 | 28.56 | 0
2025-06-23 14:00 | 71.28 | 97.38 | 71.28 | 0 | 0 | 0 | 112.59 | 26.1 | 0
2025-06-23 15:00 | 72.29 | 92.9 | 72.29 | 0 | 0 | 0 | 112.59 | 20.61 | 0
2025-06-23 16:00 | 70.38 | 55.51 | 55.51 | 0 | 0 | 14.88 | 96.93 | 0 | 0
2025-06-23 17:00 | 70.36 | 50.25 | 50.25 | 0 | 0 | 20.11 | 75.76 | 0 | 0
2025-06-23 18:00 | 69.26 | 20.26 | 20.26 | 0 | 0 | 49 | 24.18 | 0 | 0
2025-06-23 19:00 | 66.83 | 6.24 | 6.24 | 49.5 | 0 | 11.08 | 12.51 | 0 | 0
2025-06-23 20:00 | 65.2 | 0 | 0 | 65.2 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 21:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 22:00 | 60 | 0 | 0 | 60 | 0 | 0 | 12.51 | 0 | 0
2025-06-23 23:00 | 57.4 | 0 | 0 | 57.4 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 01:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 02:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 03:00 | 50.91 | 0 | 0 | 50.91 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 04:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 05:00 | 51.05 | 21.29 | 21.29 | 29.76 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 06:00 | 55.04 | 73.65 | 73.65 | 0 | 18.61 | 0 | 30.19 | 0 | 0
2025-06-24 07:00 | 57.01 | 92.31 | 92.31 | 0 | 35.3 | 0 | 63.72 | 0 | 0
2025-06-24 08:00 | 59.31 | 102.51 | 102.51 | 0 | 43.2 | 0 | 104.77 | 0 | 0
2025-06-24 09:00 | 62.99 | 107.06 | 71.23 | 0 | 8.24 | 0 | 112.59 | 35.83 | 0
2025-06-24 10:00 | 64.73 | 103.39 | 64.73 | 0 | 0 | 0 | 112.59 | 38.66 | 0
2025-06-24 11:00 | 66.93 | 102.34 | 66.93 | 0 | 0 | 0 | 112.59 | 35.41 | 0
2025-06-24 12:00 | 69.21 | 103.38 | 69.21 | 0 | 0 | 0 | 112.59 | 34.17 | 0
2025-06-24 13:00 | 71.17 | 102.41 | 71.17 | 0 | 0 | 0 | 112.59 | 31.23 | 0
2025-06-24 14:00 | 71.84 | 106.34 | 71.84 | 0 | 0 | 0 | 112.59 | 34.5 | 0
2025-06-24 15:00 | 71.46 | 110.41 | 71.46 | 0 | 0 | 0 | 112.59 | 38.95 | 0
2025-06-24 16:00 | 71.26 | 96.48 | 71.26 | 0 | 0 | 0 | 112.59 | 25.22 | 0
2025-06-24 17:00 | 70.68 | 77.93 | 70.68 | 0 | 0 | 0 | 112.59 | 7.25 | 0
2025-06-24 18:00 | 68.4 | 64.02 | 64.02 | 0 | 0 | 4.38 | 107.98 | 0 | 0
2025-06-24 19:00 | 67.6 | 12.92 | 12.92 | 0 | 0 | 54.68 | 50.43 | 0 | 0
2025-06-24 20:00 | 64.7 | 0 | 0 | 28.68 | 0 | 36.02 | 12.51 | 0 | 0
2025-06-24 21:00 | 62.65 | 0 | 0 | 62.65 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 22:00 | 59.6 | 0 | 0 | 59.6 | 0 | 0 | 12.51 | 0 | 0
2025-06-24 23:00 | 57.2 | 0 | 0 | 57.2 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 | 54.71 | 0 | 0 | 54.71 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 01:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 02:00 | 51.24 | 0 | 0 | 51.24 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 03:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 04:00 | 51.37 | 0 | 0 | 51.37 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 05:00 | 52.44 | 2.55 | 2.55 | 49.9 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 06:00 | 55.47 | 9.48 | 9.48 | 45.99 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 07:00 | 57.63 | 22.43 | 22.43 | 35.19 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 08:00 | 61 | 30.7 | 30.7 | 30.3 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 09:00 | 64.88 | 36.5 | 36.5 | 28.38 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 10:00 | 68.14 | 38.23 | 38.23 | 29.91 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 11:00 | 70.9 | 40.85 | 40.85 | 30.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 12:00 | 73.06 | 59.97 | 59.97 | 13.08 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 13:00 | 76.3 | 55.71 | 55.71 | 20.58 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 14:00 | 78.34 | 45.82 | 45.82 | 32.52 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 15:00 | 78.27 | 82.1 | 82.1 | 0 | 3.83 | 0 | 16.15 | 0 | 0
2025-06-25 16:00 | 78.36 | 66 | 66 | 8.9 | 0 | 3.46 | 12.51 | 0 | 0
2025-06-25 17:00 | 76.61 | 70.2 | 70.2 | 6.41 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 18:00 | 74.92 | 80.9 | 80.9 | 0 | 5.98 | 0 | 18.19 | 0 | 0
2025-06-25 19:00 | 71.2 | 24.3 | 24.3 | 41.5 | 0 | 5.4 | 12.51 | 0 | 0
2025-06-25 20:00 | 68.2 | 0 | 0 | 68.2 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 21:00 | 64.61 | 0 | 0 | 64.61 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 22:00 | 61.53 | 0 | 0 | 61.53 | 0 | 0 | 12.51 | 0 | 0
2025-06-25 23:00 | 56.62 | 0 | 0 | 56.62 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 01:00 | 53.02 | 0 | 0 | 53.02 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 02:00 | 51.99 | 0 | 0 | 51.99 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 03:00 | 50.87 | 0 | 0 | 50.87 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 04:00 | 51.07 | 0 | 0 | 51.07 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 05:00 | 52.97 | 3.21 | 3.21 | 49.76 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 06:00 | 55.31 | 13.27 | 13.27 | 42.03 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 07:00 | 57.8 | 24.88 | 24.88 | 32.93 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 08:00 | 61.98 | 41.01 | 41.01 | 20.97 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 09:00 | 66.77 | 46.1 | 46.1 | 20.66 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 10:00 | 71.74 | 59.35 | 59.35 | 12.39 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 11:00 | 75.7 | 73.27 | 73.27 | 2.43 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 12:00 | 79.42 | 55.26 | 55.26 | 24.16 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 13:00 | 82.61 | 45.37 | 45.37 | 37.24 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 14:00 | 85 | 52.88 | 52.88 | 32.12 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 15:00 | 85.38 | 42.62 | 42.62 | 42.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 16:00 | 84.82 | 21.94 | 21.94 | 62.88 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 17:00 | 82.11 | 12.1 | 12.1 | 70.01 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 18:00 | 80.05 | 5.22 | 5.22 | 74.83 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 19:00 | 74.76 | 0 | 0 | 74.76 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 20:00 | 70.58 | 0 | 0 | 70.58 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 21:00 | 66.22 | 0 | 0 | 66.22 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 22:00 | 62.81 | 0 | 0 | 62.81 | 0 | 0 | 12.51 | 0 | 0
2025-06-26 23:00 | 57.77 | 0 | 0 | 57.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 | 54.46 | 0 | 0 | 54.46 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 01:00 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 02:00 | 52.1 | 0 | 0 | 52.1 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 03:00 | 49.41 | 0 | 0 | 49.41 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 04:00 | 50.77 | 0 | 0 | 50.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 05:00 | 54 | 30.67 | 30.67 | 23.32 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 06:00 | 55.09 | 89.48 | 89.48 | 0 | 34.39 | 0 | 45.18 | 0 | 0
2025-06-27 07:00 | 57.08 | 111.4 | 111.4 | 0 | 54.32 | 0 | 96.79 | 0 | 0
2025-06-27 08:00 | 60.94 | 119.75 | 77.58 | 0 | 16.64 | 0 | 112.59 | 42.18 | 0
2025-06-27 09:00 | 64.59 | 120.52 | 64.59 | 0 | 0 | 0 | 112.59 | 55.93 | 0
2025-06-27 10:00 | 68.6 | 120.22 | 68.6 | 0 | 0 | 0 | 112.59 | 51.62 | 0
2025-06-27 11:00 | 72.5 | 117.71 | 72.5 | 0 | 0 | 0 | 112.59 | 45.21 | 0
2025-06-27 12:00 | 74.71 | 115.41 | 74.71 | 0 | 0 | 0 | 112.59 | 40.7 | 0
2025-06-27 13:00 | 76.51 | 116.03 | 76.51 | 0 | 0 | 0 | 112.59 | 39.53 | 0
2025-06-27 14:00 | 78.6 | 116.62 | 78.6 | 0 | 0 | 0 | 112.59 | 38.03 | 0
2025-06-27 15:00 | 78.34 | 116.12 | 78.34 | 0 | 0 | 0 | 112.59 | 37.77 | 0
2025-06-27 16:00 | 77.69 | 113.85 | 77.69 | 0 | 0 | 0 | 112.59 | 36.16 | 0
2025-06-27 17:00 | 75.9 | 100.84 | 75.9 | 0 | 0 | 0 | 112.59 | 24.95 | 0
2025-06-27 18:00 | 73.73 | 78.94 | 73.73 | 0 | 0 | 0 | 112.59 | 5.21 | 0
2025-06-27 19:00 | 71.13 | 20.66 | 20.66 | 0 | 0 | 50.47 | 59.46 | 0 | 0
2025-06-27 20:00 | 67.59 | 0 | 0 | 22.98 | 0 | 44.6 | 12.51 | 0 | 0
2025-06-27 21:00 | 64.71 | 0 | 0 | 64.71 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 22:00 | 60.36 | 0 | 0 | 60.36 | 0 | 0 | 12.51 | 0 | 0
2025-06-27 23:00 | 56.06 | 0 | 0 | 56.06 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 | 54.32 | 0 | 0 | 54.32 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 01:00 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 02:00 | 51.03 | 0 | 0 | 51.03 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 03:00 | 51.63 | 0 | 0 | 51.63 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 04:00 | 51.03 | 0 | 0 | 51.03 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 05:00 | 53.13 | 33.71 | 33.71 | 19.42 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 06:00 | 54.83 | 86.86 | 86.86 | 0 | 32.03 | 0 | 42.94 | 0 | 0
2025-06-28 07:00 | 57.61 | 108.02 | 108.02 | 0 | 50.41 | 0 | 90.82 | 0 | 0
2025-06-28 08:00 | 60.45 | 113.88 | 83.36 | 0 | 22.91 | 0 | 112.59 | 30.52 | 0
2025-06-28 09:00 | 64.29 | 82.11 | 64.29 | 0 | 0 | 0 | 112.59 | 17.82 | 0
2025-06-28 10:00 | 67.37 | 11.75 | 11.75 | 0 | 0 | 55.62 | 54.04 | 0 | 0
2025-06-28 11:00 | 71.02 | 31.07 | 31.07 | 0.49 | 0 | 39.45 | 12.51 | 0 | 0
2025-06-28 12:00 | 73.53 | 48.46 | 48.46 | 25.08 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 13:00 | 75.26 | 55.63 | 55.63 | 19.63 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 14:00 | 77.53 | 104.32 | 104.32 | 0 | 26.79 | 0 | 37.96 | 0 | 0
2025-06-28 15:00 | 77.69 | 86.45 | 86.45 | 0 | 8.76 | 0 | 46.29 | 0 | 0
2025-06-28 16:00 | 76.81 | 122.89 | 122.89 | 0 | 46.09 | 0 | 90.07 | 0 | 0
2025-06-28 17:00 | 75.8 | 125.64 | 99.51 | 0 | 23.7 | 0 | 112.59 | 26.13 | 0
2025-06-28 18:00 | 73.61 | 103.5 | 73.61 | 0 | 0 | 0 | 112.59 | 29.89 | 0
2025-06-28 19:00 | 70.5 | 21.41 | 21.41 | 0 | 0 | 49.09 | 60.92 | 0 | 0
2025-06-28 20:00 | 67.79 | 0 | 0 | 21.8 | 0 | 45.99 | 12.51 | 0 | 0
2025-06-28 21:00 | 64.01 | 0 | 0 | 64.01 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 22:00 | 60.39 | 0 | 0 | 60.39 | 0 | 0 | 12.51 | 0 | 0
2025-06-28 23:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 | 54.77 | 0 | 0 | 54.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 01:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 02:00 | 51.05 | 0 | 0 | 51.05 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 03:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 04:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 05:00 | 53.41 | 30.43 | 30.43 | 22.99 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 06:00 | 55.35 | 91.12 | 91.12 | 0 | 35.77 | 0 | 46.49 | 0 | 0
2025-06-29 07:00 | 58.76 | 111.16 | 111.16 | 0 | 52.41 | 0 | 96.28 | 0 | 0
2025-06-29 08:00 | 60.83 | 120.18 | 78 | 0 | 17.17 | 0 | 112.59 | 42.18 | 0
2025-06-29 09:00 | 63.63 | 121.68 | 63.63 | 0 | 0 | 0 | 112.59 | 58.05 | 0
2025-06-29 10:00 | 68.42 | 119.62 | 68.42 | 0 | 0 | 0 | 112.59 | 51.2 | 0
2025-06-29 11:00 | 72.45 | 118.28 | 72.45 | 0 | 0 | 0 | 112.59 | 45.83 | 0
2025-06-29 12:00 | 75.3 | 116 | 75.3 | 0 | 0 | 0 | 112.59 | 40.7 | 0
2025-06-29 13:00 | 77.73 | 117.48 | 77.73 | 0 | 0 | 0 | 112.59 | 39.75 | 0
2025-06-29 14:00 | 79.75 | 118.1 | 79.75 | 0 | 0 | 0 | 112.59 | 38.35 | 0
2025-06-29 15:00 | 79.79 | 118.03 | 79.79 | 0 | 0 | 0 | 112.59 | 38.24 | 0
2025-06-29 16:00 | 79.48 | 113.45 | 79.48 | 0 | 0 | 0 | 112.59 | 33.97 | 0
2025-06-29 17:00 | 77.12 | 104.38 | 77.12 | 0 | 0 | 0 | 112.59 | 27.26 | 0
2025-06-29 18:00 | 74.68 | 84.08 | 74.68 | 0 | 0 | 0 | 112.59 | 9.4 | 0
2025-06-29 19:00 | 72.97 | 21.36 | 21.36 | 0 | 0 | 51.61 | 58.26 | 0 | 0
2025-06-29 20:00 | 68.7 | 0 | 0 | 25.23 | 0 | 43.47 | 12.51 | 0 | 0
2025-06-29 21:00 | 64.6 | 0 | 0 | 64.6 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 22:00 | 60.91 | 0 | 0 | 60.91 | 0 | 0 | 12.51 | 0 | 0
2025-06-29 23:00 | 57.51 | 0 | 0 | 57.51 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 | 54.77 | 0 | 0 | 54.77 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 01:00 | 52.2 | 0 | 0 | 52.2 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 02:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 03:00 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 04:00 | 51.15 | 0 | 0 | 51.15 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 05:00 | 53.4 | 24.92 | 24.92 | 28.48 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 06:00 | 55.27 | 87.22 | 87.22 | 0 | 31.95 | 0 | 42.86 | 0 | 0
2025-06-30 07:00 | 58.35 | 100.18 | 100.18 | 0 | 41.82 | 0 | 82.59 | 0 | 0
2025-06-30 08:00 | 61.63 | 119.41 | 93.21 | 0 | 31.58 | 0 | 112.59 | 26.2 | 0
2025-06-30 09:00 | 66.2 | 140.67 | 66.2 | 0 | 0 | 0 | 112.59 | 74.47 | 0
2025-06-30 10:00 | 70.92 | 133.34 | 70.92 | 0 | 0 | 0 | 112.59 | 62.42 | 0
2025-06-30 11:00 | 75.47 | 81.76 | 75.47 | 0 | 0 | 0 | 112.59 | 6.29 | 0
2025-06-30 12:00 | 78.96 | 79.1 | 78.96 | 0 | 0 | 0 | 112.59 | 0.14 | 0
2025-06-30 13:00 | 82.63 | 61.87 | 61.87 | 0 | 0 | 20.76 | 90.74 | 0 | 0
2025-06-30 14:00 | 84.08 | 70.99 | 70.99 | 0 | 0 | 13.09 | 76.96 | 0 | 0
2025-06-30 15:00 | 85.15 | 66.72 | 66.72 | 0 | 0 | 18.43 | 57.55 | 0 | 0
2025-06-30 16:00 | 83.83 | 56.76 | 56.76 | 0 | 0 | 27.07 | 29.06 | 0 | 0
2025-06-30 17:00 | 81.19 | 47.29 | 47.29 | 18.17 | 0 | 15.73 | 12.51 | 0 | 0
2025-06-30 18:00 | 79.14 | 20.78 | 20.78 | 58.37 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 19:00 | 75.47 | 5.22 | 5.22 | 70.25 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 20:00 | 71.03 | 0 | 0 | 71.03 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 21:00 | 66.47 | 0 | 0 | 66.47 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 22:00 | 61.82 | 0 | 0 | 61.82 | 0 | 0 | 12.51 | 0 | 0
2025-06-30 23:00 | 57.82 | 0 | 0 | 57.82 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 | 55.35 | 0 | 0 | 55.35 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 01:00 | 53.09 | 0 | 0 | 53.09 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 02:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 03:00 | 51.59 | 0 | 0 | 51.59 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 04:00 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 05:00 | 52.59 | 20.34 | 20.34 | 32.25 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 06:00 | 55.89 | 37.41 | 37.41 | 18.48 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 07:00 | 58.39 | 71.05 | 71.05 | 0 | 12.65 | 0 | 24.53 | 0 | 0
2025-07-01 08:00 | 61.17 | 89.48 | 89.48 | 0 | 28.31 | 0 | 51.43 | 0 | 0
2025-07-01 09:00 | 65.16 | 107.57 | 107.57 | 0 | 42.41 | 0 | 91.72 | 0 | 0
2025-07-01 10:00 | 68.8 | 108.89 | 90.77 | 0 | 21.97 | 0 | 112.59 | 18.12 | 0
2025-07-01 11:00 | 70.84 | 112.96 | 70.84 | 0 | 0 | 0 | 112.59 | 42.12 | 0
2025-07-01 12:00 | 74.78 | 102.5 | 74.78 | 0 | 0 | 0 | 112.59 | 27.72 | 0
2025-07-01 13:00 | 77.54 | 112.8 | 77.54 | 0 | 0 | 0 | 112.59 | 35.26 | 0
2025-07-01 14:00 | 78.86 | 114.77 | 78.86 | 0 | 0 | 0 | 112.59 | 35.91 | 0
2025-07-01 15:00 | 79.66 | 123.8 | 79.66 | 0 | 0 | 0 | 112.59 | 44.14 | 0
2025-07-01 16:00 | 79.6 | 124.96 | 79.6 | 0 | 0 | 0 | 112.59 | 45.36 | 0
2025-07-01 17:00 | 77.4 | 120.71 | 77.4 | 0 | 0 | 0 | 112.59 | 43.31 | 0
2025-07-01 18:00 | 74.7 | 100.34 | 74.7 | 0 | 0 | 0 | 112.59 | 25.63 | 0
2025-07-01 19:00 | 72.37 | 27.1 | 27.1 | 0 | 0 | 45.27 | 64.94 | 0 | 0
2025-07-01 20:00 | 68.56 | 0 | 0 | 18.75 | 0 | 49.81 | 12.51 | 0 | 0
2025-07-01 21:00 | 64.94 | 0 | 0 | 64.94 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 22:00 | 61.2 | 0 | 0 | 61.2 | 0 | 0 | 12.51 | 0 | 0
2025-07-01 23:00 | 59.08 | 0 | 0 | 59.08 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 | 53.95 | 0 | 0 | 53.95 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 01:00 | 52.72 | 0 | 0 | 52.72 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 02:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 03:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 04:00 | 52 | 0 | 0 | 52 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 05:00 | 53.33 | 30.42 | 30.42 | 22.9 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 06:00 | 55.05 | 96.84 | 96.84 | 0 | 41.79 | 0 | 52.21 | 0 | 0
2025-07-02 07:00 | 57.7 | 118.62 | 118.62 | 0 | 60.92 | 0 | 110.09 | 0 | 0
2025-07-02 08:00 | 60.94 | 128.52 | 63.57 | 0 | 2.63 | 0 | 112.59 | 64.95 | 0
2025-07-02 09:00 | 64.27 | 130.92 | 64.27 | 0 | 0 | 0 | 112.59 | 66.65 | 0
2025-07-02 10:00 | 67.55 | 130.13 | 67.55 | 0 | 0 | 0 | 112.59 | 62.58 | 0
2025-07-02 11:00 | 70.47 | 128.14 | 70.47 | 0 | 0 | 0 | 112.59 | 57.67 | 0
2025-07-02 12:00 | 73.2 | 96.02 | 73.2 | 0 | 0 | 0 | 112.59 | 22.82 | 0
2025-07-02 13:00 | 75.35 | 84.02 | 75.35 | 0 | 0 | 0 | 112.59 | 8.68 | 0
2025-07-02 14:00 | 75.53 | 123.56 | 75.53 | 0 | 0 | 0 | 112.59 | 48.02 | 0
2025-07-02 15:00 | 76.02 | 111.71 | 76.02 | 0 | 0 | 0 | 112.59 | 35.69 | 0
2025-07-02 16:00 | 75.27 | 124.52 | 75.27 | 0 | 0 | 0 | 112.59 | 49.25 | 0
2025-07-02 17:00 | 75.4 | 114.56 | 75.4 | 0 | 0 | 0 | 112.59 | 39.15 | 0
2025-07-02 18:00 | 73.2 | 83.57 | 73.2 | 0 | 0 | 0 | 112.59 | 10.37 | 0
2025-07-02 19:00 | 70.82 | 17.3 | 17.3 | 0 | 0 | 53.52 | 56.26 | 0 | 0
2025-07-02 20:00 | 66.87 | 0 | 0 | 25.31 | 0 | 41.56 | 12.51 | 0 | 0
2025-07-02 21:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 22:00 | 60.69 | 0 | 0 | 60.69 | 0 | 0 | 12.51 | 0 | 0
2025-07-02 23:00 | 57.92 | 0 | 0 | 57.92 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 | 55.72 | 0 | 0 | 55.72 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 01:00 | 52.51 | 0 | 0 | 52.51 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 02:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 04:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 05:00 | 53.16 | 26.82 | 26.82 | 26.33 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 06:00 | 56.09 | 87.85 | 87.85 | 0 | 31.75 | 0 | 42.68 | 0 | 0
2025-07-03 07:00 | 58.97 | 109.3 | 109.3 | 0 | 50.32 | 0 | 90.49 | 0 | 0
2025-07-03 08:00 | 62.29 | 118.65 | 85.56 | 0 | 23.27 | 0 | 112.59 | 33.09 | 0
2025-07-03 09:00 | 65.8 | 120.39 | 65.8 | 0 | 0 | 0 | 112.59 | 54.59 | 0
2025-07-03 10:00 | 71.19 | 120.48 | 71.19 | 0 | 0 | 0 | 112.59 | 49.29 | 0
2025-07-03 11:00 | 74.15 | 118.63 | 74.15 | 0 | 0 | 0 | 112.59 | 44.48 | 0
2025-07-03 12:00 | 79.46 | 116.22 | 79.46 | 0 | 0 | 0 | 112.59 | 36.76 | 0
2025-07-03 13:00 | 81.73 | 116.89 | 81.73 | 0 | 0 | 0 | 112.59 | 35.16 | 0
2025-07-03 14:00 | 82.21 | 118.15 | 82.21 | 0 | 0 | 0 | 112.59 | 35.94 | 0
2025-07-03 15:00 | 84.02 | 117.56 | 84.02 | 0 | 0 | 0 | 112.59 | 33.54 | 0
2025-07-03 16:00 | 83.86 | 114.26 | 83.86 | 0 | 0 | 0 | 112.59 | 30.4 | 0
2025-07-03 17:00 | 81.51 | 103.72 | 81.51 | 0 | 0 | 0 | 112.59 | 22.21 | 0
2025-07-03 18:00 | 79.02 | 82.43 | 79.02 | 0 | 0 | 0 | 112.59 | 3.41 | 0
2025-07-03 19:00 | 74.47 | 20.04 | 20.04 | 0 | 0 | 54.44 | 55.29 | 0 | 0
2025-07-03 20:00 | 70.01 | 0 | 0 | 29.37 | 0 | 40.64 | 12.51 | 0 | 0
2025-07-03 21:00 | 66.26 | 0 | 0 | 66.26 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 22:00 | 62.12 | 0 | 0 | 62.12 | 0 | 0 | 12.51 | 0 | 0
2025-07-03 23:00 | 58.2 | 0 | 0 | 58.2 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 | 55.89 | 0 | 0 | 55.89 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 01:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 02:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 04:00 | 50.87 | 0 | 0 | 50.87 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 05:00 | 52.38 | 21.79 | 21.79 | 30.6 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 06:00 | 55.28 | 75.2 | 75.2 | 0 | 19.92 | 0 | 31.44 | 0 | 0
2025-07-04 07:00 | 59.21 | 99.26 | 99.26 | 0 | 40.04 | 0 | 69.48 | 0 | 0
2025-07-04 08:00 | 62.01 | 110.72 | 107.39 | 0 | 45.38 | 0 | 112.59 | 3.33 | 0
2025-07-04 09:00 | 64.67 | 117.28 | 64.67 | 0 | 0 | 0 | 112.59 | 52.62 | 0
2025-07-04 10:00 | 67.86 | 117.04 | 67.86 | 0 | 0 | 0 | 112.59 | 49.17 | 0
2025-07-04 11:00 | 73.47 | 112.27 | 73.47 | 0 | 0 | 0 | 112.59 | 38.79 | 0
2025-07-04 12:00 | 76.27 | 111.41 | 76.27 | 0 | 0 | 0 | 112.59 | 35.14 | 0
2025-07-04 13:00 | 79.39 | 111.17 | 79.39 | 0 | 0 | 0 | 112.59 | 31.78 | 0
2025-07-04 14:00 | 79.96 | 110.18 | 79.96 | 0 | 0 | 0 | 112.59 | 30.21 | 0
2025-07-04 15:00 | 81.12 | 107.73 | 81.12 | 0 | 0 | 0 | 112.59 | 26.61 | 0
2025-07-04 16:00 | 80.83 | 102.02 | 80.83 | 0 | 0 | 0 | 112.59 | 21.19 | 0
2025-07-04 17:00 | 78.6 | 93.09 | 78.6 | 0 | 0 | 0 | 112.59 | 14.49 | 0
2025-07-04 18:00 | 76.11 | 64.7 | 64.7 | 0 | 0 | 11.41 | 100.58 | 0 | 0
2025-07-04 19:00 | 73.12 | 16.37 | 16.37 | 0 | 0 | 56.75 | 40.84 | 0 | 0
2025-07-04 20:00 | 69.69 | 0 | 0 | 42.78 | 0 | 26.91 | 12.51 | 0 | 0
2025-07-04 21:00 | 65.52 | 0 | 0 | 65.52 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 22:00 | 62.2 | 0 | 0 | 62.2 | 0 | 0 | 12.51 | 0 | 0
2025-07-04 23:00 | 57.99 | 0 | 0 | 57.99 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 | 54.78 | 0 | 0 | 54.78 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 01:00 | 54.1 | 0 | 0 | 54.1 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 02:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 03:00 | 50.94 | 0 | 0 | 50.94 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 04:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 05:00 | 53.15 | 1.6 | 1.6 | 51.55 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 06:00 | 55.25 | 38.61 | 38.61 | 16.64 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 07:00 | 58.62 | 39.13 | 39.13 | 19.49 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 08:00 | 62.52 | 38.64 | 38.64 | 23.89 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 09:00 | 67.08 | 57.27 | 57.27 | 9.81 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 10:00 | 70.51 | 75.94 | 75.94 | 0 | 5.43 | 0 | 17.67 | 0 | 0
2025-07-05 11:00 | 77.25 | 93.21 | 93.21 | 0 | 15.96 | 0 | 32.83 | 0 | 0
2025-07-05 12:00 | 80.37 | 105.11 | 105.11 | 0 | 24.73 | 0 | 56.33 | 0 | 0
2025-07-05 13:00 | 84.02 | 115.43 | 115.43 | 0 | 31.41 | 0 | 86.17 | 0 | 0
2025-07-05 14:00 | 85.16 | 67.77 | 67.77 | 0 | 0 | 17.39 | 67.86 | 0 | 0
2025-07-05 15:00 | 86.34 | 63.96 | 63.96 | 0 | 0 | 22.39 | 44.3 | 0 | 0
2025-07-05 16:00 | 85.51 | 81.43 | 81.43 | 0 | 0 | 4.09 | 40 | 0 | 0
2025-07-05 17:00 | 84.47 | 58.47 | 58.47 | 0 | 0 | 26 | 12.63 | 0 | 0
2025-07-05 18:00 | 80.15 | 3.54 | 3.54 | 76.49 | 0 | 0.12 | 12.51 | 0 | 0
2025-07-05 19:00 | 76.69 | 1.92 | 1.92 | 74.77 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 20:00 | 71.37 | 0 | 0 | 71.37 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 21:00 | 66.76 | 0 | 0 | 66.76 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 22:00 | 62.42 | 0 | 0 | 62.42 | 0 | 0 | 12.51 | 0 | 0
2025-07-05 23:00 | 59.27 | 0 | 0 | 59.27 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 01:00 | 52.47 | 0 | 0 | 52.47 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 02:00 | 50.77 | 0 | 0 | 50.77 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 03:00 | 50.72 | 0 | 0 | 50.72 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 04:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 05:00 | 52.33 | 24.8 | 24.8 | 27.52 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 06:00 | 54.99 | 91.6 | 91.6 | 0 | 36.61 | 0 | 47.29 | 0 | 0
2025-07-06 07:00 | 57.26 | 106.19 | 106.19 | 0 | 48.93 | 0 | 93.78 | 0 | 0
2025-07-06 08:00 | 61.17 | 109.66 | 80.98 | 0 | 19.8 | 0 | 112.59 | 28.68 | 0
2025-07-06 09:00 | 65.98 | 83.41 | 65.98 | 0 | 0 | 0 | 112.59 | 17.43 | 0
2025-07-06 10:00 | 69.3 | 62.04 | 62.04 | 0 | 0 | 7.27 | 104.94 | 0 | 0
2025-07-06 11:00 | 72.7 | 83.31 | 80.75 | 0 | 8.05 | 0 | 112.59 | 2.56 | 0
2025-07-06 12:00 | 75.13 | 55.54 | 55.54 | 0 | 0 | 19.59 | 91.97 | 0 | 0
2025-07-06 13:00 | 77.2 | 59.91 | 59.91 | 0 | 0 | 17.29 | 73.77 | 0 | 0
2025-07-06 14:00 | 78.87 | 86.98 | 86.98 | 0 | 8.11 | 0 | 81.48 | 0 | 0
2025-07-06 15:00 | 79.92 | 88.53 | 88.53 | 0 | 8.61 | 0 | 89.66 | 0 | 0
2025-07-06 16:00 | 79.87 | 79.43 | 79.43 | 0 | 0 | 0.44 | 89.19 | 0 | 0
2025-07-06 17:00 | 78.42 | 68.97 | 68.97 | 0 | 0 | 9.44 | 79.25 | 0 | 0
2025-07-06 18:00 | 75.94 | 61.51 | 61.51 | 0 | 0 | 14.44 | 64.05 | 0 | 0
2025-07-06 19:00 | 72.23 | 20.65 | 20.65 | 2.62 | 0 | 48.96 | 12.51 | 0 | 0
2025-07-06 20:00 | 69.12 | 0 | 0 | 69.12 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 21:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 22:00 | 61.58 | 0 | 0 | 61.58 | 0 | 0 | 12.51 | 0 | 0
2025-07-06 23:00 | 59.28 | 0 | 0 | 59.28 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 | 54.37 | 0 | 0 | 54.37 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 01:00 | 53.03 | 0 | 0 | 53.03 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 02:00 | 52.39 | 0 | 0 | 52.39 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 03:00 | 50.58 | 0 | 0 | 50.58 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 04:00 | 51.46 | 0 | 0 | 51.46 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 05:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 06:00 | 55.14 | 10.02 | 10.02 | 45.12 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 07:00 | 57.08 | 26.98 | 26.98 | 30.1 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 08:00 | 61.07 | 36.2 | 36.2 | 24.88 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 09:00 | 64.02 | 42.95 | 42.95 | 21.07 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 10:00 | 66.64 | 43.59 | 43.59 | 23.05 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 11:00 | 68.29 | 60.61 | 60.61 | 7.68 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 12:00 | 70.63 | 90.38 | 90.38 | 0 | 19.74 | 0 | 31.27 | 0 | 0
2025-07-07 13:00 | 71.48 | 122.54 | 122.54 | 0 | 51.07 | 0 | 79.78 | 0 | 0
2025-07-07 14:00 | 72.56 | 118.81 | 107.1 | 0 | 34.54 | 0 | 112.59 | 11.71 | 0
2025-07-07 15:00 | 74.07 | 109.64 | 74.07 | 0 | 0 | 0 | 112.59 | 35.57 | 0
2025-07-07 16:00 | 72.78 | 116.84 | 72.78 | 0 | 0 | 0 | 112.59 | 44.07 | 0
2025-07-07 17:00 | 71.33 | 50.87 | 50.87 | 0 | 0 | 20.46 | 91.06 | 0 | 0
2025-07-07 18:00 | 70.68 | 29.85 | 29.85 | 0 | 0 | 40.83 | 48.08 | 0 | 0
2025-07-07 19:00 | 68.05 | 11.12 | 11.12 | 23.14 | 0 | 33.79 | 12.51 | 0 | 0
2025-07-07 20:00 | 65.79 | 0 | 0 | 65.79 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 21:00 | 63.17 | 0 | 0 | 63.17 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 22:00 | 60.55 | 0 | 0 | 60.55 | 0 | 0 | 12.51 | 0 | 0
2025-07-07 23:00 | 58.35 | 0 | 0 | 58.35 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 | 55.57 | 0 | 0 | 55.57 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 01:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 02:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 03:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 04:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 05:00 | 52.87 | 20.87 | 20.87 | 32 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 06:00 | 55.14 | 82.04 | 82.04 | 0 | 26.9 | 0 | 38.06 | 0 | 0
2025-07-08 07:00 | 58.11 | 109.06 | 109.06 | 0 | 50.95 | 0 | 86.47 | 0 | 0
2025-07-08 08:00 | 60.56 | 121.36 | 88.06 | 0 | 27.5 | 0 | 112.59 | 33.31 | 0
2025-07-08 09:00 | 63.68 | 124.07 | 63.68 | 0 | 0 | 0 | 112.59 | 60.39 | 0
2025-07-08 10:00 | 66.97 | 119.53 | 66.97 | 0 | 0 | 0 | 112.59 | 52.56 | 0
2025-07-08 11:00 | 68.3 | 7.29 | 7.29 | 0 | 0 | 61.02 | 48.36 | 0 | 0
2025-07-08 12:00 | 70.73 | 93.7 | 93.7 | 0 | 22.98 | 0 | 70.19 | 0 | 0
2025-07-08 13:00 | 71.66 | 123.66 | 116.29 | 0 | 44.63 | 0 | 112.59 | 7.37 | 0
2025-07-08 14:00 | 71.38 | 6.52 | 6.52 | 2.36 | 0 | 62.5 | 46.8 | 0 | 0
2025-07-08 15:00 | 71.8 | 119.8 | 119.8 | 0 | 48 | 0 | 92.4 | 0 | 0
2025-07-08 16:00 | 71.7 | 120.51 | 92.95 | 0 | 21.25 | 0 | 112.59 | 27.56 | 0
2025-07-08 17:00 | 70.95 | 107.59 | 70.95 | 0 | 0 | 0 | 112.59 | 36.64 | 0
2025-07-08 18:00 | 70.09 | 80.46 | 70.09 | 0 | 0 | 0 | 112.59 | 10.37 | 0
2025-07-08 19:00 | 68.7 | 17.89 | 17.89 | 0 | 0 | 50.8 | 59.11 | 0 | 0
2025-07-08 20:00 | 66.8 | 0 | 0 | 22.53 | 0 | 44.27 | 12.51 | 0 | 0
2025-07-08 21:00 | 63.72 | 0 | 0 | 63.72 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 22:00 | 60.51 | 0 | 0 | 60.51 | 0 | 0 | 12.51 | 0 | 0
2025-07-08 23:00 | 56.85 | 0 | 0 | 56.85 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 | 55.69 | 0 | 0 | 55.69 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 01:00 | 53.3 | 0 | 0 | 53.3 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 03:00 | 52.44 | 0 | 0 | 52.44 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 04:00 | 52.48 | 0 | 0 | 52.48 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 05:00 | 53.68 | 10.75 | 10.75 | 42.93 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 06:00 | 55.17 | 64.79 | 64.79 | 0 | 9.61 | 0 | 21.64 | 0 | 0
2025-07-09 07:00 | 58.63 | 98.08 | 98.08 | 0 | 39.45 | 0 | 59.12 | 0 | 0
2025-07-09 08:00 | 62.82 | 90.46 | 90.46 | 0 | 27.64 | 0 | 85.38 | 0 | 0
2025-07-09 09:00 | 67.03 | 100.18 | 95.68 | 0 | 28.64 | 0 | 112.59 | 4.51 | 0
2025-07-09 10:00 | 72.5 | 119.47 | 72.5 | 0 | 0 | 0 | 112.59 | 46.97 | 0
2025-07-09 11:00 | 77.17 | 109.21 | 77.17 | 0 | 0 | 0 | 112.59 | 32.04 | 0
2025-07-09 12:00 | 80.72 | 102.1 | 80.72 | 0 | 0 | 0 | 112.59 | 21.38 | 0
2025-07-09 13:00 | 85.26 | 87.94 | 85.26 | 0 | 0 | 0 | 112.59 | 2.68 | 0
2025-07-09 14:00 | 86.9 | 76.35 | 76.35 | 0 | 0 | 10.55 | 101.48 | 0 | 0
2025-07-09 15:00 | 86.74 | 56.23 | 56.23 | 0 | 0 | 30.51 | 69.36 | 0 | 0
2025-07-09 16:00 | 86.83 | 56.84 | 56.84 | 0 | 0 | 29.98 | 37.8 | 0 | 0
2025-07-09 17:00 | 84.8 | 48.59 | 48.59 | 12.19 | 0 | 24.02 | 12.51 | 0 | 0
2025-07-09 18:00 | 81.75 | 12.03 | 12.03 | 69.72 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 19:00 | 76.83 | 1.01 | 1.01 | 75.81 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 20:00 | 72.66 | 0 | 0 | 72.66 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 21:00 | 67.52 | 0 | 0 | 67.52 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 22:00 | 62.22 | 0 | 0 | 62.22 | 0 | 0 | 12.51 | 0 | 0
2025-07-09 23:00 | 58.18 | 0 | 0 | 58.18 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 | 56.26 | 0 | 0 | 56.26 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 01:00 | 53.93 | 0 | 0 | 53.93 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 02:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 03:00 | 52.17 | 0 | 0 | 52.17 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 04:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 05:00 | 53.67 | 15.9 | 15.9 | 37.77 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 06:00 | 55.24 | 70.16 | 70.16 | 0 | 14.91 | 0 | 26.68 | 0 | 0
2025-07-10 07:00 | 59.82 | 97.88 | 97.88 | 0 | 38.05 | 0 | 62.83 | 0 | 0
2025-07-10 08:00 | 63.24 | 107.27 | 107.27 | 0 | 44.03 | 0 | 104.66 | 0 | 0
2025-07-10 09:00 | 67.38 | 105.47 | 75.73 | 0 | 8.35 | 0 | 112.59 | 29.74 | 0
2025-07-10 10:00 | 72.13 | 109.26 | 72.13 | 0 | 0 | 0 | 112.59 | 37.13 | 0
2025-07-10 11:00 | 77.41 | 108.47 | 77.41 | 0 | 0 | 0 | 112.59 | 31.06 | 0
2025-07-10 12:00 | 80.78 | 107.02 | 80.78 | 0 | 0 | 0 | 112.59 | 26.23 | 0
2025-07-10 13:00 | 85.42 | 108.99 | 85.42 | 0 | 0 | 0 | 112.59 | 23.57 | 0
2025-07-10 14:00 | 86.82 | 109.97 | 86.82 | 0 | 0 | 0 | 112.59 | 23.15 | 0
2025-07-10 15:00 | 88.26 | 109.52 | 88.26 | 0 | 0 | 0 | 112.59 | 21.26 | 0
2025-07-10 16:00 | 87.04 | 102.26 | 87.04 | 0 | 0 | 0 | 112.59 | 15.22 | 0
2025-07-10 17:00 | 84.94 | 81.87 | 81.87 | 0 | 0 | 3.07 | 109.36 | 0 | 0
2025-07-10 18:00 | 81.24 | 61 | 61 | 0 | 0 | 20.24 | 88.05 | 0 | 0
2025-07-10 19:00 | 77.2 | 15.27 | 15.27 | 0 | 0 | 61.93 | 22.86 | 0 | 0
2025-07-10 20:00 | 73.41 | 0 | 0 | 63.58 | 0 | 9.83 | 12.51 | 0 | 0
2025-07-10 21:00 | 68.27 | 0 | 0 | 68.27 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 22:00 | 63.15 | 0 | 0 | 63.15 | 0 | 0 | 12.51 | 0 | 0
2025-07-10 23:00 | 58.94 | 0 | 0 | 58.94 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 | 55.96 | 0 | 0 | 55.96 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 01:00 | 53.89 | 0 | 0 | 53.89 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 02:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 03:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 04:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 05:00 | 53.88 | 1.51 | 1.51 | 52.38 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 06:00 | 56.57 | 10.44 | 10.44 | 46.13 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 07:00 | 58.44 | 12.22 | 12.22 | 46.22 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 08:00 | 60.65 | 26.25 | 26.25 | 34.4 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 09:00 | 65.54 | 43.08 | 43.08 | 22.46 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 10:00 | 68.28 | 49.52 | 49.52 | 18.76 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 11:00 | 71.62 | 52.27 | 52.27 | 19.36 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 12:00 | 75.02 | 73.95 | 73.95 | 1.07 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 13:00 | 76.93 | 78.18 | 78.18 | 0 | 1.25 | 0 | 13.7 | 0 | 0
2025-07-11 14:00 | 77.87 | 53.67 | 53.67 | 23.08 | 0 | 1.13 | 12.51 | 0 | 0
2025-07-11 15:00 | 78.24 | 26.63 | 26.63 | 51.61 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 16:00 | 78.18 | 4.22 | 4.22 | 73.96 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 17:00 | 76.6 | 3.12 | 3.12 | 73.48 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 18:00 | 74.15 | 8.42 | 8.42 | 65.74 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 19:00 | 71.79 | 1.32 | 1.32 | 70.47 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 20:00 | 68.9 | 0 | 0 | 68.9 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 21:00 | 65.15 | 0 | 0 | 65.15 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 22:00 | 61 | 0 | 0 | 61 | 0 | 0 | 12.51 | 0 | 0
2025-07-11 23:00 | 58.89 | 0 | 0 | 58.89 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 | 54.18 | 0 | 0 | 54.18 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 01:00 | 53.13 | 0 | 0 | 53.13 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 02:00 | 51.65 | 0 | 0 | 51.65 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 03:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 04:00 | 52.24 | 0 | 0 | 52.24 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 05:00 | 53.91 | 18.4 | 18.4 | 35.51 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 06:00 | 55.19 | 77.63 | 77.63 | 0 | 22.44 | 0 | 33.83 | 0 | 0
2025-07-12 07:00 | 58.67 | 91.5 | 91.5 | 0 | 32.83 | 0 | 65.02 | 0 | 0
2025-07-12 08:00 | 61.71 | 105.15 | 105.15 | 0 | 43.44 | 0 | 106.29 | 0 | 0
2025-07-12 09:00 | 64.17 | 108.86 | 70.81 | 0 | 6.64 | 0 | 112.59 | 38.06 | 0
2025-07-12 10:00 | 69.33 | 111.08 | 69.33 | 0 | 0 | 0 | 112.59 | 41.75 | 0
2025-07-12 11:00 | 70.72 | 109.46 | 70.72 | 0 | 0 | 0 | 112.59 | 38.74 | 0
2025-07-12 12:00 | 74.23 | 106.16 | 74.23 | 0 | 0 | 0 | 112.59 | 31.93 | 0
2025-07-12 13:00 | 76.17 | 107.32 | 76.17 | 0 | 0 | 0 | 112.59 | 31.15 | 0
2025-07-12 14:00 | 77.33 | 108.22 | 77.33 | 0 | 0 | 0 | 112.59 | 30.88 | 0
2025-07-12 15:00 | 77.36 | 101.46 | 77.36 | 0 | 0 | 0 | 112.59 | 24.1 | 0
2025-07-12 16:00 | 77.61 | 96.32 | 77.61 | 0 | 0 | 0 | 112.59 | 18.71 | 0
2025-07-12 17:00 | 75.2 | 85.72 | 75.2 | 0 | 0 | 0 | 112.59 | 10.52 | 0
2025-07-12 18:00 | 73.99 | 75.41 | 73.99 | 0 | 0 | 0 | 112.59 | 1.42 | 0
2025-07-12 19:00 | 71.16 | 15.51 | 15.51 | 0 | 0 | 55.65 | 54.01 | 0 | 0
2025-07-12 20:00 | 68.04 | 0 | 0 | 28.61 | 0 | 39.43 | 12.51 | 0 | 0
2025-07-12 21:00 | 65.24 | 0 | 0 | 65.24 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 22:00 | 62.15 | 0 | 0 | 62.15 | 0 | 0 | 12.51 | 0 | 0
2025-07-12 23:00 | 58.2 | 0 | 0 | 58.2 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 | 56.17 | 0 | 0 | 56.17 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 01:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 02:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 03:00 | 51.38 | 0 | 0 | 51.38 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 04:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 05:00 | 53.08 | 17.9 | 17.9 | 35.18 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 06:00 | 56 | 81.16 | 81.16 | 0 | 25.16 | 0 | 36.41 | 0 | 0
2025-07-13 07:00 | 59.11 | 105.58 | 105.58 | 0 | 46.47 | 0 | 80.56 | 0 | 0
2025-07-13 08:00 | 62.14 | 115.26 | 95.85 | 0 | 33.71 | 0 | 112.59 | 19.41 | 0
2025-07-13 09:00 | 66.58 | 118.5 | 66.58 | 0 | 0 | 0 | 112.59 | 51.92 | 0
2025-07-13 10:00 | 72.34 | 118.46 | 72.34 | 0 | 0 | 0 | 112.59 | 46.12 | 0
2025-07-13 11:00 | 76.34 | 115.63 | 76.34 | 0 | 0 | 0 | 112.59 | 39.29 | 0
2025-07-13 12:00 | 81.03 | 114.14 | 81.03 | 0 | 0 | 0 | 112.59 | 33.11 | 0
2025-07-13 13:00 | 84.55 | 115.4 | 84.55 | 0 | 0 | 0 | 112.59 | 30.85 | 0
2025-07-13 14:00 | 85.64 | 115.11 | 85.64 | 0 | 0 | 0 | 112.59 | 29.47 | 0
2025-07-13 15:00 | 86.3 | 114.6 | 86.3 | 0 | 0 | 0 | 112.59 | 28.3 | 0
2025-07-13 16:00 | 87.11 | 109.53 | 87.11 | 0 | 0 | 0 | 112.59 | 22.42 | 0
2025-07-13 17:00 | 84.34 | 94.03 | 84.34 | 0 | 0 | 0 | 112.59 | 9.69 | 0
2025-07-13 18:00 | 80.67 | 68.65 | 68.65 | 0 | 0 | 12.02 | 99.94 | 0 | 0
2025-07-13 19:00 | 76.28 | 13.55 | 13.55 | 0.23 | 0 | 62.5 | 34.15 | 0 | 0
2025-07-13 20:00 | 71.87 | 0 | 0 | 51.31 | 0 | 20.56 | 12.51 | 0 | 0
2025-07-13 21:00 | 66.81 | 0 | 0 | 66.81 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 22:00 | 63.38 | 0 | 0 | 63.38 | 0 | 0 | 12.51 | 0 | 0
2025-07-13 23:00 | 58.61 | 0 | 0 | 58.61 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 01:00 | 53.19 | 0 | 0 | 53.19 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 02:00 | 51.49 | 0 | 0 | 51.49 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 03:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 04:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 05:00 | 53.33 | 17.51 | 17.51 | 35.82 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 06:00 | 55.45 | 76.77 | 76.77 | 0 | 21.32 | 0 | 32.77 | 0 | 0
2025-07-14 07:00 | 58.63 | 95.94 | 95.94 | 0 | 37.31 | 0 | 68.21 | 0 | 0
2025-07-14 08:00 | 60.25 | 107.74 | 106.96 | 0 | 46.71 | 0 | 112.59 | 0.78 | 0
2025-07-14 09:00 | 64.78 | 112.55 | 64.78 | 0 | 0 | 0 | 112.59 | 47.77 | 0
2025-07-14 10:00 | 67.43 | 114.01 | 67.43 | 0 | 0 | 0 | 112.59 | 46.58 | 0
2025-07-14 11:00 | 70.11 | 112.24 | 70.11 | 0 | 0 | 0 | 112.59 | 42.13 | 0
2025-07-14 12:00 | 71.44 | 112.96 | 71.44 | 0 | 0 | 0 | 112.59 | 41.53 | 0
2025-07-14 13:00 | 73.41 | 114.59 | 73.41 | 0 | 0 | 0 | 112.59 | 41.18 | 0
2025-07-14 14:00 | 73.04 | 118.09 | 73.04 | 0 | 0 | 0 | 112.59 | 45.05 | 0
2025-07-14 15:00 | 74.42 | 120.46 | 74.42 | 0 | 0 | 0 | 112.59 | 46.04 | 0
2025-07-14 16:00 | 73.39 | 117.68 | 73.39 | 0 | 0 | 0 | 112.59 | 44.29 | 0
2025-07-14 17:00 | 72.08 | 109.92 | 72.08 | 0 | 0 | 0 | 112.59 | 37.84 | 0
2025-07-14 18:00 | 70.9 | 91.74 | 70.9 | 0 | 0 | 0 | 112.59 | 20.84 | 0
2025-07-14 19:00 | 69.49 | 19.59 | 19.59 | 0 | 0 | 49.89 | 60.07 | 0 | 0
2025-07-14 20:00 | 66.61 | 0 | 0 | 21.43 | 0 | 45.18 | 12.51 | 0 | 0
2025-07-14 21:00 | 64.39 | 0 | 0 | 64.39 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 22:00 | 60.29 | 0 | 0 | 60.29 | 0 | 0 | 12.51 | 0 | 0
2025-07-14 23:00 | 57.15 | 0 | 0 | 57.15 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 | 56.27 | 0 | 0 | 56.27 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 01:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 02:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 03:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 04:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 05:00 | 53.63 | 15.52 | 15.52 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 06:00 | 55.66 | 76.23 | 76.23 | 0 | 20.57 | 0 | 32.05 | 0 | 0
2025-07-15 07:00 | 58.86 | 99.21 | 99.21 | 0 | 40.35 | 0 | 70.38 | 0 | 0
2025-07-15 08:00 | 61.01 | 112.53 | 105.44 | 0 | 44.43 | 0 | 112.59 | 7.09 | 0
2025-07-15 09:00 | 64.52 | 115.29 | 64.52 | 0 | 0 | 0 | 112.59 | 50.77 | 0
2025-07-15 10:00 | 67.48 | 116.91 | 67.48 | 0 | 0 | 0 | 112.59 | 49.43 | 0
2025-07-15 11:00 | 70 | 116.37 | 70 | 0 | 0 | 0 | 112.59 | 46.37 | 0
2025-07-15 12:00 | 72.1 | 115.64 | 72.1 | 0 | 0 | 0 | 112.59 | 43.54 | 0
2025-07-15 13:00 | 73.93 | 116.96 | 73.93 | 0 | 0 | 0 | 112.59 | 43.03 | 0
2025-07-15 14:00 | 74.88 | 116.46 | 74.88 | 0 | 0 | 0 | 112.59 | 41.58 | 0
2025-07-15 15:00 | 74.67 | 115.88 | 74.67 | 0 | 0 | 0 | 112.59 | 41.21 | 0
2025-07-15 16:00 | 75.27 | 110.2 | 75.27 | 0 | 0 | 0 | 112.59 | 34.94 | 0
2025-07-15 17:00 | 73.4 | 95.62 | 73.4 | 0 | 0 | 0 | 112.59 | 22.21 | 0
2025-07-15 18:00 | 72.19 | 75.88 | 72.19 | 0 | 0 | 0 | 112.59 | 3.69 | 0
2025-07-15 19:00 | 69.99 | 14.69 | 14.69 | 0 | 0 | 55.3 | 54.38 | 0 | 0
2025-07-15 20:00 | 67.67 | 0 | 0 | 27.89 | 0 | 39.78 | 12.51 | 0 | 0
2025-07-15 21:00 | 63.45 | 0 | 0 | 63.45 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 22:00 | 61.82 | 0 | 0 | 61.82 | 0 | 0 | 12.51 | 0 | 0
2025-07-15 23:00 | 57.98 | 0 | 0 | 57.98 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 | 56.39 | 0 | 0 | 56.39 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 01:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 02:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 03:00 | 52.53 | 0 | 0 | 52.53 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 04:00 | 51.92 | 0 | 0 | 51.92 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 05:00 | 54.1 | 10.09 | 10.09 | 44.01 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 06:00 | 55.8 | 22 | 22 | 33.8 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 07:00 | 59.04 | 37.18 | 37.18 | 21.86 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 08:00 | 62.51 | 70.97 | 70.97 | 0 | 8.46 | 0 | 20.54 | 0 | 0
2025-07-16 09:00 | 66.92 | 122.33 | 122.33 | 0 | 55.41 | 0 | 73.19 | 0 | 0
2025-07-16 10:00 | 70.28 | 89 | 89 | 0 | 18.72 | 0 | 90.97 | 0 | 0
2025-07-16 11:00 | 74.08 | 96.06 | 96.06 | 0 | 21.98 | 0 | 111.86 | 0 | 0
2025-07-16 12:00 | 77.71 | 101.3 | 78.48 | 0 | 0.77 | 0 | 112.59 | 22.82 | 0
2025-07-16 13:00 | 80.78 | 104.37 | 80.78 | 0 | 0 | 0 | 112.59 | 23.59 | 0
2025-07-16 14:00 | 82.34 | 85.66 | 82.34 | 0 | 0 | 0 | 112.59 | 3.32 | 0
2025-07-16 15:00 | 83.4 | 83.84 | 83.4 | 0 | 0 | 0 | 112.59 | 0.43 | 0
2025-07-16 16:00 | 83.11 | 64.15 | 64.15 | 0 | 0 | 18.95 | 92.64 | 0 | 0
2025-07-16 17:00 | 80.25 | 15.72 | 15.72 | 2.03 | 0 | 62.5 | 26.85 | 0 | 0
2025-07-16 18:00 | 77.66 | 10.6 | 10.6 | 53.44 | 0 | 13.62 | 12.51 | 0 | 0
2025-07-16 19:00 | 73.85 | 1.34 | 1.34 | 72.51 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 20:00 | 71.64 | 0 | 0 | 71.64 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 21:00 | 66.65 | 0 | 0 | 66.65 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 22:00 | 62.72 | 0 | 0 | 62.72 | 0 | 0 | 12.51 | 0 | 0
2025-07-16 23:00 | 58.16 | 0 | 0 | 58.16 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 | 55.69 | 0 | 0 | 55.69 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 01:00 | 53.73 | 0 | 0 | 53.73 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 03:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 04:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 05:00 | 53 | 10.28 | 10.28 | 42.73 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 06:00 | 55.18 | 48.68 | 48.68 | 6.5 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 07:00 | 58.09 | 89.81 | 89.81 | 0 | 31.72 | 0 | 42.65 | 0 | 0
2025-07-17 08:00 | 62.59 | 79.56 | 79.56 | 0 | 16.97 | 0 | 58.77 | 0 | 0
2025-07-17 09:00 | 65.73 | 96.06 | 96.06 | 0 | 30.33 | 0 | 87.59 | 0 | 0
2025-07-17 10:00 | 68.5 | 101.09 | 94.82 | 0 | 26.32 | 0 | 112.59 | 6.27 | 0
2025-07-17 11:00 | 71.66 | 109.39 | 71.66 | 0 | 0 | 0 | 112.59 | 37.73 | 0
2025-07-17 12:00 | 73.82 | 96.28 | 73.82 | 0 | 0 | 0 | 112.59 | 22.45 | 0
2025-07-17 13:00 | 76.63 | 97.83 | 76.63 | 0 | 0 | 0 | 112.59 | 21.2 | 0
2025-07-17 14:00 | 77.22 | 101.76 | 77.22 | 0 | 0 | 0 | 112.59 | 24.54 | 0
2025-07-17 15:00 | 77.69 | 88.57 | 77.69 | 0 | 0 | 0 | 112.59 | 10.88 | 0
2025-07-17 16:00 | 77.71 | 91 | 77.71 | 0 | 0 | 0 | 112.59 | 13.29 | 0
2025-07-17 17:00 | 76.1 | 86.47 | 76.1 | 0 | 0 | 0 | 112.59 | 10.37 | 0
2025-07-17 18:00 | 74.11 | 76.18 | 74.11 | 0 | 0 | 0 | 112.59 | 2.07 | 0
2025-07-17 19:00 | 71.65 | 11.17 | 11.17 | 0 | 0 | 60.48 | 48.93 | 0 | 0
2025-07-17 20:00 | 68.97 | 0 | 0 | 34.37 | 0 | 34.6 | 12.51 | 0 | 0
2025-07-17 21:00 | 66.03 | 0 | 0 | 66.03 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 22:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 12.51 | 0 | 0
2025-07-17 23:00 | 58.93 | 0 | 0 | 58.93 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 | 55.65 | 0 | 0 | 55.65 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 01:00 | 53.15 | 0 | 0 | 53.15 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 02:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 03:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 04:00 | 51.38 | 0 | 0 | 51.38 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 05:00 | 53.34 | 12.91 | 12.91 | 40.43 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 06:00 | 55.71 | 76.14 | 76.14 | 0 | 20.43 | 0 | 31.92 | 0 | 0
2025-07-18 07:00 | 58.42 | 97.39 | 97.39 | 0 | 38.97 | 0 | 68.94 | 0 | 0
2025-07-18 08:00 | 62.82 | 110.96 | 108.77 | 0 | 45.95 | 0 | 112.59 | 2.19 | 0
2025-07-18 09:00 | 65.97 | 113.72 | 65.97 | 0 | 0 | 0 | 112.59 | 47.74 | 0
2025-07-18 10:00 | 70.07 | 114.14 | 70.07 | 0 | 0 | 0 | 112.59 | 44.07 | 0
2025-07-18 11:00 | 72.92 | 114.88 | 72.92 | 0 | 0 | 0 | 112.59 | 41.96 | 0
2025-07-18 12:00 | 75.75 | 112.98 | 75.75 | 0 | 0 | 0 | 112.59 | 37.23 | 0
2025-07-18 13:00 | 77.48 | 115.3 | 77.48 | 0 | 0 | 0 | 112.59 | 37.81 | 0
2025-07-18 14:00 | 79.37 | 115.89 | 79.37 | 0 | 0 | 0 | 112.59 | 36.52 | 0
2025-07-18 15:00 | 79.85 | 114.02 | 79.85 | 0 | 0 | 0 | 112.59 | 34.17 | 0
2025-07-18 16:00 | 78.68 | 107.69 | 78.68 | 0 | 0 | 0 | 112.59 | 29.02 | 0
2025-07-18 17:00 | 77.68 | 94.82 | 77.68 | 0 | 0 | 0 | 112.59 | 17.13 | 0
2025-07-18 18:00 | 75.55 | 68.09 | 68.09 | 0 | 0 | 7.46 | 104.74 | 0 | 0
2025-07-18 19:00 | 73 | 11.85 | 11.85 | 0 | 0 | 61.15 | 40.37 | 0 | 0
2025-07-18 20:00 | 69.62 | 0 | 0 | 43.15 | 0 | 26.47 | 12.51 | 0 | 0
2025-07-18 21:00 | 65.44 | 0 | 0 | 65.44 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 22:00 | 62.31 | 0 | 0 | 62.31 | 0 | 0 | 12.51 | 0 | 0
2025-07-18 23:00 | 58.58 | 0 | 0 | 58.58 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 | 54.32 | 0 | 0 | 54.32 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 01:00 | 53.27 | 0 | 0 | 53.27 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 02:00 | 52.65 | 0 | 0 | 52.65 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 03:00 | 50.79 | 0 | 0 | 50.79 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 04:00 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 05:00 | 54.31 | 11.78 | 11.78 | 42.53 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 06:00 | 55.37 | 72.05 | 72.05 | 0 | 16.68 | 0 | 28.35 | 0 | 0
2025-07-19 07:00 | 58.64 | 97.88 | 97.88 | 0 | 39.24 | 0 | 65.63 | 0 | 0
2025-07-19 08:00 | 61.34 | 111.66 | 110.77 | 0 | 49.43 | 0 | 112.59 | 0.89 | 0
2025-07-19 09:00 | 66.37 | 117.26 | 66.37 | 0 | 0 | 0 | 112.59 | 50.89 | 0
2025-07-19 10:00 | 69.05 | 117.77 | 69.05 | 0 | 0 | 0 | 112.59 | 48.72 | 0
2025-07-19 11:00 | 72.39 | 115.41 | 72.39 | 0 | 0 | 0 | 112.59 | 43.02 | 0
2025-07-19 12:00 | 75.83 | 116.32 | 75.83 | 0 | 0 | 0 | 112.59 | 40.49 | 0
2025-07-19 13:00 | 77.61 | 116.04 | 77.61 | 0 | 0 | 0 | 112.59 | 38.43 | 0
2025-07-19 14:00 | 78.18 | 116.36 | 78.18 | 0 | 0 | 0 | 112.59 | 38.18 | 0
2025-07-19 15:00 | 78.75 | 116.51 | 78.75 | 0 | 0 | 0 | 112.59 | 37.77 | 0
2025-07-19 16:00 | 78.86 | 113.79 | 78.86 | 0 | 0 | 0 | 112.59 | 34.93 | 0
2025-07-19 17:00 | 76.97 | 103.88 | 76.97 | 0 | 0 | 0 | 112.59 | 26.9 | 0
2025-07-19 18:00 | 74.1 | 77.99 | 74.1 | 0 | 0 | 0 | 112.59 | 3.9 | 0
2025-07-19 19:00 | 72.34 | 12.55 | 12.55 | 0 | 0 | 59.79 | 49.66 | 0 | 0
2025-07-19 20:00 | 68.35 | 0 | 0 | 33.07 | 0 | 35.29 | 12.51 | 0 | 0
2025-07-19 21:00 | 66.37 | 0 | 0 | 66.37 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 22:00 | 62.08 | 0 | 0 | 62.08 | 0 | 0 | 12.51 | 0 | 0
2025-07-19 23:00 | 58.19 | 0 | 0 | 58.19 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 | 55.47 | 0 | 0 | 55.47 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 01:00 | 52.6 | 0 | 0 | 52.6 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 02:00 | 51.57 | 0 | 0 | 51.57 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 03:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 04:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 05:00 | 53.9 | 12.13 | 12.13 | 41.78 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 06:00 | 55.77 | 76.65 | 76.65 | 0 | 20.88 | 0 | 32.34 | 0 | 0
2025-07-20 07:00 | 58.6 | 101.3 | 101.3 | 0 | 42.7 | 0 | 72.91 | 0 | 0
2025-07-20 08:00 | 61.88 | 114.14 | 103.65 | 0 | 41.77 | 0 | 112.59 | 10.49 | 0
2025-07-20 09:00 | 67.24 | 116.53 | 67.24 | 0 | 0 | 0 | 112.59 | 49.29 | 0
2025-07-20 10:00 | 70.03 | 116.92 | 70.03 | 0 | 0 | 0 | 112.59 | 46.89 | 0
2025-07-20 11:00 | 74.88 | 114.67 | 74.88 | 0 | 0 | 0 | 112.59 | 39.78 | 0
2025-07-20 12:00 | 77.74 | 113.78 | 77.74 | 0 | 0 | 0 | 112.59 | 36.04 | 0
2025-07-20 13:00 | 78.66 | 114.47 | 78.66 | 0 | 0 | 0 | 112.59 | 35.81 | 0
2025-07-20 14:00 | 80.78 | 115.82 | 80.78 | 0 | 0 | 0 | 112.59 | 35.04 | 0
2025-07-20 15:00 | 81.32 | 114.5 | 81.32 | 0 | 0 | 0 | 112.59 | 33.19 | 0
2025-07-20 16:00 | 81.07 | 110.93 | 81.07 | 0 | 0 | 0 | 112.59 | 29.85 | 0
2025-07-20 17:00 | 79.5 | 97.36 | 79.5 | 0 | 0 | 0 | 112.59 | 17.85 | 0
2025-07-20 18:00 | 78.54 | 70.65 | 70.65 | 0 | 0 | 7.89 | 104.29 | 0 | 0
2025-07-20 19:00 | 73.29 | 11.16 | 11.16 | 0 | 0 | 62.12 | 38.89 | 0 | 0
2025-07-20 20:00 | 70.24 | 0 | 0 | 45.18 | 0 | 25.06 | 12.51 | 0 | 0
2025-07-20 21:00 | 66.52 | 0 | 0 | 66.52 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 22:00 | 62.36 | 0 | 0 | 62.36 | 0 | 0 | 12.51 | 0 | 0
2025-07-20 23:00 | 58.88 | 0 | 0 | 58.88 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 01:00 | 53.63 | 0 | 0 | 53.63 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 02:00 | 52.39 | 0 | 0 | 52.39 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 03:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 04:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 05:00 | 54.28 | 10.48 | 10.48 | 43.8 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 06:00 | 56.42 | 66.4 | 66.4 | 0 | 9.98 | 0 | 22 | 0 | 0
2025-07-21 07:00 | 59.21 | 90.83 | 90.83 | 0 | 31.62 | 0 | 52.04 | 0 | 0
2025-07-21 08:00 | 62.54 | 107.84 | 107.84 | 0 | 45.3 | 0 | 95.07 | 0 | 0
2025-07-21 09:00 | 67.3 | 110.26 | 85.74 | 0 | 18.44 | 0 | 112.59 | 24.52 | 0
2025-07-21 10:00 | 72.2 | 114.16 | 72.2 | 0 | 0 | 0 | 112.59 | 41.96 | 0
2025-07-21 11:00 | 77.04 | 111.88 | 77.04 | 0 | 0 | 0 | 112.59 | 34.85 | 0
2025-07-21 12:00 | 80.8 | 111.03 | 80.8 | 0 | 0 | 0 | 112.59 | 30.23 | 0
2025-07-21 13:00 | 83.84 | 111.56 | 83.84 | 0 | 0 | 0 | 112.59 | 27.72 | 0
2025-07-21 14:00 | 85.81 | 109.78 | 85.81 | 0 | 0 | 0 | 112.59 | 23.98 | 0
2025-07-21 15:00 | 86.3 | 105.19 | 86.3 | 0 | 0 | 0 | 112.59 | 18.88 | 0
2025-07-21 16:00 | 86.29 | 97.47 | 86.29 | 0 | 0 | 0 | 112.59 | 11.18 | 0
2025-07-21 17:00 | 83.57 | 81.36 | 81.36 | 0 | 0 | 2.21 | 110.27 | 0 | 0
2025-07-21 18:00 | 80.54 | 58.34 | 58.34 | 0 | 0 | 22.19 | 86.9 | 0 | 0
2025-07-21 19:00 | 76.72 | 9.35 | 9.35 | 4.87 | 0 | 62.5 | 21.11 | 0 | 0
2025-07-21 20:00 | 71.64 | 0 | 0 | 63.47 | 0 | 8.17 | 12.51 | 0 | 0
2025-07-21 21:00 | 67.79 | 0 | 0 | 67.79 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 22:00 | 63.49 | 0 | 0 | 63.49 | 0 | 0 | 12.51 | 0 | 0
2025-07-21 23:00 | 58.9 | 0 | 0 | 58.9 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 | 55.59 | 0 | 0 | 55.59 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 01:00 | 53.82 | 0 | 0 | 53.82 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 02:00 | 51.78 | 0 | 0 | 51.78 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 03:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 04:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 05:00 | 54 | 9.79 | 9.79 | 44.21 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 06:00 | 56.11 | 62.41 | 62.41 | 0 | 6.29 | 0 | 18.49 | 0 | 0
2025-07-22 07:00 | 59.23 | 85.18 | 85.18 | 0 | 25.96 | 0 | 43.15 | 0 | 0
2025-07-22 08:00 | 61.23 | 104.86 | 104.86 | 0 | 43.63 | 0 | 84.6 | 0 | 0
2025-07-22 09:00 | 66.61 | 108.84 | 96.08 | 0 | 29.47 | 0 | 112.59 | 12.76 | 0
2025-07-22 10:00 | 69.86 | 109.91 | 69.86 | 0 | 0 | 0 | 112.59 | 40.05 | 0
2025-07-22 11:00 | 73.66 | 104.89 | 73.66 | 0 | 0 | 0 | 112.59 | 31.23 | 0
2025-07-22 12:00 | 76.36 | 102.65 | 76.36 | 0 | 0 | 0 | 112.59 | 26.29 | 0
2025-07-22 13:00 | 78.5 | 103.8 | 78.5 | 0 | 0 | 0 | 112.59 | 25.3 | 0
2025-07-22 14:00 | 79.8 | 104.84 | 79.8 | 0 | 0 | 0 | 112.59 | 25.03 | 0
2025-07-22 15:00 | 80.62 | 102.73 | 80.62 | 0 | 0 | 0 | 112.59 | 22.11 | 0
2025-07-22 16:00 | 79.78 | 91.61 | 79.78 | 0 | 0 | 0 | 112.59 | 11.83 | 0
2025-07-22 17:00 | 78.91 | 77.74 | 77.74 | 0 | 0 | 1.18 | 111.35 | 0 | 0
2025-07-22 18:00 | 75.37 | 56.05 | 56.05 | 0 | 0 | 19.33 | 91.01 | 0 | 0
2025-07-22 19:00 | 72.89 | 8.94 | 8.94 | 1.45 | 0 | 62.5 | 25.22 | 0 | 0
2025-07-22 20:00 | 70.69 | 0 | 0 | 58.61 | 0 | 12.07 | 12.51 | 0 | 0
2025-07-22 21:00 | 65.62 | 0 | 0 | 65.62 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 22:00 | 62.1 | 0 | 0 | 62.1 | 0 | 0 | 12.51 | 0 | 0
2025-07-22 23:00 | 58.32 | 0 | 0 | 58.32 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 01:00 | 53.21 | 0 | 0 | 53.21 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 02:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 03:00 | 52.09 | 0 | 0 | 52.09 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 04:00 | 51.8 | 0 | 0 | 51.8 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 05:00 | 53.97 | 8.99 | 8.99 | 44.98 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 06:00 | 56.29 | 64.98 | 64.98 | 0 | 8.69 | 0 | 20.76 | 0 | 0
2025-07-23 07:00 | 59.48 | 92.82 | 92.82 | 0 | 33.34 | 0 | 52.44 | 0 | 0
2025-07-23 08:00 | 62.68 | 107.68 | 107.68 | 0 | 45 | 0 | 95.19 | 0 | 0
2025-07-23 09:00 | 68.27 | 113.52 | 86.58 | 0 | 18.31 | 0 | 112.59 | 26.94 | 0
2025-07-23 10:00 | 71.32 | 115.36 | 71.32 | 0 | 0 | 0 | 112.59 | 44.04 | 0
2025-07-23 11:00 | 74.92 | 114.39 | 74.92 | 0 | 0 | 0 | 112.59 | 39.47 | 0
2025-07-23 12:00 | 77.8 | 112.57 | 77.8 | 0 | 0 | 0 | 112.59 | 34.78 | 0
2025-07-23 13:00 | 80.9 | 113.31 | 80.9 | 0 | 0 | 0 | 112.59 | 32.41 | 0
2025-07-23 14:00 | 83.39 | 114.04 | 83.39 | 0 | 0 | 0 | 112.59 | 30.65 | 0
2025-07-23 15:00 | 84.13 | 112.66 | 84.13 | 0 | 0 | 0 | 112.59 | 28.54 | 0
2025-07-23 16:00 | 83.42 | 105.26 | 83.42 | 0 | 0 | 0 | 112.59 | 21.84 | 0
2025-07-23 17:00 | 81.34 | 91.44 | 81.34 | 0 | 0 | 0 | 112.59 | 10.1 | 0
2025-07-23 18:00 | 77.6 | 65.4 | 65.4 | 0 | 0 | 12.21 | 99.74 | 0 | 0
2025-07-23 19:00 | 75 | 8.54 | 8.54 | 3.96 | 0 | 62.5 | 33.95 | 0 | 0
2025-07-23 20:00 | 70.17 | 0 | 0 | 49.8 | 0 | 20.37 | 12.51 | 0 | 0
2025-07-23 21:00 | 65.9 | 0 | 0 | 65.9 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 22:00 | 62.73 | 0 | 0 | 62.73 | 0 | 0 | 12.51 | 0 | 0
2025-07-23 23:00 | 59.21 | 0 | 0 | 59.21 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 | 56.04 | 0 | 0 | 56.04 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 01:00 | 53.76 | 0 | 0 | 53.76 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 02:00 | 52.41 | 0 | 0 | 52.41 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 03:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 04:00 | 52.09 | 0 | 0 | 52.09 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 05:00 | 52.76 | 6.73 | 6.73 | 46.03 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 06:00 | 54.59 | 60.36 | 60.36 | 0 | 5.77 | 0 | 18 | 0 | 0
2025-07-24 07:00 | 58.46 | 87.78 | 87.78 | 0 | 29.32 | 0 | 45.84 | 0 | 0
2025-07-24 08:00 | 60.35 | 101.23 | 101.23 | 0 | 40.88 | 0 | 84.68 | 0 | 0
2025-07-24 09:00 | 63.65 | 105.31 | 93.03 | 0 | 29.38 | 0 | 112.59 | 12.28 | 0
2025-07-24 10:00 | 65.91 | 108.4 | 65.91 | 0 | 0 | 0 | 112.59 | 42.5 | 0
2025-07-24 11:00 | 66.72 | 104.11 | 66.72 | 0 | 0 | 0 | 112.59 | 37.38 | 0
2025-07-24 12:00 | 68.53 | 100.8 | 68.53 | 0 | 0 | 0 | 112.59 | 32.27 | 0
2025-07-24 13:00 | 68.67 | 101.92 | 68.67 | 0 | 0 | 0 | 112.59 | 33.26 | 0
2025-07-24 14:00 | 68.49 | 106.57 | 68.49 | 0 | 0 | 0 | 112.59 | 38.08 | 0
2025-07-24 15:00 | 69.6 | 103.99 | 69.6 | 0 | 0 | 0 | 112.59 | 34.38 | 0
2025-07-24 16:00 | 69.18 | 95.65 | 69.18 | 0 | 0 | 0 | 112.59 | 26.47 | 0
2025-07-24 17:00 | 68.78 | 83.98 | 68.78 | 0 | 0 | 0 | 112.59 | 15.21 | 0
2025-07-24 18:00 | 69.22 | 62.72 | 62.72 | 0 | 0 | 6.5 | 105.75 | 0 | 0
2025-07-24 19:00 | 66.27 | 7.61 | 7.61 | 0 | 0 | 58.66 | 44.01 | 0 | 0
2025-07-24 20:00 | 65.55 | 0 | 0 | 35.63 | 0 | 29.92 | 12.51 | 0 | 0
2025-07-24 21:00 | 62.72 | 0 | 0 | 62.72 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 22:00 | 61.18 | 0 | 0 | 61.18 | 0 | 0 | 12.51 | 0 | 0
2025-07-24 23:00 | 58.24 | 0 | 0 | 58.24 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 | 56 | 0 | 0 | 56 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 01:00 | 53.09 | 0 | 0 | 53.09 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 02:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 03:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 04:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 05:00 | 53.8 | 8.71 | 8.71 | 45.09 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 06:00 | 55.36 | 78.4 | 78.4 | 0 | 23.04 | 0 | 34.39 | 0 | 0
2025-07-25 07:00 | 58.9 | 106.63 | 106.63 | 0 | 47.72 | 0 | 79.73 | 0 | 0
2025-07-25 08:00 | 63.35 | 119.37 | 97.93 | 0 | 34.59 | 0 | 112.59 | 21.44 | 0
2025-07-25 09:00 | 65.82 | 120.68 | 65.82 | 0 | 0 | 0 | 112.59 | 54.86 | 0
2025-07-25 10:00 | 70.13 | 120.73 | 70.13 | 0 | 0 | 0 | 112.59 | 50.6 | 0
2025-07-25 11:00 | 72.41 | 118.24 | 72.41 | 0 | 0 | 0 | 112.59 | 45.83 | 0
2025-07-25 12:00 | 75.65 | 116.39 | 75.65 | 0 | 0 | 0 | 112.59 | 40.74 | 0
2025-07-25 13:00 | 78.2 | 117.4 | 78.2 | 0 | 0 | 0 | 112.59 | 39.2 | 0
2025-07-25 14:00 | 79.48 | 118.64 | 79.48 | 0 | 0 | 0 | 112.59 | 39.17 | 0
2025-07-25 15:00 | 79.37 | 119.6 | 79.37 | 0 | 0 | 0 | 112.59 | 40.23 | 0
2025-07-25 16:00 | 78.87 | 116.75 | 78.87 | 0 | 0 | 0 | 112.59 | 37.88 | 0
2025-07-25 17:00 | 78.38 | 105.49 | 78.38 | 0 | 0 | 0 | 112.59 | 27.11 | 0
2025-07-25 18:00 | 76.27 | 78.95 | 76.27 | 0 | 0 | 0 | 112.59 | 2.69 | 0
2025-07-25 19:00 | 73.53 | 8.2 | 8.2 | 2.84 | 0 | 62.5 | 46.8 | 0 | 0
2025-07-25 20:00 | 70.3 | 0 | 0 | 37.73 | 0 | 32.58 | 12.51 | 0 | 0
2025-07-25 21:00 | 65.84 | 0 | 0 | 65.84 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 22:00 | 61.98 | 0 | 0 | 61.98 | 0 | 0 | 12.51 | 0 | 0
2025-07-25 23:00 | 59.41 | 0 | 0 | 59.41 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 01:00 | 53.05 | 0 | 0 | 53.05 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 02:00 | 51.63 | 0 | 0 | 51.63 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 03:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 04:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 05:00 | 53.53 | 9.93 | 9.93 | 43.6 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 06:00 | 56.26 | 8.9 | 8.9 | 47.36 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 07:00 | 58.86 | 55.83 | 55.83 | 3.03 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 08:00 | 62.24 | 95.9 | 95.9 | 0 | 33.66 | 0 | 44.49 | 0 | 0
2025-07-26 09:00 | 63.79 | 111.69 | 111.69 | 0 | 47.9 | 0 | 89.99 | 0 | 0
2025-07-26 10:00 | 67.92 | 104.11 | 91.71 | 0 | 23.78 | 0 | 112.59 | 12.4 | 0
2025-07-26 11:00 | 70.84 | 85.09 | 70.84 | 0 | 0 | 0 | 112.59 | 14.25 | 0
2025-07-26 12:00 | 71.95 | 45.58 | 45.58 | 0 | 0 | 26.37 | 84.83 | 0 | 0
2025-07-26 13:00 | 74.03 | 26.67 | 26.67 | 0 | 0 | 47.36 | 34.98 | 0 | 0
2025-07-26 14:00 | 74.94 | 111.76 | 111.76 | 0 | 36.82 | 0 | 69.96 | 0 | 0
2025-07-26 15:00 | 75.71 | 42.52 | 42.52 | 0 | 0 | 33.18 | 35.03 | 0 | 0
2025-07-26 16:00 | 76.17 | 36.28 | 36.28 | 18.5 | 0 | 21.39 | 12.51 | 0 | 0
2025-07-26 17:00 | 75.37 | 18.04 | 18.04 | 57.33 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 18:00 | 72.31 | 0.85 | 0.85 | 71.46 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 19:00 | 70.76 | 10.68 | 10.68 | 60.08 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 20:00 | 68.07 | 0 | 0 | 68.07 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 21:00 | 64.95 | 0 | 0 | 64.95 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 22:00 | 61.77 | 0 | 0 | 61.77 | 0 | 0 | 12.51 | 0 | 0
2025-07-26 23:00 | 58.63 | 0 | 0 | 58.63 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 | 56.52 | 0 | 0 | 56.52 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 01:00 | 54.08 | 0 | 0 | 54.08 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 02:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 03:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 04:00 | 52.59 | 0 | 0 | 52.59 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 05:00 | 53.69 | 7.23 | 7.23 | 46.46 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 06:00 | 56.24 | 74.55 | 74.55 | 0 | 18.3 | 0 | 29.9 | 0 | 0
2025-07-27 07:00 | 58.45 | 102.17 | 102.17 | 0 | 43.72 | 0 | 71.44 | 0 | 0
2025-07-27 08:00 | 61.41 | 112.7 | 104.73 | 0 | 43.32 | 0 | 112.59 | 7.97 | 0
2025-07-27 09:00 | 64.33 | 116.54 | 64.33 | 0 | 0 | 0 | 112.59 | 52.21 | 0
2025-07-27 10:00 | 66.02 | 116.2 | 66.02 | 0 | 0 | 0 | 112.59 | 50.18 | 0
2025-07-27 11:00 | 69.37 | 113.6 | 69.37 | 0 | 0 | 0 | 112.59 | 44.23 | 0
2025-07-27 12:00 | 70.98 | 111.26 | 70.98 | 0 | 0 | 0 | 112.59 | 40.28 | 0
2025-07-27 13:00 | 72.09 | 112.72 | 72.09 | 0 | 0 | 0 | 112.59 | 40.64 | 0
2025-07-27 14:00 | 74.22 | 114.53 | 74.22 | 0 | 0 | 0 | 112.59 | 40.31 | 0
2025-07-27 15:00 | 74.03 | 115.06 | 74.03 | 0 | 0 | 0 | 112.59 | 41.03 | 0
2025-07-27 16:00 | 73.49 | 112.18 | 73.49 | 0 | 0 | 0 | 112.59 | 38.7 | 0
2025-07-27 17:00 | 72.4 | 102.36 | 72.4 | 0 | 0 | 0 | 112.59 | 29.96 | 0
2025-07-27 18:00 | 71.46 | 76.27 | 71.46 | 0 | 0 | 0 | 112.59 | 4.81 | 0
2025-07-27 19:00 | 69.91 | 6.88 | 6.88 | 0.53 | 0 | 62.5 | 46.8 | 0 | 0
2025-07-27 20:00 | 66.62 | 0 | 0 | 34.04 | 0 | 32.58 | 12.51 | 0 | 0
2025-07-27 21:00 | 64.27 | 0 | 0 | 64.27 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 22:00 | 61.74 | 0 | 0 | 61.74 | 0 | 0 | 12.51 | 0 | 0
2025-07-27 23:00 | 57.39 | 0 | 0 | 57.39 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 | 55.68 | 0 | 0 | 55.68 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 01:00 | 53.32 | 0 | 0 | 53.32 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 02:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 03:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 04:00 | 52.21 | 0 | 0 | 52.21 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 05:00 | 54.5 | 1.76 | 1.76 | 52.74 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 06:00 | 55.55 | 34.42 | 34.42 | 21.12 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 07:00 | 58.6 | 72.48 | 72.48 | 0 | 13.88 | 0 | 25.69 | 0 | 0
2025-07-28 08:00 | 62.53 | 104.53 | 104.53 | 0 | 41.99 | 0 | 65.59 | 0 | 0
2025-07-28 09:00 | 64.42 | 107.54 | 107.54 | 0 | 43.12 | 0 | 106.55 | 0 | 0
2025-07-28 10:00 | 68.61 | 90.78 | 74.97 | 0 | 6.36 | 0 | 112.59 | 15.81 | 0
2025-07-28 11:00 | 70.38 | 92.16 | 70.38 | 0 | 0 | 0 | 112.59 | 21.78 | 0
2025-07-28 12:00 | 73.46 | 69.64 | 69.64 | 0 | 0 | 3.82 | 108.57 | 0 | 0
2025-07-28 13:00 | 74.56 | 67.42 | 67.42 | 0 | 0 | 7.14 | 101.05 | 0 | 0
2025-07-28 14:00 | 75.32 | 70.45 | 70.45 | 0 | 0 | 4.87 | 95.93 | 0 | 0
2025-07-28 15:00 | 75.47 | 88.94 | 88.94 | 0 | 13.48 | 0 | 108.73 | 0 | 0
2025-07-28 16:00 | 74.86 | 110.59 | 78.92 | 0 | 4.06 | 0 | 112.59 | 31.67 | 0
2025-07-28 17:00 | 74.22 | 116.87 | 74.22 | 0 | 0 | 0 | 112.59 | 42.65 | 0
2025-07-28 18:00 | 73.02 | 92.69 | 73.02 | 0 | 0 | 0 | 112.59 | 19.68 | 0
2025-07-28 19:00 | 70.37 | 10.98 | 10.98 | 0 | 0 | 59.39 | 50.07 | 0 | 0
2025-07-28 20:00 | 67.55 | 0 | 0 | 31.87 | 0 | 35.68 | 12.51 | 0 | 0
2025-07-28 21:00 | 64.57 | 0 | 0 | 64.57 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 22:00 | 62.03 | 0 | 0 | 62.03 | 0 | 0 | 12.51 | 0 | 0
2025-07-28 23:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 | 55.42 | 0 | 0 | 55.42 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 01:00 | 53.2 | 0 | 0 | 53.2 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 02:00 | 52.32 | 0 | 0 | 52.32 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 03:00 | 52.41 | 0 | 0 | 52.41 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 04:00 | 52.7 | 0 | 0 | 52.7 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 05:00 | 52.91 | 0.87 | 0.87 | 52.04 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 06:00 | 55.63 | 55.55 | 55.55 | 0.07 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 07:00 | 58.15 | 115.14 | 115.14 | 0 | 56.99 | 0 | 66.65 | 0 | 0
2025-07-29 08:00 | 61.77 | 117.4 | 110.13 | 0 | 48.36 | 0 | 112.59 | 7.26 | 0
2025-07-29 09:00 | 66.18 | 90.38 | 66.18 | 0 | 0 | 0 | 112.59 | 24.2 | 0
2025-07-29 10:00 | 68.08 | 87.19 | 68.08 | 0 | 0 | 0 | 112.59 | 19.11 | 0
2025-07-29 11:00 | 71.11 | 66.03 | 66.03 | 0 | 0 | 5.08 | 107.24 | 0 | 0
2025-07-29 12:00 | 74.16 | 87.75 | 79.79 | 0 | 5.63 | 0 | 112.59 | 7.96 | 0
2025-07-29 13:00 | 76.72 | 20.34 | 20.34 | 0 | 0 | 56.38 | 53.24 | 0 | 0
2025-07-29 14:00 | 78.14 | 7.29 | 7.29 | 32.15 | 0 | 38.69 | 12.51 | 0 | 0
2025-07-29 15:00 | 78.47 | 21.16 | 21.16 | 57.31 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 16:00 | 78.42 | 4.23 | 4.23 | 74.19 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 17:00 | 75.7 | 2.37 | 2.37 | 73.32 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 18:00 | 75.16 | 0.72 | 0.72 | 74.44 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 19:00 | 71.77 | 0 | 0 | 71.77 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 20:00 | 69.16 | 0 | 0 | 69.16 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 21:00 | 64.72 | 0 | 0 | 64.72 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 22:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 12.51 | 0 | 0
2025-07-29 23:00 | 58.74 | 0 | 0 | 58.74 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 | 56.46 | 0 | 0 | 56.46 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 01:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 02:00 | 52.14 | 0 | 0 | 52.14 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 03:00 | 51.1 | 0 | 0 | 51.1 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 04:00 | 52.38 | 0 | 0 | 52.38 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 05:00 | 53.94 | 0.02 | 0.02 | 53.93 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 06:00 | 56.53 | 15.89 | 15.89 | 40.63 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 07:00 | 58.74 | 9.34 | 9.34 | 49.4 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 08:00 | 63.23 | 64.1 | 64.1 | 0 | 0.87 | 0 | 13.34 | 0 | 0
2025-07-30 09:00 | 67.63 | 68.63 | 68.63 | 0 | 1 | 0 | 14.29 | 0 | 0
2025-07-30 10:00 | 70.47 | 14.56 | 14.56 | 54.22 | 0 | 1.69 | 12.51 | 0 | 0
2025-07-30 11:00 | 75.79 | 7.51 | 7.51 | 68.28 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 12:00 | 79.67 | 39.52 | 39.52 | 40.15 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 13:00 | 81.97 | 94.27 | 94.27 | 0 | 12.3 | 0 | 24.19 | 0 | 0
2025-07-30 14:00 | 83.35 | 93.09 | 93.09 | 0 | 9.74 | 0 | 33.45 | 0 | 0
2025-07-30 15:00 | 85.07 | 5.87 | 5.87 | 59.31 | 0 | 19.89 | 12.51 | 0 | 0
2025-07-30 16:00 | 83.36 | 88.06 | 88.06 | 0 | 4.7 | 0 | 16.97 | 0 | 0
2025-07-30 17:00 | 82.01 | 96.7 | 96.7 | 0 | 14.69 | 0 | 30.93 | 0 | 0
2025-07-30 18:00 | 79.17 | 59.22 | 59.22 | 2.45 | 0 | 17.5 | 12.51 | 0 | 0
2025-07-30 19:00 | 75.84 | 2.83 | 2.83 | 73.01 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 20:00 | 70.98 | 0 | 0 | 70.98 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 21:00 | 66.61 | 0 | 0 | 66.61 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 22:00 | 62.81 | 0 | 0 | 62.81 | 0 | 0 | 12.51 | 0 | 0
2025-07-30 23:00 | 59.51 | 0 | 0 | 59.51 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 | 56.77 | 0 | 0 | 56.77 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 01:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 02:00 | 52.26 | 0 | 0 | 52.26 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 03:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 04:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 05:00 | 53.02 | 8.51 | 8.51 | 44.51 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 06:00 | 55.29 | 82.69 | 82.69 | 0 | 27.41 | 0 | 38.55 | 0 | 0
2025-07-31 07:00 | 57.98 | 105.96 | 105.96 | 0 | 47.98 | 0 | 84.13 | 0 | 0
2025-07-31 08:00 | 61.14 | 130.17 | 91.1 | 0 | 29.96 | 0 | 112.59 | 39.07 | 0
2025-07-31 09:00 | 64.24 | 132.89 | 64.24 | 0 | 0 | 0 | 112.59 | 68.65 | 0
2025-07-31 10:00 | 66.99 | 131.21 | 66.99 | 0 | 0 | 0 | 112.59 | 64.22 | 0
2025-07-31 11:00 | 69.03 | 93.86 | 69.03 | 0 | 0 | 0 | 112.59 | 24.82 | 0
2025-07-31 12:00 | 70.18 | 59.59 | 59.59 | 0 | 0 | 10.59 | 101.44 | 0 | 0
2025-07-31 13:00 | 72.5 | 68.13 | 68.13 | 0 | 0 | 4.36 | 96.85 | 0 | 0
2025-07-31 14:00 | 72.87 | 53.84 | 53.84 | 0 | 0 | 19.04 | 76.81 | 0 | 0
2025-07-31 15:00 | 73.73 | 53.47 | 53.47 | 0 | 0 | 20.26 | 55.48 | 0 | 0
2025-07-31 16:00 | 72.54 | 13.78 | 13.78 | 17.94 | 0 | 40.82 | 12.51 | 0 | 0
2025-07-31 17:00 | 71.33 | 6.93 | 6.93 | 64.4 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 18:00 | 70.83 | 0.78 | 0.78 | 70.05 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 19:00 | 69.68 | 0 | 0 | 69.68 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 20:00 | 66.83 | 0 | 0 | 66.83 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 21:00 | 63.98 | 0 | 0 | 63.98 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 22:00 | 60.74 | 0 | 0 | 60.74 | 0 | 0 | 12.51 | 0 | 0
2025-07-31 23:00 | 59.15 | 0 | 0 | 59.15 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 | 55.24 | 0 | 0 | 55.24 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 01:00 | 53.14 | 0 | 0 | 53.14 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 02:00 | 52.38 | 0 | 0 | 52.38 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 03:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 04:00 | 52.73 | 0 | 0 | 52.73 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 05:00 | 53.82 | 0.03 | 0.03 | 53.78 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 06:00 | 56.2 | 9.5 | 9.5 | 46.7 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 07:00 | 58.96 | 30.39 | 30.39 | 28.58 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 08:00 | 62.02 | 64.65 | 64.65 | 0 | 2.62 | 0 | 15 | 0 | 0
2025-08-01 09:00 | 65.25 | 55.41 | 55.41 | 7.47 | 0 | 2.37 | 12.51 | 0 | 0
2025-08-01 10:00 | 69.39 | 48.7 | 48.7 | 20.69 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 11:00 | 72.4 | 41.39 | 41.39 | 31.02 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 12:00 | 76.09 | 8.05 | 8.05 | 68.04 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 13:00 | 78.51 | 8.05 | 8.05 | 70.47 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 14:00 | 80.27 | 20.11 | 20.11 | 60.16 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 15:00 | 80.21 | 24.2 | 24.2 | 56.01 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 16:00 | 80 | 14.48 | 14.48 | 65.52 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 17:00 | 77.96 | 11.6 | 11.6 | 66.36 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 18:00 | 75.6 | 2.03 | 2.03 | 73.57 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 19:00 | 73.13 | 0 | 0 | 73.13 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 20:00 | 69.26 | 0 | 0 | 69.26 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 21:00 | 65.91 | 0 | 0 | 65.91 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 22:00 | 61.57 | 0 | 0 | 61.57 | 0 | 0 | 12.51 | 0 | 0
2025-08-01 23:00 | 58.24 | 0 | 0 | 58.24 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 | 56 | 0 | 0 | 56 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 01:00 | 53.92 | 0 | 0 | 53.92 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 02:00 | 51.58 | 0 | 0 | 51.58 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 03:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 04:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 05:00 | 53.48 | 1.68 | 1.68 | 51.81 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 06:00 | 56.39 | 20.79 | 20.79 | 35.6 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 07:00 | 58.9 | 38.09 | 38.09 | 20.82 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 08:00 | 62.12 | 72.48 | 72.48 | 0 | 10.36 | 0 | 22.36 | 0 | 0
2025-08-02 09:00 | 66.05 | 101.7 | 101.7 | 0 | 35.65 | 0 | 56.22 | 0 | 0
2025-08-02 10:00 | 68.04 | 106.4 | 106.4 | 0 | 38.36 | 0 | 92.66 | 0 | 0
2025-08-02 11:00 | 70.89 | 88.94 | 88.94 | 0 | 18.04 | 0 | 109.8 | 0 | 0
2025-08-02 12:00 | 73.54 | 86.72 | 76.47 | 0 | 2.93 | 0 | 112.59 | 10.25 | 0
2025-08-02 13:00 | 75.67 | 87.77 | 75.67 | 0 | 0 | 0 | 112.59 | 12.11 | 0
2025-08-02 14:00 | 75.79 | 100.46 | 75.79 | 0 | 0 | 0 | 112.59 | 24.67 | 0
2025-08-02 15:00 | 77.26 | 69.25 | 69.25 | 0 | 0 | 8.01 | 104.16 | 0 | 0
2025-08-02 16:00 | 76.7 | 57.18 | 57.18 | 0 | 0 | 19.51 | 83.62 | 0 | 0
2025-08-02 17:00 | 76.19 | 38.14 | 38.14 | 0 | 0 | 38.04 | 43.57 | 0 | 0
2025-08-02 18:00 | 74.08 | 27.25 | 27.25 | 17.31 | 0 | 29.51 | 12.51 | 0 | 0
2025-08-02 19:00 | 71.08 | 2.48 | 2.48 | 68.61 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 20:00 | 68.68 | 0 | 0 | 68.68 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 21:00 | 65.46 | 0 | 0 | 65.46 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 22:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 12.51 | 0 | 0
2025-08-02 23:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 01:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 02:00 | 51.69 | 0 | 0 | 51.69 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 03:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 04:00 | 51.58 | 0 | 0 | 51.58 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 05:00 | 53.2 | 3.55 | 3.55 | 49.65 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 06:00 | 55.06 | 71.57 | 71.57 | 0 | 16.51 | 0 | 28.2 | 0 | 0
2025-08-03 07:00 | 58.61 | 113.33 | 113.33 | 0 | 54.72 | 0 | 80.18 | 0 | 0
2025-08-03 08:00 | 62.01 | 126.72 | 96.12 | 0 | 34.11 | 0 | 112.59 | 30.6 | 0
2025-08-03 09:00 | 65.46 | 124.76 | 65.46 | 0 | 0 | 0 | 112.59 | 59.3 | 0
2025-08-03 10:00 | 68.68 | 116.48 | 68.68 | 0 | 0 | 0 | 112.59 | 47.81 | 0
2025-08-03 11:00 | 71.02 | 55.64 | 55.64 | 0 | 0 | 15.38 | 96.4 | 0 | 0
2025-08-03 12:00 | 74.13 | 75.94 | 75.94 | 0 | 1.82 | 0 | 98.12 | 0 | 0
2025-08-03 13:00 | 76.24 | 75.27 | 75.27 | 0 | 0 | 0.97 | 97.1 | 0 | 0
2025-08-03 14:00 | 77.49 | 65.24 | 65.24 | 0 | 0 | 12.25 | 84.21 | 0 | 0
2025-08-03 15:00 | 78.15 | 64.68 | 64.68 | 0 | 0 | 13.48 | 70.02 | 0 | 0
2025-08-03 16:00 | 78.4 | 47.8 | 47.8 | 0 | 0 | 30.6 | 37.81 | 0 | 0
2025-08-03 17:00 | 76.85 | 32.05 | 32.05 | 20.76 | 0 | 24.04 | 12.51 | 0 | 0
2025-08-03 18:00 | 73.94 | 16.1 | 16.1 | 57.84 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 19:00 | 72.13 | 1.2 | 1.2 | 70.94 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 20:00 | 68.99 | 0 | 0 | 68.99 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 21:00 | 64.86 | 0 | 0 | 64.86 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 22:00 | 62.22 | 0 | 0 | 62.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-03 23:00 | 58.44 | 0 | 0 | 58.44 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 | 55.09 | 0 | 0 | 55.09 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 01:00 | 53.69 | 0 | 0 | 53.69 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 02:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 03:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 04:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 05:00 | 53.11 | 2.68 | 2.68 | 50.43 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 06:00 | 56.1 | 57.25 | 57.25 | 0 | 1.16 | 0 | 13.61 | 0 | 0
2025-08-04 07:00 | 58.9 | 91.65 | 91.65 | 0 | 32.75 | 0 | 44.72 | 0 | 0
2025-08-04 08:00 | 62.78 | 103.52 | 103.52 | 0 | 40.74 | 0 | 83.42 | 0 | 0
2025-08-04 09:00 | 67.09 | 111.52 | 97.79 | 0 | 30.7 | 0 | 112.59 | 13.72 | 0
2025-08-04 10:00 | 70.73 | 110.2 | 70.73 | 0 | 0 | 0 | 112.59 | 39.48 | 0
2025-08-04 11:00 | 75.1 | 111.82 | 75.1 | 0 | 0 | 0 | 112.59 | 36.73 | 0
2025-08-04 12:00 | 78.2 | 108.56 | 78.2 | 0 | 0 | 0 | 112.59 | 30.35 | 0
2025-08-04 13:00 | 82.55 | 106.04 | 82.55 | 0 | 0 | 0 | 112.59 | 23.49 | 0
2025-08-04 14:00 | 83.56 | 105.9 | 83.56 | 0 | 0 | 0 | 112.59 | 22.34 | 0
2025-08-04 15:00 | 84.88 | 104.83 | 84.88 | 0 | 0 | 0 | 112.59 | 19.95 | 0
2025-08-04 16:00 | 84.35 | 103.73 | 84.35 | 0 | 0 | 0 | 112.59 | 19.39 | 0
2025-08-04 17:00 | 82.57 | 82.17 | 82.17 | 0 | 0 | 0.4 | 112.17 | 0 | 0
2025-08-04 18:00 | 78.71 | 49.7 | 49.7 | 0 | 0 | 29.01 | 81.63 | 0 | 0
2025-08-04 19:00 | 75.51 | 2.49 | 2.49 | 10.52 | 0 | 62.5 | 15.84 | 0 | 0
2025-08-04 20:00 | 72.14 | 0 | 0 | 68.97 | 0 | 3.17 | 12.51 | 0 | 0
2025-08-04 21:00 | 67.77 | 0 | 0 | 67.77 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 22:00 | 63.19 | 0 | 0 | 63.19 | 0 | 0 | 12.51 | 0 | 0
2025-08-04 23:00 | 59.09 | 0 | 0 | 59.09 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 01:00 | 53.79 | 0 | 0 | 53.79 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 02:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 03:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 04:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 05:00 | 53.34 | 1.82 | 1.82 | 51.52 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 06:00 | 55.79 | 48.65 | 48.65 | 7.14 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 07:00 | 58.86 | 81.38 | 81.38 | 0 | 22.51 | 0 | 33.9 | 0 | 0
2025-08-05 08:00 | 62.58 | 94.12 | 94.12 | 0 | 31.53 | 0 | 63.86 | 0 | 0
2025-08-05 09:00 | 65.99 | 99.43 | 99.43 | 0 | 33.43 | 0 | 95.62 | 0 | 0
2025-08-05 10:00 | 69.65 | 104.29 | 87.52 | 0 | 17.86 | 0 | 112.59 | 16.78 | 0
2025-08-05 11:00 | 74.98 | 104.69 | 74.98 | 0 | 0 | 0 | 112.59 | 29.71 | 0
2025-08-05 12:00 | 78.78 | 101.65 | 78.78 | 0 | 0 | 0 | 112.59 | 22.87 | 0
2025-08-05 13:00 | 80.38 | 103.22 | 80.38 | 0 | 0 | 0 | 112.59 | 22.83 | 0
2025-08-05 14:00 | 81.16 | 105.53 | 81.16 | 0 | 0 | 0 | 112.59 | 24.37 | 0
2025-08-05 15:00 | 82.01 | 106.68 | 82.01 | 0 | 0 | 0 | 112.59 | 24.67 | 0
2025-08-05 16:00 | 82.08 | 95.23 | 82.08 | 0 | 0 | 0 | 112.59 | 13.15 | 0
2025-08-05 17:00 | 80.83 | 75.42 | 75.42 | 0 | 0 | 5.41 | 106.89 | 0 | 0
2025-08-05 18:00 | 76.93 | 38.1 | 38.1 | 0 | 0 | 38.83 | 66.02 | 0 | 0
2025-08-05 19:00 | 74.11 | 1.83 | 1.83 | 21.45 | 0 | 50.83 | 12.51 | 0 | 0
2025-08-05 20:00 | 70.42 | 0 | 0 | 70.42 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 21:00 | 66.72 | 0 | 0 | 66.72 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 22:00 | 62.16 | 0 | 0 | 62.16 | 0 | 0 | 12.51 | 0 | 0
2025-08-05 23:00 | 57.96 | 0 | 0 | 57.96 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 01:00 | 53.98 | 0 | 0 | 53.98 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 03:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 04:00 | 51.75 | 0 | 0 | 51.75 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 05:00 | 53 | 3.05 | 3.05 | 49.95 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 06:00 | 56.28 | 71.84 | 71.84 | 0 | 15.56 | 0 | 27.29 | 0 | 0
2025-08-06 07:00 | 59.15 | 114.68 | 114.68 | 0 | 55.53 | 0 | 80.05 | 0 | 0
2025-08-06 08:00 | 63.1 | 125.67 | 97.35 | 0 | 34.25 | 0 | 112.59 | 28.32 | 0
2025-08-06 09:00 | 68 | 127.84 | 68 | 0 | 0 | 0 | 112.59 | 59.84 | 0
2025-08-06 10:00 | 71.35 | 126.04 | 71.35 | 0 | 0 | 0 | 112.59 | 54.69 | 0
2025-08-06 11:00 | 76.11 | 119.86 | 76.11 | 0 | 0 | 0 | 112.59 | 43.75 | 0
2025-08-06 12:00 | 80.5 | 121.21 | 80.5 | 0 | 0 | 0 | 112.59 | 40.7 | 0
2025-08-06 13:00 | 83.34 | 122.61 | 83.34 | 0 | 0 | 0 | 112.59 | 39.28 | 0
2025-08-06 14:00 | 86.06 | 76.11 | 76.11 | 0 | 0 | 9.95 | 102.12 | 0 | 0
2025-08-06 15:00 | 86.28 | 26.62 | 26.62 | 0 | 0 | 59.66 | 39.32 | 0 | 0
2025-08-06 16:00 | 85.17 | 108.05 | 108.05 | 0 | 22.88 | 0 | 61.05 | 0 | 0
2025-08-06 17:00 | 83.65 | 60.44 | 60.44 | 0 | 0 | 23.21 | 36.63 | 0 | 0
2025-08-06 18:00 | 80.51 | 44.02 | 44.02 | 13.57 | 0 | 22.91 | 12.51 | 0 | 0
2025-08-06 19:00 | 76.86 | 4.46 | 4.46 | 72.4 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 20:00 | 72.07 | 0 | 0 | 72.07 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 21:00 | 67.48 | 0 | 0 | 67.48 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 22:00 | 63.01 | 0 | 0 | 63.01 | 0 | 0 | 12.51 | 0 | 0
2025-08-06 23:00 | 58.86 | 0 | 0 | 58.86 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 01:00 | 53.5 | 0 | 0 | 53.5 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 02:00 | 51.79 | 0 | 0 | 51.79 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 03:00 | 52.32 | 0 | 0 | 52.32 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 04:00 | 52.63 | 0 | 0 | 52.63 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 05:00 | 53.67 | 1.34 | 1.34 | 52.33 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 06:00 | 55.76 | 35.2 | 35.2 | 20.56 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 07:00 | 58.4 | 82.91 | 82.91 | 0 | 24.5 | 0 | 35.79 | 0 | 0
2025-08-07 08:00 | 61.14 | 101.54 | 101.54 | 0 | 40.39 | 0 | 74.16 | 0 | 0
2025-08-07 09:00 | 65.21 | 105.79 | 105.66 | 0 | 40.45 | 0 | 112.59 | 0.13 | 0
2025-08-07 10:00 | 68.88 | 107.88 | 68.88 | 0 | 0 | 0 | 112.59 | 39 | 0
2025-08-07 11:00 | 72.2 | 102.86 | 72.2 | 0 | 0 | 0 | 112.59 | 30.66 | 0
2025-08-07 12:00 | 75.1 | 95.51 | 75.1 | 0 | 0 | 0 | 112.59 | 20.41 | 0
2025-08-07 13:00 | 77.44 | 94.52 | 77.44 | 0 | 0 | 0 | 112.59 | 17.08 | 0
2025-08-07 14:00 | 77.96 | 96.74 | 77.96 | 0 | 0 | 0 | 112.59 | 18.78 | 0
2025-08-07 15:00 | 78.42 | 78.55 | 78.42 | 0 | 0 | 0 | 112.59 | 0.13 | 0
2025-08-07 16:00 | 79.04 | 77.44 | 77.44 | 0 | 0 | 1.6 | 110.91 | 0 | 0
2025-08-07 17:00 | 77.37 | 64.61 | 64.61 | 0 | 0 | 12.76 | 97.48 | 0 | 0
2025-08-07 18:00 | 74.67 | 35.99 | 35.99 | 0 | 0 | 38.68 | 56.77 | 0 | 0
2025-08-07 19:00 | 72.03 | 1.14 | 1.14 | 28.85 | 0 | 42.04 | 12.51 | 0 | 0
2025-08-07 20:00 | 68.78 | 0 | 0 | 68.78 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 21:00 | 65.33 | 0 | 0 | 65.33 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 22:00 | 62.01 | 0 | 0 | 62.01 | 0 | 0 | 12.51 | 0 | 0
2025-08-07 23:00 | 59.71 | 0 | 0 | 59.71 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 | 55.57 | 0 | 0 | 55.57 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 01:00 | 53.64 | 0 | 0 | 53.64 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 02:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 03:00 | 51.21 | 0 | 0 | 51.21 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 04:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 05:00 | 53.51 | 2.9 | 2.9 | 50.62 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 06:00 | 53.28 | 32.28 | 32.28 | 21 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 07:00 | 58.57 | 29.11 | 29.11 | 29.46 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 08:00 | 62.31 | 55.4 | 55.4 | 6.91 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 09:00 | 63.58 | 107.68 | 107.68 | 0 | 44.09 | 0 | 54.4 | 0 | 0
2025-08-08 10:00 | 68.46 | 134.54 | 129.71 | 0 | 61.25 | 0 | 112.59 | 4.83 | 0
2025-08-08 11:00 | 69.1 | 119.27 | 69.1 | 0 | 0 | 0 | 112.59 | 50.17 | 0
2025-08-08 12:00 | 73.28 | 54.22 | 54.22 | 0 | 0 | 19.06 | 92.53 | 0 | 0
2025-08-08 13:00 | 74.53 | 9.08 | 9.08 | 2.95 | 0 | 62.5 | 26.74 | 0 | 0
2025-08-08 14:00 | 74.43 | 8.18 | 8.18 | 52.73 | 0 | 13.51 | 12.51 | 0 | 0
2025-08-08 15:00 | 76.18 | 17.96 | 17.96 | 58.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 16:00 | 76.18 | 53.71 | 53.71 | 22.46 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 17:00 | 74.72 | 62.09 | 62.09 | 12.63 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 18:00 | 73.1 | 63.25 | 63.25 | 9.85 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 19:00 | 70.28 | 2.28 | 2.28 | 68 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 20:00 | 66.76 | 0 | 0 | 66.76 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 21:00 | 64.93 | 0 | 0 | 64.93 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 22:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 12.51 | 0 | 0
2025-08-08 23:00 | 58.8 | 0 | 0 | 58.8 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 01:00 | 52.53 | 0 | 0 | 52.53 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 02:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 03:00 | 50.62 | 0 | 0 | 50.62 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 04:00 | 51.92 | 0 | 0 | 51.92 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 05:00 | 53.48 | 0.06 | 0.06 | 53.43 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 06:00 | 54.78 | 7.34 | 7.34 | 47.44 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 07:00 | 58.73 | 11.16 | 11.16 | 47.57 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 08:00 | 61.93 | 17.12 | 17.12 | 44.81 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 09:00 | 64.85 | 37.63 | 37.63 | 27.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 10:00 | 68.49 | 66.1 | 66.1 | 2.39 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 11:00 | 70.79 | 44.63 | 44.63 | 26.16 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 12:00 | 74.31 | 54.55 | 54.55 | 19.75 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 13:00 | 76.54 | 63.43 | 63.43 | 13.11 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 14:00 | 77.91 | 59.23 | 59.23 | 18.68 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 15:00 | 78.45 | 45.1 | 45.1 | 33.35 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 16:00 | 77.95 | 22.63 | 22.63 | 55.32 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 17:00 | 76.4 | 9.81 | 9.81 | 66.6 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 18:00 | 74.62 | 0 | 0 | 74.62 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 19:00 | 72.27 | 0 | 0 | 72.27 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 20:00 | 68.53 | 0 | 0 | 68.53 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 21:00 | 65.28 | 0 | 0 | 65.28 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 22:00 | 61.54 | 0 | 0 | 61.54 | 0 | 0 | 12.51 | 0 | 0
2025-08-09 23:00 | 58.02 | 0 | 0 | 58.02 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 01:00 | 52.98 | 0 | 0 | 52.98 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 02:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 03:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 04:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 05:00 | 53.1 | 1.02 | 1.02 | 52.08 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 06:00 | 55.25 | 66.56 | 66.56 | 0 | 11.32 | 0 | 23.26 | 0 | 0
2025-08-10 07:00 | 57.62 | 111.57 | 111.57 | 0 | 53.95 | 0 | 74.52 | 0 | 0
2025-08-10 08:00 | 62.09 | 121.92 | 102.17 | 0 | 40.08 | 0 | 112.59 | 19.75 | 0
2025-08-10 09:00 | 65.77 | 123.12 | 65.77 | 0 | 0 | 0 | 112.59 | 57.35 | 0
2025-08-10 10:00 | 69.87 | 120.86 | 69.87 | 0 | 0 | 0 | 112.59 | 50.99 | 0
2025-08-10 11:00 | 72.75 | 117.57 | 72.75 | 0 | 0 | 0 | 112.59 | 44.82 | 0
2025-08-10 12:00 | 77.05 | 115.54 | 77.05 | 0 | 0 | 0 | 112.59 | 38.48 | 0
2025-08-10 13:00 | 78.31 | 116.64 | 78.31 | 0 | 0 | 0 | 112.59 | 38.33 | 0
2025-08-10 14:00 | 79.57 | 119.19 | 79.57 | 0 | 0 | 0 | 112.59 | 39.62 | 0
2025-08-10 15:00 | 80.03 | 120.22 | 80.03 | 0 | 0 | 0 | 112.59 | 40.19 | 0
2025-08-10 16:00 | 79.14 | 118.19 | 79.14 | 0 | 0 | 0 | 112.59 | 39.05 | 0
2025-08-10 17:00 | 79.27 | 107.48 | 79.27 | 0 | 0 | 0 | 112.59 | 28.21 | 0
2025-08-10 18:00 | 76.79 | 62.66 | 62.66 | 0 | 0 | 14.13 | 97.72 | 0 | 0
2025-08-10 19:00 | 73.31 | 0.89 | 0.89 | 9.92 | 0 | 62.5 | 31.93 | 0 | 0
2025-08-10 20:00 | 68.99 | 0 | 0 | 50.55 | 0 | 18.45 | 12.51 | 0 | 0
2025-08-10 21:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 22:00 | 61.72 | 0 | 0 | 61.72 | 0 | 0 | 12.51 | 0 | 0
2025-08-10 23:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 | 56.17 | 0 | 0 | 56.17 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 01:00 | 53.55 | 0 | 0 | 53.55 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 02:00 | 52.92 | 0 | 0 | 52.92 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 03:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 04:00 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 05:00 | 52.91 | 0.92 | 0.92 | 51.99 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 06:00 | 54.52 | 47.79 | 47.79 | 6.74 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 07:00 | 58.23 | 65.95 | 65.95 | 0 | 7.72 | 0 | 19.84 | 0 | 0
2025-08-11 08:00 | 62.37 | 97.16 | 97.16 | 0 | 34.78 | 0 | 52.89 | 0 | 0
2025-08-11 09:00 | 65.8 | 87.26 | 87.26 | 0 | 21.45 | 0 | 73.26 | 0 | 0
2025-08-11 10:00 | 69.25 | 97.06 | 97.06 | 0 | 27.81 | 0 | 99.69 | 0 | 0
2025-08-11 11:00 | 72.25 | 111.28 | 85.84 | 0 | 13.58 | 0 | 112.59 | 25.45 | 0
2025-08-11 12:00 | 75.9 | 124.36 | 75.9 | 0 | 0 | 0 | 112.59 | 48.46 | 0
2025-08-11 13:00 | 78.63 | 124.52 | 78.63 | 0 | 0 | 0 | 112.59 | 45.89 | 0
2025-08-11 14:00 | 79.82 | 128.06 | 79.82 | 0 | 0 | 0 | 112.59 | 48.25 | 0
2025-08-11 15:00 | 80.19 | 129.49 | 80.19 | 0 | 0 | 0 | 112.59 | 49.3 | 0
2025-08-11 16:00 | 79.2 | 127.28 | 79.2 | 0 | 0 | 0 | 112.59 | 48.08 | 0
2025-08-11 17:00 | 78.56 | 116.18 | 78.56 | 0 | 0 | 0 | 112.59 | 37.62 | 0
2025-08-11 18:00 | 74.22 | 69.63 | 69.63 | 0 | 0 | 4.59 | 107.76 | 0 | 0
2025-08-11 19:00 | 72.94 | 1.86 | 1.86 | 8.59 | 0 | 62.5 | 41.97 | 0 | 0
2025-08-11 20:00 | 70.53 | 0 | 0 | 42.54 | 0 | 27.98 | 12.51 | 0 | 0
2025-08-11 21:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 22:00 | 61.68 | 0 | 0 | 61.68 | 0 | 0 | 12.51 | 0 | 0
2025-08-11 23:00 | 58.37 | 0 | 0 | 58.37 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 | 55.04 | 0 | 0 | 55.04 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 01:00 | 53.67 | 0 | 0 | 53.67 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 02:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 03:00 | 51.39 | 0 | 0 | 51.39 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 04:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 05:00 | 53.16 | 0.77 | 0.77 | 52.39 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 06:00 | 56.86 | 48.65 | 48.65 | 8.21 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 07:00 | 58 | 92.58 | 92.58 | 0 | 34.58 | 0 | 45.36 | 0 | 0
2025-08-12 08:00 | 60.97 | 108.95 | 108.95 | 0 | 47.98 | 0 | 90.94 | 0 | 0
2025-08-12 09:00 | 63.01 | 113.12 | 85.79 | 0 | 22.78 | 0 | 112.59 | 27.32 | 0
2025-08-12 10:00 | 66.4 | 110.61 | 66.4 | 0 | 0 | 0 | 112.59 | 44.21 | 0
2025-08-12 11:00 | 69.69 | 109.43 | 69.69 | 0 | 0 | 0 | 112.59 | 39.74 | 0
2025-08-12 12:00 | 70.43 | 107.87 | 70.43 | 0 | 0 | 0 | 112.59 | 37.44 | 0
2025-08-12 13:00 | 71.46 | 108.52 | 71.46 | 0 | 0 | 0 | 112.59 | 37.07 | 0
2025-08-12 14:00 | 73.42 | 109.97 | 73.42 | 0 | 0 | 0 | 112.59 | 36.55 | 0
2025-08-12 15:00 | 74.38 | 111.29 | 74.38 | 0 | 0 | 0 | 112.59 | 36.91 | 0
2025-08-12 16:00 | 73.43 | 108.28 | 73.43 | 0 | 0 | 0 | 112.59 | 34.85 | 0
2025-08-12 17:00 | 72.37 | 92.48 | 72.37 | 0 | 0 | 0 | 112.59 | 20.11 | 0
2025-08-12 18:00 | 70.17 | 47.84 | 47.84 | 0 | 0 | 22.33 | 89.09 | 0 | 0
2025-08-12 19:00 | 69.34 | 0.64 | 0.64 | 6.21 | 0 | 62.5 | 23.3 | 0 | 0
2025-08-12 20:00 | 67 | 0 | 0 | 56.75 | 0 | 10.25 | 12.51 | 0 | 0
2025-08-12 21:00 | 62.97 | 0 | 0 | 62.97 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 22:00 | 61.44 | 0 | 0 | 61.44 | 0 | 0 | 12.51 | 0 | 0
2025-08-12 23:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 01:00 | 53.42 | 0 | 0 | 53.42 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 02:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 03:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 04:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 05:00 | 52.22 | 0.62 | 0.62 | 51.61 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 06:00 | 54.59 | 13.18 | 13.18 | 41.41 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 07:00 | 57.87 | 2.23 | 2.23 | 55.64 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 08:00 | 61.55 | 21.47 | 21.47 | 40.09 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 09:00 | 65.46 | 23.96 | 23.96 | 41.5 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 10:00 | 69.08 | 44.7 | 44.7 | 24.38 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 11:00 | 72.9 | 37.2 | 37.2 | 35.7 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 12:00 | 75.87 | 81 | 81 | 0 | 5.13 | 0 | 17.39 | 0 | 0
2025-08-13 13:00 | 77.13 | 129.61 | 129.61 | 0 | 52.48 | 0 | 67.24 | 0 | 0
2025-08-13 14:00 | 79.11 | 124.17 | 124.17 | 0 | 45.06 | 0 | 110.05 | 0 | 0
2025-08-13 15:00 | 79.06 | 124.52 | 81.73 | 0 | 2.67 | 0 | 112.59 | 42.79 | 0
2025-08-13 16:00 | 78.9 | 99.67 | 78.9 | 0 | 0 | 0 | 112.59 | 20.77 | 0
2025-08-13 17:00 | 77.72 | 45.69 | 45.69 | 0 | 0 | 32.03 | 78.87 | 0 | 0
2025-08-13 18:00 | 73.59 | 20.63 | 20.63 | 0 | 0 | 52.96 | 23.13 | 0 | 0
2025-08-13 19:00 | 73.55 | 0.13 | 0.13 | 63.33 | 0 | 10.09 | 12.51 | 0 | 0
2025-08-13 20:00 | 69.2 | 0 | 0 | 69.2 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 21:00 | 64.96 | 0 | 0 | 64.96 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 22:00 | 62.58 | 0 | 0 | 62.58 | 0 | 0 | 12.51 | 0 | 0
2025-08-13 23:00 | 58.06 | 0 | 0 | 58.06 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 | 55.37 | 0 | 0 | 55.37 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 01:00 | 52.84 | 0 | 0 | 52.84 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 02:00 | 52.52 | 0 | 0 | 52.52 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 03:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 04:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 05:00 | 53.69 | 0.53 | 0.53 | 53.16 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 06:00 | 55.6 | 55.05 | 55.05 | 0.55 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 07:00 | 58.2 | 103.93 | 103.93 | 0 | 45.73 | 0 | 55.96 | 0 | 0
2025-08-14 08:00 | 62.2 | 115.2 | 115.2 | 0 | 53 | 0 | 106.3 | 0 | 0
2025-08-14 09:00 | 66.63 | 117 | 73.25 | 0 | 6.62 | 0 | 112.59 | 43.75 | 0
2025-08-14 10:00 | 69.27 | 115.36 | 69.27 | 0 | 0 | 0 | 112.59 | 46.09 | 0
2025-08-14 11:00 | 72.7 | 112.78 | 72.7 | 0 | 0 | 0 | 112.59 | 40.08 | 0
2025-08-14 12:00 | 75.78 | 110.89 | 75.78 | 0 | 0 | 0 | 112.59 | 35.1 | 0
2025-08-14 13:00 | 78.71 | 112.3 | 78.71 | 0 | 0 | 0 | 112.59 | 33.59 | 0
2025-08-14 14:00 | 79.25 | 114.07 | 79.25 | 0 | 0 | 0 | 112.59 | 34.82 | 0
2025-08-14 15:00 | 79.92 | 113.71 | 79.92 | 0 | 0 | 0 | 112.59 | 33.78 | 0
2025-08-14 16:00 | 78.78 | 112.54 | 78.78 | 0 | 0 | 0 | 112.59 | 33.75 | 0
2025-08-14 17:00 | 77.47 | 98.56 | 77.47 | 0 | 0 | 0 | 112.59 | 21.09 | 0
2025-08-14 18:00 | 75.44 | 50.58 | 50.58 | 0 | 0 | 24.85 | 86.43 | 0 | 0
2025-08-14 19:00 | 72.61 | 0.33 | 0.33 | 9.78 | 0 | 62.5 | 20.64 | 0 | 0
2025-08-14 20:00 | 69.99 | 0 | 0 | 62.27 | 0 | 7.72 | 12.51 | 0 | 0
2025-08-14 21:00 | 65.63 | 0 | 0 | 65.63 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 22:00 | 61.19 | 0 | 0 | 61.19 | 0 | 0 | 12.51 | 0 | 0
2025-08-14 23:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 | 56.18 | 0 | 0 | 56.18 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 01:00 | 53.65 | 0 | 0 | 53.65 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 02:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 03:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 04:00 | 52.22 | 0 | 0 | 52.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 05:00 | 52.59 | 0.43 | 0.43 | 52.17 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 06:00 | 55.69 | 45.74 | 45.74 | 9.95 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 07:00 | 60.01 | 93.33 | 93.33 | 0 | 33.32 | 0 | 44.16 | 0 | 0
2025-08-15 08:00 | 63.24 | 107.21 | 107.21 | 0 | 43.97 | 0 | 85.93 | 0 | 0
2025-08-15 09:00 | 67.74 | 109.66 | 95.8 | 0 | 28.06 | 0 | 112.59 | 13.86 | 0
2025-08-15 10:00 | 73.74 | 110.22 | 73.74 | 0 | 0 | 0 | 112.59 | 36.48 | 0
2025-08-15 11:00 | 78.72 | 105.34 | 78.72 | 0 | 0 | 0 | 112.59 | 26.62 | 0
2025-08-15 12:00 | 83.19 | 103.48 | 83.19 | 0 | 0 | 0 | 112.59 | 20.29 | 0
2025-08-15 13:00 | 88.22 | 107.01 | 88.22 | 0 | 0 | 0 | 112.59 | 18.79 | 0
2025-08-15 14:00 | 91 | 109.73 | 91 | 0 | 0 | 0 | 112.59 | 18.73 | 0
2025-08-15 15:00 | 91.18 | 108.42 | 91.18 | 0 | 0 | 0 | 112.59 | 17.24 | 0
2025-08-15 16:00 | 90.25 | 102.98 | 90.25 | 0 | 0 | 0 | 112.59 | 12.73 | 0
2025-08-15 17:00 | 87.38 | 86.28 | 86.28 | 0 | 0 | 1.1 | 111.43 | 0 | 0
2025-08-15 18:00 | 83.82 | 38.55 | 38.55 | 0 | 0 | 45.27 | 63.78 | 0 | 0
2025-08-15 19:00 | 78.67 | 0.24 | 0.24 | 29.72 | 0 | 48.7 | 12.51 | 0 | 0
2025-08-15 20:00 | 73.03 | 0 | 0 | 73.03 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 21:00 | 69.08 | 0 | 0 | 69.08 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 22:00 | 63.38 | 0 | 0 | 63.38 | 0 | 0 | 12.51 | 0 | 0
2025-08-15 23:00 | 59.16 | 0 | 0 | 59.16 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 | 55.81 | 0 | 0 | 55.81 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 01:00 | 53.41 | 0 | 0 | 53.41 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 02:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 03:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 04:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 05:00 | 53.24 | 0.34 | 0.34 | 52.9 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 06:00 | 55.54 | 44.03 | 44.03 | 11.51 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 07:00 | 58.42 | 93.76 | 93.76 | 0 | 35.34 | 0 | 46.08 | 0 | 0
2025-08-16 08:00 | 61.96 | 104.89 | 104.89 | 0 | 42.93 | 0 | 86.87 | 0 | 0
2025-08-16 09:00 | 67.32 | 110.06 | 94.4 | 0 | 27.08 | 0 | 112.59 | 15.67 | 0
2025-08-16 10:00 | 72.07 | 105.17 | 72.07 | 0 | 0 | 0 | 112.59 | 33.1 | 0
2025-08-16 11:00 | 76.1 | 98.33 | 76.1 | 0 | 0 | 0 | 112.59 | 22.23 | 0
2025-08-16 12:00 | 81.7 | 100.72 | 81.7 | 0 | 0 | 0 | 112.59 | 19.02 | 0
2025-08-16 13:00 | 85.44 | 101.44 | 85.44 | 0 | 0 | 0 | 112.59 | 16 | 0
2025-08-16 14:00 | 88.49 | 102.03 | 88.49 | 0 | 0 | 0 | 112.59 | 13.54 | 0
2025-08-16 15:00 | 87.82 | 94.62 | 87.82 | 0 | 0 | 0 | 112.59 | 6.8 | 0
2025-08-16 16:00 | 86.96 | 87.17 | 86.96 | 0 | 0 | 0 | 112.59 | 0.21 | 0
2025-08-16 17:00 | 84.41 | 74.99 | 74.99 | 0 | 0 | 9.42 | 102.68 | 0 | 0
2025-08-16 18:00 | 81.55 | 33.37 | 33.37 | 0 | 0 | 48.18 | 51.96 | 0 | 0
2025-08-16 19:00 | 77.15 | 0.13 | 0.13 | 39.55 | 0 | 37.47 | 12.51 | 0 | 0
2025-08-16 20:00 | 71.77 | 0 | 0 | 71.77 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 21:00 | 67.16 | 0 | 0 | 67.16 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 22:00 | 61.64 | 0 | 0 | 61.64 | 0 | 0 | 12.51 | 0 | 0
2025-08-16 23:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 01:00 | 52.89 | 0 | 0 | 52.89 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 02:00 | 50.84 | 0 | 0 | 50.84 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 03:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 04:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 05:00 | 52.9 | 0.26 | 0.26 | 52.64 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 06:00 | 55.26 | 40.8 | 40.8 | 14.47 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 07:00 | 58.42 | 85.78 | 85.78 | 0 | 27.36 | 0 | 38.5 | 0 | 0
2025-08-17 08:00 | 61.06 | 101.54 | 101.54 | 0 | 40.48 | 0 | 76.96 | 0 | 0
2025-08-17 09:00 | 64.26 | 108.75 | 101.76 | 0 | 37.51 | 0 | 112.59 | 6.99 | 0
2025-08-17 10:00 | 67.44 | 109.31 | 67.44 | 0 | 0 | 0 | 112.59 | 41.87 | 0
2025-08-17 11:00 | 69.62 | 106.78 | 69.62 | 0 | 0 | 0 | 112.59 | 37.17 | 0
2025-08-17 12:00 | 71.46 | 107.25 | 71.46 | 0 | 0 | 0 | 112.59 | 35.79 | 0
2025-08-17 13:00 | 73.57 | 108.72 | 73.57 | 0 | 0 | 0 | 112.59 | 35.15 | 0
2025-08-17 14:00 | 74.57 | 110.81 | 74.57 | 0 | 0 | 0 | 112.59 | 36.24 | 0
2025-08-17 15:00 | 74.68 | 107.07 | 74.68 | 0 | 0 | 0 | 112.59 | 32.39 | 0
2025-08-17 16:00 | 73.31 | 98.26 | 73.31 | 0 | 0 | 0 | 112.59 | 24.96 | 0
2025-08-17 17:00 | 72.64 | 84.7 | 72.64 | 0 | 0 | 0 | 112.59 | 12.05 | 0
2025-08-17 18:00 | 71.34 | 35.13 | 35.13 | 0 | 0 | 36.21 | 74.48 | 0 | 0
2025-08-17 19:00 | 69.72 | 0 | 0 | 10.85 | 0 | 58.87 | 12.51 | 0 | 0
2025-08-17 20:00 | 66.71 | 0 | 0 | 66.71 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 21:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 22:00 | 61.35 | 0 | 0 | 61.35 | 0 | 0 | 12.51 | 0 | 0
2025-08-17 23:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 | 55.62 | 0 | 0 | 55.62 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 01:00 | 52.35 | 0 | 0 | 52.35 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 02:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 03:00 | 50.73 | 0 | 0 | 50.73 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 04:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 05:00 | 52.72 | 0.07 | 0.07 | 52.65 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 06:00 | 55.68 | 33.84 | 33.84 | 21.84 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 07:00 | 58.03 | 95.61 | 95.61 | 0 | 37.58 | 0 | 48.21 | 0 | 0
2025-08-18 08:00 | 62.01 | 116.35 | 116.35 | 0 | 54.34 | 0 | 99.83 | 0 | 0
2025-08-18 09:00 | 64.48 | 120.73 | 77.91 | 0 | 13.43 | 0 | 112.59 | 42.82 | 0
2025-08-18 10:00 | 68.96 | 99.4 | 68.96 | 0 | 0 | 0 | 112.59 | 30.44 | 0
2025-08-18 11:00 | 70.89 | 100.74 | 70.89 | 0 | 0 | 0 | 112.59 | 29.85 | 0
2025-08-18 12:00 | 73.42 | 77.99 | 73.42 | 0 | 0 | 0 | 112.59 | 4.57 | 0
2025-08-18 13:00 | 74.75 | 21.99 | 21.99 | 0 | 0 | 52.76 | 57.06 | 0 | 0
2025-08-18 14:00 | 77.18 | 91.35 | 91.35 | 0 | 14.17 | 0 | 70.52 | 0 | 0
2025-08-18 15:00 | 76.79 | 78.59 | 78.59 | 0 | 1.8 | 0 | 72.24 | 0 | 0
2025-08-18 16:00 | 76.3 | 113.98 | 113.98 | 0 | 37.69 | 0 | 108.04 | 0 | 0
2025-08-18 17:00 | 76.03 | 95.56 | 80.81 | 0 | 4.79 | 0 | 112.59 | 14.74 | 0
2025-08-18 18:00 | 73.99 | 39.38 | 39.38 | 0 | 0 | 34.6 | 76.16 | 0 | 0
2025-08-18 19:00 | 71.37 | 0.09 | 0.09 | 10.81 | 0 | 60.47 | 12.51 | 0 | 0
2025-08-18 20:00 | 67.55 | 0 | 0 | 67.55 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 21:00 | 64.37 | 0 | 0 | 64.37 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 22:00 | 60.97 | 0 | 0 | 60.97 | 0 | 0 | 12.51 | 0 | 0
2025-08-18 23:00 | 58.19 | 0 | 0 | 58.19 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 | 55.61 | 0 | 0 | 55.61 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 01:00 | 52.97 | 0 | 0 | 52.97 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 02:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 03:00 | 51.43 | 0 | 0 | 51.43 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 04:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 05:00 | 53.2 | 0 | 0 | 53.2 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 06:00 | 55.69 | 6.37 | 6.37 | 49.31 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 07:00 | 58.37 | 29.57 | 29.57 | 28.8 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 08:00 | 60.72 | 75.18 | 75.18 | 0 | 14.46 | 0 | 26.25 | 0 | 0
2025-08-19 09:00 | 62.87 | 70.01 | 70.01 | 0 | 7.15 | 0 | 33.04 | 0 | 0
2025-08-19 10:00 | 65.23 | 73.23 | 73.23 | 0 | 8 | 0 | 40.63 | 0 | 0
2025-08-19 11:00 | 67.73 | 88.45 | 88.45 | 0 | 20.72 | 0 | 60.32 | 0 | 0
2025-08-19 12:00 | 69.91 | 89.1 | 89.1 | 0 | 19.19 | 0 | 78.54 | 0 | 0
2025-08-19 13:00 | 70.44 | 89.57 | 89.57 | 0 | 19.13 | 0 | 96.72 | 0 | 0
2025-08-19 14:00 | 71.13 | 96.25 | 87.84 | 0 | 16.71 | 0 | 112.59 | 8.41 | 0
2025-08-19 15:00 | 71.15 | 67.61 | 67.61 | 0 | 0 | 3.54 | 108.86 | 0 | 0
2025-08-19 16:00 | 70.74 | 86.4 | 74.66 | 0 | 3.92 | 0 | 112.59 | 11.74 | 0
2025-08-19 17:00 | 70.14 | 94.62 | 70.14 | 0 | 0 | 0 | 112.59 | 24.47 | 0
2025-08-19 18:00 | 69.14 | 37.53 | 37.53 | 0 | 0 | 31.62 | 79.31 | 0 | 0
2025-08-19 19:00 | 68.3 | 0 | 0 | 5.8 | 0 | 62.5 | 13.52 | 0 | 0
2025-08-19 20:00 | 65.22 | 0 | 0 | 64.26 | 0 | 0.96 | 12.51 | 0 | 0
2025-08-19 21:00 | 62.88 | 0 | 0 | 62.88 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 22:00 | 59.7 | 0 | 0 | 59.7 | 0 | 0 | 12.51 | 0 | 0
2025-08-19 23:00 | 57.73 | 0 | 0 | 57.73 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 01:00 | 53.55 | 0 | 0 | 53.55 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 02:00 | 51.49 | 0 | 0 | 51.49 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 04:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 05:00 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 06:00 | 55.02 | 27.23 | 27.23 | 27.78 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 07:00 | 57.59 | 60.54 | 60.54 | 0 | 2.95 | 0 | 15.31 | 0 | 0
2025-08-20 08:00 | 60.7 | 72.78 | 72.78 | 0 | 12.08 | 0 | 26.78 | 0 | 0
2025-08-20 09:00 | 64.06 | 82.12 | 82.12 | 0 | 18.06 | 0 | 43.94 | 0 | 0
2025-08-20 10:00 | 66.79 | 92.7 | 92.7 | 0 | 25.91 | 0 | 68.55 | 0 | 0
2025-08-20 11:00 | 69.63 | 94.4 | 94.4 | 0 | 24.77 | 0 | 92.08 | 0 | 0
2025-08-20 12:00 | 72.94 | 96.22 | 94.53 | 0 | 21.59 | 0 | 112.59 | 1.69 | 0
2025-08-20 13:00 | 75.2 | 94.74 | 75.2 | 0 | 0 | 0 | 112.59 | 19.54 | 0
2025-08-20 14:00 | 74.33 | 101.89 | 74.33 | 0 | 0 | 0 | 112.59 | 27.57 | 0
2025-08-20 15:00 | 74.67 | 100.08 | 74.67 | 0 | 0 | 0 | 112.59 | 25.41 | 0
2025-08-20 16:00 | 74.45 | 104.43 | 74.45 | 0 | 0 | 0 | 112.59 | 29.98 | 0
2025-08-20 17:00 | 73.79 | 85.74 | 73.79 | 0 | 0 | 0 | 112.59 | 11.95 | 0
2025-08-20 18:00 | 72.54 | 30.92 | 30.92 | 0 | 0 | 41.62 | 68.78 | 0 | 0
2025-08-20 19:00 | 70.04 | 0 | 0 | 16.58 | 0 | 53.46 | 12.51 | 0 | 0
2025-08-20 20:00 | 67.03 | 0 | 0 | 67.03 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 21:00 | 64.1 | 0 | 0 | 64.1 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 22:00 | 60.29 | 0 | 0 | 60.29 | 0 | 0 | 12.51 | 0 | 0
2025-08-20 23:00 | 57.44 | 0 | 0 | 57.44 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 | 54.87 | 0 | 0 | 54.87 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 01:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 02:00 | 50.75 | 0 | 0 | 50.75 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 03:00 | 50.31 | 0 | 0 | 50.31 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 04:00 | 51.72 | 0 | 0 | 51.72 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 05:00 | 52.82 | 0.18 | 0.18 | 52.64 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 06:00 | 55.19 | 57.49 | 57.49 | 0 | 2.3 | 0 | 14.69 | 0 | 0
2025-08-21 07:00 | 56.84 | 118.97 | 118.97 | 0 | 62.13 | 0 | 73.71 | 0 | 0
2025-08-21 08:00 | 60.42 | 129.4 | 101.34 | 0 | 40.92 | 0 | 112.59 | 28.06 | 0
2025-08-21 09:00 | 65.18 | 130.71 | 65.18 | 0 | 0 | 0 | 112.59 | 65.53 | 0
2025-08-21 10:00 | 67.2 | 128.06 | 67.2 | 0 | 0 | 0 | 112.59 | 60.85 | 0
2025-08-21 11:00 | 72.74 | 124.36 | 72.74 | 0 | 0 | 0 | 112.59 | 51.63 | 0
2025-08-21 12:00 | 74.29 | 122.26 | 74.29 | 0 | 0 | 0 | 112.59 | 47.98 | 0
2025-08-21 13:00 | 78 | 115.29 | 78 | 0 | 0 | 0 | 112.59 | 37.29 | 0
2025-08-21 14:00 | 78.64 | 19.95 | 19.95 | 0 | 0 | 58.69 | 50.81 | 0 | 0
2025-08-21 15:00 | 80.12 | 5.51 | 5.51 | 38.23 | 0 | 36.39 | 12.51 | 0 | 0
2025-08-21 16:00 | 80.69 | 3.66 | 3.66 | 77.03 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 17:00 | 76.44 | 1.77 | 1.77 | 74.67 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 18:00 | 75.55 | 0 | 0 | 75.55 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 19:00 | 71.22 | 0 | 0 | 71.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 20:00 | 68.81 | 0 | 0 | 68.81 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 21:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 22:00 | 61.22 | 0 | 0 | 61.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-21 23:00 | 57.31 | 0 | 0 | 57.31 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 | 55.3 | 0 | 0 | 55.3 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 01:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 02:00 | 51.9 | 0 | 0 | 51.9 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 03:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 04:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 05:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 06:00 | 54.87 | 39.71 | 39.71 | 15.16 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 07:00 | 58.91 | 89.19 | 89.19 | 0 | 30.28 | 0 | 41.28 | 0 | 0
2025-08-22 08:00 | 62.27 | 23.77 | 23.77 | 11.17 | 0 | 27.33 | 12.51 | 0 | 0
2025-08-22 09:00 | 65.43 | 48.49 | 48.49 | 16.94 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 10:00 | 70.16 | 123.87 | 123.87 | 0 | 53.71 | 0 | 63.54 | 0 | 0
2025-08-22 11:00 | 74.51 | 96.28 | 96.28 | 0 | 21.77 | 0 | 84.22 | 0 | 0
2025-08-22 12:00 | 78.99 | 96.27 | 96.27 | 0 | 17.28 | 0 | 100.64 | 0 | 0
2025-08-22 13:00 | 81.43 | 94.9 | 94.02 | 0 | 12.58 | 0 | 112.59 | 0.88 | 0
2025-08-22 14:00 | 83.22 | 71.77 | 71.77 | 0 | 0 | 11.45 | 100.54 | 0 | 0
2025-08-22 15:00 | 83.69 | 9.79 | 9.79 | 11.4 | 0 | 62.5 | 34.75 | 0 | 0
2025-08-22 16:00 | 83.11 | 17.92 | 17.92 | 44.06 | 0 | 21.12 | 12.51 | 0 | 0
2025-08-22 17:00 | 81.87 | 3.88 | 3.88 | 77.99 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 18:00 | 78.23 | 0 | 0 | 78.23 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 19:00 | 74.25 | 0 | 0 | 74.25 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 20:00 | 69.92 | 0 | 0 | 69.92 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 21:00 | 65.55 | 0 | 0 | 65.55 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 22:00 | 60.96 | 0 | 0 | 60.96 | 0 | 0 | 12.51 | 0 | 0
2025-08-22 23:00 | 57.58 | 0 | 0 | 57.58 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 | 55.38 | 0 | 0 | 55.38 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 01:00 | 52.44 | 0 | 0 | 52.44 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 02:00 | 51.56 | 0 | 0 | 51.56 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 03:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 04:00 | 51.5 | 0 | 0 | 51.5 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 05:00 | 52.46 | 0 | 0 | 52.46 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 06:00 | 54.39 | 42.23 | 42.23 | 12.16 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 07:00 | 57.37 | 104.42 | 104.42 | 0 | 47.05 | 0 | 57.21 | 0 | 0
2025-08-23 08:00 | 60.03 | 86.74 | 86.74 | 0 | 26.72 | 0 | 82.59 | 0 | 0
2025-08-23 09:00 | 62.31 | 68.01 | 68.01 | 0 | 5.7 | 0 | 88.01 | 0 | 0
2025-08-23 10:00 | 66.81 | 116.99 | 92.68 | 0 | 25.88 | 0 | 112.59 | 24.31 | 0
2025-08-23 11:00 | 69.14 | 105.25 | 69.14 | 0 | 0 | 0 | 112.59 | 36.11 | 0
2025-08-23 12:00 | 71.07 | 90.29 | 71.07 | 0 | 0 | 0 | 112.59 | 19.23 | 0
2025-08-23 13:00 | 72.38 | 84.26 | 72.38 | 0 | 0 | 0 | 112.59 | 11.88 | 0
2025-08-23 14:00 | 73.14 | 80.67 | 73.14 | 0 | 0 | 0 | 112.59 | 7.53 | 0
2025-08-23 15:00 | 74.33 | 50.83 | 50.83 | 0 | 0 | 23.5 | 87.85 | 0 | 0
2025-08-23 16:00 | 74.68 | 67.71 | 67.71 | 0 | 0 | 6.98 | 80.5 | 0 | 0
2025-08-23 17:00 | 72.97 | 68.41 | 68.41 | 0 | 0 | 4.56 | 75.71 | 0 | 0
2025-08-23 18:00 | 70.53 | 29.35 | 29.35 | 0 | 0 | 41.18 | 32.36 | 0 | 0
2025-08-23 19:00 | 69.13 | 0 | 0 | 50.27 | 0 | 18.86 | 12.51 | 0 | 0
2025-08-23 20:00 | 66.32 | 0 | 0 | 66.32 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 21:00 | 63.8 | 0 | 0 | 63.8 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 22:00 | 60.58 | 0 | 0 | 60.58 | 0 | 0 | 12.51 | 0 | 0
2025-08-23 23:00 | 55.79 | 0 | 0 | 55.79 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 | 54.84 | 0 | 0 | 54.84 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 01:00 | 51.98 | 0 | 0 | 51.98 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 02:00 | 50.44 | 0 | 0 | 50.44 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 03:00 | 50.59 | 0 | 0 | 50.59 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 04:00 | 51.35 | 0 | 0 | 51.35 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 05:00 | 51.66 | 0 | 0 | 51.66 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 06:00 | 54.91 | 40.69 | 40.69 | 14.23 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 07:00 | 57.6 | 99.28 | 99.28 | 0 | 41.68 | 0 | 52.1 | 0 | 0
2025-08-24 08:00 | 60.25 | 112.93 | 112.93 | 0 | 52.67 | 0 | 102.14 | 0 | 0
2025-08-24 09:00 | 62.92 | 115.57 | 73.92 | 0 | 11 | 0 | 112.59 | 41.65 | 0
2025-08-24 10:00 | 65.89 | 112.67 | 65.89 | 0 | 0 | 0 | 112.59 | 46.78 | 0
2025-08-24 11:00 | 69.61 | 109.47 | 69.61 | 0 | 0 | 0 | 112.59 | 39.86 | 0
2025-08-24 12:00 | 70.6 | 105.79 | 70.6 | 0 | 0 | 0 | 112.59 | 35.19 | 0
2025-08-24 13:00 | 73.58 | 107.74 | 73.58 | 0 | 0 | 0 | 112.59 | 34.16 | 0
2025-08-24 14:00 | 74 | 109.88 | 74 | 0 | 0 | 0 | 112.59 | 35.87 | 0
2025-08-24 15:00 | 74.39 | 107.95 | 74.39 | 0 | 0 | 0 | 112.59 | 33.56 | 0
2025-08-24 16:00 | 73.23 | 101.54 | 73.23 | 0 | 0 | 0 | 112.59 | 28.31 | 0
2025-08-24 17:00 | 72.97 | 84.4 | 72.97 | 0 | 0 | 0 | 112.59 | 11.42 | 0
2025-08-24 18:00 | 71.66 | 25.64 | 25.64 | 0 | 0 | 46.02 | 64.15 | 0 | 0
2025-08-24 19:00 | 68.43 | 0 | 0 | 19.37 | 0 | 49.06 | 12.51 | 0 | 0
2025-08-24 20:00 | 66.63 | 0 | 0 | 66.63 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 21:00 | 63.4 | 0 | 0 | 63.4 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 22:00 | 59.91 | 0 | 0 | 59.91 | 0 | 0 | 12.51 | 0 | 0
2025-08-24 23:00 | 57.65 | 0 | 0 | 57.65 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 01:00 | 52.55 | 0 | 0 | 52.55 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 02:00 | 51.89 | 0 | 0 | 51.89 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 03:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 04:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 05:00 | 52.22 | 0 | 0 | 52.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 06:00 | 54.01 | 8.14 | 8.14 | 45.87 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 07:00 | 56.53 | 25.2 | 25.2 | 31.33 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 08:00 | 59.41 | 44.44 | 44.44 | 14.98 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 09:00 | 61.04 | 59 | 59 | 2.04 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 10:00 | 63.78 | 55.38 | 55.38 | 8.4 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 11:00 | 65.98 | 46.07 | 46.07 | 19.91 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 12:00 | 65.94 | 40.17 | 40.17 | 25.76 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 13:00 | 65.96 | 38.68 | 38.68 | 27.27 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 14:00 | 66.3 | 20.43 | 20.43 | 45.87 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 15:00 | 67.47 | 24.53 | 24.53 | 42.94 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 16:00 | 66.94 | 15.38 | 15.38 | 51.57 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 17:00 | 67.07 | 8.02 | 8.02 | 59.04 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 18:00 | 65.7 | 0 | 0 | 65.7 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 19:00 | 65.33 | 0 | 0 | 65.33 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 20:00 | 63.32 | 0 | 0 | 63.32 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 21:00 | 61.08 | 0 | 0 | 61.08 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 22:00 | 58.94 | 0 | 0 | 58.94 | 0 | 0 | 12.51 | 0 | 0
2025-08-25 23:00 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 | 55.45 | 0 | 0 | 55.45 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 01:00 | 52.3 | 0 | 0 | 52.3 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 02:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 03:00 | 50.29 | 0 | 0 | 50.29 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 04:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 05:00 | 52.23 | 0 | 0 | 52.23 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 06:00 | 55.01 | 30.93 | 30.93 | 24.08 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 07:00 | 56.93 | 78.34 | 78.34 | 0 | 21.41 | 0 | 32.85 | 0 | 0
2025-08-26 08:00 | 59.92 | 17.57 | 17.57 | 23.03 | 0 | 19.33 | 12.51 | 0 | 0
2025-08-26 09:00 | 63.8 | 42.46 | 42.46 | 21.34 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 10:00 | 67.32 | 81.44 | 81.44 | 0 | 14.12 | 0 | 25.92 | 0 | 0
2025-08-26 11:00 | 70.99 | 97.95 | 97.95 | 0 | 26.96 | 0 | 51.54 | 0 | 0
2025-08-26 12:00 | 72.98 | 70.36 | 70.36 | 0 | 0 | 2.62 | 48.78 | 0 | 0
2025-08-26 13:00 | 75.14 | 63.73 | 63.73 | 0 | 0 | 11.4 | 36.77 | 0 | 0
2025-08-26 14:00 | 76.44 | 97.88 | 97.88 | 0 | 21.45 | 0 | 57.15 | 0 | 0
2025-08-26 15:00 | 75.93 | 92.38 | 92.38 | 0 | 16.45 | 0 | 72.77 | 0 | 0
2025-08-26 16:00 | 75.6 | 107.22 | 107.22 | 0 | 31.62 | 0 | 102.82 | 0 | 0
2025-08-26 17:00 | 74.27 | 83.94 | 83.94 | 0 | 9.67 | 0 | 112 | 0 | 0
2025-08-26 18:00 | 72.14 | 23.39 | 23.39 | 0 | 0 | 48.74 | 60.69 | 0 | 0
2025-08-26 19:00 | 70.56 | 0 | 0 | 24.79 | 0 | 45.77 | 12.51 | 0 | 0
2025-08-26 20:00 | 67.22 | 0 | 0 | 67.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 21:00 | 63.77 | 0 | 0 | 63.77 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 22:00 | 59.06 | 0 | 0 | 59.06 | 0 | 0 | 12.51 | 0 | 0
2025-08-26 23:00 | 58.22 | 0 | 0 | 58.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 | 53.83 | 0 | 0 | 53.83 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 01:00 | 53.28 | 0 | 0 | 53.28 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 02:00 | 50.22 | 0 | 0 | 50.22 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 03:00 | 50.08 | 0 | 0 | 50.08 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 04:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 05:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 06:00 | 53.73 | 30.22 | 30.22 | 23.51 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 07:00 | 56.29 | 106.58 | 106.58 | 0 | 50.29 | 0 | 60.29 | 0 | 0
2025-08-27 08:00 | 58.97 | 110.94 | 110.94 | 0 | 51.97 | 0 | 109.66 | 0 | 0
2025-08-27 09:00 | 62.92 | 127.06 | 66.01 | 0 | 3.09 | 0 | 112.59 | 61.05 | 0
2025-08-27 10:00 | 65.59 | 119.26 | 65.59 | 0 | 0 | 0 | 112.59 | 53.67 | 0
2025-08-27 11:00 | 68.5 | 7.65 | 7.65 | 0 | 0 | 60.85 | 48.54 | 0 | 0
2025-08-27 12:00 | 69.17 | 119.15 | 119.15 | 0 | 49.98 | 0 | 96.02 | 0 | 0
2025-08-27 13:00 | 71.01 | 120.28 | 88.45 | 0 | 17.44 | 0 | 112.59 | 31.83 | 0
2025-08-27 14:00 | 71.1 | 69.98 | 69.98 | 0 | 0 | 1.12 | 111.41 | 0 | 0
2025-08-27 15:00 | 71.86 | 34.58 | 34.58 | 0 | 0 | 37.28 | 72.17 | 0 | 0
2025-08-27 16:00 | 71.49 | 108.26 | 108.26 | 0 | 36.77 | 0 | 107.1 | 0 | 0
2025-08-27 17:00 | 71.13 | 1.44 | 1.44 | 7.2 | 0 | 62.5 | 41.31 | 0 | 0
2025-08-27 18:00 | 70.02 | 0 | 0 | 42.66 | 0 | 27.36 | 12.51 | 0 | 0
2025-08-27 19:00 | 68.09 | 0 | 0 | 68.09 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 20:00 | 64.81 | 0 | 0 | 64.81 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 21:00 | 63.03 | 0 | 0 | 63.03 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 22:00 | 59.64 | 0 | 0 | 59.64 | 0 | 0 | 12.51 | 0 | 0
2025-08-27 23:00 | 56.67 | 0 | 0 | 56.67 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 | 53.9 | 0 | 0 | 53.9 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 01:00 | 51.9 | 0 | 0 | 51.9 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 02:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 03:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 04:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 05:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 06:00 | 55.47 | 36.39 | 36.39 | 19.09 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 07:00 | 57.54 | 79.22 | 79.22 | 0 | 21.68 | 0 | 33.1 | 0 | 0
2025-08-28 08:00 | 59.54 | 99.28 | 99.28 | 0 | 39.74 | 0 | 70.85 | 0 | 0
2025-08-28 09:00 | 62.91 | 47.38 | 47.38 | 0 | 0 | 15.53 | 54.5 | 0 | 0
2025-08-28 10:00 | 66.01 | 119.02 | 119.02 | 0 | 53.01 | 0 | 104.86 | 0 | 0
2025-08-28 11:00 | 68.97 | 83.28 | 77.1 | 0 | 8.14 | 0 | 112.59 | 6.18 | 0
2025-08-28 12:00 | 70.87 | 85.22 | 70.87 | 0 | 0 | 0 | 112.59 | 14.34 | 0
2025-08-28 13:00 | 73.19 | 48.13 | 48.13 | 0 | 0 | 25.06 | 86.22 | 0 | 0
2025-08-28 14:00 | 74.78 | 61.46 | 61.46 | 0 | 0 | 13.32 | 72.19 | 0 | 0
2025-08-28 15:00 | 73.76 | 120.36 | 116.29 | 0 | 42.52 | 0 | 112.59 | 4.07 | 0
2025-08-28 16:00 | 73.49 | 74.92 | 73.49 | 0 | 0 | 0 | 112.59 | 1.44 | 0
2025-08-28 17:00 | 72.73 | 34.77 | 34.77 | 0 | 0 | 37.96 | 72.64 | 0 | 0
2025-08-28 18:00 | 71 | 0 | 0 | 13.88 | 0 | 57.12 | 12.51 | 0 | 0
2025-08-28 19:00 | 69.89 | 0 | 0 | 69.89 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 20:00 | 66.62 | 0 | 0 | 66.62 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 21:00 | 63.52 | 0 | 0 | 63.52 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 22:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 12.51 | 0 | 0
2025-08-28 23:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 | 53.4 | 0 | 0 | 53.4 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 01:00 | 52.49 | 0 | 0 | 52.49 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 02:00 | 51.04 | 0 | 0 | 51.04 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 03:00 | 50.99 | 0 | 0 | 50.99 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 04:00 | 50.69 | 0 | 0 | 50.69 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 05:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 06:00 | 54.21 | 33.8 | 33.8 | 20.41 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 07:00 | 57.14 | 79.69 | 79.69 | 0 | 22.55 | 0 | 33.93 | 0 | 0
2025-08-29 08:00 | 58.83 | 120.22 | 120.22 | 0 | 61.39 | 0 | 92.25 | 0 | 0
2025-08-29 09:00 | 62.88 | 123.19 | 84.3 | 0 | 21.41 | 0 | 112.59 | 38.89 | 0
2025-08-29 10:00 | 65.32 | 118.77 | 65.32 | 0 | 0 | 0 | 112.59 | 53.45 | 0
2025-08-29 11:00 | 67.29 | 66.29 | 66.29 | 0 | 0 | 1 | 111.54 | 0 | 0
2025-08-29 12:00 | 68.82 | 66.24 | 66.24 | 0 | 0 | 2.58 | 108.82 | 0 | 0
2025-08-29 13:00 | 71.3 | 63.09 | 63.09 | 0 | 0 | 8.21 | 100.17 | 0 | 0
2025-08-29 14:00 | 73.02 | 51.11 | 51.11 | 0 | 0 | 21.91 | 77.11 | 0 | 0
2025-08-29 15:00 | 73.44 | 61.91 | 61.91 | 0 | 0 | 11.53 | 64.97 | 0 | 0
2025-08-29 16:00 | 72.47 | 35.22 | 35.22 | 0 | 0 | 37.25 | 25.76 | 0 | 0
2025-08-29 17:00 | 72.35 | 27.94 | 27.94 | 31.82 | 0 | 12.59 | 12.51 | 0 | 0
2025-08-29 18:00 | 69.84 | 6.98 | 6.98 | 62.86 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 19:00 | 68.3 | 0 | 0 | 68.3 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 20:00 | 65.1 | 0 | 0 | 65.1 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 21:00 | 62.26 | 0 | 0 | 62.26 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 22:00 | 59.23 | 0 | 0 | 59.23 | 0 | 0 | 12.51 | 0 | 0
2025-08-29 23:00 | 55.66 | 0 | 0 | 55.66 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 | 54.76 | 0 | 0 | 54.76 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 01:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 02:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 03:00 | 49.68 | 0 | 0 | 49.68 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 04:00 | 50.62 | 0 | 0 | 50.62 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 05:00 | 52.92 | 0 | 0 | 52.92 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 06:00 | 55.16 | 24.11 | 24.11 | 31.05 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 07:00 | 55.99 | 83.31 | 83.31 | 0 | 27.32 | 0 | 38.46 | 0 | 0
2025-08-30 08:00 | 59.79 | 101.86 | 101.86 | 0 | 42.07 | 0 | 78.43 | 0 | 0
2025-08-30 09:00 | 62.8 | 106.67 | 98.76 | 0 | 35.96 | 0 | 112.59 | 7.91 | 0
2025-08-30 10:00 | 67.16 | 105.28 | 67.16 | 0 | 0 | 0 | 112.59 | 38.13 | 0
2025-08-30 11:00 | 69.9 | 104.1 | 69.9 | 0 | 0 | 0 | 112.59 | 34.2 | 0
2025-08-30 12:00 | 72.09 | 101.73 | 72.09 | 0 | 0 | 0 | 112.59 | 29.64 | 0
2025-08-30 13:00 | 74.48 | 104.41 | 74.48 | 0 | 0 | 0 | 112.59 | 29.93 | 0
2025-08-30 14:00 | 75.47 | 109.77 | 75.47 | 0 | 0 | 0 | 112.59 | 34.3 | 0
2025-08-30 15:00 | 76.95 | 111.25 | 76.95 | 0 | 0 | 0 | 112.59 | 34.3 | 0
2025-08-30 16:00 | 75.98 | 107.5 | 75.98 | 0 | 0 | 0 | 112.59 | 31.51 | 0
2025-08-30 17:00 | 74.77 | 87.22 | 74.77 | 0 | 0 | 0 | 112.59 | 12.44 | 0
2025-08-30 18:00 | 71.08 | 18.3 | 18.3 | 0 | 0 | 52.78 | 57.04 | 0 | 0
2025-08-30 19:00 | 69.73 | 0 | 0 | 27.43 | 0 | 42.3 | 12.51 | 0 | 0
2025-08-30 20:00 | 67.7 | 0 | 0 | 67.7 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 21:00 | 63.98 | 0 | 0 | 63.98 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 22:00 | 59.04 | 0 | 0 | 59.04 | 0 | 0 | 12.51 | 0 | 0
2025-08-30 23:00 | 56.67 | 0 | 0 | 56.67 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 | 53.26 | 0 | 0 | 53.26 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 01:00 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 02:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 03:00 | 49.81 | 0 | 0 | 49.81 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 04:00 | 50.66 | 0 | 0 | 50.66 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 05:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 06:00 | 53.31 | 0 | 0 | 53.31 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 07:00 | 56.25 | 18.63 | 18.63 | 37.61 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 08:00 | 59.19 | 36.53 | 36.53 | 22.67 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 09:00 | 60.26 | 58.13 | 58.13 | 2.13 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 10:00 | 63.22 | 61.47 | 61.47 | 1.74 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 11:00 | 65.69 | 84.31 | 84.31 | 0 | 18.61 | 0 | 30.19 | 0 | 0
2025-08-31 12:00 | 65.8 | 80.85 | 80.85 | 0 | 15.05 | 0 | 44.49 | 0 | 0
2025-08-31 13:00 | 67.55 | 78.76 | 78.76 | 0 | 11.21 | 0 | 55.14 | 0 | 0
2025-08-31 14:00 | 67.98 | 52.85 | 52.85 | 0 | 0 | 15.13 | 39.21 | 0 | 0
2025-08-31 15:00 | 68.97 | 29.01 | 29.01 | 14.59 | 0 | 25.37 | 12.51 | 0 | 0
2025-08-31 16:00 | 67.83 | 28.95 | 28.95 | 38.88 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 17:00 | 67.34 | 5.42 | 5.42 | 61.93 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 18:00 | 66.95 | 0.72 | 0.72 | 66.23 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 19:00 | 64.53 | 0 | 0 | 64.53 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 20:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 21:00 | 61 | 0 | 0 | 61 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 22:00 | 58.7 | 0 | 0 | 58.7 | 0 | 0 | 12.51 | 0 | 0
2025-08-31 23:00 | 56.65 | 0 | 0 | 56.65 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 | 54.07 | 0 | 0 | 54.07 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 01:00 | 51.46 | 0 | 0 | 51.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 03:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 04:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 05:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 06:00 | 53.7 | 9.3 | 9.3 | 44.39 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 07:00 | 56.18 | 12.15 | 12.15 | 44.03 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 08:00 | 58.03 | 35.63 | 35.63 | 22.4 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 09:00 | 62.15 | 63.49 | 63.49 | 0 | 1.34 | 0 | 13.78 | 0 | 0
2025-09-01 10:00 | 63.43 | 70.28 | 70.28 | 0 | 6.85 | 0 | 20.29 | 0 | 0
2025-09-01 11:00 | 66.33 | 69.37 | 69.37 | 0 | 3.04 | 0 | 23.18 | 0 | 0
2025-09-01 12:00 | 67.06 | 73.5 | 73.5 | 0 | 6.44 | 0 | 29.29 | 0 | 0
2025-09-01 13:00 | 68.16 | 70.81 | 70.81 | 0 | 2.65 | 0 | 31.82 | 0 | 0
2025-09-01 14:00 | 69.72 | 55.64 | 55.64 | 0 | 0 | 14.07 | 17 | 0 | 0
2025-09-01 15:00 | 69.82 | 87.64 | 87.64 | 0 | 17.82 | 0 | 33.93 | 0 | 0
2025-09-01 16:00 | 69.22 | 99.96 | 99.96 | 0 | 30.74 | 0 | 63.14 | 0 | 0
2025-09-01 17:00 | 68.85 | 48.13 | 48.13 | 0 | 0 | 20.72 | 41.33 | 0 | 0
2025-09-01 18:00 | 67.23 | 14.3 | 14.3 | 25.55 | 0 | 27.37 | 12.51 | 0 | 0
2025-09-01 19:00 | 65.81 | 0 | 0 | 65.81 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 20:00 | 63.48 | 0 | 0 | 63.48 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 21:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 22:00 | 58.5 | 0 | 0 | 58.5 | 0 | 0 | 12.51 | 0 | 0
2025-09-01 23:00 | 56.95 | 0 | 0 | 56.95 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 | 53.9 | 0 | 0 | 53.9 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 01:00 | 51.83 | 0 | 0 | 51.83 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 02:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 03:00 | 50.05 | 0 | 0 | 50.05 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 04:00 | 50.34 | 0 | 0 | 50.34 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 05:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 06:00 | 54.5 | 27.57 | 27.57 | 26.93 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 07:00 | 56.83 | 96.82 | 96.82 | 0 | 40 | 0 | 50.51 | 0 | 0
2025-09-02 08:00 | 60.97 | 114.8 | 114.8 | 0 | 53.82 | 0 | 101.64 | 0 | 0
2025-09-02 09:00 | 65.53 | 119.21 | 77.05 | 0 | 11.53 | 0 | 112.59 | 42.15 | 0
2025-09-02 10:00 | 70.77 | 115.88 | 70.77 | 0 | 0 | 0 | 112.59 | 45.1 | 0
2025-09-02 11:00 | 75.08 | 111.76 | 75.08 | 0 | 0 | 0 | 112.59 | 36.68 | 0
2025-09-02 12:00 | 80.38 | 103.39 | 80.38 | 0 | 0 | 0 | 112.59 | 23.02 | 0
2025-09-02 13:00 | 82.87 | 53.46 | 53.46 | 0 | 0 | 29.41 | 81.64 | 0 | 0
2025-09-02 14:00 | 85.08 | 111.59 | 111.59 | 0 | 26.51 | 0 | 106.82 | 0 | 0
2025-09-02 15:00 | 85.89 | 64.9 | 64.9 | 0 | 0 | 21 | 84.72 | 0 | 0
2025-09-02 16:00 | 84.54 | 2.35 | 2.35 | 19.69 | 0 | 62.5 | 18.93 | 0 | 0
2025-09-02 17:00 | 82.43 | 0.78 | 0.78 | 75.55 | 0 | 6.1 | 12.51 | 0 | 0
2025-09-02 18:00 | 79.21 | 0 | 0 | 79.21 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 19:00 | 75.7 | 0 | 0 | 75.7 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 20:00 | 70.32 | 0 | 0 | 70.32 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 21:00 | 65.28 | 0 | 0 | 65.28 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 22:00 | 61.65 | 0 | 0 | 61.65 | 0 | 0 | 12.51 | 0 | 0
2025-09-02 23:00 | 57.93 | 0 | 0 | 57.93 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 | 54.24 | 0 | 0 | 54.24 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 01:00 | 51.24 | 0 | 0 | 51.24 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 02:00 | 50.15 | 0 | 0 | 50.15 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 03:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 04:00 | 50.52 | 0 | 0 | 50.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 05:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 06:00 | 53.98 | 24.11 | 24.11 | 29.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 07:00 | 56.55 | 86.88 | 86.88 | 0 | 30.33 | 0 | 41.32 | 0 | 0
2025-09-03 08:00 | 58.43 | 100.83 | 100.83 | 0 | 42.4 | 0 | 81.6 | 0 | 0
2025-09-03 09:00 | 61.5 | 103.78 | 94.13 | 0 | 32.62 | 0 | 112.59 | 9.65 | 0
2025-09-03 10:00 | 64.33 | 107.03 | 64.33 | 0 | 0 | 0 | 112.59 | 42.71 | 0
2025-09-03 11:00 | 65.4 | 101.38 | 65.4 | 0 | 0 | 0 | 112.59 | 35.98 | 0
2025-09-03 12:00 | 67.67 | 99.62 | 67.67 | 0 | 0 | 0 | 112.59 | 31.95 | 0
2025-09-03 13:00 | 68.32 | 98.89 | 68.32 | 0 | 0 | 0 | 112.59 | 30.57 | 0
2025-09-03 14:00 | 69.1 | 103.35 | 69.1 | 0 | 0 | 0 | 112.59 | 34.25 | 0
2025-09-03 15:00 | 69.55 | 100.8 | 69.55 | 0 | 0 | 0 | 112.59 | 31.25 | 0
2025-09-03 16:00 | 69.83 | 90.98 | 69.83 | 0 | 0 | 0 | 112.59 | 21.15 | 0
2025-09-03 17:00 | 68.71 | 68.23 | 68.23 | 0 | 0 | 0.49 | 112.08 | 0 | 0
2025-09-03 18:00 | 67.34 | 9.54 | 9.54 | 0 | 0 | 57.81 | 51.23 | 0 | 0
2025-09-03 19:00 | 66.01 | 0 | 0 | 29.23 | 0 | 36.78 | 12.51 | 0 | 0
2025-09-03 20:00 | 63.29 | 0 | 0 | 63.29 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 21:00 | 61.61 | 0 | 0 | 61.61 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 22:00 | 59.29 | 0 | 0 | 59.29 | 0 | 0 | 12.51 | 0 | 0
2025-09-03 23:00 | 56.01 | 0 | 0 | 56.01 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 | 53.44 | 0 | 0 | 53.44 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 01:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 02:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 03:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 04:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 06:00 | 53.48 | 25.44 | 25.44 | 28.03 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 07:00 | 56.37 | 89.22 | 89.22 | 0 | 32.85 | 0 | 43.72 | 0 | 0
2025-09-04 08:00 | 59.54 | 109.36 | 109.36 | 0 | 49.82 | 0 | 91.05 | 0 | 0
2025-09-04 09:00 | 61.96 | 110.94 | 84.64 | 0 | 22.68 | 0 | 112.59 | 26.3 | 0
2025-09-04 10:00 | 62.99 | 107.6 | 62.99 | 0 | 0 | 0 | 112.59 | 44.61 | 0
2025-09-04 11:00 | 66.61 | 103.09 | 66.61 | 0 | 0 | 0 | 112.59 | 36.49 | 0
2025-09-04 12:00 | 69.43 | 101.58 | 69.43 | 0 | 0 | 0 | 112.59 | 32.15 | 0
2025-09-04 13:00 | 69.78 | 102.57 | 69.78 | 0 | 0 | 0 | 112.59 | 32.79 | 0
2025-09-04 14:00 | 69.69 | 104.55 | 69.69 | 0 | 0 | 0 | 112.59 | 34.86 | 0
2025-09-04 15:00 | 70.68 | 104.85 | 70.68 | 0 | 0 | 0 | 112.59 | 34.17 | 0
2025-09-04 16:00 | 69.63 | 95.95 | 69.63 | 0 | 0 | 0 | 112.59 | 26.32 | 0
2025-09-04 17:00 | 70.09 | 74.41 | 70.09 | 0 | 0 | 0 | 112.59 | 4.32 | 0
2025-09-04 18:00 | 67.67 | 8.92 | 8.92 | 0 | 0 | 58.75 | 50.75 | 0 | 0
2025-09-04 19:00 | 66.36 | 0 | 0 | 30.04 | 0 | 36.33 | 12.51 | 0 | 0
2025-09-04 20:00 | 63.64 | 0 | 0 | 63.64 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 21:00 | 61.2 | 0 | 0 | 61.2 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 22:00 | 59.46 | 0 | 0 | 59.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-04 23:00 | 56.04 | 0 | 0 | 56.04 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 | 53.44 | 0 | 0 | 53.44 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 01:00 | 50.97 | 0 | 0 | 50.97 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 02:00 | 49.29 | 0 | 0 | 49.29 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 03:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 04:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 05:00 | 52.04 | 0 | 0 | 52.04 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 06:00 | 53.44 | 22.76 | 22.76 | 30.68 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 07:00 | 57.51 | 87.82 | 87.82 | 0 | 30.31 | 0 | 41.31 | 0 | 0
2025-09-05 08:00 | 60.09 | 107.42 | 107.42 | 0 | 47.33 | 0 | 86.27 | 0 | 0
2025-09-05 09:00 | 64.6 | 110.1 | 92.3 | 0 | 27.7 | 0 | 112.59 | 17.8 | 0
2025-09-05 10:00 | 68.73 | 107.97 | 68.73 | 0 | 0 | 0 | 112.59 | 39.24 | 0
2025-09-05 11:00 | 74.27 | 104.39 | 74.27 | 0 | 0 | 0 | 112.59 | 30.12 | 0
2025-09-05 12:00 | 78.88 | 101.41 | 78.88 | 0 | 0 | 0 | 112.59 | 22.52 | 0
2025-09-05 13:00 | 80.19 | 103.39 | 80.19 | 0 | 0 | 0 | 112.59 | 23.2 | 0
2025-09-05 14:00 | 82.99 | 105.68 | 82.99 | 0 | 0 | 0 | 112.59 | 22.68 | 0
2025-09-05 15:00 | 84.52 | 104.89 | 84.52 | 0 | 0 | 0 | 112.59 | 20.38 | 0
2025-09-05 16:00 | 82.44 | 97.7 | 82.44 | 0 | 0 | 0 | 112.59 | 15.26 | 0
2025-09-05 17:00 | 81.36 | 76.46 | 76.46 | 0 | 0 | 4.9 | 107.43 | 0 | 0
2025-09-05 18:00 | 78.44 | 7.71 | 7.71 | 8.23 | 0 | 62.5 | 41.64 | 0 | 0
2025-09-05 19:00 | 73.81 | 0 | 0 | 46.14 | 0 | 27.68 | 12.51 | 0 | 0
2025-09-05 20:00 | 69.55 | 0 | 0 | 69.55 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 21:00 | 65.6 | 0 | 0 | 65.6 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 22:00 | 61.42 | 0 | 0 | 61.42 | 0 | 0 | 12.51 | 0 | 0
2025-09-05 23:00 | 56.7 | 0 | 0 | 56.7 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 | 53.46 | 0 | 0 | 53.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 01:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 03:00 | 49.02 | 0 | 0 | 49.02 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 04:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 06:00 | 53.47 | 0.85 | 0.85 | 52.62 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 07:00 | 57.05 | 8.48 | 8.48 | 48.57 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 08:00 | 62.27 | 51.05 | 51.05 | 11.22 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 09:00 | 65.73 | 57.74 | 57.74 | 7.99 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 10:00 | 70.82 | 63.02 | 63.02 | 7.8 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 11:00 | 76.84 | 34.32 | 34.32 | 42.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 12:00 | 81.3 | 53.7 | 53.7 | 27.6 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 13:00 | 85.82 | 39.17 | 39.17 | 46.66 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 14:00 | 87.73 | 113.53 | 113.53 | 0 | 25.79 | 0 | 37.01 | 0 | 0
2025-09-06 15:00 | 88.41 | 109.47 | 109.47 | 0 | 21.06 | 0 | 57.02 | 0 | 0
2025-09-06 16:00 | 86.76 | 98.04 | 98.04 | 0 | 11.28 | 0 | 67.74 | 0 | 0
2025-09-06 17:00 | 84.29 | 42.73 | 42.73 | 0 | 0 | 41.56 | 23.99 | 0 | 0
2025-09-06 18:00 | 80.26 | 1.08 | 1.08 | 68.28 | 0 | 10.91 | 12.51 | 0 | 0
2025-09-06 19:00 | 76.52 | 0 | 0 | 76.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 20:00 | 70.35 | 0 | 0 | 70.35 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 21:00 | 66.41 | 0 | 0 | 66.41 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 22:00 | 61 | 0 | 0 | 61 | 0 | 0 | 12.51 | 0 | 0
2025-09-06 23:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 | 52.8 | 0 | 0 | 52.8 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 01:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 02:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 03:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 04:00 | 50.64 | 0 | 0 | 50.64 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 05:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 06:00 | 53.1 | 14.2 | 14.2 | 38.9 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 07:00 | 55.95 | 64.13 | 64.13 | 0 | 8.18 | 0 | 20.28 | 0 | 0
2025-09-07 08:00 | 58.29 | 77.38 | 77.38 | 0 | 19.09 | 0 | 38.42 | 0 | 0
2025-09-07 09:00 | 61.16 | 83.27 | 83.27 | 0 | 22.12 | 0 | 59.43 | 0 | 0
2025-09-07 10:00 | 63.06 | 75.39 | 75.39 | 0 | 12.33 | 0 | 71.14 | 0 | 0
2025-09-07 11:00 | 66.67 | 79.8 | 79.8 | 0 | 13.13 | 0 | 83.62 | 0 | 0
2025-09-07 12:00 | 67.08 | 95.54 | 95.54 | 0 | 28.45 | 0 | 110.65 | 0 | 0
2025-09-07 13:00 | 69.41 | 95.25 | 71.46 | 0 | 2.05 | 0 | 112.59 | 23.79 | 0
2025-09-07 14:00 | 69.29 | 99.94 | 69.29 | 0 | 0 | 0 | 112.59 | 30.65 | 0
2025-09-07 15:00 | 70.04 | 86.64 | 70.04 | 0 | 0 | 0 | 112.59 | 16.6 | 0
2025-09-07 16:00 | 69.75 | 106.64 | 69.75 | 0 | 0 | 0 | 112.59 | 36.88 | 0
2025-09-07 17:00 | 69.2 | 79.8 | 69.2 | 0 | 0 | 0 | 112.59 | 10.6 | 0
2025-09-07 18:00 | 66.95 | 9.15 | 9.15 | 0 | 0 | 57.8 | 51.74 | 0 | 0
2025-09-07 19:00 | 66.17 | 0 | 0 | 28.9 | 0 | 37.27 | 12.51 | 0 | 0
2025-09-07 20:00 | 64.39 | 0 | 0 | 64.39 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 21:00 | 60.83 | 0 | 0 | 60.83 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 22:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 12.51 | 0 | 0
2025-09-07 23:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 01:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 02:00 | 49.45 | 0 | 0 | 49.45 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 03:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 04:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 06:00 | 54.25 | 1.21 | 1.21 | 53.03 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 07:00 | 55.51 | 2.45 | 2.45 | 53.06 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 08:00 | 58.72 | 19.34 | 19.34 | 39.37 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 09:00 | 61.4 | 71.93 | 71.93 | 0 | 10.53 | 0 | 22.52 | 0 | 0
2025-09-08 10:00 | 64.82 | 101.38 | 101.38 | 0 | 36.55 | 0 | 57.24 | 0 | 0
2025-09-08 11:00 | 66.63 | 111.5 | 111.5 | 0 | 44.87 | 0 | 99.87 | 0 | 0
2025-09-08 12:00 | 70.2 | 100.92 | 83.58 | 0 | 13.39 | 0 | 112.59 | 17.34 | 0
2025-09-08 13:00 | 71.78 | 69.45 | 69.45 | 0 | 0 | 2.34 | 110.13 | 0 | 0
2025-09-08 14:00 | 72.69 | 10.43 | 10.43 | 0 | 0 | 62.26 | 44.59 | 0 | 0
2025-09-08 15:00 | 72.9 | 8.68 | 8.68 | 33.74 | 0 | 30.48 | 12.51 | 0 | 0
2025-09-08 16:00 | 72.28 | 2.34 | 2.34 | 69.93 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 17:00 | 71.99 | 0.75 | 0.75 | 71.23 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 18:00 | 69.27 | 1.49 | 1.49 | 67.78 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 19:00 | 67.77 | 0 | 0 | 67.77 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 20:00 | 65.79 | 0 | 0 | 65.79 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 21:00 | 62.47 | 0 | 0 | 62.47 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 22:00 | 57.9 | 0 | 0 | 57.9 | 0 | 0 | 12.51 | 0 | 0
2025-09-08 23:00 | 55.46 | 0 | 0 | 55.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 | 53.36 | 0 | 0 | 53.36 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 01:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 02:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 03:00 | 49.63 | 0 | 0 | 49.63 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 04:00 | 49.86 | 0 | 0 | 49.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 05:00 | 52.08 | 0 | 0 | 52.08 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 06:00 | 53.02 | 17.02 | 17.02 | 36 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 07:00 | 56.39 | 83.09 | 83.09 | 0 | 26.7 | 0 | 37.87 | 0 | 0
2025-09-09 08:00 | 58.32 | 85.11 | 85.11 | 0 | 26.79 | 0 | 63.32 | 0 | 0
2025-09-09 09:00 | 61.86 | 98.58 | 98.58 | 0 | 36.72 | 0 | 98.2 | 0 | 0
2025-09-09 10:00 | 66.21 | 98.28 | 81.36 | 0 | 15.14 | 0 | 112.59 | 16.92 | 0
2025-09-09 11:00 | 69.68 | 93.14 | 69.68 | 0 | 0 | 0 | 112.59 | 23.46 | 0
2025-09-09 12:00 | 71.52 | 89.32 | 71.52 | 0 | 0 | 0 | 112.59 | 17.8 | 0
2025-09-09 13:00 | 74.22 | 93.94 | 74.22 | 0 | 0 | 0 | 112.59 | 19.72 | 0
2025-09-09 14:00 | 74.92 | 98.28 | 74.92 | 0 | 0 | 0 | 112.59 | 23.36 | 0
2025-09-09 15:00 | 76 | 90.09 | 76 | 0 | 0 | 0 | 112.59 | 14.09 | 0
2025-09-09 16:00 | 76.03 | 87.46 | 76.03 | 0 | 0 | 0 | 112.59 | 11.44 | 0
2025-09-09 17:00 | 73.99 | 54.75 | 54.75 | 0 | 0 | 19.24 | 92.34 | 0 | 0
2025-09-09 18:00 | 71.87 | 3.21 | 3.21 | 6.16 | 0 | 62.5 | 26.55 | 0 | 0
2025-09-09 19:00 | 68.57 | 0 | 0 | 55.23 | 0 | 13.34 | 12.51 | 0 | 0
2025-09-09 20:00 | 65.53 | 0 | 0 | 65.53 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 21:00 | 63.26 | 0 | 0 | 63.26 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 22:00 | 58.99 | 0 | 0 | 58.99 | 0 | 0 | 12.51 | 0 | 0
2025-09-09 23:00 | 55.31 | 0 | 0 | 55.31 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 01:00 | 50.25 | 0 | 0 | 50.25 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 02:00 | 49.26 | 0 | 0 | 49.26 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 03:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 04:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 05:00 | 52 | 0 | 0 | 52 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 06:00 | 53.12 | 14.61 | 14.61 | 38.51 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 07:00 | 56.06 | 61.79 | 61.79 | 0 | 5.73 | 0 | 17.96 | 0 | 0
2025-09-10 08:00 | 59.99 | 89.07 | 89.07 | 0 | 29.08 | 0 | 45.59 | 0 | 0
2025-09-10 09:00 | 62.44 | 91.68 | 91.68 | 0 | 29.24 | 0 | 73.37 | 0 | 0
2025-09-10 10:00 | 68.24 | 87.37 | 87.37 | 0 | 19.12 | 0 | 91.53 | 0 | 0
2025-09-10 11:00 | 72.42 | 96.81 | 94.59 | 0 | 22.17 | 0 | 112.59 | 2.22 | 0
2025-09-10 12:00 | 77.07 | 93.66 | 77.07 | 0 | 0 | 0 | 112.59 | 16.59 | 0
2025-09-10 13:00 | 79.9 | 87.58 | 79.9 | 0 | 0 | 0 | 112.59 | 7.69 | 0
2025-09-10 14:00 | 80.84 | 63.45 | 63.45 | 0 | 0 | 17.39 | 94.29 | 0 | 0
2025-09-10 15:00 | 82.71 | 47.44 | 47.44 | 0 | 0 | 35.28 | 57.16 | 0 | 0
2025-09-10 16:00 | 81.27 | 16.67 | 16.67 | 22.18 | 0 | 42.41 | 12.51 | 0 | 0
2025-09-10 17:00 | 78.96 | 0.2 | 0.2 | 78.76 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 18:00 | 76.42 | 0.24 | 0.24 | 76.18 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 19:00 | 72.35 | 0 | 0 | 72.35 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 20:00 | 68.91 | 0 | 0 | 68.91 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 21:00 | 63.94 | 0 | 0 | 63.94 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 22:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 12.51 | 0 | 0
2025-09-10 23:00 | 56.52 | 0 | 0 | 56.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 01:00 | 51.28 | 0 | 0 | 51.28 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 02:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 03:00 | 49.55 | 0 | 0 | 49.55 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 04:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 05:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 06:00 | 52.75 | 8.89 | 8.89 | 43.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 07:00 | 55.2 | 91.62 | 91.62 | 0 | 36.42 | 0 | 47.11 | 0 | 0
2025-09-11 08:00 | 58.71 | 86.72 | 86.72 | 0 | 28.01 | 0 | 73.72 | 0 | 0
2025-09-11 09:00 | 61.38 | 63.38 | 63.38 | 0 | 2.01 | 0 | 75.63 | 0 | 0
2025-09-11 10:00 | 63.13 | 70.5 | 70.5 | 0 | 7.37 | 0 | 82.63 | 0 | 0
2025-09-11 11:00 | 65.17 | 80.74 | 80.74 | 0 | 15.57 | 0 | 97.42 | 0 | 0
2025-09-11 12:00 | 67.97 | 72.33 | 72.33 | 0 | 4.36 | 0 | 101.56 | 0 | 0
2025-09-11 13:00 | 68.98 | 82.42 | 80.59 | 0 | 11.61 | 0 | 112.59 | 1.83 | 0
2025-09-11 14:00 | 69.56 | 78.67 | 69.56 | 0 | 0 | 0 | 112.59 | 9.11 | 0
2025-09-11 15:00 | 69.52 | 72.18 | 69.52 | 0 | 0 | 0 | 112.59 | 2.67 | 0
2025-09-11 16:00 | 69.57 | 35.72 | 35.72 | 0 | 0 | 33.85 | 76.96 | 0 | 0
2025-09-11 17:00 | 68.57 | 11.91 | 11.91 | 0 | 0 | 56.67 | 17.31 | 0 | 0
2025-09-11 18:00 | 66.9 | 0.84 | 0.84 | 61.5 | 0 | 4.56 | 12.51 | 0 | 0
2025-09-11 19:00 | 65.46 | 0 | 0 | 65.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 20:00 | 63.27 | 0 | 0 | 63.27 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 21:00 | 60.38 | 0 | 0 | 60.38 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 22:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 12.51 | 0 | 0
2025-09-11 23:00 | 55.83 | 0 | 0 | 55.83 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 01:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 02:00 | 49.95 | 0 | 0 | 49.95 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 03:00 | 49.19 | 0 | 0 | 49.19 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 04:00 | 48.96 | 0 | 0 | 48.96 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 05:00 | 51.14 | 0 | 0 | 51.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 06:00 | 52.82 | 13.19 | 13.19 | 39.63 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 07:00 | 56.56 | 85.9 | 85.9 | 0 | 29.34 | 0 | 40.38 | 0 | 0
2025-09-12 08:00 | 58.89 | 105.5 | 105.5 | 0 | 46.62 | 0 | 84.67 | 0 | 0
2025-09-12 09:00 | 61.59 | 105.4 | 90.98 | 0 | 29.39 | 0 | 112.59 | 14.42 | 0
2025-09-12 10:00 | 64.39 | 94.96 | 64.39 | 0 | 0 | 0 | 112.59 | 30.56 | 0
2025-09-12 11:00 | 67.15 | 92.63 | 67.15 | 0 | 0 | 0 | 112.59 | 25.48 | 0
2025-09-12 12:00 | 68.94 | 92.33 | 68.94 | 0 | 0 | 0 | 112.59 | 23.39 | 0
2025-09-12 13:00 | 70.38 | 95.38 | 70.38 | 0 | 0 | 0 | 112.59 | 25 | 0
2025-09-12 14:00 | 71.95 | 96.77 | 71.95 | 0 | 0 | 0 | 112.59 | 24.83 | 0
2025-09-12 15:00 | 72.74 | 99.01 | 72.74 | 0 | 0 | 0 | 112.59 | 26.27 | 0
2025-09-12 16:00 | 71.33 | 92.01 | 71.33 | 0 | 0 | 0 | 112.59 | 20.68 | 0
2025-09-12 17:00 | 70.98 | 56.97 | 56.97 | 0 | 0 | 14.01 | 97.85 | 0 | 0
2025-09-12 18:00 | 69.32 | 1.58 | 1.58 | 5.24 | 0 | 62.5 | 32.06 | 0 | 0
2025-09-12 19:00 | 66.96 | 0 | 0 | 48.39 | 0 | 18.57 | 12.51 | 0 | 0
2025-09-12 20:00 | 63.94 | 0 | 0 | 63.94 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 21:00 | 61.06 | 0 | 0 | 61.06 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 22:00 | 59.02 | 0 | 0 | 59.02 | 0 | 0 | 12.51 | 0 | 0
2025-09-12 23:00 | 55.59 | 0 | 0 | 55.59 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 01:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 02:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 03:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 04:00 | 49.09 | 0 | 0 | 49.09 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 05:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 06:00 | 52.52 | 5.94 | 5.94 | 46.57 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 07:00 | 54.86 | 3.52 | 3.52 | 51.34 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 08:00 | 58.61 | 12.02 | 12.02 | 46.59 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 09:00 | 62.26 | 31.91 | 31.91 | 30.34 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 10:00 | 64.89 | 47.53 | 47.53 | 17.36 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 11:00 | 69.39 | 51.23 | 51.23 | 18.16 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 12:00 | 72.96 | 80.68 | 80.68 | 0 | 7.73 | 0 | 19.85 | 0 | 0
2025-09-13 13:00 | 75.19 | 74.77 | 74.77 | 0 | 0 | 0.42 | 19.41 | 0 | 0
2025-09-13 14:00 | 77.64 | 85.94 | 85.94 | 0 | 8.31 | 0 | 27.3 | 0 | 0
2025-09-13 15:00 | 77.68 | 116.18 | 116.18 | 0 | 38.5 | 0 | 63.88 | 0 | 0
2025-09-13 16:00 | 77.24 | 113.73 | 113.73 | 0 | 36.49 | 0 | 98.54 | 0 | 0
2025-09-13 17:00 | 76.36 | 70.59 | 70.59 | 0 | 0 | 5.77 | 92.46 | 0 | 0
2025-09-13 18:00 | 72.9 | 1.35 | 1.35 | 9.06 | 0 | 62.5 | 26.67 | 0 | 0
2025-09-13 19:00 | 69.49 | 0 | 0 | 56.04 | 0 | 13.45 | 12.51 | 0 | 0
2025-09-13 20:00 | 66.36 | 0 | 0 | 66.36 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 21:00 | 61.92 | 0 | 0 | 61.92 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 22:00 | 58.68 | 0 | 0 | 58.68 | 0 | 0 | 12.51 | 0 | 0
2025-09-13 23:00 | 55.09 | 0 | 0 | 55.09 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 01:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 02:00 | 49.03 | 0 | 0 | 49.03 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 03:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 04:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 05:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 06:00 | 51.85 | 6.99 | 6.99 | 44.85 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 07:00 | 54.61 | 66.16 | 66.16 | 0 | 11.55 | 0 | 23.48 | 0 | 0
2025-09-14 08:00 | 57.83 | 64.43 | 64.43 | 0 | 6.61 | 0 | 29.76 | 0 | 0
2025-09-14 09:00 | 61.85 | 112.56 | 112.56 | 0 | 50.71 | 0 | 77.93 | 0 | 0
2025-09-14 10:00 | 65.19 | 85.38 | 85.38 | 0 | 20.19 | 0 | 97.11 | 0 | 0
2025-09-14 11:00 | 68.88 | 47.66 | 47.66 | 0 | 0 | 21.22 | 74.77 | 0 | 0
2025-09-14 12:00 | 71.57 | 54 | 54 | 0 | 0 | 17.57 | 56.27 | 0 | 0
2025-09-14 13:00 | 73.94 | 37.34 | 37.34 | 0 | 0 | 36.61 | 17.74 | 0 | 0
2025-09-14 14:00 | 75.11 | 37.44 | 37.44 | 32.7 | 0 | 4.97 | 12.51 | 0 | 0
2025-09-14 15:00 | 75.39 | 35.46 | 35.46 | 39.93 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 16:00 | 75.36 | 75.48 | 75.48 | 0 | 0.12 | 0 | 12.63 | 0 | 0
2025-09-14 17:00 | 73.86 | 43.27 | 43.27 | 30.48 | 0 | 0.11 | 12.51 | 0 | 0
2025-09-14 18:00 | 71.38 | 1 | 1 | 70.38 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 19:00 | 68.98 | 0 | 0 | 68.98 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 20:00 | 63.91 | 0 | 0 | 63.91 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 21:00 | 61.5 | 0 | 0 | 61.5 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 22:00 | 58.12 | 0 | 0 | 58.12 | 0 | 0 | 12.51 | 0 | 0
2025-09-14 23:00 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 | 53.16 | 0 | 0 | 53.16 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 01:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 02:00 | 49.98 | 0 | 0 | 49.98 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 03:00 | 48.27 | 0 | 0 | 48.27 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 04:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 05:00 | 50.36 | 0 | 0 | 50.36 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 06:00 | 52.22 | 13.78 | 13.78 | 38.44 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 07:00 | 54.04 | 88.49 | 88.49 | 0 | 34.45 | 0 | 45.24 | 0 | 0
2025-09-15 08:00 | 57.95 | 108.03 | 108.03 | 0 | 50.08 | 0 | 92.81 | 0 | 0
2025-09-15 09:00 | 60.92 | 111.73 | 81.74 | 0 | 20.82 | 0 | 112.59 | 29.98 | 0
2025-09-15 10:00 | 64.01 | 107.36 | 64.01 | 0 | 0 | 0 | 112.59 | 43.34 | 0
2025-09-15 11:00 | 65.92 | 102.52 | 65.92 | 0 | 0 | 0 | 112.59 | 36.6 | 0
2025-09-15 12:00 | 68.36 | 100.36 | 68.36 | 0 | 0 | 0 | 112.59 | 32 | 0
2025-09-15 13:00 | 70.06 | 103.28 | 70.06 | 0 | 0 | 0 | 112.59 | 33.22 | 0
2025-09-15 14:00 | 71.97 | 105.83 | 71.97 | 0 | 0 | 0 | 112.59 | 33.86 | 0
2025-09-15 15:00 | 70.07 | 52.43 | 52.43 | 0 | 0 | 17.64 | 94.02 | 0 | 0
2025-09-15 16:00 | 70.65 | 8.44 | 8.44 | 0 | 0 | 62.21 | 28.54 | 0 | 0
2025-09-15 17:00 | 70.08 | 0.03 | 0.03 | 54.82 | 0 | 15.23 | 12.51 | 0 | 0
2025-09-15 18:00 | 67.84 | 0 | 0 | 67.84 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 19:00 | 66.01 | 0 | 0 | 66.01 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 20:00 | 63.42 | 0 | 0 | 63.42 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 21:00 | 60.26 | 0 | 0 | 60.26 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 22:00 | 57.66 | 0 | 0 | 57.66 | 0 | 0 | 12.51 | 0 | 0
2025-09-15 23:00 | 55.14 | 0 | 0 | 55.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 01:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 02:00 | 49.08 | 0 | 0 | 49.08 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 03:00 | 48.75 | 0 | 0 | 48.75 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 04:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 05:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 06:00 | 52.05 | 2.17 | 2.17 | 49.89 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 07:00 | 55.38 | 1.7 | 1.7 | 53.69 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 08:00 | 57.91 | 36.39 | 36.39 | 21.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 09:00 | 61.26 | 32.29 | 32.29 | 28.97 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 10:00 | 63.21 | 59.74 | 59.74 | 3.47 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 11:00 | 66.34 | 58.98 | 58.98 | 7.36 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 12:00 | 68.31 | 52.3 | 52.3 | 16.01 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 13:00 | 70.41 | 58.51 | 58.51 | 11.9 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 14:00 | 72.54 | 64.73 | 64.73 | 7.81 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 15:00 | 73.05 | 107.2 | 107.2 | 0 | 34.16 | 0 | 44.96 | 0 | 0
2025-09-16 16:00 | 71.34 | 103.44 | 103.44 | 0 | 32.1 | 0 | 75.46 | 0 | 0
2025-09-16 17:00 | 70.53 | 59.11 | 59.11 | 0 | 0 | 11.42 | 63.43 | 0 | 0
2025-09-16 18:00 | 68.89 | 1.21 | 1.21 | 19.31 | 0 | 48.38 | 12.51 | 0 | 0
2025-09-16 19:00 | 66.82 | 0 | 0 | 66.82 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 20:00 | 62.83 | 0 | 0 | 62.83 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 21:00 | 59.87 | 0 | 0 | 59.87 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 22:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-16 23:00 | 53.78 | 0 | 0 | 53.78 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 01:00 | 50.31 | 0 | 0 | 50.31 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 02:00 | 49.27 | 0 | 0 | 49.27 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 03:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 04:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 05:00 | 50.66 | 0 | 0 | 50.66 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 06:00 | 52.18 | 2 | 2 | 50.18 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 07:00 | 53.95 | 79.82 | 79.82 | 0 | 25.86 | 0 | 37.08 | 0 | 0
2025-09-17 08:00 | 56.74 | 55.29 | 55.29 | 0 | 0 | 1.45 | 35.55 | 0 | 0
2025-09-17 09:00 | 59.35 | 19.2 | 19.2 | 18.26 | 0 | 21.89 | 12.51 | 0 | 0
2025-09-17 10:00 | 62.25 | 56.33 | 56.33 | 5.92 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 11:00 | 63.69 | 20.16 | 20.16 | 43.53 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 12:00 | 65.4 | 27.89 | 27.89 | 37.51 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 13:00 | 65.56 | 37.07 | 37.07 | 28.49 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 14:00 | 66.23 | 85.52 | 85.52 | 0 | 19.29 | 0 | 30.83 | 0 | 0
2025-09-17 15:00 | 66.58 | 65.97 | 65.97 | 0 | 0 | 0.61 | 30.19 | 0 | 0
2025-09-17 16:00 | 66.42 | 26.07 | 26.07 | 23.56 | 0 | 16.79 | 12.51 | 0 | 0
2025-09-17 17:00 | 65.36 | 9.98 | 9.98 | 55.38 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 18:00 | 65.43 | 0 | 0 | 65.43 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 19:00 | 63.74 | 0 | 0 | 63.74 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 20:00 | 61.24 | 0 | 0 | 61.24 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 21:00 | 59.48 | 0 | 0 | 59.48 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 22:00 | 56.84 | 0 | 0 | 56.84 | 0 | 0 | 12.51 | 0 | 0
2025-09-17 23:00 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 01:00 | 50.07 | 0 | 0 | 50.07 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 02:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 03:00 | 48.86 | 0 | 0 | 48.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 04:00 | 48.64 | 0 | 0 | 48.64 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 05:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 06:00 | 51.48 | 0.68 | 0.68 | 50.8 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 07:00 | 54.41 | 3.53 | 3.53 | 50.88 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 08:00 | 57.27 | 17.23 | 17.23 | 40.05 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 09:00 | 61.05 | 65.54 | 65.54 | 0 | 4.49 | 0 | 16.78 | 0 | 0
2025-09-18 10:00 | 63.43 | 51.69 | 51.69 | 7.69 | 0 | 4.05 | 12.51 | 0 | 0
2025-09-18 11:00 | 65.89 | 81.04 | 81.04 | 0 | 15.16 | 0 | 26.91 | 0 | 0
2025-09-18 12:00 | 68.13 | 27.86 | 27.86 | 26.59 | 0 | 13.68 | 12.51 | 0 | 0
2025-09-18 13:00 | 70.45 | 20.76 | 20.76 | 49.68 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 14:00 | 70.69 | 38.88 | 38.88 | 31.81 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 15:00 | 71.29 | 3.41 | 3.41 | 67.88 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 16:00 | 70.44 | 14.17 | 14.17 | 56.28 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 17:00 | 70.6 | 11.46 | 11.46 | 59.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 18:00 | 68.34 | 0 | 0 | 68.34 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 19:00 | 65.49 | 0 | 0 | 65.49 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 20:00 | 63.09 | 0 | 0 | 63.09 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 21:00 | 60.46 | 0 | 0 | 60.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 22:00 | 57.11 | 0 | 0 | 57.11 | 0 | 0 | 12.51 | 0 | 0
2025-09-18 23:00 | 54.18 | 0 | 0 | 54.18 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 | 51.56 | 0 | 0 | 51.56 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 01:00 | 50.19 | 0 | 0 | 50.19 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 02:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 03:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 04:00 | 48.18 | 0 | 0 | 48.18 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 05:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 06:00 | 51.8 | 4.81 | 4.81 | 46.98 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 07:00 | 54.13 | 69.84 | 69.84 | 0 | 15.71 | 0 | 27.43 | 0 | 0
2025-09-19 08:00 | 57.16 | 80.36 | 80.36 | 0 | 23.19 | 0 | 49.46 | 0 | 0
2025-09-19 09:00 | 60.37 | 84.17 | 84.17 | 0 | 23.8 | 0 | 72.07 | 0 | 0
2025-09-19 10:00 | 63.25 | 93.04 | 93.04 | 0 | 29.8 | 0 | 100.38 | 0 | 0
2025-09-19 11:00 | 65.84 | 94.36 | 78.69 | 0 | 12.85 | 0 | 112.59 | 15.67 | 0
2025-09-19 12:00 | 67.71 | 77.63 | 67.71 | 0 | 0 | 0 | 112.59 | 9.93 | 0
2025-09-19 13:00 | 69.26 | 76.04 | 69.26 | 0 | 0 | 0 | 112.59 | 6.77 | 0
2025-09-19 14:00 | 70.1 | 62.65 | 62.65 | 0 | 0 | 7.45 | 104.74 | 0 | 0
2025-09-19 15:00 | 70.69 | 52.74 | 52.74 | 0 | 0 | 17.95 | 85.85 | 0 | 0
2025-09-19 16:00 | 70.63 | 31.13 | 31.13 | 0 | 0 | 39.5 | 44.28 | 0 | 0
2025-09-19 17:00 | 69.15 | 3.71 | 3.71 | 35.27 | 0 | 30.18 | 12.51 | 0 | 0
2025-09-19 18:00 | 67.87 | 0 | 0 | 67.87 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 19:00 | 65.08 | 0 | 0 | 65.08 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 20:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 21:00 | 60.41 | 0 | 0 | 60.41 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 22:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 12.51 | 0 | 0
2025-09-19 23:00 | 53.87 | 0 | 0 | 53.87 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 | 51.26 | 0 | 0 | 51.26 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 02:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 03:00 | 48.14 | 0 | 0 | 48.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 04:00 | 48.63 | 0 | 0 | 48.63 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 05:00 | 50.45 | 0 | 0 | 50.45 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 06:00 | 50.9 | 1.89 | 1.89 | 49.01 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 07:00 | 55.26 | 37.72 | 37.72 | 17.54 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 08:00 | 58.41 | 52.02 | 52.02 | 6.39 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 09:00 | 58.99 | 56.89 | 56.89 | 2.1 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 10:00 | 63.48 | 50.64 | 50.64 | 12.85 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 11:00 | 66.17 | 31.02 | 31.02 | 35.15 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 12:00 | 69 | 31.14 | 31.14 | 37.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 13:00 | 70.93 | 39.58 | 39.58 | 31.35 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 14:00 | 72.82 | 24.83 | 24.83 | 47.98 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 15:00 | 72.79 | 20.76 | 20.76 | 52.02 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 16:00 | 71.95 | 7.37 | 7.37 | 64.58 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 17:00 | 71.05 | 0.02 | 0.02 | 71.03 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 18:00 | 69.39 | 0 | 0 | 69.39 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 19:00 | 65.94 | 0 | 0 | 65.94 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 20:00 | 62.71 | 0 | 0 | 62.71 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 21:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 22:00 | 56.87 | 0 | 0 | 56.87 | 0 | 0 | 12.51 | 0 | 0
2025-09-20 23:00 | 54.21 | 0 | 0 | 54.21 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 01:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 02:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 03:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 04:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 05:00 | 49.09 | 0 | 0 | 49.09 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 06:00 | 51.4 | 4.9 | 4.9 | 46.5 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 07:00 | 53.79 | 84.62 | 84.62 | 0 | 30.83 | 0 | 41.8 | 0 | 0
2025-09-21 08:00 | 55.71 | 108.55 | 108.55 | 0 | 52.84 | 0 | 92 | 0 | 0
2025-09-21 09:00 | 59.74 | 111.65 | 81.41 | 0 | 21.67 | 0 | 112.59 | 30.24 | 0
2025-09-21 10:00 | 61.47 | 86.61 | 61.47 | 0 | 0 | 0 | 112.59 | 25.14 | 0
2025-09-21 11:00 | 65.19 | 86.7 | 65.19 | 0 | 0 | 0 | 112.59 | 21.51 | 0
2025-09-21 12:00 | 67.38 | 78.3 | 67.38 | 0 | 0 | 0 | 112.59 | 10.92 | 0
2025-09-21 13:00 | 67.87 | 74.34 | 67.87 | 0 | 0 | 0 | 112.59 | 6.46 | 0
2025-09-21 14:00 | 69.16 | 38.15 | 38.15 | 0 | 0 | 31.01 | 79.95 | 0 | 0
2025-09-21 15:00 | 68.64 | 18.71 | 18.71 | 0 | 0 | 49.94 | 27.38 | 0 | 0
2025-09-21 16:00 | 69.25 | 13.4 | 13.4 | 41.73 | 0 | 14.13 | 12.51 | 0 | 0
2025-09-21 17:00 | 67.75 | 0 | 0 | 67.75 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 18:00 | 65.93 | 0 | 0 | 65.93 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 19:00 | 64.3 | 0 | 0 | 64.3 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 20:00 | 61.78 | 0 | 0 | 61.78 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 21:00 | 59.17 | 0 | 0 | 59.17 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 22:00 | 57.04 | 0 | 0 | 57.04 | 0 | 0 | 12.51 | 0 | 0
2025-09-21 23:00 | 53.53 | 0 | 0 | 53.53 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 01:00 | 49.02 | 0 | 0 | 49.02 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 02:00 | 49.32 | 0 | 0 | 49.32 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 03:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 04:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 05:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 06:00 | 51.39 | 0.08 | 0.08 | 51.31 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 07:00 | 54.45 | 1.67 | 1.67 | 52.78 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 08:00 | 57.74 | 10.92 | 10.92 | 46.82 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 09:00 | 60.81 | 13.96 | 13.96 | 46.85 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 10:00 | 63.31 | 45.95 | 45.95 | 17.36 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 11:00 | 66.73 | 68.94 | 68.94 | 0 | 2.22 | 0 | 14.62 | 0 | 0
2025-09-22 12:00 | 68.97 | 80.77 | 80.77 | 0 | 11.8 | 0 | 25.83 | 0 | 0
2025-09-22 13:00 | 70.99 | 98.68 | 98.68 | 0 | 27.68 | 0 | 52.12 | 0 | 0
2025-09-22 14:00 | 72.26 | 56.19 | 56.19 | 0 | 0 | 16.07 | 35.21 | 0 | 0
2025-09-22 15:00 | 73.08 | 37.66 | 37.66 | 13.87 | 0 | 21.56 | 12.51 | 0 | 0
2025-09-22 16:00 | 72.96 | 27.06 | 27.06 | 45.9 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 17:00 | 70.53 | 19.96 | 19.96 | 50.58 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 18:00 | 69.34 | 0 | 0 | 69.34 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 19:00 | 67.39 | 0 | 0 | 67.39 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 20:00 | 64.07 | 0 | 0 | 64.07 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 21:00 | 59.92 | 0 | 0 | 59.92 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 22:00 | 56.29 | 0 | 0 | 56.29 | 0 | 0 | 12.51 | 0 | 0
2025-09-22 23:00 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 02:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 03:00 | 48.92 | 0 | 0 | 48.92 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 04:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 05:00 | 50.03 | 0 | 0 | 50.03 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 06:00 | 51.42 | 3.23 | 3.23 | 48.2 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 07:00 | 53.87 | 37.52 | 37.52 | 16.35 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 08:00 | 56.44 | 70.44 | 70.44 | 0 | 13.99 | 0 | 25.8 | 0 | 0
2025-09-23 09:00 | 60.88 | 86.04 | 86.04 | 0 | 25.16 | 0 | 49.7 | 0 | 0
2025-09-23 10:00 | 64.52 | 89.14 | 89.14 | 0 | 24.62 | 0 | 73.1 | 0 | 0
2025-09-23 11:00 | 68.55 | 92.03 | 92.03 | 0 | 23.48 | 0 | 95.4 | 0 | 0
2025-09-23 12:00 | 71.25 | 90.28 | 89.34 | 0 | 18.09 | 0 | 112.59 | 0.94 | 0
2025-09-23 13:00 | 72.88 | 87.62 | 72.88 | 0 | 0 | 0 | 112.59 | 14.74 | 0
2025-09-23 14:00 | 74.23 | 89.98 | 74.23 | 0 | 0 | 0 | 112.59 | 15.75 | 0
2025-09-23 15:00 | 74.58 | 82.45 | 74.58 | 0 | 0 | 0 | 112.59 | 7.87 | 0
2025-09-23 16:00 | 75.46 | 66.38 | 66.38 | 0 | 0 | 9.08 | 103.03 | 0 | 0
2025-09-23 17:00 | 72.78 | 18.77 | 18.77 | 0 | 0 | 54.02 | 46.17 | 0 | 0
2025-09-23 18:00 | 71.49 | 0 | 0 | 39.51 | 0 | 31.98 | 12.51 | 0 | 0
2025-09-23 19:00 | 67.92 | 0 | 0 | 67.92 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 20:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 21:00 | 60.43 | 0 | 0 | 60.43 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 22:00 | 57.46 | 0 | 0 | 57.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-23 23:00 | 54.03 | 0 | 0 | 54.03 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 01:00 | 49.78 | 0 | 0 | 49.78 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 02:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 03:00 | 47.5 | 0 | 0 | 47.5 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 04:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 05:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 06:00 | 51.51 | 1.68 | 1.68 | 49.83 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 07:00 | 53.43 | 24.19 | 24.19 | 29.24 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 08:00 | 55.86 | 59.81 | 59.81 | 0 | 3.95 | 0 | 16.26 | 0 | 0
2025-09-24 09:00 | 60.37 | 87.49 | 87.49 | 0 | 27.12 | 0 | 42.02 | 0 | 0
2025-09-24 10:00 | 63.33 | 95.03 | 95.03 | 0 | 31.7 | 0 | 72.14 | 0 | 0
2025-09-24 11:00 | 65.87 | 81.53 | 81.53 | 0 | 15.66 | 0 | 87.02 | 0 | 0
2025-09-24 12:00 | 67.71 | 78.54 | 78.54 | 0 | 10.83 | 0 | 97.31 | 0 | 0
2025-09-24 13:00 | 69.66 | 91.04 | 85.75 | 0 | 16.08 | 0 | 112.59 | 5.3 | 0
2025-09-24 14:00 | 71.71 | 92.12 | 71.71 | 0 | 0 | 0 | 112.59 | 20.41 | 0
2025-09-24 15:00 | 71.25 | 68.22 | 68.22 | 0 | 0 | 3.03 | 109.4 | 0 | 0
2025-09-24 16:00 | 70.7 | 48.26 | 48.26 | 0 | 0 | 22.44 | 85.78 | 0 | 0
2025-09-24 17:00 | 70.75 | 11.91 | 11.91 | 0 | 0 | 58.84 | 23.84 | 0 | 0
2025-09-24 18:00 | 67.88 | 0 | 0 | 57.12 | 0 | 10.76 | 12.51 | 0 | 0
2025-09-24 19:00 | 66.31 | 0 | 0 | 66.31 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 20:00 | 61.86 | 0 | 0 | 61.86 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 21:00 | 59.76 | 0 | 0 | 59.76 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 22:00 | 57.5 | 0 | 0 | 57.5 | 0 | 0 | 12.51 | 0 | 0
2025-09-24 23:00 | 53.68 | 0 | 0 | 53.68 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 01:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 02:00 | 48.71 | 0 | 0 | 48.71 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 03:00 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 04:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 05:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 06:00 | 51.92 | 1.95 | 1.95 | 49.98 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 07:00 | 54.14 | 28.47 | 28.47 | 25.67 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 08:00 | 56.39 | 43.44 | 43.44 | 12.95 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 09:00 | 58.93 | 57.82 | 57.82 | 1.11 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 10:00 | 63.43 | 77.58 | 77.58 | 0 | 14.15 | 0 | 25.95 | 0 | 0
2025-09-25 11:00 | 65.46 | 76.12 | 76.12 | 0 | 10.66 | 0 | 36.08 | 0 | 0
2025-09-25 12:00 | 67.68 | 68.38 | 68.38 | 0 | 0.7 | 0 | 36.74 | 0 | 0
2025-09-25 13:00 | 69.36 | 82.01 | 82.01 | 0 | 12.64 | 0 | 48.75 | 0 | 0
2025-09-25 14:00 | 71.19 | 98.44 | 98.44 | 0 | 27.25 | 0 | 74.64 | 0 | 0
2025-09-25 15:00 | 71.22 | 96.93 | 96.93 | 0 | 25.71 | 0 | 99.06 | 0 | 0
2025-09-25 16:00 | 71.2 | 80.92 | 80.92 | 0 | 9.72 | 0 | 108.3 | 0 | 0
2025-09-25 17:00 | 70.61 | 27.44 | 27.44 | 0 | 0 | 43.18 | 62.85 | 0 | 0
2025-09-25 18:00 | 68.04 | 0 | 0 | 20.22 | 0 | 47.82 | 12.51 | 0 | 0
2025-09-25 19:00 | 65.82 | 0 | 0 | 65.82 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 20:00 | 62.3 | 0 | 0 | 62.3 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 21:00 | 59.54 | 0 | 0 | 59.54 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 22:00 | 57.37 | 0 | 0 | 57.37 | 0 | 0 | 12.51 | 0 | 0
2025-09-25 23:00 | 53.38 | 0 | 0 | 53.38 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 01:00 | 48.4 | 0 | 0 | 48.4 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 02:00 | 48.82 | 0 | 0 | 48.82 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 03:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 04:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 05:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 06:00 | 51.29 | 0.32 | 0.32 | 50.97 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 07:00 | 53.66 | 7.83 | 7.83 | 45.83 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 08:00 | 55.84 | 34.77 | 34.77 | 21.07 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 09:00 | 59.55 | 43.82 | 43.82 | 15.73 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 10:00 | 61.58 | 48.14 | 48.14 | 13.43 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 11:00 | 65.1 | 48.29 | 48.29 | 16.81 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 12:00 | 66.89 | 55.01 | 55.01 | 11.88 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 13:00 | 69.09 | 35.83 | 35.83 | 33.26 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 14:00 | 69.83 | 22.12 | 22.12 | 47.71 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 15:00 | 70.48 | 2.43 | 2.43 | 68.04 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 16:00 | 69.52 | 1.01 | 1.01 | 68.51 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 17:00 | 69.04 | 0.42 | 0.42 | 68.62 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 18:00 | 67.11 | 0 | 0 | 67.11 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 19:00 | 64.45 | 0 | 0 | 64.45 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 20:00 | 61.93 | 0 | 0 | 61.93 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 21:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 22:00 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 12.51 | 0 | 0
2025-09-26 23:00 | 53.26 | 0 | 0 | 53.26 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 01:00 | 50.23 | 0 | 0 | 50.23 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 02:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 03:00 | 47.69 | 0 | 0 | 47.69 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 04:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 05:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 06:00 | 49.56 | 0.5 | 0.5 | 49.06 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 07:00 | 52.96 | 9.5 | 9.5 | 43.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 08:00 | 55.17 | 13.31 | 13.31 | 41.85 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 09:00 | 58.64 | 31.85 | 31.85 | 26.79 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 10:00 | 61.76 | 28.66 | 28.66 | 33.1 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 11:00 | 64.82 | 22.67 | 22.67 | 42.15 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 12:00 | 66.11 | 55.31 | 55.31 | 10.8 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 13:00 | 68.65 | 76.42 | 76.42 | 0 | 7.77 | 0 | 19.89 | 0 | 0
2025-09-27 14:00 | 69.58 | 83.08 | 83.08 | 0 | 13.5 | 0 | 32.72 | 0 | 0
2025-09-27 15:00 | 70.13 | 87.86 | 87.86 | 0 | 17.73 | 0 | 49.57 | 0 | 0
2025-09-27 16:00 | 69.31 | 83.01 | 83.01 | 0 | 13.7 | 0 | 62.58 | 0 | 0
2025-09-27 17:00 | 69.15 | 26.07 | 26.07 | 0 | 0 | 43.08 | 17.24 | 0 | 0
2025-09-27 18:00 | 66.62 | 0 | 0 | 62.13 | 0 | 4.49 | 12.51 | 0 | 0
2025-09-27 19:00 | 65.24 | 0 | 0 | 65.24 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 20:00 | 61.26 | 0 | 0 | 61.26 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 21:00 | 59.13 | 0 | 0 | 59.13 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 22:00 | 55.83 | 0 | 0 | 55.83 | 0 | 0 | 12.51 | 0 | 0
2025-09-27 23:00 | 52.99 | 0 | 0 | 52.99 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 | 50.95 | 0 | 0 | 50.95 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 01:00 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 02:00 | 46.49 | 0 | 0 | 46.49 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 03:00 | 45.91 | 0 | 0 | 45.91 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 04:00 | 48.46 | 0 | 0 | 48.46 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 05:00 | 49.53 | 0 | 0 | 49.53 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 06:00 | 51.58 | 0.81 | 0.81 | 50.77 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 07:00 | 52.81 | 0.03 | 0.03 | 52.78 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 08:00 | 54.64 | 32.07 | 32.07 | 22.57 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 09:00 | 57.63 | 19.01 | 19.01 | 38.62 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 10:00 | 60.3 | 37.36 | 37.36 | 22.94 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 11:00 | 61.99 | 52.84 | 52.84 | 9.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 12:00 | 65.14 | 45.17 | 45.17 | 19.96 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 13:00 | 66.79 | 91.9 | 91.9 | 0 | 25.12 | 0 | 36.37 | 0 | 0
2025-09-28 14:00 | 66.74 | 83.23 | 83.23 | 0 | 16.49 | 0 | 52.04 | 0 | 0
2025-09-28 15:00 | 66.78 | 32.84 | 32.84 | 0 | 0 | 33.94 | 16.32 | 0 | 0
2025-09-28 16:00 | 65.86 | 58.63 | 58.63 | 3.61 | 0 | 3.62 | 12.51 | 0 | 0
2025-09-28 17:00 | 66.44 | 20.18 | 20.18 | 46.26 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 18:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 19:00 | 62.35 | 0 | 0 | 62.35 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 20:00 | 60.53 | 0 | 0 | 60.53 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 21:00 | 57.54 | 0 | 0 | 57.54 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 22:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 12.51 | 0 | 0
2025-09-28 23:00 | 52.1 | 0 | 0 | 52.1 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 | 51.13 | 0 | 0 | 51.13 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 01:00 | 48.76 | 0 | 0 | 48.76 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 02:00 | 48.28 | 0 | 0 | 48.28 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 03:00 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 04:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 05:00 | 48.2 | 0 | 0 | 48.2 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 06:00 | 50.96 | 0.92 | 0.92 | 50.04 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 07:00 | 52.48 | 50.94 | 50.94 | 1.54 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 08:00 | 55.43 | 58.8 | 58.8 | 0 | 3.37 | 0 | 15.71 | 0 | 0
2025-09-29 09:00 | 58.67 | 67.58 | 67.58 | 0 | 8.91 | 0 | 24.18 | 0 | 0
2025-09-29 10:00 | 61.77 | 70.38 | 70.38 | 0 | 8.61 | 0 | 32.36 | 0 | 0
2025-09-29 11:00 | 63.72 | 56.93 | 56.93 | 0 | 0 | 6.8 | 25.21 | 0 | 0
2025-09-29 12:00 | 66.96 | 50.46 | 50.46 | 4.44 | 0 | 12.06 | 12.51 | 0 | 0
2025-09-29 13:00 | 69.4 | 55.09 | 55.09 | 14.31 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 14:00 | 70.04 | 42.32 | 42.32 | 27.72 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 15:00 | 70.53 | 44.02 | 44.02 | 26.51 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 16:00 | 70.31 | 70.74 | 70.74 | 0 | 0.43 | 0 | 12.92 | 0 | 0
2025-09-29 17:00 | 68.94 | 23.15 | 23.15 | 45.4 | 0 | 0.39 | 12.51 | 0 | 0
2025-09-29 18:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 19:00 | 64.56 | 0 | 0 | 64.56 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 20:00 | 62.21 | 0 | 0 | 62.21 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 21:00 | 58.14 | 0 | 0 | 58.14 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 22:00 | 55.49 | 0 | 0 | 55.49 | 0 | 0 | 12.51 | 0 | 0
2025-09-29 23:00 | 52.23 | 0 | 0 | 52.23 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 | 50.88 | 0 | 0 | 50.88 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 01:00 | 48.63 | 0 | 0 | 48.63 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 02:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 03:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 04:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 05:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 06:00 | 49.68 | 1.18 | 1.18 | 48.49 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 07:00 | 52.12 | 49.43 | 49.43 | 2.69 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 08:00 | 55.95 | 64.59 | 64.59 | 0 | 8.64 | 0 | 20.72 | 0 | 0
2025-09-30 09:00 | 57.69 | 82.71 | 82.71 | 0 | 25.02 | 0 | 44.49 | 0 | 0
2025-09-30 10:00 | 61.07 | 85.65 | 85.65 | 0 | 24.58 | 0 | 67.84 | 0 | 0
2025-09-30 11:00 | 62.99 | 80.61 | 80.61 | 0 | 17.62 | 0 | 84.58 | 0 | 0
2025-09-30 12:00 | 65.99 | 77.23 | 77.23 | 0 | 11.23 | 0 | 95.25 | 0 | 0
2025-09-30 13:00 | 66.79 | 80.38 | 80.38 | 0 | 13.59 | 0 | 108.16 | 0 | 0
2025-09-30 14:00 | 68.38 | 89.78 | 73.04 | 0 | 4.66 | 0 | 112.59 | 16.74 | 0
2025-09-30 15:00 | 68.74 | 87.36 | 68.74 | 0 | 0 | 0 | 112.59 | 18.62 | 0
2025-09-30 16:00 | 69.52 | 68.03 | 68.03 | 0 | 0 | 1.5 | 111.02 | 0 | 0
2025-09-30 17:00 | 67.61 | 18.34 | 18.34 | 0 | 0 | 49.28 | 59.15 | 0 | 0
2025-09-30 18:00 | 65.32 | 0 | 0 | 21.01 | 0 | 44.3 | 12.51 | 0 | 0
2025-09-30 19:00 | 63.75 | 0 | 0 | 63.75 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 20:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 21:00 | 57.24 | 0 | 0 | 57.24 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 22:00 | 54.85 | 0 | 0 | 54.85 | 0 | 0 | 12.51 | 0 | 0
2025-09-30 23:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 | 50.24 | 0 | 0 | 50.24 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 01:00 | 48.41 | 0 | 0 | 48.41 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 02:00 | 46.81 | 0 | 0 | 46.81 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 03:00 | 47.79 | 0 | 0 | 47.79 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 04:00 | 46.75 | 0 | 0 | 46.75 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 05:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 06:00 | 50.97 | 0.84 | 0.84 | 50.13 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 07:00 | 53.02 | 51.23 | 51.23 | 1.79 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 08:00 | 55.77 | 90.39 | 90.39 | 0 | 34.62 | 0 | 45.4 | 0 | 0
2025-10-01 09:00 | 59.32 | 95.21 | 95.21 | 0 | 35.88 | 0 | 79.49 | 0 | 0
2025-10-01 10:00 | 63.89 | 92.94 | 92.94 | 0 | 29.05 | 0 | 107.09 | 0 | 0
2025-10-01 11:00 | 67.6 | 86.1 | 73.4 | 0 | 5.79 | 0 | 112.59 | 12.7 | 0
2025-10-01 12:00 | 71.69 | 86.91 | 71.69 | 0 | 0 | 0 | 112.59 | 15.22 | 0
2025-10-01 13:00 | 73.78 | 88.57 | 73.78 | 0 | 0 | 0 | 112.59 | 14.79 | 0
2025-10-01 14:00 | 76.75 | 90.98 | 76.75 | 0 | 0 | 0 | 112.59 | 14.23 | 0
2025-10-01 15:00 | 77.05 | 87.02 | 77.05 | 0 | 0 | 0 | 112.59 | 9.97 | 0
2025-10-01 16:00 | 76.44 | 76.38 | 76.38 | 0 | 0 | 0.06 | 112.52 | 0 | 0
2025-10-01 17:00 | 75.2 | 16.36 | 16.36 | 0 | 0 | 58.84 | 50.59 | 0 | 0
2025-10-01 18:00 | 71.37 | 0 | 0 | 35.2 | 0 | 36.18 | 12.51 | 0 | 0
2025-10-01 19:00 | 67.62 | 0 | 0 | 67.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 20:00 | 63.73 | 0 | 0 | 63.73 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 21:00 | 59.9 | 0 | 0 | 59.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 22:00 | 56.22 | 0 | 0 | 56.22 | 0 | 0 | 12.51 | 0 | 0
2025-10-01 23:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 | 49.24 | 0 | 0 | 49.24 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 01:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 02:00 | 47.52 | 0 | 0 | 47.52 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 03:00 | 47.04 | 0 | 0 | 47.04 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 04:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 05:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 06:00 | 50.64 | 0.54 | 0.54 | 50.1 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 07:00 | 53.43 | 26.33 | 26.33 | 27.1 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 08:00 | 56.18 | 79.48 | 79.48 | 0 | 23.31 | 0 | 34.65 | 0 | 0
2025-10-02 09:00 | 60.12 | 51.43 | 51.43 | 0 | 0 | 8.7 | 25.5 | 0 | 0
2025-10-02 10:00 | 63.88 | 47.89 | 47.89 | 3.64 | 0 | 12.34 | 12.51 | 0 | 0
2025-10-02 11:00 | 67.04 | 60.96 | 60.96 | 6.08 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 12:00 | 70.16 | 44.99 | 44.99 | 25.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 13:00 | 72.28 | 76.99 | 76.99 | 0 | 4.71 | 0 | 16.99 | 0 | 0
2025-10-02 14:00 | 74.03 | 54.86 | 54.86 | 14.91 | 0 | 4.25 | 12.51 | 0 | 0
2025-10-02 15:00 | 74.45 | 92.81 | 92.81 | 0 | 18.36 | 0 | 29.95 | 0 | 0
2025-10-02 16:00 | 74.36 | 66.56 | 66.56 | 0 | 0 | 7.8 | 21.75 | 0 | 0
2025-10-02 17:00 | 72.03 | 1.4 | 1.4 | 61.85 | 0 | 8.77 | 12.51 | 0 | 0
2025-10-02 18:00 | 69.71 | 0 | 0 | 69.71 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 19:00 | 65.39 | 0 | 0 | 65.39 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 20:00 | 63.81 | 0 | 0 | 63.81 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 21:00 | 59.16 | 0 | 0 | 59.16 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 22:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 12.51 | 0 | 0
2025-10-02 23:00 | 53.47 | 0 | 0 | 53.47 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 | 50.16 | 0 | 0 | 50.16 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 01:00 | 49.01 | 0 | 0 | 49.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 02:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 03:00 | 48.05 | 0 | 0 | 48.05 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 04:00 | 47.76 | 0 | 0 | 47.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 05:00 | 48.39 | 0 | 0 | 48.39 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 06:00 | 50.72 | 0.48 | 0.48 | 50.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 07:00 | 51.7 | 37.9 | 37.9 | 13.8 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 08:00 | 54.83 | 74.66 | 74.66 | 0 | 19.83 | 0 | 31.35 | 0 | 0
2025-10-03 09:00 | 58.63 | 92.42 | 92.42 | 0 | 33.78 | 0 | 63.45 | 0 | 0
2025-10-03 10:00 | 59.96 | 89.66 | 89.66 | 0 | 29.7 | 0 | 91.67 | 0 | 0
2025-10-03 11:00 | 64 | 83.05 | 83.05 | 0 | 19.05 | 0 | 109.77 | 0 | 0
2025-10-03 12:00 | 66.44 | 81.07 | 69.41 | 0 | 2.97 | 0 | 112.59 | 11.65 | 0
2025-10-03 13:00 | 69.07 | 74.46 | 69.07 | 0 | 0 | 0 | 112.59 | 5.4 | 0
2025-10-03 14:00 | 68.5 | 70.19 | 68.5 | 0 | 0 | 0 | 112.59 | 1.68 | 0
2025-10-03 15:00 | 70.51 | 65.82 | 65.82 | 0 | 0 | 4.7 | 107.65 | 0 | 0
2025-10-03 16:00 | 69.01 | 36.7 | 36.7 | 0 | 0 | 32.32 | 73.63 | 0 | 0
2025-10-03 17:00 | 67.86 | 10.22 | 10.22 | 0 | 0 | 57.64 | 12.95 | 0 | 0
2025-10-03 18:00 | 65.56 | 0 | 0 | 65.14 | 0 | 0.42 | 12.51 | 0 | 0
2025-10-03 19:00 | 63.17 | 0 | 0 | 63.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 21:00 | 57.35 | 0 | 0 | 57.35 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 22:00 | 55.34 | 0 | 0 | 55.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-03 23:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 01:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 02:00 | 47.26 | 0 | 0 | 47.26 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 03:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 04:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 05:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 06:00 | 50.31 | 0.09 | 0.09 | 50.23 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 07:00 | 51.69 | 25 | 25 | 26.69 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 08:00 | 53.66 | 42.57 | 42.57 | 11.09 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 09:00 | 56.64 | 15.96 | 15.96 | 40.68 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 10:00 | 59.15 | 41.47 | 41.47 | 17.69 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 11:00 | 60.26 | 48.33 | 48.33 | 11.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 12:00 | 62.26 | 65.1 | 65.1 | 0 | 2.85 | 0 | 15.21 | 0 | 0
2025-10-04 13:00 | 63.61 | 78.25 | 78.25 | 0 | 14.63 | 0 | 29.11 | 0 | 0
2025-10-04 14:00 | 64.65 | 51.04 | 51.04 | 0 | 0 | 13.61 | 14.79 | 0 | 0
2025-10-04 15:00 | 64.64 | 42.25 | 42.25 | 20.22 | 0 | 2.17 | 12.51 | 0 | 0
2025-10-04 16:00 | 65.11 | 77.17 | 77.17 | 0 | 12.06 | 0 | 23.97 | 0 | 0
2025-10-04 17:00 | 63.17 | 15.21 | 15.21 | 37.08 | 0 | 10.88 | 12.51 | 0 | 0
2025-10-04 18:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 19:00 | 60.82 | 0 | 0 | 60.82 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 20:00 | 58.83 | 0 | 0 | 58.83 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 21:00 | 55.87 | 0 | 0 | 55.87 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 22:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-04 23:00 | 51.65 | 0 | 0 | 51.65 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 01:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 02:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 03:00 | 47.35 | 0 | 0 | 47.35 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 04:00 | 47.21 | 0 | 0 | 47.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 05:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 06:00 | 49.64 | 0.45 | 0.45 | 49.19 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 07:00 | 51.66 | 39.65 | 39.65 | 12.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 08:00 | 54.43 | 66.65 | 66.65 | 0 | 12.23 | 0 | 24.13 | 0 | 0
2025-10-05 09:00 | 55.77 | 76.46 | 76.46 | 0 | 20.7 | 0 | 43.79 | 0 | 0
2025-10-05 10:00 | 58.56 | 79.95 | 79.95 | 0 | 21.39 | 0 | 64.11 | 0 | 0
2025-10-05 11:00 | 60.03 | 65.72 | 65.72 | 0 | 5.69 | 0 | 69.52 | 0 | 0
2025-10-05 12:00 | 62.23 | 72.82 | 72.82 | 0 | 10.59 | 0 | 79.58 | 0 | 0
2025-10-05 13:00 | 63.2 | 39.24 | 39.24 | 0 | 0 | 23.96 | 54.36 | 0 | 0
2025-10-05 14:00 | 63.3 | 42.84 | 42.84 | 0 | 0 | 20.47 | 32.81 | 0 | 0
2025-10-05 15:00 | 63.29 | 66.87 | 66.87 | 0 | 3.58 | 0 | 36.21 | 0 | 0
2025-10-05 16:00 | 63.46 | 54.37 | 54.37 | 0 | 0 | 9.09 | 26.65 | 0 | 0
2025-10-05 17:00 | 62.47 | 1.65 | 1.65 | 47.39 | 0 | 13.43 | 12.51 | 0 | 0
2025-10-05 18:00 | 62.33 | 0 | 0 | 62.33 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 19:00 | 60.05 | 0 | 0 | 60.05 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 20:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 21:00 | 55.84 | 0 | 0 | 55.84 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 22:00 | 53.21 | 0 | 0 | 53.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-05 23:00 | 51.88 | 0 | 0 | 51.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 01:00 | 48.45 | 0 | 0 | 48.45 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 02:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 03:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 04:00 | 47.42 | 0 | 0 | 47.42 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 05:00 | 46.82 | 0 | 0 | 46.82 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 06:00 | 50.64 | 0 | 0 | 50.64 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 07:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 08:00 | 54.9 | 2.02 | 2.02 | 52.87 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 09:00 | 58.31 | 3.7 | 3.7 | 54.61 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 10:00 | 61.74 | 11.56 | 11.56 | 50.18 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 11:00 | 64.77 | 13.91 | 13.91 | 50.86 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 12:00 | 68.03 | 11 | 11 | 57.03 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 13:00 | 70.09 | 65.33 | 65.33 | 4.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 14:00 | 72.18 | 64.61 | 64.61 | 7.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 15:00 | 72.06 | 44.34 | 44.34 | 27.72 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 16:00 | 72.28 | 27.58 | 27.58 | 44.7 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 17:00 | 70.28 | 3.7 | 3.7 | 66.58 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 18:00 | 66.63 | 0 | 0 | 66.63 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 19:00 | 65.94 | 0 | 0 | 65.94 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 21:00 | 58.77 | 0 | 0 | 58.77 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 22:00 | 54.84 | 0 | 0 | 54.84 | 0 | 0 | 12.51 | 0 | 0
2025-10-06 23:00 | 52.51 | 0 | 0 | 52.51 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 01:00 | 48.06 | 0 | 0 | 48.06 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 02:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 03:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 04:00 | 46.93 | 0 | 0 | 46.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 05:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 06:00 | 48.33 | 0.28 | 0.28 | 48.04 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 07:00 | 51.55 | 41 | 41 | 10.54 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 08:00 | 54.36 | 83.96 | 83.96 | 0 | 29.59 | 0 | 40.62 | 0 | 0
2025-10-07 09:00 | 57.05 | 93.19 | 93.19 | 0 | 36.14 | 0 | 74.95 | 0 | 0
2025-10-07 10:00 | 60.24 | 78.48 | 78.48 | 0 | 18.24 | 0 | 92.28 | 0 | 0
2025-10-07 11:00 | 62.23 | 48.21 | 48.21 | 0 | 0 | 14.02 | 77.53 | 0 | 0
2025-10-07 12:00 | 64.74 | 42.61 | 42.61 | 0 | 0 | 22.13 | 54.23 | 0 | 0
2025-10-07 13:00 | 67.09 | 64.61 | 64.61 | 0 | 0 | 2.48 | 51.62 | 0 | 0
2025-10-07 14:00 | 66.48 | 40.75 | 40.75 | 0 | 0 | 25.74 | 24.53 | 0 | 0
2025-10-07 15:00 | 68.3 | 27.14 | 27.14 | 29.75 | 0 | 11.42 | 12.51 | 0 | 0
2025-10-07 16:00 | 67.46 | 5.71 | 5.71 | 61.75 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 17:00 | 66.04 | 0.82 | 0.82 | 65.22 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 18:00 | 64.88 | 0 | 0 | 64.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 19:00 | 63.03 | 0 | 0 | 63.03 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 20:00 | 60.28 | 0 | 0 | 60.28 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 21:00 | 56.87 | 0 | 0 | 56.87 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 22:00 | 54.59 | 0 | 0 | 54.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-07 23:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 | 49.23 | 0 | 0 | 49.23 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 01:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 02:00 | 46.27 | 0 | 0 | 46.27 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 03:00 | 46.66 | 0 | 0 | 46.66 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 04:00 | 46.57 | 0 | 0 | 46.57 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 05:00 | 47.1 | 0 | 0 | 47.1 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 06:00 | 48.43 | 0 | 0 | 48.43 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 07:00 | 51.89 | 46.8 | 46.8 | 5.09 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 08:00 | 53.8 | 97.7 | 97.7 | 0 | 43.89 | 0 | 54.21 | 0 | 0
2025-10-08 09:00 | 57.09 | 99.25 | 99.25 | 0 | 42.16 | 0 | 94.26 | 0 | 0
2025-10-08 10:00 | 60.46 | 71.66 | 71.66 | 0 | 11.21 | 0 | 104.91 | 0 | 0
2025-10-08 11:00 | 61.95 | 21.42 | 21.42 | 0 | 0 | 40.53 | 62.24 | 0 | 0
2025-10-08 12:00 | 65 | 31.52 | 31.52 | 0 | 0 | 33.48 | 27 | 0 | 0
2025-10-08 13:00 | 66.81 | 60.65 | 60.65 | 0 | 0 | 6.16 | 20.52 | 0 | 0
2025-10-08 14:00 | 68.28 | 47.35 | 47.35 | 13.33 | 0 | 7.61 | 12.51 | 0 | 0
2025-10-08 15:00 | 69.12 | 58.01 | 58.01 | 11.11 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 16:00 | 67.43 | 4.57 | 4.57 | 62.86 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 17:00 | 67.18 | 0.03 | 0.03 | 67.16 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 18:00 | 65.53 | 0 | 0 | 65.53 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 19:00 | 62.51 | 0 | 0 | 62.51 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 20:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 21:00 | 57.14 | 0 | 0 | 57.14 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 22:00 | 54.25 | 0 | 0 | 54.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-08 23:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 | 49.23 | 0 | 0 | 49.23 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 01:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 02:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 03:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 04:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 05:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 06:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 07:00 | 50.89 | 0.1 | 0.1 | 50.79 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 08:00 | 52.19 | 2.92 | 2.92 | 49.27 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 09:00 | 54.49 | 4.84 | 4.84 | 49.65 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 10:00 | 55.67 | 6.71 | 6.71 | 48.96 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 11:00 | 58.06 | 8.17 | 8.17 | 49.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 12:00 | 58.89 | 8.7 | 8.7 | 50.19 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 13:00 | 58.69 | 7.48 | 7.48 | 51.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 14:00 | 60.09 | 6.13 | 6.13 | 53.96 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 15:00 | 60.02 | 3.69 | 3.69 | 56.33 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 16:00 | 60.17 | 1.57 | 1.57 | 58.6 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 17:00 | 59.32 | 0 | 0 | 59.32 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 18:00 | 58.4 | 0 | 0 | 58.4 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 19:00 | 57.37 | 0 | 0 | 57.37 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 20:00 | 56.1 | 0 | 0 | 56.1 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 21:00 | 54.68 | 0 | 0 | 54.68 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 22:00 | 52.84 | 0 | 0 | 52.84 | 0 | 0 | 12.51 | 0 | 0
2025-10-09 23:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 01:00 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 02:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 03:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 04:00 | 46.05 | 0 | 0 | 46.05 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 05:00 | 49 | 0 | 0 | 49 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 06:00 | 49.22 | 0 | 0 | 49.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 07:00 | 50.54 | 42.11 | 42.11 | 8.44 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 08:00 | 54.33 | 90.9 | 90.9 | 0 | 36.57 | 0 | 47.25 | 0 | 0
2025-10-10 09:00 | 56.44 | 68.19 | 68.19 | 0 | 11.76 | 0 | 58.42 | 0 | 0
2025-10-10 10:00 | 60.44 | 35.1 | 35.1 | 0 | 0 | 25.35 | 31.74 | 0 | 0
2025-10-10 11:00 | 62.87 | 49.11 | 49.11 | 0 | 0 | 13.76 | 17.25 | 0 | 0
2025-10-10 12:00 | 65.4 | 52.62 | 52.62 | 8.28 | 0 | 4.5 | 12.51 | 0 | 0
2025-10-10 13:00 | 68.5 | 71.3 | 71.3 | 0 | 2.8 | 0 | 15.17 | 0 | 0
2025-10-10 14:00 | 69.31 | 90.4 | 90.4 | 0 | 21.1 | 0 | 35.22 | 0 | 0
2025-10-10 15:00 | 69.97 | 94.07 | 94.07 | 0 | 24.11 | 0 | 58.12 | 0 | 0
2025-10-10 16:00 | 69.24 | 70.16 | 70.16 | 0 | 0.91 | 0 | 58.99 | 0 | 0
2025-10-10 17:00 | 67.47 | 6.84 | 6.84 | 16.48 | 0 | 44.15 | 12.51 | 0 | 0
2025-10-10 18:00 | 65.92 | 0 | 0 | 65.92 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 19:00 | 63.58 | 0 | 0 | 63.58 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 20:00 | 60.06 | 0 | 0 | 60.06 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 21:00 | 57.79 | 0 | 0 | 57.79 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 22:00 | 54.34 | 0 | 0 | 54.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-10 23:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 01:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 02:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 03:00 | 45.82 | 0 | 0 | 45.82 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 04:00 | 46.31 | 0 | 0 | 46.31 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 05:00 | 47 | 0 | 0 | 47 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 06:00 | 48.99 | 0 | 0 | 48.99 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 07:00 | 50.96 | 42.65 | 42.65 | 8.31 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 08:00 | 53.87 | 89.36 | 89.36 | 0 | 35.5 | 0 | 46.23 | 0 | 0
2025-10-11 09:00 | 56.58 | 93.07 | 93.07 | 0 | 36.49 | 0 | 80.9 | 0 | 0
2025-10-11 10:00 | 59.15 | 87.26 | 87.26 | 0 | 28.11 | 0 | 107.61 | 0 | 0
2025-10-11 11:00 | 61.06 | 79.52 | 66.31 | 0 | 5.25 | 0 | 112.59 | 13.22 | 0
2025-10-11 12:00 | 64.97 | 79.53 | 64.97 | 0 | 0 | 0 | 112.59 | 14.56 | 0
2025-10-11 13:00 | 65.82 | 85.64 | 65.82 | 0 | 0 | 0 | 112.59 | 19.81 | 0
2025-10-11 14:00 | 67.01 | 91.97 | 67.01 | 0 | 0 | 0 | 112.59 | 24.96 | 0
2025-10-11 15:00 | 67.27 | 89.87 | 67.27 | 0 | 0 | 0 | 112.59 | 22.6 | 0
2025-10-11 16:00 | 66.8 | 67.4 | 66.8 | 0 | 0 | 0 | 112.59 | 0.59 | 0
2025-10-11 17:00 | 66.67 | 2.29 | 2.29 | 1.88 | 0 | 62.5 | 46.8 | 0 | 0
2025-10-11 18:00 | 64.77 | 0 | 0 | 32.2 | 0 | 32.58 | 12.51 | 0 | 0
2025-10-11 19:00 | 61.96 | 0 | 0 | 61.96 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 20:00 | 59.01 | 0 | 0 | 59.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 21:00 | 56.56 | 0 | 0 | 56.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 22:00 | 53.52 | 0 | 0 | 53.52 | 0 | 0 | 12.51 | 0 | 0
2025-10-11 23:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 01:00 | 46.82 | 0 | 0 | 46.82 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 02:00 | 46.2 | 0 | 0 | 46.2 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 03:00 | 45.84 | 0 | 0 | 45.84 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 04:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 05:00 | 46.73 | 0 | 0 | 46.73 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 06:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 07:00 | 49.98 | 4.67 | 4.67 | 45.3 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 08:00 | 52.23 | 35.51 | 35.51 | 16.72 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 09:00 | 54.37 | 60.46 | 60.46 | 0 | 6.09 | 0 | 18.29 | 0 | 0
2025-10-12 10:00 | 56.08 | 68.84 | 68.84 | 0 | 12.76 | 0 | 30.41 | 0 | 0
2025-10-12 11:00 | 58.85 | 63.08 | 63.08 | 0 | 4.23 | 0 | 34.44 | 0 | 0
2025-10-12 12:00 | 59.25 | 65.41 | 65.41 | 0 | 6.16 | 0 | 40.29 | 0 | 0
2025-10-12 13:00 | 60.39 | 67.91 | 67.91 | 0 | 7.52 | 0 | 47.44 | 0 | 0
2025-10-12 14:00 | 61.98 | 77.76 | 77.76 | 0 | 15.78 | 0 | 62.43 | 0 | 0
2025-10-12 15:00 | 61.27 | 97.51 | 97.51 | 0 | 36.24 | 0 | 96.86 | 0 | 0
2025-10-12 16:00 | 61.26 | 72.36 | 72.36 | 0 | 11.1 | 0 | 107.4 | 0 | 0
2025-10-12 17:00 | 60.23 | 5.11 | 5.11 | 0 | 0 | 55.12 | 49.38 | 0 | 0
2025-10-12 18:00 | 60.15 | 0 | 0 | 25.12 | 0 | 35.03 | 12.51 | 0 | 0
2025-10-12 19:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 20:00 | 56.98 | 0 | 0 | 56.98 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 21:00 | 54.9 | 0 | 0 | 54.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 22:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-12 23:00 | 50.17 | 0 | 0 | 50.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 | 48.04 | 0 | 0 | 48.04 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 01:00 | 47.56 | 0 | 0 | 47.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 02:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 03:00 | 45.26 | 0 | 0 | 45.26 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 04:00 | 45.96 | 0 | 0 | 45.96 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 05:00 | 46.76 | 0 | 0 | 46.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 06:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 07:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 08:00 | 52.43 | 1.63 | 1.63 | 50.8 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 09:00 | 54.51 | 3.15 | 3.15 | 51.36 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 10:00 | 56.54 | 4.6 | 4.6 | 51.94 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 11:00 | 58.58 | 5.91 | 5.91 | 52.67 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 12:00 | 60.93 | 6.61 | 6.61 | 54.32 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 13:00 | 62.39 | 58.31 | 58.31 | 4.08 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 14:00 | 62.82 | 57.25 | 57.25 | 5.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 15:00 | 63.86 | 53.52 | 53.52 | 10.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 16:00 | 63.22 | 37.62 | 37.62 | 25.6 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 17:00 | 62.72 | 0.88 | 0.88 | 61.85 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 18:00 | 61.02 | 0 | 0 | 61.02 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 19:00 | 58.97 | 0 | 0 | 58.97 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 20:00 | 57.34 | 0 | 0 | 57.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 21:00 | 54.36 | 0 | 0 | 54.36 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 22:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 12.51 | 0 | 0
2025-10-13 23:00 | 49.93 | 0 | 0 | 49.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 01:00 | 46.62 | 0 | 0 | 46.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 02:00 | 46.34 | 0 | 0 | 46.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 03:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 04:00 | 45.48 | 0 | 0 | 45.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 05:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 06:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 07:00 | 51.22 | 21.89 | 21.89 | 29.33 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 08:00 | 52.82 | 78.45 | 78.45 | 0 | 25.63 | 0 | 36.86 | 0 | 0
2025-10-14 09:00 | 56.33 | 64.9 | 64.9 | 0 | 8.57 | 0 | 45 | 0 | 0
2025-10-14 10:00 | 57.92 | 36.55 | 36.55 | 0 | 0 | 21.36 | 22.51 | 0 | 0
2025-10-14 11:00 | 61.1 | 52.95 | 52.95 | 0 | 0 | 8.16 | 13.93 | 0 | 0
2025-10-14 12:00 | 62.24 | 68.24 | 68.24 | 0 | 5.99 | 0 | 19.62 | 0 | 0
2025-10-14 13:00 | 64.6 | 15.24 | 15.24 | 42.6 | 0 | 6.76 | 12.51 | 0 | 0
2025-10-14 14:00 | 64.27 | 8.45 | 8.45 | 55.83 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 15:00 | 65.24 | 8.68 | 8.68 | 56.57 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 16:00 | 65.68 | 0.66 | 0.66 | 65.02 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 17:00 | 63.73 | 0 | 0 | 63.73 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 18:00 | 62.93 | 0 | 0 | 62.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 19:00 | 61.01 | 0 | 0 | 61.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 20:00 | 57.81 | 0 | 0 | 57.81 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 21:00 | 54.93 | 0 | 0 | 54.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 22:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-14 23:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 | 48.12 | 0 | 0 | 48.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 01:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 02:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 03:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 04:00 | 45.32 | 0 | 0 | 45.32 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 05:00 | 47.34 | 0 | 0 | 47.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 06:00 | 47.65 | 0 | 0 | 47.65 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 07:00 | 50.21 | 0 | 0 | 50.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 08:00 | 53.09 | 25.93 | 25.93 | 27.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 09:00 | 55.58 | 2.74 | 2.74 | 52.84 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 10:00 | 57.31 | 13.57 | 13.57 | 43.74 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 11:00 | 60.15 | 45.75 | 45.75 | 14.4 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 12:00 | 62.1 | 56.7 | 56.7 | 5.41 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 13:00 | 63.17 | 42.83 | 42.83 | 20.35 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 14:00 | 64.73 | 75.01 | 75.01 | 0 | 10.28 | 0 | 22.27 | 0 | 0
2025-10-15 15:00 | 65.69 | 86.08 | 86.08 | 0 | 20.39 | 0 | 41.65 | 0 | 0
2025-10-15 16:00 | 64.66 | 32.6 | 32.6 | 4.38 | 0 | 27.68 | 12.51 | 0 | 0
2025-10-15 17:00 | 63.73 | 0.78 | 0.78 | 62.95 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 18:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 19:00 | 59.14 | 0 | 0 | 59.14 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 20:00 | 57.75 | 0 | 0 | 57.75 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 21:00 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 22:00 | 52.21 | 0 | 0 | 52.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-15 23:00 | 51.25 | 0 | 0 | 51.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 01:00 | 46.13 | 0 | 0 | 46.13 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 02:00 | 46.13 | 0 | 0 | 46.13 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 03:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 04:00 | 45.33 | 0 | 0 | 45.33 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 05:00 | 47.12 | 0 | 0 | 47.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 06:00 | 48.02 | 0 | 0 | 48.02 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 07:00 | 49.14 | 8.93 | 8.93 | 40.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 08:00 | 52.42 | 36.3 | 36.3 | 16.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 09:00 | 54.3 | 54.54 | 54.54 | 0 | 0.25 | 0 | 12.74 | 0 | 0
2025-10-16 10:00 | 57.58 | 75.02 | 75.02 | 0 | 17.44 | 0 | 29.31 | 0 | 0
2025-10-16 11:00 | 58.64 | 64.46 | 64.46 | 0 | 5.82 | 0 | 34.84 | 0 | 0
2025-10-16 12:00 | 61.27 | 61.24 | 61.24 | 0 | 0 | 0.03 | 34.81 | 0 | 0
2025-10-16 13:00 | 63 | 50.54 | 50.54 | 0 | 0 | 12.46 | 21.69 | 0 | 0
2025-10-16 14:00 | 62.55 | 64.54 | 64.54 | 0 | 1.99 | 0 | 23.59 | 0 | 0
2025-10-16 15:00 | 63.16 | 80.77 | 80.77 | 0 | 17.6 | 0 | 40.31 | 0 | 0
2025-10-16 16:00 | 63.16 | 62.3 | 62.3 | 0 | 0 | 0.87 | 39.39 | 0 | 0
2025-10-16 17:00 | 61.69 | 1.59 | 1.59 | 34.56 | 0 | 25.54 | 12.51 | 0 | 0
2025-10-16 18:00 | 60.88 | 0 | 0 | 60.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 19:00 | 58.83 | 0 | 0 | 58.83 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 20:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 21:00 | 54.52 | 0 | 0 | 54.52 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 22:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 12.51 | 0 | 0
2025-10-16 23:00 | 50.01 | 0 | 0 | 50.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 | 47.55 | 0 | 0 | 47.55 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 01:00 | 46.08 | 0 | 0 | 46.08 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 02:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 03:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 04:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 05:00 | 46.52 | 0 | 0 | 46.52 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 06:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 07:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 08:00 | 51.9 | 3.42 | 3.42 | 48.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 09:00 | 54.01 | 7.72 | 7.72 | 46.29 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 10:00 | 57.64 | 7.61 | 7.61 | 50.03 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 11:00 | 59.05 | 4.93 | 4.93 | 54.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 12:00 | 61.02 | 8.17 | 8.17 | 52.85 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 13:00 | 62.14 | 60.45 | 60.45 | 1.69 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 14:00 | 63.28 | 61.58 | 61.58 | 1.7 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 15:00 | 62.99 | 56.82 | 56.82 | 6.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 16:00 | 63.2 | 37.69 | 37.69 | 25.52 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 17:00 | 61.91 | 0.37 | 0.37 | 61.54 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 18:00 | 60.79 | 0 | 0 | 60.79 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 19:00 | 57.76 | 0 | 0 | 57.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 20:00 | 56.26 | 0 | 0 | 56.26 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 21:00 | 55.17 | 0 | 0 | 55.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 22:00 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 12.51 | 0 | 0
2025-10-17 23:00 | 50.45 | 0 | 0 | 50.45 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 | 48.38 | 0 | 0 | 48.38 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 01:00 | 46.56 | 0 | 0 | 46.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 02:00 | 45.06 | 0 | 0 | 45.06 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 03:00 | 44.45 | 0 | 0 | 44.45 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 04:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 05:00 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 06:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 07:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 08:00 | 52.76 | 7 | 7 | 45.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 09:00 | 54.01 | 4.68 | 4.68 | 49.33 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 10:00 | 57.05 | 3.94 | 3.94 | 53.11 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 11:00 | 59.34 | 11.2 | 11.2 | 48.14 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 12:00 | 59.77 | 67.57 | 67.57 | 0 | 7.8 | 0 | 19.92 | 0 | 0
2025-10-18 13:00 | 61.41 | 83.53 | 83.53 | 0 | 22.12 | 0 | 40.93 | 0 | 0
2025-10-18 14:00 | 61.98 | 92.96 | 92.96 | 0 | 30.97 | 0 | 70.35 | 0 | 0
2025-10-18 15:00 | 62.17 | 50.53 | 50.53 | 0 | 0 | 11.64 | 58.1 | 0 | 0
2025-10-18 16:00 | 62.83 | 47.32 | 47.32 | 0 | 0 | 15.51 | 41.77 | 0 | 0
2025-10-18 17:00 | 61.55 | 0.45 | 0.45 | 33.3 | 0 | 27.8 | 12.51 | 0 | 0
2025-10-18 18:00 | 60.31 | 0 | 0 | 60.31 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 19:00 | 58.77 | 0 | 0 | 58.77 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 20:00 | 55.46 | 0 | 0 | 55.46 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 21:00 | 54.74 | 0 | 0 | 54.74 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 22:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 12.51 | 0 | 0
2025-10-18 23:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 01:00 | 46.77 | 0 | 0 | 46.77 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 02:00 | 45.11 | 0 | 0 | 45.11 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 03:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 04:00 | 45.19 | 0 | 0 | 45.19 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 05:00 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 06:00 | 47.04 | 0 | 0 | 47.04 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 07:00 | 49.57 | 12.74 | 12.74 | 36.83 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 08:00 | 51.58 | 14.99 | 14.99 | 36.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 09:00 | 53.54 | 54.87 | 54.87 | 0 | 1.33 | 0 | 13.78 | 0 | 0
2025-10-19 10:00 | 57.01 | 66.98 | 66.98 | 0 | 9.97 | 0 | 23.25 | 0 | 0
2025-10-19 11:00 | 58.7 | 38.35 | 38.35 | 10.15 | 0 | 10.21 | 12.51 | 0 | 0
2025-10-19 12:00 | 60.78 | 27.86 | 27.86 | 32.92 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 13:00 | 62.29 | 27.99 | 27.99 | 34.31 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 14:00 | 64.11 | 13.3 | 13.3 | 50.82 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 15:00 | 63.81 | 6.12 | 6.12 | 57.69 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 16:00 | 63.54 | 5.28 | 5.28 | 58.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 17:00 | 62.3 | 0 | 0 | 62.3 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 18:00 | 61.22 | 0 | 0 | 61.22 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 19:00 | 59.66 | 0 | 0 | 59.66 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 20:00 | 57 | 0 | 0 | 57 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 21:00 | 54.55 | 0 | 0 | 54.55 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 22:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 12.51 | 0 | 0
2025-10-19 23:00 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 01:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 02:00 | 44.66 | 0 | 0 | 44.66 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 03:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 04:00 | 44.09 | 0 | 0 | 44.09 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 05:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 06:00 | 47.37 | 0 | 0 | 47.37 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 07:00 | 49.56 | 5.55 | 5.55 | 44.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 08:00 | 51.76 | 24.88 | 24.88 | 26.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 09:00 | 55.11 | 25.46 | 25.46 | 29.65 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 10:00 | 57.93 | 23.04 | 23.04 | 34.89 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 11:00 | 61.7 | 10.22 | 10.22 | 51.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 12:00 | 63.78 | 15.31 | 15.31 | 48.47 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 13:00 | 66.35 | 23.97 | 23.97 | 42.38 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 14:00 | 67.48 | 31.36 | 31.36 | 36.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 15:00 | 67.15 | 20.94 | 20.94 | 46.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 16:00 | 67.33 | 8.59 | 8.59 | 58.74 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 17:00 | 65.38 | 0 | 0 | 65.38 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 18:00 | 63.8 | 0 | 0 | 63.8 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 19:00 | 60.79 | 0 | 0 | 60.79 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 20:00 | 58.34 | 0 | 0 | 58.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 21:00 | 54.4 | 0 | 0 | 54.4 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 22:00 | 52.17 | 0 | 0 | 52.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-20 23:00 | 49.88 | 0 | 0 | 49.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 | 47.51 | 0 | 0 | 47.51 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 01:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 02:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 03:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 04:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 05:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 06:00 | 46.6 | 0 | 0 | 46.6 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 07:00 | 49.99 | 4.98 | 4.98 | 45.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 08:00 | 50.01 | 19.07 | 19.07 | 30.94 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 09:00 | 50.6 | 58.02 | 58.02 | 0 | 7.42 | 0 | 19.56 | 0 | 0
2025-10-21 10:00 | 52.38 | 50.37 | 50.37 | 0 | 0 | 2 | 17.45 | 0 | 0
2025-10-21 11:00 | 52.08 | 73.81 | 73.81 | 0 | 21.74 | 0 | 38.1 | 0 | 0
2025-10-21 12:00 | 54.07 | 74.73 | 74.73 | 0 | 20.67 | 0 | 57.73 | 0 | 0
2025-10-21 13:00 | 54.6 | 80.35 | 80.35 | 0 | 25.74 | 0 | 82.19 | 0 | 0
2025-10-21 14:00 | 53.84 | 85.91 | 85.85 | 0 | 32 | 0 | 112.59 | 0.07 | 0
2025-10-21 15:00 | 54.09 | 82.72 | 54.09 | 0 | 0 | 0 | 112.59 | 28.63 | 0
2025-10-21 16:00 | 54.76 | 42.29 | 42.29 | 0 | 0 | 12.48 | 99.46 | 0 | 0
2025-10-21 17:00 | 53.32 | 0.29 | 0.29 | 0 | 0 | 53.03 | 43.64 | 0 | 0
2025-10-21 18:00 | 53.28 | 0 | 0 | 23.71 | 0 | 29.57 | 12.51 | 0 | 0
2025-10-21 19:00 | 53.35 | 0 | 0 | 53.35 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 20:00 | 52.29 | 0 | 0 | 52.29 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 21:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 22:00 | 49.52 | 0 | 0 | 49.52 | 0 | 0 | 12.51 | 0 | 0
2025-10-21 23:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 | 46.99 | 0 | 0 | 46.99 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 01:00 | 45.93 | 0 | 0 | 45.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 02:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 03:00 | 44.56 | 0 | 0 | 44.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 04:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 05:00 | 45.9 | 0 | 0 | 45.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 06:00 | 46.9 | 0 | 0 | 46.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 07:00 | 48.81 | 20.67 | 20.67 | 28.13 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 08:00 | 51.52 | 77.87 | 77.87 | 0 | 26.36 | 0 | 37.55 | 0 | 0
2025-10-22 09:00 | 52.87 | 85.15 | 85.15 | 0 | 32.28 | 0 | 68.21 | 0 | 0
2025-10-22 10:00 | 56.11 | 64.39 | 64.39 | 0 | 8.29 | 0 | 76.09 | 0 | 0
2025-10-22 11:00 | 58.19 | 55.36 | 55.36 | 0 | 0 | 2.83 | 73.11 | 0 | 0
2025-10-22 12:00 | 59.57 | 54.45 | 54.45 | 0 | 0 | 5.12 | 67.72 | 0 | 0
2025-10-22 13:00 | 60.02 | 68.98 | 68.98 | 0 | 8.96 | 0 | 76.23 | 0 | 0
2025-10-22 14:00 | 60.24 | 29.66 | 29.66 | 0 | 0 | 30.58 | 44.03 | 0 | 0
2025-10-22 15:00 | 62.15 | 13.13 | 13.13 | 19.07 | 0 | 29.95 | 12.51 | 0 | 0
2025-10-22 16:00 | 61.39 | 6.26 | 6.26 | 55.13 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 17:00 | 60.14 | 0 | 0 | 60.14 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 18:00 | 59.78 | 0 | 0 | 59.78 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 19:00 | 57.04 | 0 | 0 | 57.04 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 20:00 | 55.22 | 0 | 0 | 55.22 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 21:00 | 53.49 | 0 | 0 | 53.49 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 22:00 | 50.44 | 0 | 0 | 50.44 | 0 | 0 | 12.51 | 0 | 0
2025-10-22 23:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 | 47.48 | 0 | 0 | 47.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 01:00 | 45.62 | 0 | 0 | 45.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 02:00 | 45.25 | 0 | 0 | 45.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 03:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 04:00 | 44.63 | 0 | 0 | 44.63 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 05:00 | 44.35 | 0 | 0 | 44.35 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 06:00 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 07:00 | 49.18 | 3.71 | 3.71 | 45.47 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 08:00 | 50.2 | 19.2 | 19.2 | 31 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 09:00 | 53.17 | 26.12 | 26.12 | 27.05 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 10:00 | 55.88 | 33.24 | 33.24 | 22.64 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 11:00 | 58.68 | 43.89 | 43.89 | 14.79 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 12:00 | 59.59 | 47 | 47 | 12.58 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 13:00 | 61.04 | 29.48 | 29.48 | 31.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 14:00 | 62.28 | 21.67 | 21.67 | 40.61 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 15:00 | 62.8 | 7.56 | 7.56 | 55.24 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 16:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 17:00 | 61.89 | 0 | 0 | 61.89 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 18:00 | 59.48 | 0 | 0 | 59.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 19:00 | 58 | 0 | 0 | 58 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 20:00 | 55.94 | 0 | 0 | 55.94 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 21:00 | 53.14 | 0 | 0 | 53.14 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 22:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 12.51 | 0 | 0
2025-10-23 23:00 | 48.87 | 0 | 0 | 48.87 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 01:00 | 45.48 | 0 | 0 | 45.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 02:00 | 44.69 | 0 | 0 | 44.69 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 03:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 04:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 05:00 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 06:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 07:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 08:00 | 50.92 | 10.36 | 10.36 | 40.56 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 09:00 | 52.02 | 18.85 | 18.85 | 33.16 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 10:00 | 55.33 | 8.08 | 8.08 | 47.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 11:00 | 58.36 | 4.44 | 4.44 | 53.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 12:00 | 59.79 | 11.03 | 11.03 | 48.77 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 13:00 | 61.44 | 79.97 | 79.97 | 0 | 18.53 | 0 | 30.11 | 0 | 0
2025-10-24 14:00 | 60.84 | 59.12 | 59.12 | 0 | 0 | 1.73 | 28.3 | 0 | 0
2025-10-24 15:00 | 62.48 | 32.51 | 32.51 | 14.98 | 0 | 15 | 12.51 | 0 | 0
2025-10-24 16:00 | 62.52 | 32.38 | 32.38 | 30.14 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 17:00 | 61.62 | 0 | 0 | 61.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 18:00 | 60.34 | 0 | 0 | 60.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 19:00 | 57.78 | 0 | 0 | 57.78 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 20:00 | 55.53 | 0 | 0 | 55.53 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 21:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 22:00 | 50.73 | 0 | 0 | 50.73 | 0 | 0 | 12.51 | 0 | 0
2025-10-24 23:00 | 48.01 | 0 | 0 | 48.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 | 45.66 | 0 | 0 | 45.66 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 01:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 02:00 | 45.12 | 0 | 0 | 45.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 03:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 04:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 05:00 | 44.97 | 0 | 0 | 44.97 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 06:00 | 45.69 | 0 | 0 | 45.69 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 07:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 08:00 | 49.26 | 7.75 | 7.75 | 41.5 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 09:00 | 52.18 | 41.01 | 41.01 | 11.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 10:00 | 54.51 | 38.7 | 38.7 | 15.81 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 11:00 | 56.55 | 38.68 | 38.68 | 17.87 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 12:00 | 57.68 | 33.97 | 33.97 | 23.71 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 13:00 | 58.34 | 33.76 | 33.76 | 24.58 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 14:00 | 59.61 | 13.37 | 13.37 | 46.24 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 15:00 | 59.89 | 1.43 | 1.43 | 58.46 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 16:00 | 59.62 | 1.86 | 1.86 | 57.77 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 17:00 | 59.74 | 0 | 0 | 59.74 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 18:00 | 57.43 | 0 | 0 | 57.43 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 19:00 | 56.59 | 0 | 0 | 56.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 20:00 | 54.62 | 0 | 0 | 54.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 21:00 | 52.94 | 0 | 0 | 52.94 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 22:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 12.51 | 0 | 0
2025-10-25 23:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 01:00 | 45.28 | 0 | 0 | 45.28 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 02:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 03:00 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 04:00 | 44.42 | 0 | 0 | 44.42 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 05:00 | 45.28 | 0 | 0 | 45.28 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 06:00 | 46.58 | 0 | 0 | 46.58 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 07:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 08:00 | 50.3 | 1.08 | 1.08 | 49.22 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 09:00 | 50.94 | 2.57 | 2.57 | 48.37 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 10:00 | 52.81 | 82.06 | 82.06 | 0 | 29.25 | 0 | 40.3 | 0 | 0
2025-10-26 11:00 | 54.06 | 78.47 | 78.47 | 0 | 24.41 | 0 | 63.48 | 0 | 0
2025-10-26 12:00 | 55.5 | 76.59 | 76.59 | 0 | 21.09 | 0 | 83.52 | 0 | 0
2025-10-26 13:00 | 55.08 | 83.42 | 83.42 | 0 | 28.34 | 0 | 110.44 | 0 | 0
2025-10-26 14:00 | 55.25 | 91.5 | 57.51 | 0 | 2.27 | 0 | 112.59 | 33.99 | 0
2025-10-26 15:00 | 54.94 | 92.98 | 54.94 | 0 | 0 | 0 | 112.59 | 38.04 | 0
2025-10-26 16:00 | 56.35 | 42.52 | 42.52 | 0 | 0 | 13.83 | 98.03 | 0 | 0
2025-10-26 17:00 | 55.45 | 0 | 0 | 0 | 0 | 55.45 | 39.67 | 0 | 0
2025-10-26 18:00 | 54.87 | 0 | 0 | 29.07 | 0 | 25.8 | 12.51 | 0 | 0
2025-10-26 19:00 | 55.32 | 0 | 0 | 55.32 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 20:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 21:00 | 50.52 | 0 | 0 | 50.52 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 22:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 12.51 | 0 | 0
2025-10-26 23:00 | 47.41 | 0 | 0 | 47.41 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 | 46.12 | 0 | 0 | 46.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 01:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 02:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 03:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 04:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 05:00 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 06:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 07:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 08:00 | 50.48 | 5.14 | 5.14 | 45.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 09:00 | 52.69 | 2.6 | 2.6 | 50.09 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 10:00 | 55.24 | 3.9 | 3.9 | 51.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 11:00 | 57.18 | 4.67 | 4.67 | 52.51 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 12:00 | 59.38 | 4.78 | 4.78 | 54.6 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 13:00 | 60.91 | 68.43 | 68.43 | 0 | 7.52 | 0 | 19.65 | 0 | 0
2025-10-27 14:00 | 61.56 | 93.64 | 93.64 | 0 | 32.08 | 0 | 50.13 | 0 | 0
2025-10-27 15:00 | 61.69 | 96.07 | 96.07 | 0 | 34.38 | 0 | 82.79 | 0 | 0
2025-10-27 16:00 | 62.24 | 43.22 | 43.22 | 0 | 0 | 19.02 | 62.77 | 0 | 0
2025-10-27 17:00 | 60.3 | 0 | 0 | 12.55 | 0 | 47.75 | 12.51 | 0 | 0
2025-10-27 18:00 | 59.24 | 0 | 0 | 59.24 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 19:00 | 57.32 | 0 | 0 | 57.32 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 20:00 | 54.6 | 0 | 0 | 54.6 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 21:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 22:00 | 50.07 | 0 | 0 | 50.07 | 0 | 0 | 12.51 | 0 | 0
2025-10-27 23:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 01:00 | 44.51 | 0 | 0 | 44.51 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 02:00 | 44.1 | 0 | 0 | 44.1 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 03:00 | 44.32 | 0 | 0 | 44.32 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 04:00 | 44.25 | 0 | 0 | 44.25 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 05:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 06:00 | 46.58 | 0 | 0 | 46.58 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 07:00 | 47.93 | 10.22 | 10.22 | 37.71 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 08:00 | 50.85 | 88.4 | 88.4 | 0 | 37.54 | 0 | 48.17 | 0 | 0
2025-10-28 09:00 | 53.38 | 92.23 | 92.23 | 0 | 38.85 | 0 | 85.08 | 0 | 0
2025-10-28 10:00 | 56.23 | 83.94 | 83.94 | 0 | 27.71 | 0 | 111.4 | 0 | 0
2025-10-28 11:00 | 59.17 | 74.88 | 60.42 | 0 | 1.25 | 0 | 112.59 | 14.46 | 0
2025-10-28 12:00 | 61.82 | 72.43 | 61.82 | 0 | 0 | 0 | 112.59 | 10.62 | 0
2025-10-28 13:00 | 64.58 | 79.01 | 64.58 | 0 | 0 | 0 | 112.59 | 14.43 | 0
2025-10-28 14:00 | 65.24 | 86.72 | 65.24 | 0 | 0 | 0 | 112.59 | 21.49 | 0
2025-10-28 15:00 | 66.25 | 85.97 | 66.25 | 0 | 0 | 0 | 112.59 | 19.72 | 0
2025-10-28 16:00 | 65.72 | 34.71 | 34.71 | 0 | 0 | 31.01 | 79.95 | 0 | 0
2025-10-28 17:00 | 64.24 | 0 | 0 | 1.74 | 0 | 62.5 | 14.16 | 0 | 0
2025-10-28 18:00 | 60.94 | 0 | 0 | 59.36 | 0 | 1.57 | 12.51 | 0 | 0
2025-10-28 19:00 | 59.78 | 0 | 0 | 59.78 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 20:00 | 56.1 | 0 | 0 | 56.1 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 21:00 | 53.75 | 0 | 0 | 53.75 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 22:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 12.51 | 0 | 0
2025-10-28 23:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 | 46.88 | 0 | 0 | 46.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 01:00 | 44.17 | 0 | 0 | 44.17 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 02:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 03:00 | 43.61 | 0 | 0 | 43.61 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 04:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 05:00 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 06:00 | 45.24 | 0 | 0 | 45.24 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 07:00 | 47.41 | 0 | 0 | 47.41 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 08:00 | 48.54 | 2.51 | 2.51 | 46.03 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 09:00 | 50.52 | 5.53 | 5.53 | 44.99 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 10:00 | 52.66 | 8.27 | 8.27 | 44.39 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 11:00 | 53.56 | 8.93 | 8.93 | 44.64 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 12:00 | 53.65 | 10.16 | 10.16 | 43.49 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 13:00 | 55.49 | 9.15 | 9.15 | 46.34 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 14:00 | 55.45 | 6.65 | 6.65 | 48.8 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 15:00 | 55.31 | 3.73 | 3.73 | 51.58 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 16:00 | 55.83 | 0.22 | 0.22 | 55.61 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 17:00 | 54.98 | 0 | 0 | 54.98 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 18:00 | 53.81 | 0 | 0 | 53.81 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 19:00 | 54.36 | 0 | 0 | 54.36 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 20:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 21:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 22:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 12.51 | 0 | 0
2025-10-29 23:00 | 48.01 | 0 | 0 | 48.01 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 | 45.62 | 0 | 0 | 45.62 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 01:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 02:00 | 43.37 | 0 | 0 | 43.37 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 03:00 | 44.09 | 0 | 0 | 44.09 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 04:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 05:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 06:00 | 46.57 | 0 | 0 | 46.57 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 07:00 | 48.07 | 9.33 | 9.33 | 38.74 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 08:00 | 49.73 | 81.6 | 81.6 | 0 | 31.87 | 0 | 42.78 | 0 | 0
2025-10-30 09:00 | 52.2 | 87.08 | 87.08 | 0 | 34.88 | 0 | 75.92 | 0 | 0
2025-10-30 10:00 | 54.94 | 76.26 | 76.26 | 0 | 21.32 | 0 | 96.17 | 0 | 0
2025-10-30 11:00 | 56.77 | 69.35 | 69.35 | 0 | 12.59 | 0 | 108.13 | 0 | 0
2025-10-30 12:00 | 59.31 | 65.61 | 64.01 | 0 | 4.7 | 0 | 112.59 | 1.6 | 0
2025-10-30 13:00 | 61.13 | 72.31 | 61.13 | 0 | 0 | 0 | 112.59 | 11.18 | 0
2025-10-30 14:00 | 61.2 | 77.98 | 61.2 | 0 | 0 | 0 | 112.59 | 16.79 | 0
2025-10-30 15:00 | 62.32 | 74.05 | 62.32 | 0 | 0 | 0 | 112.59 | 11.73 | 0
2025-10-30 16:00 | 61.89 | 25.5 | 25.5 | 0 | 0 | 36.39 | 74.29 | 0 | 0
2025-10-30 17:00 | 61.49 | 0 | 0 | 2.8 | 0 | 58.69 | 12.51 | 0 | 0
2025-10-30 18:00 | 58.39 | 0 | 0 | 58.39 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 19:00 | 56.99 | 0 | 0 | 56.99 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 20:00 | 54.54 | 0 | 0 | 54.54 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 21:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 22:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 12.51 | 0 | 0
2025-10-30 23:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 01:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 02:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 03:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 04:00 | 44 | 0 | 0 | 44 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 05:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 06:00 | 45.24 | 0 | 0 | 45.24 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 07:00 | 47.53 | 7.4 | 7.4 | 40.12 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 08:00 | 49.8 | 73.86 | 73.86 | 0 | 24.06 | 0 | 35.37 | 0 | 0
2025-10-31 09:00 | 50.08 | 83.02 | 83.02 | 0 | 32.94 | 0 | 66.66 | 0 | 0
2025-10-31 10:00 | 53.83 | 77.12 | 77.12 | 0 | 23.29 | 0 | 88.79 | 0 | 0
2025-10-31 11:00 | 54.87 | 69.56 | 69.56 | 0 | 14.69 | 0 | 102.75 | 0 | 0
2025-10-31 12:00 | 55.52 | 67.55 | 65.88 | 0 | 10.36 | 0 | 112.59 | 1.67 | 0
2025-10-31 13:00 | 56.12 | 71.26 | 56.12 | 0 | 0 | 0 | 112.59 | 15.14 | 0
2025-10-31 14:00 | 57.57 | 77.76 | 57.57 | 0 | 0 | 0 | 112.59 | 20.19 | 0
2025-10-31 15:00 | 58.57 | 71.61 | 58.57 | 0 | 0 | 0 | 112.59 | 13.04 | 0
2025-10-31 16:00 | 58.3 | 24.32 | 24.32 | 0 | 0 | 33.98 | 76.82 | 0 | 0
2025-10-31 17:00 | 57.93 | 0 | 0 | 0 | 0 | 57.93 | 15.84 | 0 | 0
2025-10-31 18:00 | 56.19 | 0 | 0 | 53.02 | 0 | 3.16 | 12.51 | 0 | 0
2025-10-31 19:00 | 54.39 | 0 | 0 | 54.39 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 20:00 | 52.93 | 0 | 0 | 52.93 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 21:00 | 51.2 | 0 | 0 | 51.2 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 22:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 12.51 | 0 | 0
2025-10-31 23:00 | 46.9 | 0 | 0 | 46.9 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 | 45.97 | 0 | 0 | 45.97 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 01:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 02:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 03:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 04:00 | 43.98 | 0 | 0 | 43.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 05:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 06:00 | 45.17 | 0 | 0 | 45.17 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 07:00 | 47.64 | 8.66 | 8.66 | 38.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 08:00 | 50.17 | 78.96 | 78.96 | 0 | 28.79 | 0 | 39.86 | 0 | 0
2025-11-01 09:00 | 51.26 | 84.54 | 84.54 | 0 | 33.28 | 0 | 71.48 | 0 | 0
2025-11-01 10:00 | 53.82 | 75.31 | 75.31 | 0 | 21.48 | 0 | 91.89 | 0 | 0
2025-11-01 11:00 | 55.63 | 66.36 | 66.36 | 0 | 10.73 | 0 | 102.09 | 0 | 0
2025-11-01 12:00 | 56.44 | 64.83 | 64.83 | 0 | 8.38 | 0 | 110.05 | 0 | 0
2025-11-01 13:00 | 58.01 | 72.9 | 60.69 | 0 | 2.67 | 0 | 112.59 | 12.21 | 0
2025-11-01 14:00 | 58.14 | 81.99 | 58.14 | 0 | 0 | 0 | 112.59 | 23.85 | 0
2025-11-01 15:00 | 58.95 | 81.75 | 58.95 | 0 | 0 | 0 | 112.59 | 22.8 | 0
2025-11-01 16:00 | 58.47 | 25.92 | 25.92 | 0 | 0 | 32.55 | 78.32 | 0 | 0
2025-11-01 17:00 | 57.8 | 0 | 0 | 0 | 0 | 57.8 | 17.49 | 0 | 0
2025-11-01 18:00 | 56.37 | 0 | 0 | 51.65 | 0 | 4.73 | 12.51 | 0 | 0
2025-11-01 19:00 | 54.97 | 0 | 0 | 54.97 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 20:00 | 53.47 | 0 | 0 | 53.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 21:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 22:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 12.51 | 0 | 0
2025-11-01 23:00 | 46.8 | 0 | 0 | 46.8 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 | 44.54 | 0 | 0 | 44.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 01:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 02:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 03:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 04:00 | 42.92 | 0 | 0 | 42.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 05:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 06:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 07:00 | 46.25 | 13.05 | 13.05 | 33.2 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 08:00 | 48.88 | 92.32 | 92.32 | 0 | 43.44 | 0 | 53.77 | 0 | 0
2025-11-02 09:00 | 50.64 | 97.09 | 97.09 | 0 | 46.45 | 0 | 97.9 | 0 | 0
2025-11-02 10:00 | 52.32 | 88.73 | 67.77 | 0 | 15.46 | 0 | 112.59 | 20.96 | 0
2025-11-02 11:00 | 52.95 | 77.86 | 52.95 | 0 | 0 | 0 | 112.59 | 24.91 | 0
2025-11-02 12:00 | 54.99 | 16.46 | 16.46 | 0 | 0 | 38.53 | 72.03 | 0 | 0
2025-11-02 13:00 | 54.99 | 42.96 | 42.96 | 0 | 0 | 12.03 | 59.37 | 0 | 0
2025-11-02 14:00 | 56.07 | 34.96 | 34.96 | 0 | 0 | 21.11 | 37.16 | 0 | 0
2025-11-02 15:00 | 55.65 | 1.17 | 1.17 | 31.07 | 0 | 23.42 | 12.51 | 0 | 0
2025-11-02 16:00 | 55.63 | 0 | 0 | 55.63 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 17:00 | 54.02 | 0 | 0 | 54.02 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 18:00 | 54.25 | 0 | 0 | 54.25 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 19:00 | 53.3 | 0 | 0 | 53.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 20:00 | 51.64 | 0 | 0 | 51.64 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 21:00 | 51.1 | 0 | 0 | 51.1 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 22:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-02 23:00 | 46.54 | 0 | 0 | 46.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 | 44.74 | 0 | 0 | 44.74 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 01:00 | 43.68 | 0 | 0 | 43.68 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 02:00 | 43.7 | 0 | 0 | 43.7 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 03:00 | 43.65 | 0 | 0 | 43.65 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 04:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 05:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 06:00 | 44.61 | 0 | 0 | 44.61 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 07:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 08:00 | 49.16 | 0.9 | 0.9 | 48.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 09:00 | 50.47 | 2.13 | 2.13 | 48.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 10:00 | 51.72 | 3.34 | 3.34 | 48.37 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 11:00 | 53.5 | 4.62 | 4.62 | 48.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 12:00 | 55.7 | 5.43 | 5.43 | 50.27 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 13:00 | 57 | 53.1 | 53.1 | 3.9 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 14:00 | 56.39 | 55.58 | 55.58 | 0.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 15:00 | 57.5 | 52.71 | 52.71 | 4.78 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 16:00 | 58.23 | 17.33 | 17.33 | 40.91 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 17:00 | 56.62 | 0 | 0 | 56.62 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 18:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 19:00 | 54.48 | 0 | 0 | 54.48 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 20:00 | 51.87 | 0 | 0 | 51.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 21:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 22:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 12.51 | 0 | 0
2025-11-03 23:00 | 46.3 | 0 | 0 | 46.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 | 44.65 | 0 | 0 | 44.65 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 01:00 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 02:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 03:00 | 43.33 | 0 | 0 | 43.33 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 04:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 05:00 | 43.83 | 0 | 0 | 43.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 06:00 | 45.42 | 0 | 0 | 45.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 07:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 08:00 | 49.32 | 5.42 | 5.42 | 43.89 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 09:00 | 50.42 | 10.87 | 10.87 | 39.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 10:00 | 54.2 | 16.98 | 16.98 | 37.22 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 11:00 | 55.22 | 16.53 | 16.53 | 38.7 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 12:00 | 58.55 | 16.47 | 16.47 | 42.08 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 13:00 | 60.84 | 13.74 | 13.74 | 47.1 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 14:00 | 61.85 | 12.16 | 12.16 | 49.69 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 15:00 | 61.27 | 4.95 | 4.95 | 56.32 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 16:00 | 60.95 | 0.5 | 0.5 | 60.45 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 17:00 | 60.07 | 0 | 0 | 60.07 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 18:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 19:00 | 55.44 | 0 | 0 | 55.44 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 20:00 | 53.98 | 0 | 0 | 53.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 21:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 22:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 12.51 | 0 | 0
2025-11-04 23:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 | 45.05 | 0 | 0 | 45.05 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 01:00 | 43.42 | 0 | 0 | 43.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 02:00 | 41.95 | 0 | 0 | 41.95 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 03:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 04:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 05:00 | 43.4 | 0 | 0 | 43.4 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 06:00 | 45.18 | 0 | 0 | 45.18 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 07:00 | 47.3 | 0 | 0 | 47.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 08:00 | 48.54 | 1.4 | 1.4 | 47.14 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 09:00 | 51 | 3.46 | 3.46 | 47.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 10:00 | 52.22 | 5.29 | 5.29 | 46.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 11:00 | 55.18 | 6.75 | 6.75 | 48.43 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 12:00 | 56.88 | 6.83 | 6.83 | 50.05 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 13:00 | 58.97 | 6.08 | 6.08 | 52.89 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 14:00 | 59 | 4.48 | 4.48 | 54.52 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 15:00 | 59.47 | 2.25 | 2.25 | 57.22 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 16:00 | 59.81 | 0 | 0 | 59.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 17:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 18:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 19:00 | 56.33 | 0 | 0 | 56.33 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 20:00 | 52.4 | 0 | 0 | 52.4 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 21:00 | 50.69 | 0 | 0 | 50.69 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 22:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-05 23:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 | 44.76 | 0 | 0 | 44.76 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 01:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 02:00 | 42.68 | 0 | 0 | 42.68 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 03:00 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 04:00 | 43.87 | 0 | 0 | 43.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 05:00 | 43.46 | 0 | 0 | 43.46 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 06:00 | 45.15 | 0 | 0 | 45.15 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 07:00 | 46.45 | 0.26 | 0.26 | 46.19 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 08:00 | 48.62 | 7.19 | 7.19 | 41.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 09:00 | 51.06 | 11.84 | 11.84 | 39.22 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 10:00 | 53.16 | 13.9 | 13.9 | 39.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 11:00 | 56.46 | 17.53 | 17.53 | 38.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 12:00 | 58.69 | 16.46 | 16.46 | 42.24 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 13:00 | 61.36 | 16.65 | 16.65 | 44.71 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 14:00 | 61.38 | 12.91 | 12.91 | 48.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 15:00 | 62.11 | 9.48 | 9.48 | 52.63 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 16:00 | 61.53 | 3.8 | 3.8 | 57.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 17:00 | 61.49 | 0 | 0 | 61.49 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 18:00 | 58.46 | 0 | 0 | 58.46 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 19:00 | 56.83 | 0 | 0 | 56.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 20:00 | 54.42 | 0 | 0 | 54.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 21:00 | 51.21 | 0 | 0 | 51.21 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 22:00 | 48.1 | 0 | 0 | 48.1 | 0 | 0 | 12.51 | 0 | 0
2025-11-06 23:00 | 45.93 | 0 | 0 | 45.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 01:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 02:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 03:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 04:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 05:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 06:00 | 44.2 | 0 | 0 | 44.2 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 07:00 | 45.86 | 1.77 | 1.77 | 44.09 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 08:00 | 48.74 | 7.53 | 7.53 | 41.21 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 09:00 | 50.37 | 58.58 | 58.58 | 0 | 8.21 | 0 | 20.31 | 0 | 0
2025-11-07 10:00 | 51.7 | 57.71 | 57.71 | 0 | 6.01 | 0 | 26.02 | 0 | 0
2025-11-07 11:00 | 55.74 | 40.3 | 40.3 | 2.6 | 0 | 12.83 | 12.51 | 0 | 0
2025-11-07 12:00 | 56.97 | 51.62 | 51.62 | 5.35 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 13:00 | 59.36 | 58.44 | 58.44 | 0.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 14:00 | 60.87 | 22.09 | 22.09 | 38.78 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 15:00 | 60.55 | 38.12 | 38.12 | 22.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 16:00 | 60.67 | 0 | 0 | 60.67 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 17:00 | 59.2 | 0 | 0 | 59.2 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 18:00 | 58.28 | 0 | 0 | 58.28 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 19:00 | 54.88 | 0 | 0 | 54.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 20:00 | 53.08 | 0 | 0 | 53.08 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 21:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 22:00 | 48.29 | 0 | 0 | 48.29 | 0 | 0 | 12.51 | 0 | 0
2025-11-07 23:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 01:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 02:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 03:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 04:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 05:00 | 43.87 | 0 | 0 | 43.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 06:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 07:00 | 45.39 | 0.27 | 0.27 | 45.12 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 08:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 09:00 | 50.1 | 2.11 | 2.11 | 47.99 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 10:00 | 51.93 | 17.94 | 17.94 | 33.99 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 11:00 | 54.03 | 75.13 | 75.13 | 0 | 21.1 | 0 | 32.55 | 0 | 0
2025-11-08 12:00 | 54.56 | 19.7 | 19.7 | 15.82 | 0 | 19.04 | 12.51 | 0 | 0
2025-11-08 13:00 | 56.99 | 20.22 | 20.22 | 36.78 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 14:00 | 57.56 | 79.27 | 79.27 | 0 | 21.71 | 0 | 33.14 | 0 | 0
2025-11-08 15:00 | 58.69 | 16.65 | 16.65 | 22.44 | 0 | 19.6 | 12.51 | 0 | 0
2025-11-08 16:00 | 58.44 | 15.89 | 15.89 | 42.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 17:00 | 57.38 | 0 | 0 | 57.38 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 18:00 | 55.95 | 0 | 0 | 55.95 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 19:00 | 53.27 | 0 | 0 | 53.27 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 20:00 | 52.34 | 0 | 0 | 52.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 21:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 22:00 | 48.54 | 0 | 0 | 48.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-08 23:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 01:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 02:00 | 42.04 | 0 | 0 | 42.04 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 03:00 | 42.24 | 0 | 0 | 42.24 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 04:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 05:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 06:00 | 44.91 | 0 | 0 | 44.91 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 07:00 | 45.54 | 4.72 | 4.72 | 40.82 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 08:00 | 47.68 | 77.59 | 77.59 | 0 | 29.91 | 0 | 40.93 | 0 | 0
2025-11-09 09:00 | 50.09 | 91.38 | 91.38 | 0 | 41.29 | 0 | 80.15 | 0 | 0
2025-11-09 10:00 | 52.98 | 77.83 | 77.83 | 0 | 24.85 | 0 | 103.75 | 0 | 0
2025-11-09 11:00 | 55.07 | 22.06 | 22.06 | 0 | 0 | 33.01 | 69.01 | 0 | 0
2025-11-09 12:00 | 57.93 | 5.94 | 5.94 | 0 | 0 | 51.99 | 14.28 | 0 | 0
2025-11-09 13:00 | 59.68 | 3.17 | 3.17 | 54.83 | 0 | 1.68 | 12.51 | 0 | 0
2025-11-09 14:00 | 60.54 | 2.19 | 2.19 | 58.35 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 15:00 | 61.78 | 0.88 | 0.88 | 60.9 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 16:00 | 60.91 | 0 | 0 | 60.91 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 17:00 | 60.3 | 0 | 0 | 60.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 18:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 19:00 | 55.67 | 0 | 0 | 55.67 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 20:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 21:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 22:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-09 23:00 | 45.89 | 0 | 0 | 45.89 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 01:00 | 42.6 | 0 | 0 | 42.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 02:00 | 42.66 | 0 | 0 | 42.66 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 03:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 04:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 05:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 06:00 | 44.93 | 0 | 0 | 44.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 07:00 | 45.13 | 0 | 0 | 45.13 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 08:00 | 46.8 | 0.95 | 0.95 | 45.85 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 09:00 | 49.22 | 2.96 | 2.96 | 46.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 10:00 | 50.87 | 5.26 | 5.26 | 45.61 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 11:00 | 52.8 | 6.29 | 6.29 | 46.51 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 12:00 | 55.48 | 6.61 | 6.61 | 48.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 13:00 | 56.48 | 5.69 | 5.69 | 50.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 14:00 | 57.07 | 3.91 | 3.91 | 53.16 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 15:00 | 57.4 | 1.78 | 1.78 | 55.62 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 16:00 | 57.01 | 0 | 0 | 57.01 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 17:00 | 57.3 | 0 | 0 | 57.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 18:00 | 54.8 | 0 | 0 | 54.8 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 19:00 | 52.83 | 0 | 0 | 52.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 20:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 21:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 22:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-10 23:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 01:00 | 43.42 | 0 | 0 | 43.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 02:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 03:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 04:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 05:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 06:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 07:00 | 45.04 | 0 | 0 | 45.04 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 08:00 | 46.21 | 3.7 | 3.7 | 42.51 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 09:00 | 49.86 | 10.26 | 10.26 | 39.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 10:00 | 51.58 | 3.68 | 3.68 | 47.91 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 11:00 | 53.7 | 13.61 | 13.61 | 40.09 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 12:00 | 54.77 | 22.77 | 22.77 | 32 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 13:00 | 56.5 | 24.66 | 24.66 | 31.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 14:00 | 57.72 | 21.18 | 21.18 | 36.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 15:00 | 57.94 | 10.05 | 10.05 | 47.89 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 16:00 | 58.02 | 0.73 | 0.73 | 57.29 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 17:00 | 57.34 | 0 | 0 | 57.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 18:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 19:00 | 53.78 | 0 | 0 | 53.78 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 20:00 | 52.27 | 0 | 0 | 52.27 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 21:00 | 49.15 | 0 | 0 | 49.15 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 22:00 | 46.64 | 0 | 0 | 46.64 | 0 | 0 | 12.51 | 0 | 0
2025-11-11 23:00 | 45.43 | 0 | 0 | 45.43 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 01:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 02:00 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 03:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 04:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 05:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 06:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 07:00 | 45.71 | 1.16 | 1.16 | 44.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 08:00 | 46.53 | 43.76 | 43.76 | 2.77 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 09:00 | 49.18 | 57.49 | 57.49 | 0 | 8.31 | 0 | 20.41 | 0 | 0
2025-11-12 10:00 | 49.98 | 45.12 | 45.12 | 0 | 0 | 4.85 | 15.3 | 0 | 0
2025-11-12 11:00 | 51.64 | 49.62 | 49.62 | 0 | 0 | 2.02 | 13.17 | 0 | 0
2025-11-12 12:00 | 53.42 | 49.28 | 49.28 | 3.51 | 0 | 0.63 | 12.51 | 0 | 0
2025-11-12 13:00 | 54.55 | 53.67 | 53.67 | 0.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 14:00 | 55.27 | 69.08 | 69.08 | 0 | 13.81 | 0 | 25.63 | 0 | 0
2025-11-12 15:00 | 55.06 | 77.54 | 77.54 | 0 | 22.48 | 0 | 46.99 | 0 | 0
2025-11-12 16:00 | 55.15 | 14.43 | 14.43 | 7.97 | 0 | 32.75 | 12.51 | 0 | 0
2025-11-12 17:00 | 54.63 | 0 | 0 | 54.63 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 18:00 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 19:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 20:00 | 49.62 | 0 | 0 | 49.62 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 21:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 22:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-12 23:00 | 45.05 | 0 | 0 | 45.05 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 | 44.34 | 0 | 0 | 44.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 01:00 | 41.88 | 0 | 0 | 41.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 02:00 | 42.72 | 0 | 0 | 42.72 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 03:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 04:00 | 42.06 | 0 | 0 | 42.06 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 05:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 06:00 | 42.87 | 0 | 0 | 42.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 07:00 | 45.08 | 0.68 | 0.68 | 44.4 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 08:00 | 47 | 45.31 | 45.31 | 1.69 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 09:00 | 48.99 | 54.07 | 54.07 | 0 | 5.08 | 0 | 17.34 | 0 | 0
2025-11-13 10:00 | 50.37 | 61.67 | 61.67 | 0 | 11.29 | 0 | 28.07 | 0 | 0
2025-11-13 11:00 | 51.08 | 55 | 55 | 0 | 3.92 | 0 | 31.79 | 0 | 0
2025-11-13 12:00 | 52.87 | 48.74 | 48.74 | 0 | 0 | 4.13 | 27.44 | 0 | 0
2025-11-13 13:00 | 55.79 | 47.27 | 47.27 | 0 | 0 | 8.53 | 18.47 | 0 | 0
2025-11-13 14:00 | 54.93 | 35.88 | 35.88 | 13.39 | 0 | 5.66 | 12.51 | 0 | 0
2025-11-13 15:00 | 56.43 | 23.31 | 23.31 | 33.12 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 16:00 | 55.01 | 3.52 | 3.52 | 51.49 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 17:00 | 54.68 | 0 | 0 | 54.68 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 18:00 | 53.95 | 0 | 0 | 53.95 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 19:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 20:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 21:00 | 48.69 | 0 | 0 | 48.69 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 22:00 | 47.07 | 0 | 0 | 47.07 | 0 | 0 | 12.51 | 0 | 0
2025-11-13 23:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 01:00 | 43.24 | 0 | 0 | 43.24 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 02:00 | 41.71 | 0 | 0 | 41.71 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 03:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 04:00 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 05:00 | 42.84 | 0 | 0 | 42.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 06:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 07:00 | 44.33 | 0 | 0 | 44.33 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 08:00 | 46.5 | 1.29 | 1.29 | 45.21 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 09:00 | 47.97 | 6.61 | 6.61 | 41.37 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 10:00 | 49.07 | 25.82 | 25.82 | 23.25 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 11:00 | 51.04 | 28.6 | 28.6 | 22.44 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 12:00 | 52.07 | 43.01 | 43.01 | 9.06 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 13:00 | 52.8 | 42.12 | 42.12 | 10.69 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 14:00 | 53.32 | 11.32 | 11.32 | 42 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 15:00 | 53.49 | 4.89 | 4.89 | 48.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 16:00 | 53.18 | 0.7 | 0.7 | 52.48 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 17:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 18:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 19:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 20:00 | 48.79 | 0 | 0 | 48.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 21:00 | 47.68 | 0 | 0 | 47.68 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 22:00 | 46.14 | 0 | 0 | 46.14 | 0 | 0 | 12.51 | 0 | 0
2025-11-14 23:00 | 45.88 | 0 | 0 | 45.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 01:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 02:00 | 41.78 | 0 | 0 | 41.78 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 03:00 | 41.59 | 0 | 0 | 41.59 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 04:00 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 05:00 | 42.95 | 0 | 0 | 42.95 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 06:00 | 43.23 | 0 | 0 | 43.23 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 07:00 | 45.06 | 0.33 | 0.33 | 44.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 08:00 | 45.84 | 23.22 | 23.22 | 22.62 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 09:00 | 48.84 | 52.96 | 52.96 | 0 | 4.11 | 0 | 16.42 | 0 | 0
2025-11-15 10:00 | 50.5 | 62.63 | 62.63 | 0 | 12.13 | 0 | 27.94 | 0 | 0
2025-11-15 11:00 | 52.84 | 51.12 | 51.12 | 0 | 0 | 1.72 | 26.13 | 0 | 0
2025-11-15 12:00 | 53.89 | 40.63 | 40.63 | 0.33 | 0 | 12.94 | 12.51 | 0 | 0
2025-11-15 13:00 | 56.36 | 46.06 | 46.06 | 10.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 14:00 | 56.21 | 66.14 | 66.14 | 0 | 9.93 | 0 | 21.94 | 0 | 0
2025-11-15 15:00 | 57.45 | 78.4 | 78.4 | 0 | 20.95 | 0 | 41.85 | 0 | 0
2025-11-15 16:00 | 56.45 | 9.74 | 9.74 | 18.84 | 0 | 27.87 | 12.51 | 0 | 0
2025-11-15 17:00 | 55.73 | 0 | 0 | 55.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 18:00 | 55.31 | 0 | 0 | 55.31 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 19:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 20:00 | 51.48 | 0 | 0 | 51.48 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 21:00 | 49.58 | 0 | 0 | 49.58 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 22:00 | 46.39 | 0 | 0 | 46.39 | 0 | 0 | 12.51 | 0 | 0
2025-11-15 23:00 | 45.71 | 0 | 0 | 45.71 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 | 42.47 | 0 | 0 | 42.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 01:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 02:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 04:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 05:00 | 42.66 | 0 | 0 | 42.66 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 06:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 07:00 | 44.58 | 0 | 0 | 44.58 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 08:00 | 45.93 | 37.26 | 37.26 | 8.67 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 09:00 | 47.54 | 22.44 | 22.44 | 25.1 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 10:00 | 48.74 | 42.77 | 42.77 | 5.97 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 11:00 | 50 | 46.41 | 46.41 | 3.59 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 12:00 | 50.75 | 21.76 | 21.76 | 28.99 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 13:00 | 51.73 | 18.69 | 18.69 | 33.03 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 14:00 | 50.89 | 1.59 | 1.59 | 49.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 15:00 | 51.77 | 2.8 | 2.8 | 48.97 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 16:00 | 51.01 | 0.82 | 0.82 | 50.19 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 17:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 18:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 19:00 | 49.5 | 0 | 0 | 49.5 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 20:00 | 48.66 | 0 | 0 | 48.66 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 21:00 | 47.66 | 0 | 0 | 47.66 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 22:00 | 44.83 | 0 | 0 | 44.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-16 23:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 01:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 02:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 03:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 04:00 | 41.91 | 0 | 0 | 41.91 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 05:00 | 42.26 | 0 | 0 | 42.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 06:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 07:00 | 44.71 | 0 | 0 | 44.71 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 08:00 | 46.61 | 8.43 | 8.43 | 38.18 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 09:00 | 48.09 | 17.22 | 17.22 | 30.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 10:00 | 50.28 | 29.37 | 29.37 | 20.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 11:00 | 51.81 | 40.77 | 40.77 | 11.04 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 12:00 | 54.43 | 18.25 | 18.25 | 36.19 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 13:00 | 55.87 | 62.34 | 62.34 | 0 | 6.46 | 0 | 18.65 | 0 | 0
2025-11-17 14:00 | 56.64 | 20.53 | 20.53 | 30.27 | 0 | 5.83 | 12.51 | 0 | 0
2025-11-17 15:00 | 56.03 | 0 | 0 | 56.03 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 16:00 | 55.47 | 0 | 0 | 55.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 17:00 | 55.75 | 0 | 0 | 55.75 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 18:00 | 54.07 | 0 | 0 | 54.07 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 19:00 | 52.29 | 0 | 0 | 52.29 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 20:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 21:00 | 48.46 | 0 | 0 | 48.46 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 22:00 | 45.79 | 0 | 0 | 45.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-17 23:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 | 43.65 | 0 | 0 | 43.65 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 01:00 | 42.75 | 0 | 0 | 42.75 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 02:00 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 03:00 | 40.38 | 0 | 0 | 40.38 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 04:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 05:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 06:00 | 42.53 | 0 | 0 | 42.53 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 07:00 | 44.27 | 0.18 | 0.18 | 44.09 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 08:00 | 46.54 | 53.4 | 53.4 | 0 | 6.86 | 0 | 19.03 | 0 | 0
2025-11-18 09:00 | 47.78 | 79.11 | 79.11 | 0 | 31.34 | 0 | 48.8 | 0 | 0
2025-11-18 10:00 | 50.33 | 70.82 | 70.82 | 0 | 20.5 | 0 | 68.27 | 0 | 0
2025-11-18 11:00 | 50.22 | 59.18 | 59.18 | 0 | 8.96 | 0 | 76.78 | 0 | 0
2025-11-18 12:00 | 51.36 | 57.37 | 57.37 | 0 | 6.01 | 0 | 82.49 | 0 | 0
2025-11-18 13:00 | 53.44 | 66.25 | 66.25 | 0 | 12.81 | 0 | 94.66 | 0 | 0
2025-11-18 14:00 | 52.84 | 74.62 | 71.72 | 0 | 18.88 | 0 | 112.59 | 2.9 | 0
2025-11-18 15:00 | 53.55 | 75.34 | 53.55 | 0 | 0 | 0 | 112.59 | 21.79 | 0
2025-11-18 16:00 | 53.4 | 3.74 | 3.74 | 0 | 0 | 49.66 | 60.31 | 0 | 0
2025-11-18 17:00 | 53.35 | 0 | 0 | 7.93 | 0 | 45.41 | 12.51 | 0 | 0
2025-11-18 18:00 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 19:00 | 50.81 | 0 | 0 | 50.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 20:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 21:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 22:00 | 47.84 | 0 | 0 | 47.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-18 23:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 01:00 | 41.17 | 0 | 0 | 41.17 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 02:00 | 40.85 | 0 | 0 | 40.85 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 04:00 | 40.9 | 0 | 0 | 40.9 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 05:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 06:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 07:00 | 44.96 | 0 | 0 | 44.96 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 08:00 | 46.01 | 17.02 | 17.02 | 28.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 09:00 | 47.45 | 45.98 | 45.98 | 1.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 10:00 | 50.78 | 47.48 | 47.48 | 3.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 11:00 | 52.09 | 54.21 | 54.21 | 0 | 2.12 | 0 | 14.52 | 0 | 0
2025-11-19 12:00 | 53.03 | 50.53 | 50.53 | 0.59 | 0 | 1.91 | 12.51 | 0 | 0
2025-11-19 13:00 | 55.66 | 53.35 | 53.35 | 2.31 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 14:00 | 56.72 | 40.56 | 40.56 | 16.16 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 15:00 | 55.3 | 6.88 | 6.88 | 48.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 16:00 | 55.79 | 1 | 1 | 54.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 17:00 | 55.25 | 0 | 0 | 55.25 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 18:00 | 54.26 | 0 | 0 | 54.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 19:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 20:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 21:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 22:00 | 45.85 | 0 | 0 | 45.85 | 0 | 0 | 12.51 | 0 | 0
2025-11-19 23:00 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 | 42.17 | 0 | 0 | 42.17 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 01:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 02:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 03:00 | 40.96 | 0 | 0 | 40.96 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 04:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 05:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 06:00 | 42.33 | 0 | 0 | 42.33 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 07:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 08:00 | 45.01 | 26.2 | 26.2 | 18.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 09:00 | 48.23 | 59.6 | 59.6 | 0 | 11.36 | 0 | 23.31 | 0 | 0
2025-11-20 10:00 | 50.16 | 69.03 | 69.03 | 0 | 18.87 | 0 | 41.23 | 0 | 0
2025-11-20 11:00 | 51.74 | 62.24 | 62.24 | 0 | 10.5 | 0 | 51.21 | 0 | 0
2025-11-20 12:00 | 52.57 | 39.02 | 39.02 | 0 | 0 | 13.54 | 36.95 | 0 | 0
2025-11-20 13:00 | 53.75 | 52.56 | 52.56 | 0 | 0 | 1.19 | 35.7 | 0 | 0
2025-11-20 14:00 | 54.86 | 45.86 | 45.86 | 0 | 0 | 9 | 26.22 | 0 | 0
2025-11-20 15:00 | 54.59 | 48.79 | 48.79 | 0 | 0 | 5.8 | 20.12 | 0 | 0
2025-11-20 16:00 | 54.48 | 6.06 | 6.06 | 41.19 | 0 | 7.23 | 12.51 | 0 | 0
2025-11-20 17:00 | 54.49 | 0 | 0 | 54.49 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 18:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 19:00 | 50.79 | 0 | 0 | 50.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 20:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 21:00 | 47.83 | 0 | 0 | 47.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 22:00 | 46.53 | 0 | 0 | 46.53 | 0 | 0 | 12.51 | 0 | 0
2025-11-20 23:00 | 44.4 | 0 | 0 | 44.4 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 01:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 02:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 03:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 04:00 | 40.87 | 0 | 0 | 40.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 05:00 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 06:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 07:00 | 44.33 | 0 | 0 | 44.33 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 08:00 | 46.24 | 17.32 | 17.32 | 28.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 09:00 | 48.2 | 48.77 | 48.77 | 0 | 0.57 | 0 | 13.05 | 0 | 0
2025-11-21 10:00 | 50.14 | 23.17 | 23.17 | 26.46 | 0 | 0.51 | 12.51 | 0 | 0
2025-11-21 11:00 | 52.05 | 38.27 | 38.27 | 13.77 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 12:00 | 54.94 | 42.45 | 42.45 | 12.5 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 13:00 | 56.15 | 63.4 | 63.4 | 0 | 7.26 | 0 | 19.41 | 0 | 0
2025-11-21 14:00 | 56.48 | 60.74 | 60.74 | 0 | 4.26 | 0 | 23.46 | 0 | 0
2025-11-21 15:00 | 57.24 | 52.79 | 52.79 | 0 | 0 | 4.45 | 18.77 | 0 | 0
2025-11-21 16:00 | 56.12 | 3.04 | 3.04 | 47.13 | 0 | 5.95 | 12.51 | 0 | 0
2025-11-21 17:00 | 55.99 | 0 | 0 | 55.99 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 18:00 | 54.29 | 0 | 0 | 54.29 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 19:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 20:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 21:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 22:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 12.51 | 0 | 0
2025-11-21 23:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 | 42.99 | 0 | 0 | 42.99 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 01:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 02:00 | 40.25 | 0 | 0 | 40.25 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 03:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 04:00 | 40.61 | 0 | 0 | 40.61 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 05:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 06:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 07:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 08:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 09:00 | 47.43 | 4.29 | 4.29 | 43.14 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 10:00 | 48.41 | 21.86 | 21.86 | 26.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 11:00 | 50.44 | 49.94 | 49.94 | 0.5 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 12:00 | 52.25 | 49.09 | 49.09 | 3.17 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 13:00 | 53.45 | 33.62 | 33.62 | 19.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 14:00 | 55.24 | 57.32 | 57.32 | 0 | 2.09 | 0 | 14.49 | 0 | 0
2025-11-22 15:00 | 54.7 | 4.39 | 4.39 | 48.42 | 0 | 1.88 | 12.51 | 0 | 0
2025-11-22 16:00 | 53.51 | 1.74 | 1.74 | 51.78 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 17:00 | 53.76 | 0 | 0 | 53.76 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 18:00 | 52.61 | 0 | 0 | 52.61 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 19:00 | 50.72 | 0 | 0 | 50.72 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 20:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 21:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 22:00 | 44.87 | 0 | 0 | 44.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-22 23:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 01:00 | 41.59 | 0 | 0 | 41.59 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 02:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 03:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 04:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 05:00 | 41.85 | 0 | 0 | 41.85 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 06:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 07:00 | 43.41 | 0 | 0 | 43.41 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 08:00 | 43.89 | 37.79 | 37.79 | 6.1 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 09:00 | 45.21 | 67.53 | 67.53 | 0 | 22.32 | 0 | 33.71 | 0 | 0
2025-11-23 10:00 | 46.82 | 57.62 | 57.62 | 0 | 10.79 | 0 | 43.97 | 0 | 0
2025-11-23 11:00 | 47.88 | 44.27 | 44.27 | 0 | 0 | 3.61 | 40.17 | 0 | 0
2025-11-23 12:00 | 47.53 | 47.31 | 47.31 | 0 | 0 | 0.22 | 39.93 | 0 | 0
2025-11-23 13:00 | 49.11 | 61.03 | 61.03 | 0 | 11.91 | 0 | 51.25 | 0 | 0
2025-11-23 14:00 | 48.73 | 74.86 | 74.86 | 0 | 26.12 | 0 | 76.07 | 0 | 0
2025-11-23 15:00 | 49.87 | 68.79 | 68.79 | 0 | 18.91 | 0 | 94.04 | 0 | 0
2025-11-23 16:00 | 48.97 | 5.72 | 5.72 | 0 | 0 | 43.25 | 48.52 | 0 | 0
2025-11-23 17:00 | 48.3 | 0 | 0 | 14.1 | 0 | 34.21 | 12.51 | 0 | 0
2025-11-23 18:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 19:00 | 47.24 | 0 | 0 | 47.24 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 20:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 21:00 | 45.72 | 0 | 0 | 45.72 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 22:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 12.51 | 0 | 0
2025-11-23 23:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 01:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 02:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 03:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 04:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 05:00 | 41.6 | 0 | 0 | 41.6 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 06:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 07:00 | 42.75 | 0 | 0 | 42.75 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 08:00 | 44.51 | 3.59 | 3.59 | 40.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 09:00 | 45.91 | 22.64 | 22.64 | 23.27 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 10:00 | 48.78 | 8.72 | 8.72 | 40.06 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 11:00 | 49.77 | 22.27 | 22.27 | 27.5 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 12:00 | 50.33 | 27.16 | 27.16 | 23.17 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 13:00 | 51.77 | 46.92 | 46.92 | 4.85 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 14:00 | 51.39 | 71.88 | 71.88 | 0 | 20.49 | 0 | 31.98 | 0 | 0
2025-11-24 15:00 | 51.93 | 65.1 | 65.1 | 0 | 13.18 | 0 | 44.5 | 0 | 0
2025-11-24 16:00 | 52.12 | 1.83 | 1.83 | 19.9 | 0 | 30.39 | 12.51 | 0 | 0
2025-11-24 17:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 18:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 19:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 20:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 21:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 22:00 | 44.67 | 0 | 0 | 44.67 | 0 | 0 | 12.51 | 0 | 0
2025-11-24 23:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 | 42.07 | 0 | 0 | 42.07 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 01:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 02:00 | 40.57 | 0 | 0 | 40.57 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 03:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 04:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 05:00 | 41.25 | 0 | 0 | 41.25 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 06:00 | 42.69 | 0 | 0 | 42.69 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 07:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 08:00 | 44.12 | 0.32 | 0.32 | 43.8 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 09:00 | 45.69 | 0.96 | 0.96 | 44.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 10:00 | 46.18 | 1.84 | 1.84 | 44.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 11:00 | 48.42 | 7.85 | 7.85 | 40.57 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 12:00 | 48.67 | 8.52 | 8.52 | 40.15 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 13:00 | 48.83 | 43.67 | 43.67 | 5.15 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 14:00 | 49.43 | 52.03 | 52.03 | 0 | 2.6 | 0 | 14.98 | 0 | 0
2025-11-25 15:00 | 49.37 | 37.53 | 37.53 | 9.5 | 0 | 2.34 | 12.51 | 0 | 0
2025-11-25 16:00 | 50.17 | 1.2 | 1.2 | 48.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 17:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 18:00 | 48.65 | 0 | 0 | 48.65 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 19:00 | 48.05 | 0 | 0 | 48.05 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 20:00 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 21:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 22:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 12.51 | 0 | 0
2025-11-25 23:00 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 01:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 02:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 03:00 | 40.18 | 0 | 0 | 40.18 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 04:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 05:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 06:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 07:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 08:00 | 44.68 | 29.67 | 29.67 | 15.02 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 09:00 | 45.98 | 55.08 | 55.08 | 0 | 9.1 | 0 | 21.15 | 0 | 0
2025-11-26 10:00 | 47.33 | 61.87 | 61.87 | 0 | 14.54 | 0 | 34.96 | 0 | 0
2025-11-26 11:00 | 49.7 | 51.38 | 51.38 | 0 | 1.68 | 0 | 36.56 | 0 | 0
2025-11-26 12:00 | 49.67 | 46.69 | 46.69 | 0 | 0 | 2.97 | 33.43 | 0 | 0
2025-11-26 13:00 | 50.7 | 38.99 | 38.99 | 0 | 0 | 11.71 | 21.1 | 0 | 0
2025-11-26 14:00 | 50.46 | 52.3 | 52.3 | 0 | 1.83 | 0 | 22.84 | 0 | 0
2025-11-26 15:00 | 50.28 | 30.58 | 30.58 | 9.88 | 0 | 9.82 | 12.51 | 0 | 0
2025-11-26 16:00 | 50.46 | 1.09 | 1.09 | 49.36 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 17:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 18:00 | 49.56 | 0 | 0 | 49.56 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 19:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 20:00 | 46.99 | 0 | 0 | 46.99 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 21:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 22:00 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 12.51 | 0 | 0
2025-11-26 23:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 | 42.23 | 0 | 0 | 42.23 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 01:00 | 40.34 | 0 | 0 | 40.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 02:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 03:00 | 39.72 | 0 | 0 | 39.72 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 04:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 05:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 06:00 | 42.59 | 0 | 0 | 42.59 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 07:00 | 42.93 | 0 | 0 | 42.93 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 08:00 | 44.85 | 9.88 | 9.88 | 34.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 09:00 | 46.92 | 22.21 | 22.21 | 24.71 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 10:00 | 48.13 | 37.63 | 37.63 | 10.5 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 11:00 | 50.45 | 52.6 | 52.6 | 0 | 2.16 | 0 | 14.56 | 0 | 0
2025-11-27 12:00 | 52.07 | 46.44 | 46.44 | 3.68 | 0 | 1.95 | 12.51 | 0 | 0
2025-11-27 13:00 | 53.31 | 48.34 | 48.34 | 4.97 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 14:00 | 54.22 | 47.5 | 47.5 | 6.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 15:00 | 55.3 | 47.59 | 47.59 | 7.72 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 16:00 | 54.14 | 3.49 | 3.49 | 50.66 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 17:00 | 53.85 | 0 | 0 | 53.85 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 18:00 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 19:00 | 49.79 | 0 | 0 | 49.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 20:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 21:00 | 45.91 | 0 | 0 | 45.91 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 22:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 12.51 | 0 | 0
2025-11-27 23:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 01:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 02:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 03:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 04:00 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 05:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 06:00 | 41.87 | 0 | 0 | 41.87 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 07:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 08:00 | 43.13 | 35.85 | 35.85 | 7.28 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 09:00 | 46.98 | 76.71 | 76.71 | 0 | 29.73 | 0 | 40.76 | 0 | 0
2025-11-28 10:00 | 47.9 | 64.69 | 64.69 | 0 | 16.79 | 0 | 56.7 | 0 | 0
2025-11-28 11:00 | 49.58 | 49.3 | 49.3 | 0 | 0 | 0.28 | 56.41 | 0 | 0
2025-11-28 12:00 | 50.55 | 48.13 | 48.13 | 0 | 0 | 2.42 | 53.86 | 0 | 0
2025-11-28 13:00 | 50.79 | 54.48 | 54.48 | 0 | 3.69 | 0 | 57.37 | 0 | 0
2025-11-28 14:00 | 52.75 | 37.12 | 37.12 | 0 | 0 | 15.62 | 40.92 | 0 | 0
2025-11-28 15:00 | 52.37 | 5.43 | 5.43 | 19.94 | 0 | 26.99 | 12.51 | 0 | 0
2025-11-28 16:00 | 52.68 | 0.21 | 0.21 | 52.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 17:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 18:00 | 50.74 | 0 | 0 | 50.74 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 19:00 | 48.84 | 0 | 0 | 48.84 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 20:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 21:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 22:00 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-28 23:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 01:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 02:00 | 39.99 | 0 | 0 | 39.99 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 03:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 04:00 | 39.98 | 0 | 0 | 39.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 05:00 | 39.81 | 0 | 0 | 39.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 06:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 07:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 08:00 | 43.8 | 0.28 | 0.28 | 43.52 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 09:00 | 44.49 | 3 | 3 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 10:00 | 46.06 | 5.74 | 5.74 | 40.32 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 11:00 | 46.56 | 7.02 | 7.02 | 39.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 12:00 | 48.88 | 7.9 | 7.9 | 40.98 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 13:00 | 48.3 | 6.42 | 6.42 | 41.88 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 14:00 | 49.67 | 4.51 | 4.51 | 45.16 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 15:00 | 49.25 | 1.8 | 1.8 | 47.44 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 16:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 17:00 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 18:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 19:00 | 47.9 | 0 | 0 | 47.9 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 20:00 | 45.72 | 0 | 0 | 45.72 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 21:00 | 44.73 | 0 | 0 | 44.73 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 22:00 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 12.51 | 0 | 0
2025-11-29 23:00 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 | 42.21 | 0 | 0 | 42.21 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 01:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 02:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 03:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 04:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 05:00 | 40.9 | 0 | 0 | 40.9 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 06:00 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 07:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 08:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 09:00 | 44.49 | 4.08 | 4.08 | 40.41 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 10:00 | 45.65 | 37.02 | 37.02 | 8.63 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 11:00 | 47.06 | 24.37 | 24.37 | 22.69 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 12:00 | 47.24 | 21.5 | 21.5 | 25.74 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 13:00 | 48.55 | 28.78 | 28.78 | 19.76 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 14:00 | 48.45 | 41.9 | 41.9 | 6.54 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 15:00 | 48.87 | 45.52 | 45.52 | 3.34 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 16:00 | 49.37 | 0.67 | 0.67 | 48.71 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 17:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 18:00 | 48.19 | 0 | 0 | 48.19 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 19:00 | 46.02 | 0 | 0 | 46.02 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 20:00 | 45.68 | 0 | 0 | 45.68 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 21:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 22:00 | 44.53 | 0 | 0 | 44.53 | 0 | 0 | 12.51 | 0 | 0
2025-11-30 23:00 | 41.4 | 0 | 0 | 41.4 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 01:00 | 41.09 | 0 | 0 | 41.09 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 02:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 03:00 | 39.52 | 0 | 0 | 39.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 04:00 | 39.98 | 0 | 0 | 39.98 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 05:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 06:00 | 42.02 | 0 | 0 | 42.02 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 07:00 | 42.59 | 0 | 0 | 42.59 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 08:00 | 44.36 | 27.53 | 27.53 | 16.82 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 09:00 | 44.94 | 69.51 | 69.51 | 0 | 24.57 | 0 | 35.85 | 0 | 0
2025-12-01 10:00 | 46.17 | 65.44 | 65.44 | 0 | 19.27 | 0 | 54.16 | 0 | 0
2025-12-01 11:00 | 47.76 | 55.53 | 55.53 | 0 | 7.77 | 0 | 61.54 | 0 | 0
2025-12-01 12:00 | 48.44 | 33.58 | 33.58 | 0 | 0 | 14.85 | 45.9 | 0 | 0
2025-12-01 13:00 | 50.14 | 25.47 | 25.47 | 0 | 0 | 24.67 | 19.93 | 0 | 0
2025-12-01 14:00 | 50.26 | 1.23 | 1.23 | 41.98 | 0 | 7.05 | 12.51 | 0 | 0
2025-12-01 15:00 | 50.3 | 0 | 0 | 50.3 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 16:00 | 50.7 | 1.95 | 1.95 | 48.75 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 17:00 | 49.32 | 0 | 0 | 49.32 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 18:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 19:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 20:00 | 47.12 | 0 | 0 | 47.12 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 21:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 22:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 12.51 | 0 | 0
2025-12-01 23:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 01:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 02:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 03:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 04:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 05:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 06:00 | 41.4 | 0 | 0 | 41.4 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 07:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 08:00 | 42.75 | 12.74 | 12.74 | 30 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 09:00 | 44.66 | 69.63 | 69.63 | 0 | 24.97 | 0 | 36.23 | 0 | 0
2025-12-02 10:00 | 45.23 | 70 | 70 | 0 | 24.77 | 0 | 59.76 | 0 | 0
2025-12-02 11:00 | 46.76 | 56.85 | 56.85 | 0 | 10.09 | 0 | 69.34 | 0 | 0
2025-12-02 12:00 | 46.93 | 2.61 | 2.61 | 0 | 0 | 44.32 | 22.69 | 0 | 0
2025-12-02 13:00 | 48.05 | 14.35 | 14.35 | 24.04 | 0 | 9.67 | 12.51 | 0 | 0
2025-12-02 14:00 | 48.07 | 23.8 | 23.8 | 24.27 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 15:00 | 48.1 | 2.32 | 2.32 | 45.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 16:00 | 47.67 | 2.22 | 2.22 | 45.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 17:00 | 47.66 | 0 | 0 | 47.66 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 18:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 19:00 | 46.27 | 0 | 0 | 46.27 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 20:00 | 45.65 | 0 | 0 | 45.65 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 21:00 | 44.36 | 0 | 0 | 44.36 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 22:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 12.51 | 0 | 0
2025-12-02 23:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 01:00 | 40.17 | 0 | 0 | 40.17 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 02:00 | 39.71 | 0 | 0 | 39.71 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 04:00 | 39.52 | 0 | 0 | 39.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 05:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 06:00 | 41.38 | 0 | 0 | 41.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 07:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 08:00 | 42.64 | 1.8 | 1.8 | 40.84 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 09:00 | 44.92 | 6.22 | 6.22 | 38.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 10:00 | 45.58 | 10.59 | 10.59 | 34.99 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 11:00 | 46.2 | 11.99 | 11.99 | 34.2 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 12:00 | 48.25 | 14.2 | 14.2 | 34.04 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 13:00 | 48.98 | 10.9 | 10.9 | 38.07 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 14:00 | 48.78 | 5.48 | 5.48 | 43.3 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 15:00 | 49.15 | 2.36 | 2.36 | 46.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 16:00 | 49.04 | 0 | 0 | 49.04 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 17:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 18:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 19:00 | 46.03 | 0 | 0 | 46.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 20:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 21:00 | 44.96 | 0 | 0 | 44.96 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-03 23:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 01:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 02:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 03:00 | 39.7 | 0 | 0 | 39.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 05:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 06:00 | 41.07 | 0 | 0 | 41.07 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 07:00 | 41.72 | 0 | 0 | 41.72 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 08:00 | 43.38 | 15.74 | 15.74 | 27.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 09:00 | 44.06 | 9.59 | 9.59 | 34.47 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 10:00 | 46.05 | 16.52 | 16.52 | 29.53 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 11:00 | 47.9 | 19.85 | 19.85 | 28.05 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 12:00 | 49.03 | 53.12 | 53.12 | 0 | 4.09 | 0 | 16.4 | 0 | 0
2025-12-04 13:00 | 49.25 | 64.73 | 64.73 | 0 | 15.48 | 0 | 31.1 | 0 | 0
2025-12-04 14:00 | 49.64 | 69.63 | 69.63 | 0 | 19.99 | 0 | 50.09 | 0 | 0
2025-12-04 15:00 | 50.43 | 60.34 | 60.34 | 0 | 9.9 | 0 | 59.5 | 0 | 0
2025-12-04 16:00 | 50.51 | 0.62 | 0.62 | 5.24 | 0 | 44.64 | 12.51 | 0 | 0
2025-12-04 17:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 18:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 19:00 | 47.69 | 0 | 0 | 47.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 20:00 | 46.93 | 0 | 0 | 46.93 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 21:00 | 44.83 | 0 | 0 | 44.83 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 22:00 | 42.49 | 0 | 0 | 42.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-04 23:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 01:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 02:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 03:00 | 39.12 | 0 | 0 | 39.12 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 04:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 05:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 06:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 07:00 | 42 | 0 | 0 | 42 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 08:00 | 44 | 2.43 | 2.43 | 41.57 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 09:00 | 44.89 | 13.4 | 13.4 | 31.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 10:00 | 46.43 | 63.25 | 63.25 | 0 | 16.82 | 0 | 28.49 | 0 | 0
2025-12-05 11:00 | 47.88 | 56.42 | 56.42 | 0 | 8.53 | 0 | 36.59 | 0 | 0
2025-12-05 12:00 | 48.74 | 31.17 | 31.17 | 0 | 0 | 17.57 | 18.1 | 0 | 0
2025-12-05 13:00 | 50.92 | 17 | 17 | 28.61 | 0 | 5.31 | 12.51 | 0 | 0
2025-12-05 14:00 | 52.53 | 27.71 | 27.71 | 24.82 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 15:00 | 51.98 | 0 | 0 | 51.98 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 16:00 | 51.85 | 0 | 0 | 51.85 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 17:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 18:00 | 49.53 | 0 | 0 | 49.53 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 19:00 | 48.71 | 0 | 0 | 48.71 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 20:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 21:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 22:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-05 23:00 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 | 40.76 | 0 | 0 | 40.76 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 01:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 02:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 03:00 | 38.57 | 0 | 0 | 38.57 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 04:00 | 39.33 | 0 | 0 | 39.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 05:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 06:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 07:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 08:00 | 42.92 | 0 | 0 | 42.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 09:00 | 43.94 | 1.56 | 1.56 | 42.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 10:00 | 45.83 | 2.97 | 2.97 | 42.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 11:00 | 47.27 | 6.58 | 6.58 | 40.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 12:00 | 48.37 | 8.09 | 8.09 | 40.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 13:00 | 50.11 | 45.2 | 45.2 | 4.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 14:00 | 49.32 | 48.49 | 48.49 | 0.83 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 15:00 | 49.49 | 36.19 | 36.19 | 13.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 16:00 | 50.27 | 0.51 | 0.51 | 49.76 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 17:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 18:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 19:00 | 47.16 | 0 | 0 | 47.16 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 20:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 21:00 | 44.52 | 0 | 0 | 44.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 22:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-06 23:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 | 40.26 | 0 | 0 | 40.26 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 01:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 02:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 03:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 04:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 05:00 | 40.02 | 0 | 0 | 40.02 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 06:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 07:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 08:00 | 42.3 | 0.81 | 0.81 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 09:00 | 43.09 | 3.57 | 3.57 | 39.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 10:00 | 43.45 | 7.95 | 7.95 | 35.51 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 11:00 | 44.43 | 11.24 | 11.24 | 33.19 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 12:00 | 45.63 | 11.75 | 11.75 | 33.88 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 13:00 | 45.43 | 8.79 | 8.79 | 36.65 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 14:00 | 45.09 | 6.12 | 6.12 | 38.97 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 15:00 | 45.39 | 1.97 | 1.97 | 43.43 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 16:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 17:00 | 44.7 | 0 | 0 | 44.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 18:00 | 45.09 | 0 | 0 | 45.09 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 19:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 20:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 21:00 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 22:00 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 12.51 | 0 | 0
2025-12-07 23:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 | 41.32 | 0 | 0 | 41.32 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 01:00 | 39.72 | 0 | 0 | 39.72 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 02:00 | 39.24 | 0 | 0 | 39.24 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 03:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 04:00 | 39.58 | 0 | 0 | 39.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 05:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 06:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 07:00 | 41.29 | 0 | 0 | 41.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 08:00 | 43.17 | 5.55 | 5.55 | 37.62 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 09:00 | 43.99 | 7.12 | 7.12 | 36.87 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 10:00 | 45.18 | 3.51 | 3.51 | 41.67 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 11:00 | 47.22 | 17.79 | 17.79 | 29.44 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 12:00 | 48.39 | 20.01 | 20.01 | 28.39 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 13:00 | 48.48 | 32.84 | 32.84 | 15.65 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 14:00 | 49.36 | 24.34 | 24.34 | 25.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 15:00 | 48.84 | 4.05 | 4.05 | 44.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 16:00 | 48.81 | 0.04 | 0.04 | 48.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 17:00 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 18:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 19:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 20:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 21:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-08 23:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 01:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 02:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 03:00 | 37.95 | 0 | 0 | 37.95 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 04:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 05:00 | 40.33 | 0 | 0 | 40.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 06:00 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 07:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 08:00 | 42.66 | 12.51 | 12.51 | 30.15 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 09:00 | 43.3 | 33.35 | 33.35 | 9.95 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 10:00 | 44.49 | 8.56 | 8.56 | 35.93 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 11:00 | 46.23 | 14.13 | 14.13 | 32.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 12:00 | 47.94 | 25.88 | 25.88 | 22.07 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 13:00 | 48.43 | 35.95 | 35.95 | 12.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 14:00 | 48.27 | 66.16 | 66.16 | 0 | 17.89 | 0 | 29.5 | 0 | 0
2025-12-09 15:00 | 49.16 | 60.31 | 60.31 | 0 | 11.16 | 0 | 40.1 | 0 | 0
2025-12-09 16:00 | 47.51 | 1.87 | 1.87 | 19.42 | 0 | 26.21 | 12.51 | 0 | 0
2025-12-09 17:00 | 47.75 | 0 | 0 | 47.75 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 18:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 19:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 20:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 21:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 22:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 12.51 | 0 | 0
2025-12-09 23:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 | 40.47 | 0 | 0 | 40.47 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 01:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 02:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 03:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 04:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 06:00 | 40.17 | 0 | 0 | 40.17 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 07:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 08:00 | 41.9 | 15.38 | 15.38 | 26.53 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 09:00 | 44.69 | 36.51 | 36.51 | 8.19 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 10:00 | 44.48 | 33.48 | 33.48 | 11 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 11:00 | 46.26 | 9.01 | 9.01 | 37.26 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 12:00 | 47.09 | 40.82 | 40.82 | 6.27 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 13:00 | 49.53 | 18.92 | 18.92 | 30.61 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 14:00 | 48.74 | 39.35 | 39.35 | 9.39 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 15:00 | 48.93 | 46.36 | 46.36 | 2.57 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 16:00 | 48.8 | 1.51 | 1.51 | 47.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 17:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 18:00 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 19:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 20:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 21:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 22:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 12.51 | 0 | 0
2025-12-10 23:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 01:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 02:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 03:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 05:00 | 39.04 | 0 | 0 | 39.04 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 06:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 07:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 08:00 | 43.3 | 9.29 | 9.29 | 34.01 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 09:00 | 44.24 | 53.27 | 53.27 | 0 | 9.03 | 0 | 21.09 | 0 | 0
2025-12-11 10:00 | 46.54 | 37.5 | 37.5 | 0.89 | 0 | 8.15 | 12.51 | 0 | 0
2025-12-11 11:00 | 47.04 | 53.11 | 53.11 | 0 | 6.08 | 0 | 18.28 | 0 | 0
2025-12-11 12:00 | 49.39 | 32.9 | 32.9 | 11 | 0 | 5.48 | 12.51 | 0 | 0
2025-12-11 13:00 | 49.69 | 36.55 | 36.55 | 13.15 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 14:00 | 50.88 | 25.76 | 25.76 | 25.12 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 15:00 | 51.13 | 3.38 | 3.38 | 47.75 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 16:00 | 51.09 | 0.25 | 0.25 | 50.84 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 17:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 18:00 | 48.49 | 0 | 0 | 48.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 19:00 | 47.85 | 0 | 0 | 47.85 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 20:00 | 46.66 | 0 | 0 | 46.66 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 21:00 | 43.86 | 0 | 0 | 43.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 22:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-11 23:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 01:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 02:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 03:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 04:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 06:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 07:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 08:00 | 40.98 | 11.2 | 11.2 | 29.78 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 09:00 | 41.83 | 73.88 | 73.88 | 0 | 32.05 | 0 | 42.96 | 0 | 0
2025-12-12 10:00 | 43.21 | 67.45 | 67.45 | 0 | 24.24 | 0 | 65.99 | 0 | 0
2025-12-12 11:00 | 43.13 | 54.94 | 54.94 | 0 | 11.82 | 0 | 77.21 | 0 | 0
2025-12-12 12:00 | 43.31 | 50.5 | 50.5 | 0 | 7.19 | 0 | 84.05 | 0 | 0
2025-12-12 13:00 | 44.66 | 58.41 | 58.41 | 0 | 13.75 | 0 | 97.11 | 0 | 0
2025-12-12 14:00 | 44.82 | 68.25 | 61.12 | 0 | 16.3 | 0 | 112.59 | 7.13 | 0
2025-12-12 15:00 | 44.33 | 56.24 | 44.33 | 0 | 0 | 0 | 112.59 | 11.9 | 0
2025-12-12 16:00 | 44.62 | 0.66 | 0.66 | 0 | 0 | 43.96 | 66.31 | 0 | 0
2025-12-12 17:00 | 44.44 | 0 | 0 | 0 | 0 | 44.44 | 19.54 | 0 | 0
2025-12-12 18:00 | 44.39 | 0 | 0 | 37.71 | 0 | 6.68 | 12.51 | 0 | 0
2025-12-12 19:00 | 44 | 0 | 0 | 44 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 20:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 21:00 | 42.31 | 0 | 0 | 42.31 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 22:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-12 23:00 | 40.52 | 0 | 0 | 40.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 | 39.86 | 0 | 0 | 39.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 01:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 02:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 03:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 05:00 | 39.06 | 0 | 0 | 39.06 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 06:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 07:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 08:00 | 41.65 | 8.13 | 8.13 | 33.53 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 09:00 | 42.23 | 52.39 | 52.39 | 0 | 10.16 | 0 | 22.16 | 0 | 0
2025-12-13 10:00 | 44.08 | 56.58 | 56.58 | 0 | 12.5 | 0 | 34.03 | 0 | 0
2025-12-13 11:00 | 45.01 | 48.76 | 48.76 | 0 | 3.76 | 0 | 37.6 | 0 | 0
2025-12-13 12:00 | 46.08 | 44.83 | 44.83 | 0 | 0 | 1.24 | 36.29 | 0 | 0
2025-12-13 13:00 | 47.03 | 45.63 | 45.63 | 0 | 0 | 1.4 | 34.82 | 0 | 0
2025-12-13 14:00 | 46.69 | 45.2 | 45.2 | 0 | 0 | 1.48 | 33.26 | 0 | 0
2025-12-13 15:00 | 47.96 | 36.52 | 36.52 | 0 | 0 | 11.44 | 21.21 | 0 | 0
2025-12-13 16:00 | 46.82 | 0.59 | 0.59 | 37.96 | 0 | 8.27 | 12.51 | 0 | 0
2025-12-13 17:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 18:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 19:00 | 44.74 | 0 | 0 | 44.74 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 20:00 | 44.27 | 0 | 0 | 44.27 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 21:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 22:00 | 41.67 | 0 | 0 | 41.67 | 0 | 0 | 12.51 | 0 | 0
2025-12-13 23:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 | 39.56 | 0 | 0 | 39.56 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 01:00 | 39.44 | 0 | 0 | 39.44 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 02:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 03:00 | 39 | 0 | 0 | 39 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 04:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 05:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 06:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 07:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 08:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 09:00 | 43.26 | 0 | 0 | 43.26 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 10:00 | 45.19 | 2.57 | 2.57 | 42.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 11:00 | 45.56 | 10.81 | 10.81 | 34.76 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 12:00 | 46.74 | 7.61 | 7.61 | 39.13 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 13:00 | 47.74 | 45.81 | 45.81 | 1.93 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 14:00 | 48.69 | 54.42 | 54.42 | 0 | 5.74 | 0 | 17.96 | 0 | 0
2025-12-14 15:00 | 48.35 | 37.93 | 37.93 | 5.24 | 0 | 5.18 | 12.51 | 0 | 0
2025-12-14 16:00 | 48.13 | 0.49 | 0.49 | 47.64 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 17:00 | 47.17 | 0 | 0 | 47.17 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 18:00 | 46.69 | 0 | 0 | 46.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 19:00 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 20:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 21:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 22:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-14 23:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 | 40.32 | 0 | 0 | 40.32 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 01:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 02:00 | 38.52 | 0 | 0 | 38.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 03:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 04:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 05:00 | 39.13 | 0 | 0 | 39.13 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 06:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 07:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 08:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 09:00 | 42.88 | 0.95 | 0.95 | 41.93 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 10:00 | 42.69 | 1.73 | 1.73 | 40.97 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 11:00 | 43.85 | 2.88 | 2.88 | 40.97 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 12:00 | 43.61 | 6.16 | 6.16 | 37.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 13:00 | 44.89 | 42.42 | 42.42 | 2.47 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 14:00 | 44.75 | 47.84 | 47.84 | 0 | 3.09 | 0 | 15.45 | 0 | 0
2025-12-15 15:00 | 44.97 | 40.21 | 40.21 | 1.96 | 0 | 2.79 | 12.51 | 0 | 0
2025-12-15 16:00 | 44.69 | 0.59 | 0.59 | 44.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 17:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 18:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 19:00 | 44.08 | 0 | 0 | 44.08 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 20:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 21:00 | 41.95 | 0 | 0 | 41.95 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 22:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 12.51 | 0 | 0
2025-12-15 23:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 01:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 03:00 | 37.86 | 0 | 0 | 37.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 04:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 05:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 06:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 07:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 08:00 | 40.81 | 0.55 | 0.55 | 40.25 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 09:00 | 42.42 | 4.72 | 4.72 | 37.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 10:00 | 44.84 | 11.31 | 11.31 | 33.53 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 11:00 | 47.3 | 12.25 | 12.25 | 35.05 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 12:00 | 47.29 | 14.59 | 14.59 | 32.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 13:00 | 49.12 | 15.33 | 15.33 | 33.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 14:00 | 49.12 | 6.08 | 6.08 | 43.04 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 15:00 | 49.62 | 2.94 | 2.94 | 46.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 16:00 | 49.97 | 0 | 0 | 49.97 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 17:00 | 48.51 | 0 | 0 | 48.51 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 18:00 | 47.29 | 0 | 0 | 47.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 19:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 20:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 21:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 22:00 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 12.51 | 0 | 0
2025-12-16 23:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 01:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 02:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 03:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 04:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 05:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 06:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 07:00 | 40.32 | 0 | 0 | 40.32 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 08:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 09:00 | 41.91 | 35.16 | 35.16 | 6.74 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 10:00 | 43.11 | 1.7 | 1.7 | 41.42 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 11:00 | 45.45 | 56.46 | 56.46 | 0 | 11.01 | 0 | 22.97 | 0 | 0
2025-12-17 12:00 | 45.58 | 53.24 | 53.24 | 0 | 7.66 | 0 | 30.25 | 0 | 0
2025-12-17 13:00 | 47.09 | 61.55 | 61.55 | 0 | 14.46 | 0 | 43.99 | 0 | 0
2025-12-17 14:00 | 47.51 | 71.57 | 71.57 | 0 | 24.07 | 0 | 66.85 | 0 | 0
2025-12-17 15:00 | 47.58 | 61.09 | 61.09 | 0 | 13.51 | 0 | 79.69 | 0 | 0
2025-12-17 16:00 | 47.66 | 1.39 | 1.39 | 0 | 0 | 46.27 | 30.98 | 0 | 0
2025-12-17 17:00 | 47.02 | 0 | 0 | 29.47 | 0 | 17.55 | 12.51 | 0 | 0
2025-12-17 18:00 | 44.8 | 0 | 0 | 44.8 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 19:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 20:00 | 44.19 | 0 | 0 | 44.19 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 21:00 | 43.57 | 0 | 0 | 43.57 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 22:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-17 23:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 01:00 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 02:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 03:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 04:00 | 38.42 | 0 | 0 | 38.42 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 05:00 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 06:00 | 40.1 | 0 | 0 | 40.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 07:00 | 40.97 | 0 | 0 | 40.97 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 08:00 | 42.1 | 7.54 | 7.54 | 34.55 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 09:00 | 43.03 | 71.08 | 71.08 | 0 | 28.05 | 0 | 39.16 | 0 | 0
2025-12-18 10:00 | 43.95 | 65.23 | 65.23 | 0 | 21.28 | 0 | 59.38 | 0 | 0
2025-12-18 11:00 | 45.78 | 52.28 | 52.28 | 0 | 6.49 | 0 | 65.55 | 0 | 0
2025-12-18 12:00 | 46.93 | 47.87 | 47.87 | 0 | 0.93 | 0 | 66.43 | 0 | 0
2025-12-18 13:00 | 47.31 | 55.93 | 55.93 | 0 | 8.62 | 0 | 74.62 | 0 | 0
2025-12-18 14:00 | 47.8 | 65.34 | 65.34 | 0 | 17.55 | 0 | 91.29 | 0 | 0
2025-12-18 15:00 | 48.73 | 54.97 | 54.97 | 0 | 6.24 | 0 | 97.22 | 0 | 0
2025-12-18 16:00 | 48.8 | 0.81 | 0.81 | 0 | 0 | 47.99 | 46.7 | 0 | 0
2025-12-18 17:00 | 47.03 | 0 | 0 | 14.55 | 0 | 32.48 | 12.51 | 0 | 0
2025-12-18 18:00 | 46.39 | 0 | 0 | 46.39 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 19:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 20:00 | 44.37 | 0 | 0 | 44.37 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 21:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 22:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 12.51 | 0 | 0
2025-12-18 23:00 | 40.58 | 0 | 0 | 40.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 | 39.53 | 0 | 0 | 39.53 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 01:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 02:00 | 37.95 | 0 | 0 | 37.95 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 03:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 04:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 05:00 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 06:00 | 38.52 | 0 | 0 | 38.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 07:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 08:00 | 41.31 | 7.38 | 7.38 | 33.93 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 09:00 | 41.98 | 55.49 | 55.49 | 0 | 13.51 | 0 | 25.35 | 0 | 0
2025-12-19 10:00 | 43.05 | 37.82 | 37.82 | 0 | 0 | 5.23 | 19.84 | 0 | 0
2025-12-19 11:00 | 44.38 | 48.92 | 48.92 | 0 | 4.54 | 0 | 24.15 | 0 | 0
2025-12-19 12:00 | 44.17 | 15.04 | 15.04 | 18.07 | 0 | 11.06 | 12.51 | 0 | 0
2025-12-19 13:00 | 45.4 | 19.94 | 19.94 | 25.46 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 14:00 | 46 | 10.28 | 10.28 | 35.71 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 15:00 | 44.87 | 2.72 | 2.72 | 42.15 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 16:00 | 45.99 | 0.47 | 0.47 | 45.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 17:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 18:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 19:00 | 43.41 | 0 | 0 | 43.41 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 20:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 21:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 22:00 | 40.27 | 0 | 0 | 40.27 | 0 | 0 | 12.51 | 0 | 0
2025-12-19 23:00 | 40.19 | 0 | 0 | 40.19 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 01:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 02:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 03:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 04:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 05:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 06:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 07:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 08:00 | 41.83 | 6.94 | 6.94 | 34.89 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 09:00 | 42.45 | 57.74 | 57.74 | 0 | 15.29 | 0 | 27.03 | 0 | 0
2025-12-20 10:00 | 42.6 | 57.04 | 57.04 | 0 | 14.45 | 0 | 40.76 | 0 | 0
2025-12-20 11:00 | 45.24 | 50.14 | 50.14 | 0 | 4.9 | 0 | 45.41 | 0 | 0
2025-12-20 12:00 | 46.87 | 41.76 | 41.76 | 0 | 0 | 5.11 | 40.03 | 0 | 0
2025-12-20 13:00 | 47.6 | 50.76 | 50.76 | 0 | 3.16 | 0 | 43.03 | 0 | 0
2025-12-20 14:00 | 47.76 | 61.07 | 61.07 | 0 | 13.31 | 0 | 55.67 | 0 | 0
2025-12-20 15:00 | 47.13 | 44.41 | 44.41 | 0 | 0 | 2.72 | 52.81 | 0 | 0
2025-12-20 16:00 | 47.27 | 0.82 | 0.82 | 8.16 | 0 | 38.28 | 12.51 | 0 | 0
2025-12-20 17:00 | 47.96 | 0 | 0 | 47.96 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 18:00 | 45.43 | 0 | 0 | 45.43 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 19:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 20:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 21:00 | 42.31 | 0 | 0 | 42.31 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 22:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-20 23:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 01:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 02:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 03:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 04:00 | 38.01 | 0 | 0 | 38.01 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 06:00 | 39.59 | 0 | 0 | 39.59 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 07:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 08:00 | 40.96 | 6.32 | 6.32 | 34.64 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 09:00 | 43.22 | 51.06 | 51.06 | 0 | 7.84 | 0 | 19.96 | 0 | 0
2025-12-21 10:00 | 44.55 | 57.26 | 57.26 | 0 | 12.71 | 0 | 32.03 | 0 | 0
2025-12-21 11:00 | 44.17 | 51.15 | 51.15 | 0 | 6.99 | 0 | 38.67 | 0 | 0
2025-12-21 12:00 | 46.52 | 45.12 | 45.12 | 0 | 0 | 1.4 | 37.2 | 0 | 0
2025-12-21 13:00 | 47.08 | 46.26 | 46.26 | 0 | 0 | 0.82 | 36.34 | 0 | 0
2025-12-21 14:00 | 47.2 | 54.44 | 54.44 | 0 | 7.23 | 0 | 43.21 | 0 | 0
2025-12-21 15:00 | 48.05 | 43.47 | 43.47 | 0 | 0 | 4.57 | 38.39 | 0 | 0
2025-12-21 16:00 | 47.04 | 0.9 | 0.9 | 21.55 | 0 | 24.59 | 12.51 | 0 | 0
2025-12-21 17:00 | 46.91 | 0 | 0 | 46.91 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 18:00 | 45.85 | 0 | 0 | 45.85 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 19:00 | 44.85 | 0 | 0 | 44.85 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 20:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 21:00 | 41.99 | 0 | 0 | 41.99 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 22:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 12.51 | 0 | 0
2025-12-21 23:00 | 40.33 | 0 | 0 | 40.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 | 39.93 | 0 | 0 | 39.93 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 01:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 02:00 | 37.68 | 0 | 0 | 37.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 03:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 04:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 06:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 08:00 | 41.3 | 6.67 | 6.67 | 34.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 09:00 | 42.35 | 68.52 | 68.52 | 0 | 26.17 | 0 | 37.37 | 0 | 0
2025-12-22 10:00 | 43.82 | 64.47 | 64.47 | 0 | 20.65 | 0 | 56.99 | 0 | 0
2025-12-22 11:00 | 44.69 | 52.58 | 52.58 | 0 | 7.88 | 0 | 64.48 | 0 | 0
2025-12-22 12:00 | 45.81 | 30.65 | 30.65 | 0 | 0 | 15.17 | 48.51 | 0 | 0
2025-12-22 13:00 | 45.82 | 38.27 | 38.27 | 0 | 0 | 7.55 | 40.56 | 0 | 0
2025-12-22 14:00 | 45.89 | 62.67 | 62.67 | 0 | 16.78 | 0 | 56.5 | 0 | 0
2025-12-22 15:00 | 47.53 | 59.37 | 59.37 | 0 | 11.84 | 0 | 67.75 | 0 | 0
2025-12-22 16:00 | 45.56 | 2.11 | 2.11 | 0 | 0 | 43.45 | 22.01 | 0 | 0
2025-12-22 17:00 | 45.16 | 0 | 0 | 36.13 | 0 | 9.03 | 12.51 | 0 | 0
2025-12-22 18:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 19:00 | 45.06 | 0 | 0 | 45.06 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 20:00 | 43.28 | 0 | 0 | 43.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 21:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 22:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-22 23:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 01:00 | 38.68 | 0 | 0 | 38.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 03:00 | 37.1 | 0 | 0 | 37.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 04:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 05:00 | 38.83 | 0 | 0 | 38.83 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 06:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 07:00 | 40.1 | 0 | 0 | 40.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 08:00 | 41.11 | 0 | 0 | 41.11 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 09:00 | 41.83 | 30.36 | 30.36 | 11.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 10:00 | 42.51 | 1.39 | 1.39 | 41.11 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 11:00 | 44.39 | 39.99 | 39.99 | 4.39 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 12:00 | 45.32 | 45.52 | 45.52 | 0 | 0.21 | 0 | 12.71 | 0 | 0
2025-12-23 13:00 | 46.16 | 52.62 | 52.62 | 0 | 6.46 | 0 | 18.84 | 0 | 0
2025-12-23 14:00 | 46.31 | 60.86 | 60.86 | 0 | 14.55 | 0 | 32.66 | 0 | 0
2025-12-23 15:00 | 45.73 | 52.09 | 52.09 | 0 | 6.37 | 0 | 38.71 | 0 | 0
2025-12-23 16:00 | 46.5 | 2.39 | 2.39 | 19.22 | 0 | 24.89 | 12.51 | 0 | 0
2025-12-23 17:00 | 45.71 | 0 | 0 | 45.71 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 18:00 | 44.77 | 0 | 0 | 44.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 19:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 20:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 21:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 22:00 | 40.13 | 0 | 0 | 40.13 | 0 | 0 | 12.51 | 0 | 0
2025-12-23 23:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 | 38.71 | 0 | 0 | 38.71 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 01:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 02:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 04:00 | 38.49 | 0 | 0 | 38.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 05:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 06:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 07:00 | 38.47 | 0 | 0 | 38.47 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 08:00 | 40.71 | 0 | 0 | 40.71 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 09:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 10:00 | 43.74 | 1.5 | 1.5 | 42.24 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 11:00 | 43.56 | 2.49 | 2.49 | 41.07 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 12:00 | 45.78 | 2.61 | 2.61 | 43.17 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 13:00 | 44.49 | 33.87 | 33.87 | 10.62 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 14:00 | 45.86 | 35.06 | 35.06 | 10.81 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 15:00 | 45.99 | 27.93 | 27.93 | 18.06 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 16:00 | 46.62 | 0.77 | 0.77 | 45.85 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 17:00 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 18:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 19:00 | 43.32 | 0 | 0 | 43.32 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 20:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 21:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 22:00 | 39.91 | 0 | 0 | 39.91 | 0 | 0 | 12.51 | 0 | 0
2025-12-24 23:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 | 39.28 | 0 | 0 | 39.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 01:00 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 03:00 | 37.51 | 0 | 0 | 37.51 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 04:00 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 05:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 07:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 08:00 | 40.92 | 5.51 | 5.51 | 35.41 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 09:00 | 41.15 | 30.96 | 30.96 | 10.19 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 10:00 | 42.03 | 23.64 | 23.64 | 18.39 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 11:00 | 43.12 | 26.11 | 26.11 | 17 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 12:00 | 43 | 30.88 | 30.88 | 12.11 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 13:00 | 44.18 | 49.53 | 49.53 | 0 | 5.34 | 0 | 17.59 | 0 | 0
2025-12-25 14:00 | 43.64 | 56.96 | 56.96 | 0 | 13.32 | 0 | 30.24 | 0 | 0
2025-12-25 15:00 | 44.36 | 47.82 | 47.82 | 0 | 3.46 | 0 | 33.52 | 0 | 0
2025-12-25 16:00 | 43.72 | 2.47 | 2.47 | 21.29 | 0 | 19.96 | 12.51 | 0 | 0
2025-12-25 17:00 | 43.46 | 0 | 0 | 43.46 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 18:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 19:00 | 42.97 | 0 | 0 | 42.97 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 20:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 21:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 22:00 | 40.12 | 0 | 0 | 40.12 | 0 | 0 | 12.51 | 0 | 0
2025-12-25 23:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 01:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 02:00 | 37.79 | 0 | 0 | 37.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 03:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 04:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 05:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 06:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 07:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 08:00 | 39.92 | 4.49 | 4.49 | 35.43 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 09:00 | 41.84 | 50.98 | 50.98 | 0 | 9.14 | 0 | 21.19 | 0 | 0
2025-12-26 10:00 | 41.11 | 57.88 | 57.88 | 0 | 16.77 | 0 | 37.12 | 0 | 0
2025-12-26 11:00 | 43.17 | 48.67 | 48.67 | 0 | 5.5 | 0 | 42.35 | 0 | 0
2025-12-26 12:00 | 44.89 | 36.25 | 36.25 | 0 | 0 | 8.64 | 33.26 | 0 | 0
2025-12-26 13:00 | 44.78 | 28.2 | 28.2 | 0 | 0 | 16.58 | 15.8 | 0 | 0
2025-12-26 14:00 | 45.6 | 15.06 | 15.06 | 27.42 | 0 | 3.12 | 12.51 | 0 | 0
2025-12-26 15:00 | 44.46 | 6.19 | 6.19 | 38.27 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 16:00 | 44.36 | 0.84 | 0.84 | 43.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 17:00 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 18:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 19:00 | 43.44 | 0 | 0 | 43.44 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 20:00 | 41.91 | 0 | 0 | 41.91 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 21:00 | 41.52 | 0 | 0 | 41.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 22:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 12.51 | 0 | 0
2025-12-26 23:00 | 40.12 | 0 | 0 | 40.12 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 | 40 | 0 | 0 | 40 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 01:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 02:00 | 37.31 | 0 | 0 | 37.31 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 03:00 | 36.22 | 0 | 0 | 36.22 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 04:00 | 36.78 | 0 | 0 | 36.78 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 05:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 06:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 07:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 08:00 | 40.7 | 0 | 0 | 40.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 09:00 | 42.11 | 1.65 | 1.65 | 40.46 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 10:00 | 42.25 | 4.31 | 4.31 | 37.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 11:00 | 43.06 | 6 | 6 | 37.06 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 12:00 | 44.08 | 6.12 | 6.12 | 37.96 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 13:00 | 44.32 | 5.68 | 5.68 | 38.64 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 14:00 | 44.72 | 4.63 | 4.63 | 40.09 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 15:00 | 45.34 | 2.01 | 2.01 | 43.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 16:00 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 17:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 18:00 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 19:00 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 20:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 21:00 | 41.63 | 0 | 0 | 41.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 22:00 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 12.51 | 0 | 0
2025-12-27 23:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 01:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 02:00 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 03:00 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 04:00 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 05:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 06:00 | 39.47 | 0 | 0 | 39.47 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 07:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 08:00 | 41.07 | 1.27 | 1.27 | 39.8 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 09:00 | 40.96 | 7.21 | 7.21 | 33.75 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 10:00 | 42.26 | 24.56 | 24.56 | 17.7 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 11:00 | 43.85 | 35.14 | 35.14 | 8.71 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 12:00 | 45.08 | 24.58 | 24.58 | 20.5 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 13:00 | 44.58 | 23.44 | 23.44 | 21.14 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 14:00 | 45.34 | 13.97 | 13.97 | 31.37 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 15:00 | 45.79 | 0 | 0 | 45.79 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 16:00 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 17:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 18:00 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 19:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 20:00 | 42.17 | 0 | 0 | 42.17 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 21:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 12.51 | 0 | 0
2025-12-28 23:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 01:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 02:00 | 37.28 | 0 | 0 | 37.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 03:00 | 38.37 | 0 | 0 | 38.37 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 04:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 05:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 06:00 | 38.85 | 0 | 0 | 38.85 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 07:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 08:00 | 41.06 | 1.44 | 1.44 | 39.62 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 09:00 | 41.78 | 42.2 | 42.2 | 0 | 0.42 | 0 | 12.91 | 0 | 0
2025-12-29 10:00 | 43.29 | 52.54 | 52.54 | 0 | 9.25 | 0 | 21.69 | 0 | 0
2025-12-29 11:00 | 43.59 | 30.65 | 30.65 | 4.22 | 0 | 8.73 | 12.51 | 0 | 0
2025-12-29 12:00 | 45.41 | 26.19 | 26.19 | 19.22 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 13:00 | 46.21 | 21.87 | 21.87 | 24.34 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 14:00 | 47.04 | 7.55 | 7.55 | 39.49 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 15:00 | 45.62 | 1.11 | 1.11 | 44.51 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 16:00 | 45.82 | 0.49 | 0.49 | 45.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 17:00 | 46.17 | 0 | 0 | 46.17 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 18:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 19:00 | 44.17 | 0 | 0 | 44.17 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 20:00 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 21:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 22:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 12.51 | 0 | 0
2025-12-29 23:00 | 38.85 | 0 | 0 | 38.85 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 01:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 03:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 04:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 05:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 06:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 07:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 08:00 | 40.12 | 0.6 | 0.6 | 39.52 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 09:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 10:00 | 41.25 | 14.1 | 14.1 | 27.15 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 11:00 | 41.37 | 25.69 | 25.69 | 15.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 12:00 | 41.98 | 28.94 | 28.94 | 13.04 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 13:00 | 42.56 | 25.88 | 25.88 | 16.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 14:00 | 43.5 | 41.17 | 41.17 | 2.33 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 15:00 | 44.03 | 44.8 | 44.8 | 0 | 0.78 | 0 | 13.25 | 0 | 0
2025-12-30 16:00 | 42.52 | 4.24 | 4.24 | 37.57 | 0 | 0.7 | 12.51 | 0 | 0
2025-12-30 17:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 18:00 | 42.08 | 0 | 0 | 42.08 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 19:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 20:00 | 42.08 | 0 | 0 | 42.08 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 21:00 | 40.55 | 0 | 0 | 40.55 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 22:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 12.51 | 0 | 0
2025-12-30 23:00 | 39.86 | 0 | 0 | 39.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 01:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 02:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 04:00 | 37.61 | 0 | 0 | 37.61 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 05:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 06:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 07:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 08:00 | 39.98 | 3.92 | 3.92 | 36.06 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 09:00 | 41.27 | 39.39 | 39.39 | 1.88 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 10:00 | 42.37 | 44.25 | 44.25 | 0 | 1.88 | 0 | 14.29 | 0 | 0
2025-12-31 11:00 | 43.07 | 48.76 | 48.76 | 0 | 5.69 | 0 | 19.7 | 0 | 0
2025-12-31 12:00 | 43.43 | 42.22 | 42.22 | 0 | 0 | 1.22 | 18.42 | 0 | 0
2025-12-31 13:00 | 44.63 | 57.55 | 57.55 | 0 | 12.93 | 0 | 30.7 | 0 | 0
2025-12-31 14:00 | 44.08 | 69.02 | 69.02 | 0 | 24.94 | 0 | 54.39 | 0 | 0
2025-12-31 15:00 | 43.98 | 68.72 | 68.72 | 0 | 24.74 | 0 | 77.89 | 0 | 0
2025-12-31 16:00 | 42.92 | 6.19 | 6.19 | 0 | 0 | 36.73 | 39.22 | 0 | 0
2025-12-31 17:00 | 44.12 | 0 | 0 | 18.75 | 0 | 25.38 | 12.51 | 0 | 0
2025-12-31 18:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 19:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 20:00 | 40.97 | 0 | 0 | 40.97 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 21:00 | 40.68 | 0 | 0 | 40.68 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 22:00 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 12.51 | 0 | 0
2025-12-31 23:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 12.51 | 0 | 0

## Sim_SSR50pct
Timestamp | Load (MW) | PV available (MW) | PV used on-site (MW) | Grid import (MW) | BESS charge (MW) | BESS discharge (MW) | BESS state of charge (MWh) | PV curtailed (MW) | Unmet load (MW)
2025-01-01 | 39.07 | 0 | 0 | 0 | 0 | 39.07 | 121.13 | 0 | 0
2025-01-01 01:00 | 37.35 | 0 | 0 | 0 | 0 | 37.35 | 81.81 | 0 | 0
2025-01-01 02:00 | 36.94 | 0 | 0 | 0 | 0 | 36.94 | 42.93 | 0 | 0
2025-01-01 03:00 | 37.32 | 0 | 0 | 27.37 | 0 | 9.95 | 32.45 | 0 | 0
2025-01-01 04:00 | 37.77 | 0 | 0 | 37.77 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 05:00 | 37.73 | 0 | 0 | 37.73 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 06:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 07:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 08:00 | 40.47 | 0.35 | 0.35 | 40.12 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 09:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 10:00 | 43.25 | 39.6 | 39.6 | 3.65 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 11:00 | 42.95 | 51.11 | 51.11 | 0 | 8.16 | 0 | 40.2 | 0 | 0
2025-01-01 12:00 | 42.89 | 47.41 | 47.41 | 0 | 4.52 | 0 | 44.49 | 0 | 0
2025-01-01 13:00 | 45.35 | 15.24 | 15.24 | 18.67 | 0 | 11.44 | 32.45 | 0 | 0
2025-01-01 14:00 | 44.73 | 17.49 | 17.49 | 27.24 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 15:00 | 45.16 | 7.79 | 7.79 | 37.36 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 16:00 | 45.62 | 0.73 | 0.73 | 44.89 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 17:00 | 43.75 | 0 | 0 | 43.75 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 18:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 19:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 20:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 21:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 22:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 32.45 | 0 | 0
2025-01-01 23:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 01:00 | 36.51 | 0 | 0 | 36.51 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 02:00 | 37.33 | 0 | 0 | 37.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 04:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 05:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 06:00 | 38.3 | 0 | 0 | 38.3 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 07:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 08:00 | 39.84 | 3.35 | 3.35 | 36.49 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 09:00 | 40.79 | 0.73 | 0.73 | 40.07 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 10:00 | 40.93 | 11.93 | 11.93 | 29 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 11:00 | 41.86 | 40.23 | 40.23 | 1.63 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 12:00 | 42.58 | 49.61 | 49.61 | 0 | 7.03 | 0 | 39.13 | 0 | 0
2025-01-02 13:00 | 43.28 | 52.12 | 52.12 | 0 | 8.84 | 0 | 47.53 | 0 | 0
2025-01-02 14:00 | 42.91 | 35.75 | 35.75 | 0 | 0 | 7.17 | 39.98 | 0 | 0
2025-01-02 15:00 | 43.45 | 53.79 | 53.79 | 0 | 10.34 | 0 | 49.8 | 0 | 0
2025-01-02 16:00 | 42.98 | 6.95 | 6.95 | 19.54 | 0 | 16.49 | 32.45 | 0 | 0
2025-01-02 17:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 18:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 19:00 | 40.95 | 0 | 0 | 40.95 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 20:00 | 40.64 | 0 | 0 | 40.64 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 21:00 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 22:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 32.45 | 0 | 0
2025-01-02 23:00 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 01:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 02:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 03:00 | 37.67 | 0 | 0 | 37.67 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 04:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 05:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 06:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 07:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 08:00 | 39.56 | 5.56 | 5.56 | 34 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 09:00 | 40.75 | 58.94 | 58.94 | 0 | 18.19 | 0 | 49.73 | 0 | 0
2025-01-03 10:00 | 41.4 | 61.46 | 61.46 | 0 | 20.06 | 0 | 68.79 | 0 | 0
2025-01-03 11:00 | 42.74 | 45.74 | 45.74 | 0 | 3 | 0 | 71.64 | 0 | 0
2025-01-03 12:00 | 43.93 | 43.72 | 43.72 | 0 | 0 | 0.22 | 71.41 | 0 | 0
2025-01-03 13:00 | 45.24 | 53.25 | 53.25 | 0 | 8.01 | 0 | 79.02 | 0 | 0
2025-01-03 14:00 | 46.16 | 56.05 | 56.05 | 0 | 9.89 | 0 | 88.42 | 0 | 0
2025-01-03 15:00 | 44.76 | 59.27 | 59.27 | 0 | 14.51 | 0 | 102.21 | 0 | 0
2025-01-03 16:00 | 45.49 | 2.76 | 2.76 | 0 | 0 | 42.73 | 57.23 | 0 | 0
2025-01-03 17:00 | 44.31 | 0 | 0 | 20.77 | 0 | 23.54 | 32.45 | 0 | 0
2025-01-03 18:00 | 44.35 | 0 | 0 | 44.35 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 19:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 20:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 21:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 22:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 32.45 | 0 | 0
2025-01-03 23:00 | 38.76 | 0 | 0 | 38.76 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 | 37.64 | 0 | 0 | 37.64 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 01:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 02:00 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 03:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 04:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 05:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 06:00 | 38.84 | 0 | 0 | 38.84 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 07:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 08:00 | 39.21 | 5.61 | 5.61 | 33.61 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 09:00 | 41.56 | 63.95 | 63.95 | 0 | 22.38 | 0 | 53.71 | 0 | 0
2025-01-04 10:00 | 41.98 | 65.08 | 65.08 | 0 | 23.1 | 0 | 75.66 | 0 | 0
2025-01-04 11:00 | 43.79 | 50.17 | 50.17 | 0 | 6.38 | 0 | 81.72 | 0 | 0
2025-01-04 12:00 | 44.38 | 45.3 | 45.3 | 0 | 0.92 | 0 | 82.6 | 0 | 0
2025-01-04 13:00 | 44.88 | 44.2 | 44.2 | 0 | 0 | 0.68 | 81.88 | 0 | 0
2025-01-04 14:00 | 45.6 | 40.92 | 40.92 | 0 | 0 | 4.68 | 76.96 | 0 | 0
2025-01-04 15:00 | 46.56 | 17.8 | 17.8 | 0 | 0 | 28.77 | 46.68 | 0 | 0
2025-01-04 16:00 | 46.46 | 2.17 | 2.17 | 30.78 | 0 | 13.52 | 32.45 | 0 | 0
2025-01-04 17:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 18:00 | 44.27 | 0 | 0 | 44.27 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 19:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 20:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 21:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 22:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-04 23:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 01:00 | 36.72 | 0 | 0 | 36.72 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 02:00 | 36.13 | 0 | 0 | 36.13 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 03:00 | 36.48 | 0 | 0 | 36.48 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 04:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 05:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 06:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 07:00 | 39.24 | 0 | 0 | 39.24 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 08:00 | 38.89 | 5.6 | 5.6 | 33.29 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 09:00 | 40.19 | 69.74 | 69.74 | 0 | 29.55 | 0 | 60.52 | 0 | 0
2025-01-05 10:00 | 40.38 | 56.56 | 56.56 | 0 | 16.19 | 0 | 75.9 | 0 | 0
2025-01-05 11:00 | 40.89 | 41.29 | 41.29 | 0 | 0.4 | 0 | 76.28 | 0 | 0
2025-01-05 12:00 | 41.45 | 37.95 | 37.95 | 0 | 0 | 3.5 | 72.6 | 0 | 0
2025-01-05 13:00 | 41.88 | 35.68 | 35.68 | 0 | 0 | 6.2 | 66.08 | 0 | 0
2025-01-05 14:00 | 41.52 | 22.65 | 22.65 | 0 | 0 | 18.87 | 46.21 | 0 | 0
2025-01-05 15:00 | 42.25 | 33.53 | 33.53 | 0 | 0 | 8.72 | 37.04 | 0 | 0
2025-01-05 16:00 | 41.11 | 5.31 | 5.31 | 31.45 | 0 | 4.36 | 32.45 | 0 | 0
2025-01-05 17:00 | 41.57 | 0 | 0 | 41.57 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 18:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 19:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 20:00 | 41.3 | 0 | 0 | 41.3 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 21:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 22:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-05 23:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 01:00 | 37.09 | 0 | 0 | 37.09 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 02:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 03:00 | 36.58 | 0 | 0 | 36.58 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 04:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 05:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 06:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 07:00 | 38.54 | 0 | 0 | 38.54 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 08:00 | 39.65 | 1.65 | 1.65 | 38 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 09:00 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 10:00 | 41.31 | 31.52 | 31.52 | 9.79 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 11:00 | 40.51 | 40.66 | 40.66 | 0 | 0.15 | 0 | 32.59 | 0 | 0
2025-01-06 12:00 | 41.72 | 35.39 | 35.39 | 6.2 | 0 | 0.13 | 32.45 | 0 | 0
2025-01-06 13:00 | 41.22 | 32.44 | 32.44 | 8.78 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 14:00 | 41.67 | 25.68 | 25.68 | 15.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 15:00 | 43.16 | 4.26 | 4.26 | 38.91 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 16:00 | 42.86 | 1.43 | 1.43 | 41.44 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 17:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 18:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 19:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 20:00 | 40.57 | 0 | 0 | 40.57 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 21:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 22:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 32.45 | 0 | 0
2025-01-06 23:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 01:00 | 36.66 | 0 | 0 | 36.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 03:00 | 37.02 | 0 | 0 | 37.02 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 04:00 | 37.04 | 0 | 0 | 37.04 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 05:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 06:00 | 38.18 | 0 | 0 | 38.18 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 07:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 08:00 | 39.28 | 0 | 0 | 39.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 09:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 10:00 | 42.32 | 2.3 | 2.3 | 40.01 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 11:00 | 41.9 | 6.14 | 6.14 | 35.76 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 12:00 | 42.7 | 5.59 | 5.59 | 37.12 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 13:00 | 44.4 | 41.59 | 41.59 | 2.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 14:00 | 44.01 | 44.55 | 44.55 | 0 | 0.54 | 0 | 32.97 | 0 | 0
2025-01-07 15:00 | 44.93 | 49.89 | 49.89 | 0 | 4.96 | 0 | 37.68 | 0 | 0
2025-01-07 16:00 | 43.88 | 3.06 | 3.06 | 35.85 | 0 | 4.97 | 32.45 | 0 | 0
2025-01-07 17:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 18:00 | 43.21 | 0 | 0 | 43.21 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 19:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 20:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 21:00 | 40.38 | 0 | 0 | 40.38 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 22:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 32.45 | 0 | 0
2025-01-07 23:00 | 38.53 | 0 | 0 | 38.53 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 | 38.18 | 0 | 0 | 38.18 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 01:00 | 36.62 | 0 | 0 | 36.62 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 02:00 | 37.37 | 0 | 0 | 37.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 03:00 | 36.66 | 0 | 0 | 36.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 04:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 05:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 06:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 07:00 | 37.83 | 0 | 0 | 37.83 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 08:00 | 39.08 | 2.87 | 2.87 | 36.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 09:00 | 40.48 | 54.59 | 54.59 | 0 | 14.1 | 0 | 45.85 | 0 | 0
2025-01-08 10:00 | 41.12 | 46.52 | 46.52 | 0 | 5.4 | 0 | 50.98 | 0 | 0
2025-01-08 11:00 | 41.87 | 40.62 | 40.62 | 0 | 0 | 1.24 | 49.67 | 0 | 0
2025-01-08 12:00 | 42.58 | 30.81 | 30.81 | 0 | 0 | 11.77 | 37.28 | 0 | 0
2025-01-08 13:00 | 43.26 | 30.82 | 30.82 | 7.86 | 0 | 4.58 | 32.45 | 0 | 0
2025-01-08 14:00 | 42.97 | 21.02 | 21.02 | 21.95 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 15:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 16:00 | 43.81 | 0.49 | 0.49 | 43.31 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 17:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 18:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 19:00 | 42.14 | 0 | 0 | 42.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 20:00 | 42.23 | 0 | 0 | 42.23 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 21:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 22:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 32.45 | 0 | 0
2025-01-08 23:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 | 37.41 | 0 | 0 | 37.41 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 01:00 | 36.75 | 0 | 0 | 36.75 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 02:00 | 36.57 | 0 | 0 | 36.57 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 04:00 | 37.19 | 0 | 0 | 37.19 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 05:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 06:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 07:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 08:00 | 39.86 | 4.53 | 4.53 | 35.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 09:00 | 40.32 | 54.25 | 54.25 | 0 | 13.94 | 0 | 45.69 | 0 | 0
2025-01-09 10:00 | 40.97 | 63.39 | 63.39 | 0 | 22.42 | 0 | 66.98 | 0 | 0
2025-01-09 11:00 | 42.41 | 53.19 | 53.19 | 0 | 10.78 | 0 | 77.22 | 0 | 0
2025-01-09 12:00 | 42.95 | 50.69 | 50.69 | 0 | 7.74 | 0 | 84.58 | 0 | 0
2025-01-09 13:00 | 42.69 | 61.34 | 61.34 | 0 | 18.65 | 0 | 102.3 | 0 | 0
2025-01-09 14:00 | 43.73 | 72.15 | 72.15 | 0 | 28.42 | 0 | 129.29 | 0 | 0
2025-01-09 15:00 | 44.01 | 74.05 | 74.05 | 0 | 30.03 | 0 | 157.82 | 0 | 0
2025-01-09 16:00 | 43.31 | 11.39 | 11.39 | 0 | 0 | 31.92 | 124.23 | 0 | 0
2025-01-09 17:00 | 43.51 | 0 | 0 | 0 | 0 | 43.51 | 78.43 | 0 | 0
2025-01-09 18:00 | 42.13 | 0 | 0 | 0 | 0 | 42.13 | 34.08 | 0 | 0
2025-01-09 19:00 | 42.81 | 0 | 0 | 41.26 | 0 | 1.55 | 32.45 | 0 | 0
2025-01-09 20:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 21:00 | 40.27 | 0 | 0 | 40.27 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 22:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 32.45 | 0 | 0
2025-01-09 23:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 | 37.29 | 0 | 0 | 37.29 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 01:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 02:00 | 36.45 | 0 | 0 | 36.45 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 03:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 04:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 05:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 06:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 07:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 08:00 | 40.11 | 1.65 | 1.65 | 38.46 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 09:00 | 39.47 | 23.38 | 23.38 | 16.09 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 10:00 | 40.95 | 35.23 | 35.23 | 5.72 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 11:00 | 42.4 | 16.56 | 16.56 | 25.83 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 12:00 | 41.2 | 23.28 | 23.28 | 17.92 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 13:00 | 41.79 | 36.62 | 36.62 | 5.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 14:00 | 42.46 | 10.28 | 10.28 | 32.18 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 15:00 | 42.5 | 0.06 | 0.06 | 42.44 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 16:00 | 43.08 | 0.33 | 0.33 | 42.75 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 17:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 18:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 19:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 20:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 21:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 22:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-10 23:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 01:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 02:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 03:00 | 36 | 0 | 0 | 36 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 04:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 05:00 | 36.79 | 0 | 0 | 36.79 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 07:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 08:00 | 39.78 | 5.3 | 5.3 | 34.47 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 09:00 | 40.17 | 72.35 | 72.35 | 0 | 32.18 | 0 | 63.02 | 0 | 0
2025-01-11 10:00 | 40.98 | 70.19 | 70.19 | 0 | 29.21 | 0 | 90.77 | 0 | 0
2025-01-11 11:00 | 43 | 58.87 | 58.87 | 0 | 15.87 | 0 | 105.84 | 0 | 0
2025-01-11 12:00 | 43.66 | 51.69 | 51.69 | 0 | 8.03 | 0 | 113.47 | 0 | 0
2025-01-11 13:00 | 43.94 | 56.66 | 56.66 | 0 | 12.72 | 0 | 125.56 | 0 | 0
2025-01-11 14:00 | 45.42 | 67.69 | 67.69 | 0 | 22.26 | 0 | 146.71 | 0 | 0
2025-01-11 15:00 | 44.63 | 69.51 | 69.51 | 0 | 24.88 | 0 | 170.34 | 0 | 0
2025-01-11 16:00 | 44.71 | 6.98 | 6.98 | 0 | 0 | 37.73 | 130.63 | 0 | 0
2025-01-11 17:00 | 44.38 | 0 | 0 | 0 | 0 | 44.38 | 83.91 | 0 | 0
2025-01-11 18:00 | 43.23 | 0 | 0 | 0 | 0 | 43.23 | 38.41 | 0 | 0
2025-01-11 19:00 | 42.88 | 0 | 0 | 37.22 | 0 | 5.66 | 32.45 | 0 | 0
2025-01-11 20:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 21:00 | 40.37 | 0 | 0 | 40.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 32.45 | 0 | 0
2025-01-11 23:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 | 36.64 | 0 | 0 | 36.64 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 01:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 02:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 03:00 | 36.61 | 0 | 0 | 36.61 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 04:00 | 35.96 | 0 | 0 | 35.96 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 06:00 | 37.7 | 0 | 0 | 37.7 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 07:00 | 38.5 | 0 | 0 | 38.5 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 08:00 | 38.94 | 5.94 | 5.94 | 32.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 09:00 | 40.78 | 56.69 | 56.69 | 0 | 15.91 | 0 | 47.57 | 0 | 0
2025-01-12 10:00 | 41.79 | 54.06 | 54.06 | 0 | 12.27 | 0 | 59.23 | 0 | 0
2025-01-12 11:00 | 41.77 | 52.16 | 52.16 | 0 | 10.39 | 0 | 69.1 | 0 | 0
2025-01-12 12:00 | 43.74 | 56.79 | 56.79 | 0 | 13.05 | 0 | 81.49 | 0 | 0
2025-01-12 13:00 | 45.1 | 63.13 | 63.13 | 0 | 18.04 | 0 | 98.63 | 0 | 0
2025-01-12 14:00 | 44.59 | 74.02 | 74.02 | 0 | 29.43 | 0 | 126.59 | 0 | 0
2025-01-12 15:00 | 44.49 | 76.46 | 76.46 | 0 | 31.98 | 0 | 156.97 | 0 | 0
2025-01-12 16:00 | 44.43 | 14.19 | 14.19 | 0 | 0 | 30.24 | 125.14 | 0 | 0
2025-01-12 17:00 | 44.38 | 0 | 0 | 0 | 0 | 44.38 | 78.43 | 0 | 0
2025-01-12 18:00 | 42.52 | 0 | 0 | 0 | 0 | 42.52 | 33.67 | 0 | 0
2025-01-12 19:00 | 42.6 | 0 | 0 | 41.44 | 0 | 1.16 | 32.45 | 0 | 0
2025-01-12 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 21:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 22:00 | 39.41 | 0 | 0 | 39.41 | 0 | 0 | 32.45 | 0 | 0
2025-01-12 23:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 | 37.24 | 0 | 0 | 37.24 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 01:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 02:00 | 37.07 | 0 | 0 | 37.07 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 03:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 04:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 05:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 06:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 07:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 08:00 | 39.33 | 3.52 | 3.52 | 35.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 09:00 | 39.78 | 36.98 | 36.98 | 2.8 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 10:00 | 40.96 | 30.12 | 30.12 | 10.84 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 11:00 | 41.93 | 21.09 | 21.09 | 20.84 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 12:00 | 41.84 | 13.28 | 13.28 | 28.56 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 13:00 | 42.44 | 38.06 | 38.06 | 4.38 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 14:00 | 43.83 | 61.2 | 61.2 | 0 | 17.37 | 0 | 48.95 | 0 | 0
2025-01-13 15:00 | 43.45 | 70.5 | 70.5 | 0 | 27.05 | 0 | 74.65 | 0 | 0
2025-01-13 16:00 | 42.31 | 15.81 | 15.81 | 0 | 0 | 26.5 | 46.75 | 0 | 0
2025-01-13 17:00 | 43.64 | 0 | 0 | 30.05 | 0 | 13.58 | 32.45 | 0 | 0
2025-01-13 18:00 | 42.82 | 0 | 0 | 42.82 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 19:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 20:00 | 40.47 | 0 | 0 | 40.47 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 21:00 | 40.65 | 0 | 0 | 40.65 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 22:00 | 39.51 | 0 | 0 | 39.51 | 0 | 0 | 32.45 | 0 | 0
2025-01-13 23:00 | 39.7 | 0 | 0 | 39.7 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 | 38 | 0 | 0 | 38 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 01:00 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 02:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 03:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 04:00 | 37.2 | 0 | 0 | 37.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 05:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 06:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 07:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 08:00 | 39.24 | 2.1 | 2.1 | 37.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 09:00 | 40.91 | 0 | 0 | 40.91 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 10:00 | 42.35 | 23.81 | 23.81 | 18.54 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 11:00 | 42.42 | 7.58 | 7.58 | 34.84 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 12:00 | 43.38 | 17.48 | 17.48 | 25.9 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 13:00 | 44.48 | 31.4 | 31.4 | 13.08 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 14:00 | 44.67 | 56.66 | 56.66 | 0 | 11.99 | 0 | 43.84 | 0 | 0
2025-01-14 15:00 | 45.44 | 67.78 | 67.78 | 0 | 22.35 | 0 | 65.07 | 0 | 0
2025-01-14 16:00 | 43.67 | 15.89 | 15.89 | 0 | 0 | 27.78 | 35.83 | 0 | 0
2025-01-14 17:00 | 43.91 | 0 | 0 | 40.7 | 0 | 3.21 | 32.45 | 0 | 0
2025-01-14 18:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 19:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 20:00 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 21:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 22:00 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 32.45 | 0 | 0
2025-01-14 23:00 | 39.11 | 0 | 0 | 39.11 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 01:00 | 36.69 | 0 | 0 | 36.69 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 02:00 | 36.83 | 0 | 0 | 36.83 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 03:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 04:00 | 36.37 | 0 | 0 | 36.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 05:00 | 36.75 | 0 | 0 | 36.75 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 06:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 07:00 | 38.37 | 0 | 0 | 38.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 08:00 | 39.66 | 5.23 | 5.23 | 34.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 09:00 | 40.27 | 59.3 | 59.3 | 0 | 19.03 | 0 | 50.53 | 0 | 0
2025-01-15 10:00 | 41.59 | 59.44 | 59.44 | 0 | 17.85 | 0 | 67.48 | 0 | 0
2025-01-15 11:00 | 41.64 | 52.05 | 52.05 | 0 | 10.41 | 0 | 77.37 | 0 | 0
2025-01-15 12:00 | 42.95 | 44.11 | 44.11 | 0 | 1.16 | 0 | 78.48 | 0 | 0
2025-01-15 13:00 | 43.47 | 52.23 | 52.23 | 0 | 8.77 | 0 | 86.8 | 0 | 0
2025-01-15 14:00 | 43.36 | 36.92 | 36.92 | 0 | 0 | 6.44 | 80.02 | 0 | 0
2025-01-15 15:00 | 43.32 | 50.39 | 50.39 | 0 | 7.07 | 0 | 86.74 | 0 | 0
2025-01-15 16:00 | 44.31 | 9.01 | 9.01 | 0 | 0 | 35.3 | 49.58 | 0 | 0
2025-01-15 17:00 | 43.4 | 0 | 0 | 27.12 | 0 | 16.28 | 32.45 | 0 | 0
2025-01-15 18:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 19:00 | 42.11 | 0 | 0 | 42.11 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 20:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 21:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 22:00 | 38.59 | 0 | 0 | 38.59 | 0 | 0 | 32.45 | 0 | 0
2025-01-15 23:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 01:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 02:00 | 37.23 | 0 | 0 | 37.23 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 03:00 | 36.16 | 0 | 0 | 36.16 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 04:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 05:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 06:00 | 37.72 | 0 | 0 | 37.72 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 07:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 08:00 | 39 | 0 | 0 | 39 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 09:00 | 39.98 | 0.01 | 0.01 | 39.97 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 10:00 | 40.65 | 5.61 | 5.61 | 35.04 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 11:00 | 41.6 | 8.51 | 8.51 | 33.09 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 12:00 | 42.14 | 9.57 | 9.57 | 32.57 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 13:00 | 41.31 | 42.62 | 42.62 | 0 | 1.31 | 0 | 33.69 | 0 | 0
2025-01-16 14:00 | 41.24 | 53.03 | 53.03 | 0 | 11.79 | 0 | 44.89 | 0 | 0
2025-01-16 15:00 | 42.94 | 35.77 | 35.77 | 0 | 0 | 7.18 | 37.34 | 0 | 0
2025-01-16 16:00 | 42.96 | 10.06 | 10.06 | 28.25 | 0 | 4.64 | 32.45 | 0 | 0
2025-01-16 17:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 18:00 | 40.8 | 0 | 0 | 40.8 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 19:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 20:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 21:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 22:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 32.45 | 0 | 0
2025-01-16 23:00 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 01:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 02:00 | 36.68 | 0 | 0 | 36.68 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 03:00 | 36.21 | 0 | 0 | 36.21 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 04:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 05:00 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 06:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 07:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 08:00 | 39.7 | 0.79 | 0.79 | 38.91 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 09:00 | 40.51 | 0.09 | 0.09 | 40.42 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 10:00 | 41.35 | 9.46 | 9.46 | 31.89 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 11:00 | 42.64 | 23.66 | 23.66 | 18.98 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 12:00 | 43.1 | 26.35 | 26.35 | 16.76 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 13:00 | 43.76 | 25.24 | 25.24 | 18.52 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 14:00 | 44.08 | 26.75 | 26.75 | 17.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 15:00 | 44.06 | 15.7 | 15.7 | 28.36 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 16:00 | 42.87 | 3.54 | 3.54 | 39.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 17:00 | 43.43 | 0 | 0 | 43.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 18:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 19:00 | 41.38 | 0 | 0 | 41.38 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 20:00 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 21:00 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 22:00 | 39.95 | 0 | 0 | 39.95 | 0 | 0 | 32.45 | 0 | 0
2025-01-17 23:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 01:00 | 37.15 | 0 | 0 | 37.15 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 02:00 | 36.92 | 0 | 0 | 36.92 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 03:00 | 36.15 | 0 | 0 | 36.15 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 04:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 05:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 06:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 07:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 08:00 | 38.99 | 0.3 | 0.3 | 38.69 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 09:00 | 40.67 | 3.59 | 3.59 | 37.08 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 10:00 | 40.92 | 7.21 | 7.21 | 33.7 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 11:00 | 41.09 | 8.96 | 8.96 | 32.13 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 12:00 | 41.71 | 10.82 | 10.82 | 30.9 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 13:00 | 41.98 | 11.55 | 11.55 | 30.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 14:00 | 42.08 | 8.37 | 8.37 | 33.71 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 15:00 | 41.72 | 4.23 | 4.23 | 37.48 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 16:00 | 42.11 | 0.33 | 0.33 | 41.78 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 17:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 18:00 | 40.96 | 0 | 0 | 40.96 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 19:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 20:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 21:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 22:00 | 38.97 | 0 | 0 | 38.97 | 0 | 0 | 32.45 | 0 | 0
2025-01-18 23:00 | 38.8 | 0 | 0 | 38.8 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 01:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 02:00 | 36.82 | 0 | 0 | 36.82 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 03:00 | 36.27 | 0 | 0 | 36.27 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 04:00 | 36.26 | 0 | 0 | 36.26 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 05:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 06:00 | 37.88 | 0 | 0 | 37.88 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 07:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 08:00 | 39.87 | 0 | 0 | 39.87 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 09:00 | 40.24 | 2.24 | 2.24 | 38 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 10:00 | 40.7 | 4.22 | 4.22 | 36.49 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 11:00 | 42.15 | 5.37 | 5.37 | 36.78 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 12:00 | 43.29 | 6.56 | 6.56 | 36.73 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 13:00 | 43.76 | 6.23 | 6.23 | 37.53 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 14:00 | 44.01 | 5.3 | 5.3 | 38.71 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 15:00 | 44.57 | 2.67 | 2.67 | 41.9 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 16:00 | 44.05 | 0.15 | 0.15 | 43.9 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 17:00 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 18:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 19:00 | 42.11 | 0 | 0 | 42.11 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 20:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 21:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 22:00 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 32.45 | 0 | 0
2025-01-19 23:00 | 38.19 | 0 | 0 | 38.19 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 01:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 02:00 | 35.74 | 0 | 0 | 35.74 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 03:00 | 35.75 | 0 | 0 | 35.75 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 04:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 05:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 06:00 | 37.6 | 0 | 0 | 37.6 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 07:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 08:00 | 37.81 | 9.17 | 9.17 | 28.65 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 09:00 | 40.21 | 69.34 | 69.34 | 0 | 29.14 | 0 | 60.13 | 0 | 0
2025-01-20 10:00 | 41.65 | 61.8 | 61.8 | 0 | 20.16 | 0 | 79.28 | 0 | 0
2025-01-20 11:00 | 41.1 | 52.27 | 52.27 | 0 | 11.17 | 0 | 89.89 | 0 | 0
2025-01-20 12:00 | 42.15 | 46.79 | 46.79 | 0 | 4.64 | 0 | 94.3 | 0 | 0
2025-01-20 13:00 | 42.49 | 53.41 | 53.41 | 0 | 10.92 | 0 | 104.68 | 0 | 0
2025-01-20 14:00 | 42.75 | 67.67 | 67.67 | 0 | 24.93 | 0 | 128.36 | 0 | 0
2025-01-20 15:00 | 43.14 | 74.01 | 74.01 | 0 | 30.87 | 0 | 157.68 | 0 | 0
2025-01-20 16:00 | 43.91 | 27.56 | 27.56 | 0 | 0 | 16.35 | 140.47 | 0 | 0
2025-01-20 17:00 | 43.78 | 0 | 0 | 0 | 0 | 43.78 | 94.38 | 0 | 0
2025-01-20 18:00 | 42.18 | 0 | 0 | 0 | 0 | 42.18 | 49.99 | 0 | 0
2025-01-20 19:00 | 42.61 | 0 | 0 | 25.95 | 0 | 16.66 | 32.45 | 0 | 0
2025-01-20 20:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 21:00 | 40.88 | 0 | 0 | 40.88 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 22:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 32.45 | 0 | 0
2025-01-20 23:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 | 37.83 | 0 | 0 | 37.83 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 01:00 | 38.71 | 0 | 0 | 38.71 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 02:00 | 37.21 | 0 | 0 | 37.21 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 03:00 | 36.32 | 0 | 0 | 36.32 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 04:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 05:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 06:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 07:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 08:00 | 39.13 | 9.68 | 9.68 | 29.45 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 09:00 | 40.1 | 58.65 | 58.65 | 0 | 18.55 | 0 | 50.08 | 0 | 0
2025-01-21 10:00 | 40.79 | 67.45 | 67.45 | 0 | 26.65 | 0 | 75.39 | 0 | 0
2025-01-21 11:00 | 41.72 | 56.06 | 56.06 | 0 | 14.34 | 0 | 89.01 | 0 | 0
2025-01-21 12:00 | 42.42 | 49.51 | 49.51 | 0 | 7.09 | 0 | 95.75 | 0 | 0
2025-01-21 13:00 | 41.74 | 57.79 | 57.79 | 0 | 16.04 | 0 | 110.99 | 0 | 0
2025-01-21 14:00 | 43.36 | 65.14 | 65.14 | 0 | 21.78 | 0 | 131.68 | 0 | 0
2025-01-21 15:00 | 42.64 | 69.7 | 69.7 | 0 | 27.07 | 0 | 157.4 | 0 | 0
2025-01-21 16:00 | 42.3 | 24.93 | 24.93 | 0 | 0 | 17.37 | 139.12 | 0 | 0
2025-01-21 17:00 | 42.68 | 0 | 0 | 0 | 0 | 42.68 | 94.19 | 0 | 0
2025-01-21 18:00 | 42.25 | 0 | 0 | 0 | 0 | 42.25 | 49.71 | 0 | 0
2025-01-21 19:00 | 41.21 | 0 | 0 | 24.81 | 0 | 16.4 | 32.45 | 0 | 0
2025-01-21 20:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 21:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 22:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 32.45 | 0 | 0
2025-01-21 23:00 | 38.04 | 0 | 0 | 38.04 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 | 37.6 | 0 | 0 | 37.6 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 01:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 02:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 03:00 | 37.03 | 0 | 0 | 37.03 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 04:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 05:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 06:00 | 36.65 | 0 | 0 | 36.65 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 07:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 08:00 | 38.92 | 10.55 | 10.55 | 28.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 09:00 | 39.75 | 52.26 | 52.26 | 0 | 12.51 | 0 | 44.34 | 0 | 0
2025-01-22 10:00 | 40.53 | 40.74 | 40.74 | 0 | 0.21 | 0 | 44.54 | 0 | 0
2025-01-22 11:00 | 41.32 | 32.04 | 32.04 | 0 | 0 | 9.28 | 34.77 | 0 | 0
2025-01-22 12:00 | 42.24 | 52.65 | 52.65 | 0 | 10.41 | 0 | 44.65 | 0 | 0
2025-01-22 13:00 | 41.62 | 55.13 | 55.13 | 0 | 13.51 | 0 | 57.48 | 0 | 0
2025-01-22 14:00 | 41.85 | 40.08 | 40.08 | 0 | 0 | 1.77 | 55.62 | 0 | 0
2025-01-22 15:00 | 41.97 | 53.58 | 53.58 | 0 | 11.6 | 0 | 66.64 | 0 | 0
2025-01-22 16:00 | 42.58 | 0 | 0 | 10.1 | 0 | 32.48 | 32.45 | 0 | 0
2025-01-22 17:00 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 18:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 19:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 20:00 | 39.69 | 0 | 0 | 39.69 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 21:00 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 22:00 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 32.45 | 0 | 0
2025-01-22 23:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 01:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 02:00 | 37.31 | 0 | 0 | 37.31 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 03:00 | 36.33 | 0 | 0 | 36.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 04:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 05:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 06:00 | 36.91 | 0 | 0 | 36.91 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 07:00 | 38.62 | 0 | 0 | 38.62 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 08:00 | 39.39 | 9.01 | 9.01 | 30.38 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 09:00 | 40.29 | 23.77 | 23.77 | 16.52 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 10:00 | 42.24 | 43 | 43 | 0 | 0.77 | 0 | 33.18 | 0 | 0
2025-01-23 11:00 | 42.18 | 57.82 | 57.82 | 0 | 15.64 | 0 | 48.03 | 0 | 0
2025-01-23 12:00 | 44.46 | 53.02 | 53.02 | 0 | 8.56 | 0 | 56.17 | 0 | 0
2025-01-23 13:00 | 44.05 | 61.04 | 61.04 | 0 | 16.99 | 0 | 72.3 | 0 | 0
2025-01-23 14:00 | 44 | 36.19 | 36.19 | 0 | 0 | 7.81 | 64.08 | 0 | 0
2025-01-23 15:00 | 44.84 | 35.58 | 35.58 | 0 | 0 | 9.26 | 54.33 | 0 | 0
2025-01-23 16:00 | 44.1 | 0 | 0 | 23.31 | 0 | 20.79 | 32.45 | 0 | 0
2025-01-23 17:00 | 43.79 | 0 | 0 | 43.79 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 18:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 19:00 | 42.77 | 0 | 0 | 42.77 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 20:00 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 21:00 | 40.86 | 0 | 0 | 40.86 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 22:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 32.45 | 0 | 0
2025-01-23 23:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 | 37.9 | 0 | 0 | 37.9 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 01:00 | 37.79 | 0 | 0 | 37.79 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 02:00 | 35.84 | 0 | 0 | 35.84 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 03:00 | 36.51 | 0 | 0 | 36.51 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 04:00 | 36.35 | 0 | 0 | 36.35 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 05:00 | 37.17 | 0 | 0 | 37.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 06:00 | 37.35 | 0 | 0 | 37.35 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 07:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 08:00 | 40.05 | 1.02 | 1.02 | 39.03 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 09:00 | 39.87 | 5.67 | 5.67 | 34.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 10:00 | 41 | 22.28 | 22.28 | 18.72 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 11:00 | 41.45 | 36.59 | 36.59 | 4.85 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 12:00 | 42.26 | 30.02 | 30.02 | 12.24 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 13:00 | 42.73 | 17.07 | 17.07 | 25.66 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 14:00 | 43.26 | 16.56 | 16.56 | 26.7 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 15:00 | 43.73 | 0.72 | 0.72 | 43.01 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 16:00 | 43.86 | 2 | 2 | 41.87 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 17:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 18:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 19:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 20:00 | 40.75 | 0 | 0 | 40.75 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 21:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 22:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 32.45 | 0 | 0
2025-01-24 23:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 01:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 02:00 | 37.38 | 0 | 0 | 37.38 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 03:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 04:00 | 36.61 | 0 | 0 | 36.61 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 05:00 | 37.28 | 0 | 0 | 37.28 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 06:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 07:00 | 38.5 | 0 | 0 | 38.5 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 08:00 | 37.25 | 5.03 | 5.03 | 32.21 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 09:00 | 39.01 | 57.95 | 57.95 | 0 | 18.94 | 0 | 50.44 | 0 | 0
2025-01-25 10:00 | 40.89 | 49.89 | 49.89 | 0 | 9 | 0 | 58.99 | 0 | 0
2025-01-25 11:00 | 41.62 | 38.85 | 38.85 | 0 | 0 | 2.77 | 56.07 | 0 | 0
2025-01-25 12:00 | 41.41 | 42.63 | 42.63 | 0 | 1.23 | 0 | 57.24 | 0 | 0
2025-01-25 13:00 | 42.09 | 57.38 | 57.38 | 0 | 15.29 | 0 | 71.76 | 0 | 0
2025-01-25 14:00 | 43.41 | 37.26 | 37.26 | 0 | 0 | 6.15 | 65.28 | 0 | 0
2025-01-25 15:00 | 42.58 | 5.07 | 5.07 | 6.32 | 0 | 31.19 | 32.45 | 0 | 0
2025-01-25 16:00 | 43.85 | 0 | 0 | 43.85 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 17:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 18:00 | 42.19 | 0 | 0 | 42.19 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 19:00 | 42.19 | 0 | 0 | 42.19 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 20:00 | 40.73 | 0 | 0 | 40.73 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 21:00 | 39.37 | 0 | 0 | 39.37 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 22:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 32.45 | 0 | 0
2025-01-25 23:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 01:00 | 36.99 | 0 | 0 | 36.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 02:00 | 36.42 | 0 | 0 | 36.42 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 03:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 04:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 05:00 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 06:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 07:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 08:00 | 39.4 | 3.54 | 3.54 | 35.85 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 09:00 | 39.41 | 11.53 | 11.53 | 27.88 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 10:00 | 40.19 | 12.3 | 12.3 | 27.88 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 11:00 | 42 | 25.7 | 25.7 | 16.29 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 12:00 | 41.86 | 34.22 | 34.22 | 7.64 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 13:00 | 41.83 | 44.39 | 44.39 | 0 | 2.56 | 0 | 34.88 | 0 | 0
2025-01-26 14:00 | 43.05 | 69.02 | 69.02 | 0 | 25.97 | 0 | 59.56 | 0 | 0
2025-01-26 15:00 | 43.16 | 72.81 | 72.81 | 0 | 29.65 | 0 | 87.73 | 0 | 0
2025-01-26 16:00 | 42.06 | 33.43 | 33.43 | 0 | 0 | 8.64 | 78.64 | 0 | 0
2025-01-26 17:00 | 42.65 | 0 | 0 | 0 | 0 | 42.65 | 33.74 | 0 | 0
2025-01-26 18:00 | 42.43 | 0 | 0 | 41.2 | 0 | 1.23 | 32.45 | 0 | 0
2025-01-26 19:00 | 41.63 | 0 | 0 | 41.63 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 20:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 21:00 | 39.2 | 0 | 0 | 39.2 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 22:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 32.45 | 0 | 0
2025-01-26 23:00 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 | 37.43 | 0 | 0 | 37.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 01:00 | 37.57 | 0 | 0 | 37.57 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 02:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 03:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 04:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 05:00 | 37.08 | 0 | 0 | 37.08 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 06:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 07:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 08:00 | 39.31 | 2.52 | 2.52 | 36.79 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 09:00 | 40.25 | 36.71 | 36.71 | 3.54 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 10:00 | 41.55 | 71.4 | 71.4 | 0 | 29.85 | 0 | 60.81 | 0 | 0
2025-01-27 11:00 | 42.03 | 48.64 | 48.64 | 0 | 6.62 | 0 | 67.09 | 0 | 0
2025-01-27 12:00 | 42.49 | 31.4 | 31.4 | 0 | 0 | 11.09 | 55.42 | 0 | 0
2025-01-27 13:00 | 43.27 | 14.53 | 14.53 | 6.91 | 0 | 21.83 | 32.45 | 0 | 0
2025-01-27 14:00 | 44.19 | 8.6 | 8.6 | 35.59 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 15:00 | 44.01 | 6.22 | 6.22 | 37.79 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 16:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 17:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 18:00 | 42.67 | 0 | 0 | 42.67 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 19:00 | 42.43 | 0 | 0 | 42.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 22:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 32.45 | 0 | 0
2025-01-27 23:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 | 36.85 | 0 | 0 | 36.85 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 01:00 | 36.62 | 0 | 0 | 36.62 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 02:00 | 36.29 | 0 | 0 | 36.29 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 03:00 | 36.71 | 0 | 0 | 36.71 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 04:00 | 36.67 | 0 | 0 | 36.67 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 05:00 | 36.97 | 0 | 0 | 36.97 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 07:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 08:00 | 39.39 | 24.32 | 24.32 | 15.07 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 09:00 | 40.35 | 69.08 | 69.08 | 0 | 28.72 | 0 | 59.73 | 0 | 0
2025-01-28 10:00 | 41.39 | 33.94 | 33.94 | 0 | 0 | 7.45 | 51.9 | 0 | 0
2025-01-28 11:00 | 40.91 | 24.24 | 24.24 | 0 | 0 | 16.67 | 34.35 | 0 | 0
2025-01-28 12:00 | 42.55 | 28.78 | 28.78 | 11.96 | 0 | 1.81 | 32.45 | 0 | 0
2025-01-28 13:00 | 42.23 | 21.07 | 21.07 | 21.16 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 14:00 | 43.72 | 25.41 | 25.41 | 18.31 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 15:00 | 43.83 | 45.56 | 45.56 | 0 | 1.74 | 0 | 34.1 | 0 | 0
2025-01-28 16:00 | 44.22 | 14.25 | 14.25 | 28.4 | 0 | 1.57 | 32.45 | 0 | 0
2025-01-28 17:00 | 43.92 | 0 | 0 | 43.92 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 18:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 19:00 | 41.71 | 0 | 0 | 41.71 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 20:00 | 41.32 | 0 | 0 | 41.32 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 21:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 22:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 32.45 | 0 | 0
2025-01-28 23:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 | 37.42 | 0 | 0 | 37.42 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 01:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 02:00 | 37.15 | 0 | 0 | 37.15 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 03:00 | 36.22 | 0 | 0 | 36.22 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 04:00 | 37.3 | 0 | 0 | 37.3 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 05:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 06:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 07:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 08:00 | 38.83 | 21.81 | 21.81 | 17.02 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 09:00 | 39.91 | 72.61 | 72.61 | 0 | 32.7 | 0 | 63.51 | 0 | 0
2025-01-29 10:00 | 41.4 | 61.64 | 61.64 | 0 | 20.24 | 0 | 82.74 | 0 | 0
2025-01-29 11:00 | 41.54 | 59.08 | 59.08 | 0 | 17.54 | 0 | 99.41 | 0 | 0
2025-01-29 12:00 | 43.01 | 52.21 | 52.21 | 0 | 9.2 | 0 | 108.15 | 0 | 0
2025-01-29 13:00 | 42.78 | 57.38 | 57.38 | 0 | 14.6 | 0 | 122.02 | 0 | 0
2025-01-29 14:00 | 43.68 | 41.32 | 41.32 | 0 | 0 | 2.36 | 119.53 | 0 | 0
2025-01-29 15:00 | 43.97 | 40.72 | 40.72 | 0 | 0 | 3.25 | 116.12 | 0 | 0
2025-01-29 16:00 | 45.01 | 12.53 | 12.53 | 0 | 0 | 32.47 | 81.93 | 0 | 0
2025-01-29 17:00 | 42.71 | 0 | 0 | 0 | 0 | 42.71 | 36.97 | 0 | 0
2025-01-29 18:00 | 43.53 | 0 | 0 | 39.23 | 0 | 4.3 | 32.45 | 0 | 0
2025-01-29 19:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 20:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 21:00 | 40.24 | 0 | 0 | 40.24 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 22:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 32.45 | 0 | 0
2025-01-29 23:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 01:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 02:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 03:00 | 36.39 | 0 | 0 | 36.39 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 04:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 05:00 | 36.63 | 0 | 0 | 36.63 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 06:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 07:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 08:00 | 39.24 | 14.56 | 14.56 | 24.69 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 09:00 | 40.11 | 25.94 | 25.94 | 14.17 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 10:00 | 40.6 | 49.76 | 49.76 | 0 | 9.15 | 0 | 41.15 | 0 | 0
2025-01-30 11:00 | 41.94 | 49.77 | 49.77 | 0 | 7.82 | 0 | 48.58 | 0 | 0
2025-01-30 12:00 | 42.05 | 44.9 | 44.9 | 0 | 2.85 | 0 | 51.28 | 0 | 0
2025-01-30 13:00 | 43 | 53.23 | 53.23 | 0 | 10.24 | 0 | 61.01 | 0 | 0
2025-01-30 14:00 | 43.95 | 53.8 | 53.8 | 0 | 9.85 | 0 | 70.37 | 0 | 0
2025-01-30 15:00 | 44.63 | 65.15 | 65.15 | 0 | 20.52 | 0 | 89.87 | 0 | 0
2025-01-30 16:00 | 45.24 | 36.99 | 36.99 | 0 | 0 | 8.26 | 81.18 | 0 | 0
2025-01-30 17:00 | 43.16 | 0 | 0 | 0 | 0 | 43.16 | 35.75 | 0 | 0
2025-01-30 18:00 | 43.56 | 0 | 0 | 40.43 | 0 | 3.13 | 32.45 | 0 | 0
2025-01-30 19:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 20:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 21:00 | 40.43 | 0 | 0 | 40.43 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 22:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 32.45 | 0 | 0
2025-01-30 23:00 | 38.48 | 0 | 0 | 38.48 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 | 37.57 | 0 | 0 | 37.57 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 01:00 | 36.49 | 0 | 0 | 36.49 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 02:00 | 36.07 | 0 | 0 | 36.07 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 03:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 04:00 | 36.71 | 0 | 0 | 36.71 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 05:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 06:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 07:00 | 38.98 | 0 | 0 | 38.98 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 08:00 | 39.68 | 27.73 | 27.73 | 11.95 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 09:00 | 40.43 | 79.33 | 79.33 | 0 | 38.9 | 0 | 69.41 | 0 | 0
2025-01-31 10:00 | 42.63 | 77.95 | 77.95 | 0 | 35.32 | 0 | 102.96 | 0 | 0
2025-01-31 11:00 | 44.05 | 68.62 | 68.62 | 0 | 24.57 | 0 | 126.31 | 0 | 0
2025-01-31 12:00 | 44.64 | 61.77 | 61.77 | 0 | 17.13 | 0 | 142.58 | 0 | 0
2025-01-31 13:00 | 45.79 | 57.65 | 57.65 | 0 | 11.87 | 0 | 153.85 | 0 | 0
2025-01-31 14:00 | 46.51 | 41.5 | 41.5 | 0 | 0 | 5.01 | 148.58 | 0 | 0
2025-01-31 15:00 | 46.66 | 17.34 | 17.34 | 0 | 0 | 29.32 | 117.72 | 0 | 0
2025-01-31 16:00 | 46.2 | 19.84 | 19.84 | 0 | 0 | 26.35 | 89.98 | 0 | 0
2025-01-31 17:00 | 45.6 | 0 | 0 | 0 | 0 | 45.6 | 41.98 | 0 | 0
2025-01-31 18:00 | 44.65 | 0 | 0 | 35.6 | 0 | 9.05 | 32.45 | 0 | 0
2025-01-31 19:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 20:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 21:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 22:00 | 39.19 | 0 | 0 | 39.19 | 0 | 0 | 32.45 | 0 | 0
2025-01-31 23:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 01:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 02:00 | 36.73 | 0 | 0 | 36.73 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 03:00 | 36.17 | 0 | 0 | 36.17 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 04:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 05:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 06:00 | 37.77 | 0 | 0 | 37.77 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 07:00 | 38.98 | 0 | 0 | 38.98 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 08:00 | 39.01 | 23.06 | 23.06 | 15.96 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 09:00 | 40.19 | 68.7 | 68.7 | 0 | 28.51 | 0 | 59.53 | 0 | 0
2025-02-01 10:00 | 40.33 | 69.47 | 69.47 | 0 | 29.15 | 0 | 87.22 | 0 | 0
2025-02-01 11:00 | 41.78 | 48.34 | 48.34 | 0 | 6.56 | 0 | 93.45 | 0 | 0
2025-02-01 12:00 | 42.18 | 44.42 | 44.42 | 0 | 2.25 | 0 | 95.59 | 0 | 0
2025-02-01 13:00 | 42.27 | 53.73 | 53.73 | 0 | 11.46 | 0 | 106.48 | 0 | 0
2025-02-01 14:00 | 42.82 | 62.52 | 62.52 | 0 | 19.7 | 0 | 125.19 | 0 | 0
2025-02-01 15:00 | 42.94 | 74.18 | 74.18 | 0 | 31.23 | 0 | 154.87 | 0 | 0
2025-02-01 16:00 | 42.8 | 40.83 | 40.83 | 0 | 0 | 1.97 | 152.8 | 0 | 0
2025-02-01 17:00 | 43.53 | 0 | 0 | 0 | 0 | 43.53 | 106.98 | 0 | 0
2025-02-01 18:00 | 42.12 | 0 | 0 | 0 | 0 | 42.12 | 62.64 | 0 | 0
2025-02-01 19:00 | 41.43 | 0 | 0 | 12.76 | 0 | 28.68 | 32.45 | 0 | 0
2025-02-01 20:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 22:00 | 39.06 | 0 | 0 | 39.06 | 0 | 0 | 32.45 | 0 | 0
2025-02-01 23:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 01:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 02:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 03:00 | 36.8 | 0 | 0 | 36.8 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 04:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 05:00 | 37.18 | 0 | 0 | 37.18 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 06:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 08:00 | 38.04 | 36.21 | 36.21 | 1.83 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 09:00 | 39.01 | 85.37 | 85.37 | 0 | 46.36 | 0 | 76.49 | 0 | 0
2025-02-02 10:00 | 40.53 | 79.06 | 79.06 | 0 | 38.52 | 0 | 113.09 | 0 | 0
2025-02-02 11:00 | 41.53 | 15.34 | 15.34 | 0 | 0 | 26.19 | 85.52 | 0 | 0
2025-02-02 12:00 | 42.47 | 38.81 | 38.81 | 0 | 0 | 3.66 | 81.67 | 0 | 0
2025-02-02 13:00 | 42.81 | 62.9 | 62.9 | 0 | 20.09 | 0 | 100.75 | 0 | 0
2025-02-02 14:00 | 42.66 | 72.15 | 72.15 | 0 | 29.48 | 0 | 128.76 | 0 | 0
2025-02-02 15:00 | 43.46 | 56.47 | 56.47 | 0 | 13.01 | 0 | 141.12 | 0 | 0
2025-02-02 16:00 | 43.37 | 45.51 | 45.51 | 0 | 2.14 | 0 | 143.15 | 0 | 0
2025-02-02 17:00 | 42.67 | 0 | 0 | 0 | 0 | 42.67 | 98.24 | 0 | 0
2025-02-02 18:00 | 42.6 | 0 | 0 | 0 | 0 | 42.6 | 53.39 | 0 | 0
2025-02-02 19:00 | 41.66 | 0 | 0 | 21.76 | 0 | 19.89 | 32.45 | 0 | 0
2025-02-02 20:00 | 40.52 | 0 | 0 | 40.52 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 21:00 | 40.36 | 0 | 0 | 40.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 22:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 32.45 | 0 | 0
2025-02-02 23:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 01:00 | 36.02 | 0 | 0 | 36.02 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 02:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 03:00 | 36.2 | 0 | 0 | 36.2 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 04:00 | 36.72 | 0 | 0 | 36.72 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 06:00 | 37.02 | 0 | 0 | 37.02 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 07:00 | 37.94 | 0 | 0 | 37.94 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 08:00 | 38.76 | 1.4 | 1.4 | 37.35 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 09:00 | 41.19 | 8.34 | 8.34 | 32.85 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 10:00 | 41.6 | 11.46 | 11.46 | 30.14 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 11:00 | 41.15 | 28.92 | 28.92 | 12.23 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 12:00 | 41.72 | 31.18 | 31.18 | 10.54 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 13:00 | 41.73 | 38.39 | 38.39 | 3.34 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 14:00 | 41.59 | 28.73 | 28.73 | 12.86 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 15:00 | 42.57 | 22.59 | 22.59 | 19.98 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 16:00 | 42.05 | 44.68 | 44.68 | 0 | 2.63 | 0 | 34.95 | 0 | 0
2025-02-03 17:00 | 42.26 | 0.56 | 0.56 | 39.33 | 0 | 2.37 | 32.45 | 0 | 0
2025-02-03 18:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 19:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 20:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 21:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 22:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 32.45 | 0 | 0
2025-02-03 23:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 01:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 02:00 | 37.25 | 0 | 0 | 37.25 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 03:00 | 36.81 | 0 | 0 | 36.81 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 04:00 | 36.24 | 0 | 0 | 36.24 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 05:00 | 37.12 | 0 | 0 | 37.12 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 06:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 07:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 08:00 | 39.4 | 4.79 | 4.79 | 34.61 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 09:00 | 41.21 | 25.48 | 25.48 | 15.73 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 10:00 | 41.95 | 40.94 | 40.94 | 1.01 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 11:00 | 42.27 | 15.3 | 15.3 | 26.98 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 12:00 | 43.61 | 27.48 | 27.48 | 16.14 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 13:00 | 44.86 | 20.15 | 20.15 | 24.71 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 14:00 | 45.29 | 22.48 | 22.48 | 22.81 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 15:00 | 43.84 | 12.55 | 12.55 | 31.29 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 16:00 | 43.85 | 9.39 | 9.39 | 34.46 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 17:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 18:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 19:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 20:00 | 41.2 | 0 | 0 | 41.2 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 21:00 | 40.65 | 0 | 0 | 40.65 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 22:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 32.45 | 0 | 0
2025-02-04 23:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 | 37.55 | 0 | 0 | 37.55 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 01:00 | 36.95 | 0 | 0 | 36.95 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 02:00 | 36.52 | 0 | 0 | 36.52 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 03:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 04:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 05:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 06:00 | 37.64 | 0 | 0 | 37.64 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 07:00 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 08:00 | 39.24 | 12.08 | 12.08 | 27.16 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 09:00 | 39.32 | 13.84 | 13.84 | 25.48 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 10:00 | 41.06 | 36.55 | 36.55 | 4.51 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 11:00 | 41.91 | 36.66 | 36.66 | 5.25 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 12:00 | 42.64 | 43.01 | 43.01 | 0 | 0.37 | 0 | 32.8 | 0 | 0
2025-02-05 13:00 | 43.92 | 42.44 | 42.44 | 1.14 | 0 | 0.33 | 32.45 | 0 | 0
2025-02-05 14:00 | 45.66 | 37.58 | 37.58 | 8.08 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 15:00 | 45.14 | 29.01 | 29.01 | 16.13 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 16:00 | 45.64 | 40.98 | 40.98 | 4.67 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 17:00 | 44.72 | 1.01 | 1.01 | 43.71 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 18:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 19:00 | 42.37 | 0 | 0 | 42.37 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 20:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 21:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 22:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 32.45 | 0 | 0
2025-02-05 23:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 01:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 02:00 | 36.43 | 0 | 0 | 36.43 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 03:00 | 36.28 | 0 | 0 | 36.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 04:00 | 37.03 | 0 | 0 | 37.03 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 05:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 06:00 | 37.49 | 0 | 0 | 37.49 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 07:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 32.45 | 0 | 0
2025-02-06 08:00 | 39.71 | 41.09 | 41.09 | 0 | 1.38 | 0 | 33.76 | 0 | 0
2025-02-06 09:00 | 40.62 | 89.38 | 89.38 | 0 | 48.76 | 0 | 80.08 | 0 | 0
2025-02-06 10:00 | 41.97 | 84.52 | 84.52 | 0 | 42.55 | 0 | 120.51 | 0 | 0
2025-02-06 11:00 | 42.64 | 75.48 | 75.48 | 0 | 32.84 | 0 | 151.7 | 0 | 0
2025-02-06 12:00 | 42.2 | 67.93 | 67.93 | 0 | 25.73 | 0 | 176.14 | 0 | 0
2025-02-06 13:00 | 44.08 | 72.02 | 72.02 | 0 | 27.94 | 0 | 202.68 | 0 | 0
2025-02-06 14:00 | 43.3 | 81.8 | 81.8 | 0 | 38.49 | 0 | 239.25 | 0 | 0
2025-02-06 15:00 | 44.21 | 88.01 | 88.01 | 0 | 43.81 | 0 | 280.87 | 0 | 0
2025-02-06 16:00 | 43.6 | 62.85 | 55.38 | 0 | 11.77 | 0 | 292.05 | 7.48 | 0
2025-02-06 17:00 | 43.03 | 0.62 | 0.62 | 0 | 0 | 42.41 | 247.41 | 0 | 0
2025-02-06 18:00 | 41.8 | 0 | 0 | 0 | 0 | 41.8 | 203.41 | 0 | 0
2025-02-06 19:00 | 41.92 | 0 | 0 | 0 | 0 | 41.92 | 159.29 | 0 | 0
2025-02-06 20:00 | 40.41 | 0 | 0 | 0 | 0 | 40.41 | 116.75 | 0 | 0
2025-02-06 21:00 | 40.79 | 0 | 0 | 0 | 0 | 40.79 | 73.8 | 0 | 0
2025-02-06 22:00 | 40.19 | 0 | 0 | 0.9 | 0 | 39.29 | 32.45 | 0 | 0
2025-02-06 23:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 | 38.05 | 0 | 0 | 38.05 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 01:00 | 37 | 0 | 0 | 37 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 02:00 | 36.7 | 0 | 0 | 36.7 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 03:00 | 37.29 | 0 | 0 | 37.29 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 04:00 | 37 | 0 | 0 | 37 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 05:00 | 38.23 | 0 | 0 | 38.23 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 06:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 07:00 | 39.08 | 0 | 0 | 39.08 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 08:00 | 39.4 | 40.97 | 40.97 | 0 | 1.58 | 0 | 33.95 | 0 | 0
2025-02-07 09:00 | 40.53 | 68.45 | 68.45 | 0 | 27.91 | 0 | 60.47 | 0 | 0
2025-02-07 10:00 | 40.66 | 15.93 | 15.93 | 0 | 0 | 24.73 | 34.44 | 0 | 0
2025-02-07 11:00 | 41.53 | 48.48 | 48.48 | 0 | 6.95 | 0 | 41.04 | 0 | 0
2025-02-07 12:00 | 42.05 | 63 | 63 | 0 | 20.95 | 0 | 60.94 | 0 | 0
2025-02-07 13:00 | 42.09 | 79.24 | 79.24 | 0 | 37.14 | 0 | 96.23 | 0 | 0
2025-02-07 14:00 | 43.09 | 78.03 | 78.03 | 0 | 34.94 | 0 | 129.43 | 0 | 0
2025-02-07 15:00 | 43.17 | 55.39 | 55.39 | 0 | 12.22 | 0 | 141.03 | 0 | 0
2025-02-07 16:00 | 43.06 | 0.15 | 0.15 | 0 | 0 | 42.91 | 95.87 | 0 | 0
2025-02-07 17:00 | 43.28 | 0 | 0 | 0 | 0 | 43.28 | 50.31 | 0 | 0
2025-02-07 18:00 | 42.83 | 0 | 0 | 25.86 | 0 | 16.97 | 32.45 | 0 | 0
2025-02-07 19:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 20:00 | 41.07 | 0 | 0 | 41.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 21:00 | 39.82 | 0 | 0 | 39.82 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 22:00 | 39.36 | 0 | 0 | 39.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-07 23:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 | 38.75 | 0 | 0 | 38.75 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 01:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 02:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 03:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 04:00 | 35.97 | 0 | 0 | 35.97 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 05:00 | 36.39 | 0 | 0 | 36.39 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 06:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 07:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 08:00 | 39.53 | 26.24 | 26.24 | 13.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 09:00 | 39.53 | 62.76 | 62.76 | 0 | 23.23 | 0 | 54.52 | 0 | 0
2025-02-08 10:00 | 40.94 | 69.38 | 69.38 | 0 | 28.44 | 0 | 81.54 | 0 | 0
2025-02-08 11:00 | 42.63 | 64.2 | 64.2 | 0 | 21.57 | 0 | 102.02 | 0 | 0
2025-02-08 12:00 | 42.6 | 58.78 | 58.78 | 0 | 16.18 | 0 | 117.39 | 0 | 0
2025-02-08 13:00 | 42.68 | 68.03 | 68.03 | 0 | 25.35 | 0 | 141.47 | 0 | 0
2025-02-08 14:00 | 42.63 | 68.69 | 68.69 | 0 | 26.06 | 0 | 166.23 | 0 | 0
2025-02-08 15:00 | 42.74 | 76.88 | 76.88 | 0 | 34.14 | 0 | 198.67 | 0 | 0
2025-02-08 16:00 | 41.79 | 59.93 | 59.93 | 0 | 18.14 | 0 | 215.9 | 0 | 0
2025-02-08 17:00 | 42.73 | 0.95 | 0.95 | 0 | 0 | 41.77 | 171.93 | 0 | 0
2025-02-08 18:00 | 42.61 | 0 | 0 | 0 | 0 | 42.61 | 127.08 | 0 | 0
2025-02-08 19:00 | 40.84 | 0 | 0 | 0 | 0 | 40.84 | 84.09 | 0 | 0
2025-02-08 20:00 | 40.62 | 0 | 0 | 0 | 0 | 40.62 | 41.32 | 0 | 0
2025-02-08 21:00 | 39.62 | 0 | 0 | 31.19 | 0 | 8.43 | 32.45 | 0 | 0
2025-02-08 22:00 | 38.92 | 0 | 0 | 38.92 | 0 | 0 | 32.45 | 0 | 0
2025-02-08 23:00 | 38.66 | 0 | 0 | 38.66 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 01:00 | 37.75 | 0 | 0 | 37.75 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 02:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 03:00 | 36.84 | 0 | 0 | 36.84 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 04:00 | 35.85 | 0 | 0 | 35.85 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 05:00 | 36.95 | 0 | 0 | 36.95 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 06:00 | 38.64 | 0 | 0 | 38.64 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 07:00 | 37.41 | 0 | 0 | 37.41 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 08:00 | 39.54 | 5.15 | 5.15 | 34.38 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 09:00 | 40.14 | 46.9 | 46.9 | 0 | 6.76 | 0 | 38.88 | 0 | 0
2025-02-09 10:00 | 42.17 | 63.94 | 63.94 | 0 | 21.77 | 0 | 59.56 | 0 | 0
2025-02-09 11:00 | 42.42 | 80.13 | 80.13 | 0 | 37.71 | 0 | 95.38 | 0 | 0
2025-02-09 12:00 | 43.84 | 68.89 | 68.89 | 0 | 25.05 | 0 | 119.18 | 0 | 0
2025-02-09 13:00 | 44.6 | 37.37 | 37.37 | 0 | 0 | 7.23 | 111.58 | 0 | 0
2025-02-09 14:00 | 45.67 | 11.68 | 11.68 | 0 | 0 | 33.99 | 75.8 | 0 | 0
2025-02-09 15:00 | 44.8 | 13.07 | 13.07 | 0 | 0 | 31.73 | 42.4 | 0 | 0
2025-02-09 16:00 | 44.94 | 0.1 | 0.1 | 35.38 | 0 | 9.46 | 32.45 | 0 | 0
2025-02-09 17:00 | 43.57 | 0.4 | 0.4 | 43.17 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 18:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 19:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 20:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 21:00 | 40.71 | 0 | 0 | 40.71 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 22:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 32.45 | 0 | 0
2025-02-09 23:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 | 38.56 | 0 | 0 | 38.56 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 01:00 | 37.63 | 0 | 0 | 37.63 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 02:00 | 36.33 | 0 | 0 | 36.33 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 04:00 | 37.5 | 0 | 0 | 37.5 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 05:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 06:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 32.45 | 0 | 0
2025-02-10 08:00 | 39.92 | 46.69 | 46.69 | 0 | 6.77 | 0 | 38.88 | 0 | 0
2025-02-10 09:00 | 41.03 | 87.4 | 87.4 | 0 | 46.38 | 0 | 82.94 | 0 | 0
2025-02-10 10:00 | 42.82 | 83.84 | 83.84 | 0 | 41.02 | 0 | 121.9 | 0 | 0
2025-02-10 11:00 | 43.14 | 73.06 | 73.06 | 0 | 29.91 | 0 | 150.32 | 0 | 0
2025-02-10 12:00 | 44.14 | 67.79 | 67.79 | 0 | 23.65 | 0 | 172.79 | 0 | 0
2025-02-10 13:00 | 45.87 | 71.3 | 71.3 | 0 | 25.43 | 0 | 196.95 | 0 | 0
2025-02-10 14:00 | 44.86 | 79.67 | 79.67 | 0 | 34.82 | 0 | 230.02 | 0 | 0
2025-02-10 15:00 | 44.72 | 84.97 | 84.97 | 0 | 40.25 | 0 | 268.26 | 0 | 0
2025-02-10 16:00 | 45.18 | 63.83 | 63.83 | 0 | 18.65 | 0 | 285.98 | 0 | 0
2025-02-10 17:00 | 44.73 | 1.37 | 1.37 | 0 | 0 | 43.36 | 240.34 | 0 | 0
2025-02-10 18:00 | 43.54 | 0 | 0 | 0 | 0 | 43.54 | 194.5 | 0 | 0
2025-02-10 19:00 | 42.39 | 0 | 0 | 0 | 0 | 42.39 | 149.88 | 0 | 0
2025-02-10 20:00 | 43.04 | 0 | 0 | 0 | 0 | 43.04 | 104.57 | 0 | 0
2025-02-10 21:00 | 40.98 | 0 | 0 | 0 | 0 | 40.98 | 61.43 | 0 | 0
2025-02-10 22:00 | 39.42 | 0 | 0 | 11.89 | 0 | 27.53 | 32.45 | 0 | 0
2025-02-10 23:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 01:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 02:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 03:00 | 36.4 | 0 | 0 | 36.4 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 04:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 05:00 | 38.49 | 0 | 0 | 38.49 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 06:00 | 38.35 | 0 | 0 | 38.35 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 07:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 08:00 | 39.56 | 27.92 | 27.92 | 11.64 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 09:00 | 40.62 | 20.51 | 20.51 | 20.11 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 10:00 | 41.74 | 38.6 | 38.6 | 3.14 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 11:00 | 42.66 | 44.1 | 44.1 | 0 | 1.44 | 0 | 33.82 | 0 | 0
2025-02-11 12:00 | 44.17 | 33.39 | 33.39 | 9.48 | 0 | 1.3 | 32.45 | 0 | 0
2025-02-11 13:00 | 43.52 | 54.17 | 54.17 | 0 | 10.65 | 0 | 42.56 | 0 | 0
2025-02-11 14:00 | 45.24 | 73.51 | 73.51 | 0 | 28.27 | 0 | 69.42 | 0 | 0
2025-02-11 15:00 | 44.77 | 96.26 | 96.26 | 0 | 51.49 | 0 | 118.34 | 0 | 0
2025-02-11 16:00 | 45 | 71.46 | 71.46 | 0 | 26.46 | 0 | 143.48 | 0 | 0
2025-02-11 17:00 | 43.82 | 4.65 | 4.65 | 0 | 0 | 39.17 | 102.25 | 0 | 0
2025-02-11 18:00 | 44.38 | 0 | 0 | 0 | 0 | 44.38 | 55.53 | 0 | 0
2025-02-11 19:00 | 43.47 | 0 | 0 | 21.54 | 0 | 21.93 | 32.45 | 0 | 0
2025-02-11 20:00 | 42.34 | 0 | 0 | 42.34 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 21:00 | 40.07 | 0 | 0 | 40.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 32.45 | 0 | 0
2025-02-11 23:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 | 37.33 | 0 | 0 | 37.33 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 01:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 02:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 03:00 | 37.36 | 0 | 0 | 37.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 04:00 | 37.3 | 0 | 0 | 37.3 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 05:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 06:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 07:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 08:00 | 38.23 | 20.27 | 20.27 | 17.96 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 09:00 | 40.34 | 44.77 | 44.77 | 0 | 4.43 | 0 | 36.65 | 0 | 0
2025-02-12 10:00 | 41.23 | 20.02 | 20.02 | 17.22 | 0 | 3.99 | 32.45 | 0 | 0
2025-02-12 11:00 | 41.17 | 29.6 | 29.6 | 11.58 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 12:00 | 42.7 | 16.46 | 16.46 | 26.24 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 13:00 | 43.74 | 49.2 | 49.2 | 0 | 5.47 | 0 | 37.64 | 0 | 0
2025-02-12 14:00 | 42.85 | 92.14 | 92.14 | 0 | 49.29 | 0 | 84.47 | 0 | 0
2025-02-12 15:00 | 43.65 | 100.86 | 100.86 | 0 | 57.21 | 0 | 138.82 | 0 | 0
2025-02-12 16:00 | 42.93 | 83.76 | 83.76 | 0 | 40.83 | 0 | 177.6 | 0 | 0
2025-02-12 17:00 | 42.78 | 5.42 | 5.42 | 0 | 0 | 37.36 | 138.28 | 0 | 0
2025-02-12 18:00 | 43.4 | 0 | 0 | 0 | 0 | 43.4 | 92.6 | 0 | 0
2025-02-12 19:00 | 41.78 | 0 | 0 | 0 | 0 | 41.78 | 48.62 | 0 | 0
2025-02-12 20:00 | 41.55 | 0 | 0 | 26.18 | 0 | 15.36 | 32.45 | 0 | 0
2025-02-12 21:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 22:00 | 40.59 | 0 | 0 | 40.59 | 0 | 0 | 32.45 | 0 | 0
2025-02-12 23:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 01:00 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 02:00 | 36.55 | 0 | 0 | 36.55 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 03:00 | 37.72 | 0 | 0 | 37.72 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 04:00 | 37.09 | 0 | 0 | 37.09 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 05:00 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 06:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 07:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 08:00 | 40.24 | 8.21 | 8.21 | 32.02 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 09:00 | 41 | 16.36 | 16.36 | 24.64 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 10:00 | 42.19 | 6.13 | 6.13 | 36.06 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 11:00 | 42.8 | 51.45 | 51.45 | 0 | 8.65 | 0 | 40.67 | 0 | 0
2025-02-13 12:00 | 43.87 | 68.26 | 68.26 | 0 | 24.39 | 0 | 63.84 | 0 | 0
2025-02-13 13:00 | 44.03 | 64.78 | 64.78 | 0 | 20.75 | 0 | 83.55 | 0 | 0
2025-02-13 14:00 | 45.75 | 59.18 | 59.18 | 0 | 13.43 | 0 | 96.31 | 0 | 0
2025-02-13 15:00 | 43.99 | 25.63 | 25.63 | 0 | 0 | 18.36 | 76.98 | 0 | 0
2025-02-13 16:00 | 45.26 | 54.09 | 54.09 | 0 | 8.82 | 0 | 85.36 | 0 | 0
2025-02-13 17:00 | 44.92 | 1.17 | 1.17 | 0 | 0 | 43.76 | 39.31 | 0 | 0
2025-02-13 18:00 | 43.19 | 0 | 0 | 36.67 | 0 | 6.51 | 32.45 | 0 | 0
2025-02-13 19:00 | 43.92 | 0 | 0 | 43.92 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 20:00 | 42.36 | 0 | 0 | 42.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 21:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 22:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 32.45 | 0 | 0
2025-02-13 23:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 01:00 | 37.87 | 0 | 0 | 37.87 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 02:00 | 38 | 0 | 0 | 38 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 03:00 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 04:00 | 36.84 | 0 | 0 | 36.84 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 05:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 06:00 | 38.72 | 0 | 0 | 38.72 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 07:00 | 39.36 | 0 | 0 | 39.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 08:00 | 40.31 | 13.51 | 13.51 | 26.8 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 09:00 | 40.78 | 1.76 | 1.76 | 39.02 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 10:00 | 41.43 | 45.83 | 45.83 | 0 | 4.41 | 0 | 36.64 | 0 | 0
2025-02-14 11:00 | 42.38 | 31.82 | 31.82 | 6.59 | 0 | 3.98 | 32.45 | 0 | 0
2025-02-14 12:00 | 42.79 | 34.43 | 34.43 | 8.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 13:00 | 44.33 | 34.05 | 34.05 | 10.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 14:00 | 44.56 | 22.54 | 22.54 | 22.02 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 15:00 | 44.51 | 53.08 | 53.08 | 0 | 8.57 | 0 | 40.59 | 0 | 0
2025-02-14 16:00 | 43.12 | 59.61 | 59.61 | 0 | 16.49 | 0 | 56.26 | 0 | 0
2025-02-14 17:00 | 43.59 | 0.97 | 0.97 | 20 | 0 | 22.62 | 32.45 | 0 | 0
2025-02-14 18:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 19:00 | 42.48 | 0 | 0 | 42.48 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 20:00 | 42.07 | 0 | 0 | 42.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 21:00 | 40.22 | 0 | 0 | 40.22 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 22:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 32.45 | 0 | 0
2025-02-14 23:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 | 38.47 | 0 | 0 | 38.47 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 01:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 02:00 | 38.11 | 0 | 0 | 38.11 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 03:00 | 37.07 | 0 | 0 | 37.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 04:00 | 37.05 | 0 | 0 | 37.05 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 05:00 | 37.56 | 0 | 0 | 37.56 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 06:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 07:00 | 39.06 | 0.02 | 0.02 | 39.03 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 08:00 | 39.83 | 23.32 | 23.32 | 16.51 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 09:00 | 41.76 | 68.23 | 68.23 | 0 | 26.46 | 0 | 57.59 | 0 | 0
2025-02-15 10:00 | 41.98 | 71.9 | 71.9 | 0 | 29.91 | 0 | 86.01 | 0 | 0
2025-02-15 11:00 | 44.14 | 53.27 | 53.27 | 0 | 9.13 | 0 | 94.68 | 0 | 0
2025-02-15 12:00 | 43.86 | 54.72 | 54.72 | 0 | 10.86 | 0 | 105 | 0 | 0
2025-02-15 13:00 | 45.34 | 31.92 | 31.92 | 0 | 0 | 13.42 | 90.87 | 0 | 0
2025-02-15 14:00 | 45.03 | 49 | 49 | 0 | 3.97 | 0 | 94.65 | 0 | 0
2025-02-15 15:00 | 45.47 | 73.4 | 73.4 | 0 | 27.94 | 0 | 121.18 | 0 | 0
2025-02-15 16:00 | 44.49 | 61.85 | 61.85 | 0 | 17.36 | 0 | 137.68 | 0 | 0
2025-02-15 17:00 | 44.02 | 0.75 | 0.75 | 0 | 0 | 43.27 | 92.13 | 0 | 0
2025-02-15 18:00 | 44.04 | 0 | 0 | 0 | 0 | 44.04 | 45.77 | 0 | 0
2025-02-15 19:00 | 43.48 | 0 | 0 | 30.83 | 0 | 12.66 | 32.45 | 0 | 0
2025-02-15 20:00 | 42.06 | 0 | 0 | 42.06 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 21:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 22:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 32.45 | 0 | 0
2025-02-15 23:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 01:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 02:00 | 37.96 | 0 | 0 | 37.96 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 03:00 | 37.26 | 0 | 0 | 37.26 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 04:00 | 36.27 | 0 | 0 | 36.27 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 05:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 06:00 | 38.32 | 0 | 0 | 38.32 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 07:00 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 08:00 | 39.5 | 1.21 | 1.21 | 38.3 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 09:00 | 41.14 | 2.78 | 2.78 | 38.37 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 10:00 | 43.34 | 6.08 | 6.08 | 37.26 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 11:00 | 43.82 | 5.75 | 5.75 | 38.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 12:00 | 44.85 | 9.5 | 9.5 | 35.35 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 13:00 | 45.4 | 51.23 | 51.23 | 0 | 5.83 | 0 | 37.99 | 0 | 0
2025-02-16 14:00 | 45.99 | 45.33 | 45.33 | 0 | 0 | 0.66 | 37.29 | 0 | 0
2025-02-16 15:00 | 46.38 | 36.31 | 36.31 | 5.48 | 0 | 4.6 | 32.45 | 0 | 0
2025-02-16 16:00 | 45.42 | 29.12 | 29.12 | 16.3 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 17:00 | 45.78 | 2.11 | 2.11 | 43.66 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 18:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 19:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 20:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 21:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 22:00 | 40.22 | 0 | 0 | 40.22 | 0 | 0 | 32.45 | 0 | 0
2025-02-16 23:00 | 38.92 | 0 | 0 | 38.92 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 01:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 02:00 | 36.9 | 0 | 0 | 36.9 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 03:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 04:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 05:00 | 38.19 | 0 | 0 | 38.19 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 06:00 | 37.85 | 0 | 0 | 37.85 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 07:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 08:00 | 39.88 | 0.09 | 0.09 | 39.79 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 09:00 | 41.87 | 1.72 | 1.72 | 40.15 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 10:00 | 42.4 | 3.04 | 3.04 | 39.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 11:00 | 43.1 | 4.06 | 4.06 | 39.04 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 12:00 | 44.3 | 4.48 | 4.48 | 39.82 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 13:00 | 43.64 | 47.2 | 47.2 | 0 | 3.56 | 0 | 35.83 | 0 | 0
2025-02-17 14:00 | 45.08 | 46.46 | 46.46 | 0 | 1.37 | 0 | 37.14 | 0 | 0
2025-02-17 15:00 | 46.24 | 35.17 | 35.17 | 6.62 | 0 | 4.45 | 32.45 | 0 | 0
2025-02-17 16:00 | 45.17 | 34.89 | 34.89 | 10.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 17:00 | 44.73 | 1.98 | 1.98 | 42.75 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 18:00 | 44.32 | 0 | 0 | 44.32 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 19:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 20:00 | 41.24 | 0 | 0 | 41.24 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 21:00 | 40.37 | 0 | 0 | 40.37 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 22:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 32.45 | 0 | 0
2025-02-17 23:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 01:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 02:00 | 36.54 | 0 | 0 | 36.54 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 03:00 | 36.74 | 0 | 0 | 36.74 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 04:00 | 36.13 | 0 | 0 | 36.13 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 05:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 06:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 07:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 08:00 | 40.9 | 5.26 | 5.26 | 35.64 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 09:00 | 42.06 | 7.33 | 7.33 | 34.73 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 10:00 | 42.51 | 17.9 | 17.9 | 24.61 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 11:00 | 42.61 | 28.85 | 28.85 | 13.75 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 12:00 | 44.94 | 23.36 | 23.36 | 21.58 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 13:00 | 45.65 | 18.86 | 18.86 | 26.8 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 14:00 | 46 | 14.62 | 14.62 | 31.38 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 15:00 | 46.5 | 9.8 | 9.8 | 36.7 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 16:00 | 45.27 | 2.02 | 2.02 | 43.25 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 17:00 | 46.38 | 0.05 | 0.05 | 46.33 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 18:00 | 44.15 | 0 | 0 | 44.15 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 19:00 | 44.05 | 0 | 0 | 44.05 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 20:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 21:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 22:00 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 32.45 | 0 | 0
2025-02-18 23:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 01:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 02:00 | 37.51 | 0 | 0 | 37.51 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 03:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 04:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 05:00 | 37.06 | 0 | 0 | 37.06 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 06:00 | 38.17 | 0 | 0 | 38.17 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 07:00 | 39.66 | 0.6 | 0.6 | 39.06 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 08:00 | 40.53 | 25.45 | 25.45 | 15.08 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 09:00 | 40.56 | 65.5 | 65.5 | 0 | 24.94 | 0 | 56.14 | 0 | 0
2025-02-19 10:00 | 42 | 71 | 71 | 0 | 28.99 | 0 | 83.69 | 0 | 0
2025-02-19 11:00 | 43.03 | 73.02 | 73.02 | 0 | 29.99 | 0 | 112.18 | 0 | 0
2025-02-19 12:00 | 43.96 | 68.64 | 68.64 | 0 | 24.68 | 0 | 135.63 | 0 | 0
2025-02-19 13:00 | 44.08 | 71.86 | 71.86 | 0 | 27.78 | 0 | 162.02 | 0 | 0
2025-02-19 14:00 | 44.85 | 68.45 | 68.45 | 0 | 23.6 | 0 | 184.44 | 0 | 0
2025-02-19 15:00 | 44.94 | 65.61 | 65.61 | 0 | 20.67 | 0 | 204.07 | 0 | 0
2025-02-19 16:00 | 45.55 | 32.82 | 32.82 | 0 | 0 | 12.74 | 190.67 | 0 | 0
2025-02-19 17:00 | 45.17 | 4.9 | 4.9 | 0 | 0 | 40.28 | 148.27 | 0 | 0
2025-02-19 18:00 | 44.07 | 0 | 0 | 0 | 0 | 44.07 | 101.88 | 0 | 0
2025-02-19 19:00 | 43.12 | 0 | 0 | 0 | 0 | 43.12 | 56.49 | 0 | 0
2025-02-19 20:00 | 42.43 | 0 | 0 | 19.59 | 0 | 22.84 | 32.45 | 0 | 0
2025-02-19 21:00 | 40.94 | 0 | 0 | 40.94 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 22:00 | 39.75 | 0 | 0 | 39.75 | 0 | 0 | 32.45 | 0 | 0
2025-02-19 23:00 | 38.91 | 0 | 0 | 38.91 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 01:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 02:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 03:00 | 37.86 | 0 | 0 | 37.86 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 04:00 | 36.83 | 0 | 0 | 36.83 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 05:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 06:00 | 38.54 | 0 | 0 | 38.54 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 07:00 | 39.65 | 1.23 | 1.23 | 38.43 | 0 | 0 | 32.45 | 0 | 0
2025-02-20 08:00 | 40.45 | 58.24 | 58.24 | 0 | 17.79 | 0 | 49.35 | 0 | 0
2025-02-20 09:00 | 40.8 | 77.64 | 77.64 | 0 | 36.84 | 0 | 84.35 | 0 | 0
2025-02-20 10:00 | 41.97 | 80 | 80 | 0 | 38.03 | 0 | 120.48 | 0 | 0
2025-02-20 11:00 | 43.63 | 70.88 | 70.88 | 0 | 27.25 | 0 | 146.37 | 0 | 0
2025-02-20 12:00 | 45.01 | 66.4 | 66.4 | 0 | 21.39 | 0 | 166.68 | 0 | 0
2025-02-20 13:00 | 44.07 | 70.19 | 70.19 | 0 | 26.12 | 0 | 191.49 | 0 | 0
2025-02-20 14:00 | 45.78 | 79.21 | 79.21 | 0 | 33.42 | 0 | 223.25 | 0 | 0
2025-02-20 15:00 | 46.35 | 70.73 | 70.73 | 0 | 24.38 | 0 | 246.41 | 0 | 0
2025-02-20 16:00 | 45.53 | 57.18 | 57.18 | 0 | 11.65 | 0 | 257.47 | 0 | 0
2025-02-20 17:00 | 45.45 | 7.96 | 7.96 | 0 | 0 | 37.49 | 218 | 0 | 0
2025-02-20 18:00 | 44.14 | 0 | 0 | 0 | 0 | 44.14 | 171.54 | 0 | 0
2025-02-20 19:00 | 43.56 | 0 | 0 | 0 | 0 | 43.56 | 125.69 | 0 | 0
2025-02-20 20:00 | 41.79 | 0 | 0 | 0 | 0 | 41.79 | 81.7 | 0 | 0
2025-02-20 21:00 | 40.35 | 0 | 0 | 0 | 0 | 40.35 | 39.23 | 0 | 0
2025-02-20 22:00 | 40.93 | 0 | 0 | 34.49 | 0 | 6.44 | 32.45 | 0 | 0
2025-02-20 23:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 01:00 | 37.39 | 0 | 0 | 37.39 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 02:00 | 36.98 | 0 | 0 | 36.98 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 03:00 | 37.46 | 0 | 0 | 37.46 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 04:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 06:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 07:00 | 39.75 | 0.33 | 0.33 | 39.43 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 08:00 | 40.74 | 19.2 | 19.2 | 21.53 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 09:00 | 42.54 | 49.15 | 49.15 | 0 | 6.61 | 0 | 38.73 | 0 | 0
2025-02-21 10:00 | 42.38 | 72.83 | 72.83 | 0 | 30.45 | 0 | 67.66 | 0 | 0
2025-02-21 11:00 | 43.99 | 83.86 | 83.86 | 0 | 39.87 | 0 | 105.54 | 0 | 0
2025-02-21 12:00 | 45.56 | 40.3 | 40.3 | 0 | 0 | 5.26 | 100 | 0 | 0
2025-02-21 13:00 | 46.38 | 23.61 | 23.61 | 0 | 0 | 22.77 | 76.03 | 0 | 0
2025-02-21 14:00 | 45.52 | 6.16 | 6.16 | 0 | 0 | 39.36 | 34.61 | 0 | 0
2025-02-21 15:00 | 46.24 | 4.11 | 4.11 | 40.09 | 0 | 2.05 | 32.45 | 0 | 0
2025-02-21 16:00 | 46.91 | 1.23 | 1.23 | 45.68 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 17:00 | 46 | 0.54 | 0.54 | 45.46 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 18:00 | 45.09 | 0 | 0 | 45.09 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 19:00 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 20:00 | 42.72 | 0 | 0 | 42.72 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 21:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 22:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 32.45 | 0 | 0
2025-02-21 23:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 01:00 | 37.8 | 0 | 0 | 37.8 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 02:00 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 04:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 05:00 | 38.3 | 0 | 0 | 38.3 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 06:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 07:00 | 39.78 | 1.94 | 1.94 | 37.84 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 08:00 | 40.32 | 62.8 | 62.8 | 0 | 22.48 | 0 | 53.81 | 0 | 0
2025-02-22 09:00 | 41.48 | 81.93 | 81.93 | 0 | 40.45 | 0 | 92.23 | 0 | 0
2025-02-22 10:00 | 42.42 | 64.32 | 64.32 | 0 | 21.9 | 0 | 113.03 | 0 | 0
2025-02-22 11:00 | 42.55 | 75.36 | 75.36 | 0 | 32.81 | 0 | 144.2 | 0 | 0
2025-02-22 12:00 | 43.5 | 78.18 | 78.18 | 0 | 34.68 | 0 | 177.15 | 0 | 0
2025-02-22 13:00 | 42.1 | 54.19 | 54.19 | 0 | 12.09 | 0 | 188.63 | 0 | 0
2025-02-22 14:00 | 44.27 | 41.51 | 41.51 | 0 | 0 | 2.76 | 185.73 | 0 | 0
2025-02-22 15:00 | 43.73 | 26.19 | 26.19 | 0 | 0 | 17.54 | 167.27 | 0 | 0
2025-02-22 16:00 | 44.01 | 5.74 | 5.74 | 0 | 0 | 38.28 | 126.98 | 0 | 0
2025-02-22 17:00 | 42.66 | 0.95 | 0.95 | 0 | 0 | 41.72 | 83.06 | 0 | 0
2025-02-22 18:00 | 42.52 | 0 | 0 | 0 | 0 | 42.52 | 38.31 | 0 | 0
2025-02-22 19:00 | 42.53 | 0 | 0 | 36.96 | 0 | 5.56 | 32.45 | 0 | 0
2025-02-22 20:00 | 41.83 | 0 | 0 | 41.83 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 21:00 | 41.24 | 0 | 0 | 41.24 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 22:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 32.45 | 0 | 0
2025-02-22 23:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 01:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 02:00 | 37.71 | 0 | 0 | 37.71 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 03:00 | 36.94 | 0 | 0 | 36.94 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 04:00 | 38.07 | 0 | 0 | 38.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 05:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 06:00 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 07:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 08:00 | 40.65 | 9 | 9 | 31.65 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 09:00 | 41.56 | 9.29 | 9.29 | 32.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 10:00 | 43.19 | 3.13 | 3.13 | 40.07 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 11:00 | 43.42 | 85.53 | 85.53 | 0 | 42.11 | 0 | 72.46 | 0 | 0
2025-02-23 12:00 | 43.92 | 65.48 | 65.48 | 0 | 21.55 | 0 | 92.93 | 0 | 0
2025-02-23 13:00 | 44.6 | 44.84 | 44.84 | 0 | 0.24 | 0 | 93.16 | 0 | 0
2025-02-23 14:00 | 45.85 | 42.71 | 42.71 | 0 | 0 | 3.14 | 89.85 | 0 | 0
2025-02-23 15:00 | 45.6 | 89.97 | 89.97 | 0 | 44.37 | 0 | 132 | 0 | 0
2025-02-23 16:00 | 45.02 | 81.84 | 81.84 | 0 | 36.82 | 0 | 166.98 | 0 | 0
2025-02-23 17:00 | 44.73 | 16.11 | 16.11 | 0 | 0 | 28.62 | 136.85 | 0 | 0
2025-02-23 18:00 | 43.49 | 0 | 0 | 0 | 0 | 43.49 | 91.07 | 0 | 0
2025-02-23 19:00 | 43.7 | 0 | 0 | 0 | 0 | 43.7 | 45.07 | 0 | 0
2025-02-23 20:00 | 41.73 | 0 | 0 | 29.74 | 0 | 11.99 | 32.45 | 0 | 0
2025-02-23 21:00 | 42 | 0 | 0 | 42 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 22:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 32.45 | 0 | 0
2025-02-23 23:00 | 40.87 | 0 | 0 | 40.87 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 01:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 02:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 03:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 04:00 | 37.53 | 0 | 0 | 37.53 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 05:00 | 38.4 | 0 | 0 | 38.4 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 06:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 07:00 | 39.9 | 6.12 | 6.12 | 33.78 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 08:00 | 40.34 | 77.32 | 77.32 | 0 | 36.98 | 0 | 67.58 | 0 | 0
2025-02-24 09:00 | 41.63 | 75.75 | 75.75 | 0 | 34.12 | 0 | 99.99 | 0 | 0
2025-02-24 10:00 | 41.84 | 85.13 | 85.13 | 0 | 43.29 | 0 | 141.12 | 0 | 0
2025-02-24 11:00 | 43.58 | 91.48 | 91.48 | 0 | 47.89 | 0 | 186.62 | 0 | 0
2025-02-24 12:00 | 44.48 | 85.72 | 85.72 | 0 | 41.24 | 0 | 225.79 | 0 | 0
2025-02-24 13:00 | 44.69 | 61.01 | 61.01 | 0 | 16.32 | 0 | 241.3 | 0 | 0
2025-02-24 14:00 | 44.34 | 59.19 | 59.19 | 0 | 14.85 | 0 | 255.41 | 0 | 0
2025-02-24 15:00 | 45.76 | 9.79 | 9.79 | 0 | 0 | 35.97 | 217.54 | 0 | 0
2025-02-24 16:00 | 45.33 | 1.1 | 1.1 | 0 | 0 | 44.23 | 170.98 | 0 | 0
2025-02-24 17:00 | 44.44 | 0 | 0 | 0 | 0 | 44.44 | 124.2 | 0 | 0
2025-02-24 18:00 | 44.11 | 0 | 0 | 0 | 0 | 44.11 | 77.76 | 0 | 0
2025-02-24 19:00 | 42.77 | 0 | 0 | 0 | 0 | 42.77 | 32.75 | 0 | 0
2025-02-24 20:00 | 42.13 | 0 | 0 | 41.85 | 0 | 0.28 | 32.45 | 0 | 0
2025-02-24 21:00 | 41.41 | 0 | 0 | 41.41 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 22:00 | 41.31 | 0 | 0 | 41.31 | 0 | 0 | 32.45 | 0 | 0
2025-02-24 23:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 | 39.33 | 0 | 0 | 39.33 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 01:00 | 38.09 | 0 | 0 | 38.09 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 02:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 03:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 04:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 05:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 06:00 | 38.22 | 0 | 0 | 38.22 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 07:00 | 39.14 | 2.1 | 2.1 | 37.04 | 0 | 0 | 32.45 | 0 | 0
2025-02-25 08:00 | 40.5 | 58.95 | 58.95 | 0 | 18.45 | 0 | 49.98 | 0 | 0
2025-02-25 09:00 | 41.11 | 79 | 79 | 0 | 37.89 | 0 | 85.98 | 0 | 0
2025-02-25 10:00 | 42.87 | 82.37 | 82.37 | 0 | 39.5 | 0 | 123.5 | 0 | 0
2025-02-25 11:00 | 43.28 | 72.09 | 72.09 | 0 | 28.82 | 0 | 150.88 | 0 | 0
2025-02-25 12:00 | 45.4 | 71.06 | 71.06 | 0 | 25.66 | 0 | 175.26 | 0 | 0
2025-02-25 13:00 | 43.87 | 77.21 | 77.21 | 0 | 33.34 | 0 | 206.92 | 0 | 0
2025-02-25 14:00 | 45.16 | 76.33 | 76.33 | 0 | 31.16 | 0 | 236.53 | 0 | 0
2025-02-25 15:00 | 44.61 | 64.23 | 64.23 | 0 | 19.62 | 0 | 255.17 | 0 | 0
2025-02-25 16:00 | 44.82 | 65.45 | 65.45 | 0 | 20.64 | 0 | 274.77 | 0 | 0
2025-02-25 17:00 | 44.81 | 11.01 | 11.01 | 0 | 0 | 33.8 | 239.19 | 0 | 0
2025-02-25 18:00 | 43.05 | 0 | 0 | 0 | 0 | 43.05 | 193.88 | 0 | 0
2025-02-25 19:00 | 43.63 | 0 | 0 | 0 | 0 | 43.63 | 147.95 | 0 | 0
2025-02-25 20:00 | 43.62 | 0 | 0 | 0 | 0 | 43.62 | 102.04 | 0 | 0
2025-02-25 21:00 | 41.5 | 0 | 0 | 0 | 0 | 41.5 | 58.35 | 0 | 0
2025-02-25 22:00 | 40.89 | 0 | 0 | 16.29 | 0 | 24.6 | 32.45 | 0 | 0
2025-02-25 23:00 | 40.34 | 0 | 0 | 40.34 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 01:00 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 02:00 | 36.88 | 0 | 0 | 36.88 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 03:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 04:00 | 37.97 | 0 | 0 | 37.97 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 05:00 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 06:00 | 39.17 | 0 | 0 | 39.17 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 07:00 | 39.67 | 2.84 | 2.84 | 36.82 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 08:00 | 40.68 | 24.75 | 24.75 | 15.92 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 09:00 | 42.29 | 78.92 | 78.92 | 0 | 36.64 | 0 | 67.25 | 0 | 0
2025-02-26 10:00 | 42.34 | 87.6 | 87.6 | 0 | 45.26 | 0 | 110.25 | 0 | 0
2025-02-26 11:00 | 44.48 | 78.02 | 78.02 | 0 | 33.54 | 0 | 142.11 | 0 | 0
2025-02-26 12:00 | 44.06 | 78.32 | 78.32 | 0 | 34.25 | 0 | 174.65 | 0 | 0
2025-02-26 13:00 | 45.04 | 63.27 | 63.27 | 0 | 18.23 | 0 | 191.97 | 0 | 0
2025-02-26 14:00 | 46.71 | 39.39 | 39.39 | 0 | 0 | 7.32 | 184.26 | 0 | 0
2025-02-26 15:00 | 46.44 | 19.29 | 19.29 | 0 | 0 | 27.15 | 155.68 | 0 | 0
2025-02-26 16:00 | 45.8 | 4.99 | 4.99 | 0 | 0 | 40.81 | 112.72 | 0 | 0
2025-02-26 17:00 | 44.9 | 0 | 0 | 0 | 0 | 44.9 | 65.45 | 0 | 0
2025-02-26 18:00 | 44.5 | 0 | 0 | 13.14 | 0 | 31.35 | 32.45 | 0 | 0
2025-02-26 19:00 | 44 | 0 | 0 | 44 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 20:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 21:00 | 41.94 | 0 | 0 | 41.94 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 22:00 | 40.93 | 0 | 0 | 40.93 | 0 | 0 | 32.45 | 0 | 0
2025-02-26 23:00 | 39.85 | 0 | 0 | 39.85 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 | 38.53 | 0 | 0 | 38.53 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 01:00 | 38.27 | 0 | 0 | 38.27 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 02:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 03:00 | 37.27 | 0 | 0 | 37.27 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 04:00 | 38 | 0 | 0 | 38 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 05:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 06:00 | 39.3 | 0 | 0 | 39.3 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 07:00 | 40.03 | 4.97 | 4.97 | 35.06 | 0 | 0 | 32.45 | 0 | 0
2025-02-27 08:00 | 42.16 | 77.21 | 77.21 | 0 | 35.05 | 0 | 65.75 | 0 | 0
2025-02-27 09:00 | 43.04 | 91.12 | 91.12 | 0 | 48.09 | 0 | 111.43 | 0 | 0
2025-02-27 10:00 | 43.57 | 89.2 | 89.2 | 0 | 45.63 | 0 | 154.78 | 0 | 0
2025-02-27 11:00 | 45.97 | 83.43 | 83.43 | 0 | 37.46 | 0 | 190.37 | 0 | 0
2025-02-27 12:00 | 46.51 | 76.75 | 76.75 | 0 | 30.24 | 0 | 219.1 | 0 | 0
2025-02-27 13:00 | 47.61 | 80.25 | 80.25 | 0 | 32.64 | 0 | 250.11 | 0 | 0
2025-02-27 14:00 | 48.7 | 87.23 | 87.23 | 0 | 38.53 | 0 | 286.71 | 0 | 0
2025-02-27 15:00 | 48.52 | 94.02 | 54.14 | 0 | 5.62 | 0 | 292.05 | 39.88 | 0
2025-02-27 16:00 | 48.99 | 85.24 | 48.99 | 0 | 0 | 0 | 292.05 | 36.25 | 0
2025-02-27 17:00 | 47.51 | 20.07 | 20.07 | 0 | 0 | 27.44 | 263.16 | 0 | 0
2025-02-27 18:00 | 46.59 | 0 | 0 | 0 | 0 | 46.59 | 214.13 | 0 | 0
2025-02-27 19:00 | 45.3 | 0 | 0 | 0 | 0 | 45.3 | 166.44 | 0 | 0
2025-02-27 20:00 | 43.94 | 0 | 0 | 0 | 0 | 43.94 | 120.18 | 0 | 0
2025-02-27 21:00 | 43.34 | 0 | 0 | 0 | 0 | 43.34 | 74.57 | 0 | 0
2025-02-27 22:00 | 41.74 | 0 | 0 | 1.73 | 0 | 40.01 | 32.45 | 0 | 0
2025-02-27 23:00 | 41.08 | 0 | 0 | 41.08 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 01:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 02:00 | 38.21 | 0 | 0 | 38.21 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 03:00 | 37.44 | 0 | 0 | 37.44 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 04:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 06:00 | 38.73 | 0 | 0 | 38.73 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 07:00 | 39.57 | 5.75 | 5.75 | 33.83 | 0 | 0 | 32.45 | 0 | 0
2025-02-28 08:00 | 40.96 | 86.96 | 86.96 | 0 | 46 | 0 | 76.15 | 0 | 0
2025-02-28 09:00 | 41.39 | 98.33 | 98.33 | 0 | 56.94 | 0 | 130.24 | 0 | 0
2025-02-28 10:00 | 43.34 | 94.42 | 94.42 | 0 | 51.08 | 0 | 178.77 | 0 | 0
2025-02-28 11:00 | 43.28 | 86.89 | 86.89 | 0 | 43.62 | 0 | 220.2 | 0 | 0
2025-02-28 12:00 | 45.81 | 81.98 | 81.98 | 0 | 36.17 | 0 | 254.56 | 0 | 0
2025-02-28 13:00 | 44.68 | 84.82 | 84.14 | 0 | 39.46 | 0 | 292.05 | 0.69 | 0
2025-02-28 14:00 | 45.24 | 91.46 | 45.24 | 0 | 0 | 0 | 292.05 | 46.22 | 0
2025-02-28 15:00 | 44.66 | 97.1 | 44.66 | 0 | 0 | 0 | 292.05 | 52.44 | 0
2025-02-28 16:00 | 46.06 | 91.6 | 46.06 | 0 | 0 | 0 | 292.05 | 45.55 | 0
2025-02-28 17:00 | 45.46 | 25.19 | 25.19 | 0 | 0 | 20.28 | 270.71 | 0 | 0
2025-02-28 18:00 | 44.56 | 0 | 0 | 0 | 0 | 44.56 | 223.81 | 0 | 0
2025-02-28 19:00 | 43.06 | 0 | 0 | 0 | 0 | 43.06 | 178.47 | 0 | 0
2025-02-28 20:00 | 43.03 | 0 | 0 | 0 | 0 | 43.03 | 133.18 | 0 | 0
2025-02-28 21:00 | 41.44 | 0 | 0 | 0 | 0 | 41.44 | 89.56 | 0 | 0
2025-02-28 22:00 | 41.77 | 0 | 0 | 0 | 0 | 41.77 | 45.59 | 0 | 0
2025-02-28 23:00 | 40.5 | 0 | 0 | 28.01 | 0 | 12.49 | 32.45 | 0 | 0
2025-03-01 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 01:00 | 37.47 | 0 | 0 | 37.47 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 03:00 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 04:00 | 38.86 | 0 | 0 | 38.86 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 05:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 06:00 | 38.62 | 0 | 0 | 38.62 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 07:00 | 40.53 | 4.6 | 4.6 | 35.93 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 08:00 | 42.05 | 60.17 | 60.17 | 0 | 18.12 | 0 | 49.66 | 0 | 0
2025-03-01 09:00 | 42.02 | 45.65 | 45.65 | 0 | 3.63 | 0 | 53.11 | 0 | 0
2025-03-01 10:00 | 44.2 | 70.62 | 70.62 | 0 | 26.42 | 0 | 78.22 | 0 | 0
2025-03-01 11:00 | 45.64 | 60.91 | 60.91 | 0 | 15.27 | 0 | 92.72 | 0 | 0
2025-03-01 12:00 | 46.51 | 69.53 | 69.53 | 0 | 23.02 | 0 | 114.59 | 0 | 0
2025-03-01 13:00 | 46.65 | 68.62 | 68.62 | 0 | 21.97 | 0 | 135.46 | 0 | 0
2025-03-01 14:00 | 47.99 | 71.77 | 71.77 | 0 | 23.78 | 0 | 158.05 | 0 | 0
2025-03-01 15:00 | 48.19 | 74.43 | 74.43 | 0 | 26.24 | 0 | 182.98 | 0 | 0
2025-03-01 16:00 | 48.08 | 78.28 | 78.28 | 0 | 30.19 | 0 | 211.66 | 0 | 0
2025-03-01 17:00 | 47.29 | 21.25 | 21.25 | 0 | 0 | 26.04 | 184.25 | 0 | 0
2025-03-01 18:00 | 46.44 | 0 | 0 | 0 | 0 | 46.44 | 135.36 | 0 | 0
2025-03-01 19:00 | 45.49 | 0 | 0 | 0 | 0 | 45.49 | 87.48 | 0 | 0
2025-03-01 20:00 | 44.42 | 0 | 0 | 0 | 0 | 44.42 | 40.72 | 0 | 0
2025-03-01 21:00 | 42.7 | 0 | 0 | 34.84 | 0 | 7.86 | 32.45 | 0 | 0
2025-03-01 22:00 | 41.34 | 0 | 0 | 41.34 | 0 | 0 | 32.45 | 0 | 0
2025-03-01 23:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 | 38.45 | 0 | 0 | 38.45 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 01:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 02:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 03:00 | 38.2 | 0 | 0 | 38.2 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 04:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 05:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 06:00 | 38.43 | 0 | 0 | 38.43 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 07:00 | 40.36 | 8.56 | 8.56 | 31.8 | 0 | 0 | 32.45 | 0 | 0
2025-03-02 08:00 | 41.08 | 81.17 | 81.17 | 0 | 40.08 | 0 | 70.53 | 0 | 0
2025-03-02 09:00 | 42.01 | 96.6 | 96.6 | 0 | 54.59 | 0 | 122.38 | 0 | 0
2025-03-02 10:00 | 42.45 | 93.91 | 93.91 | 0 | 51.46 | 0 | 171.27 | 0 | 0
2025-03-02 11:00 | 43.64 | 86.93 | 86.93 | 0 | 43.3 | 0 | 212.4 | 0 | 0
2025-03-02 12:00 | 44.24 | 82.38 | 82.38 | 0 | 38.14 | 0 | 248.63 | 0 | 0
2025-03-02 13:00 | 44.34 | 86.12 | 86.12 | 0 | 41.78 | 0 | 288.33 | 0 | 0
2025-03-02 14:00 | 44.15 | 92.51 | 48.07 | 0 | 3.92 | 0 | 292.05 | 44.43 | 0
2025-03-02 15:00 | 43.29 | 95.99 | 43.29 | 0 | 0 | 0 | 292.05 | 52.7 | 0
2025-03-02 16:00 | 44.67 | 85.82 | 44.67 | 0 | 0 | 0 | 292.05 | 41.16 | 0
2025-03-02 17:00 | 44.71 | 25.89 | 25.89 | 0 | 0 | 18.82 | 272.24 | 0 | 0
2025-03-02 18:00 | 44.1 | 0 | 0 | 0 | 0 | 44.1 | 225.82 | 0 | 0
2025-03-02 19:00 | 42.86 | 0 | 0 | 0 | 0 | 42.86 | 180.7 | 0 | 0
2025-03-02 20:00 | 43.02 | 0 | 0 | 0 | 0 | 43.02 | 135.42 | 0 | 0
2025-03-02 21:00 | 42.36 | 0 | 0 | 0 | 0 | 42.36 | 90.83 | 0 | 0
2025-03-02 22:00 | 41.87 | 0 | 0 | 0 | 0 | 41.87 | 46.76 | 0 | 0
2025-03-02 23:00 | 39.78 | 0 | 0 | 26.19 | 0 | 13.59 | 32.45 | 0 | 0
2025-03-03 | 39.44 | 0 | 0 | 39.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 01:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 02:00 | 38.44 | 0 | 0 | 38.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 03:00 | 37.7 | 0 | 0 | 37.7 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 04:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 06:00 | 39.6 | 0 | 0 | 39.6 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 07:00 | 40.57 | 0.13 | 0.13 | 40.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 08:00 | 41.37 | 19.83 | 19.83 | 21.55 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 09:00 | 43.34 | 2.59 | 2.59 | 40.74 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 10:00 | 43.23 | 33.59 | 33.59 | 9.64 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 11:00 | 44.38 | 62.55 | 62.55 | 0 | 18.17 | 0 | 49.71 | 0 | 0
2025-03-03 12:00 | 45.51 | 44.69 | 44.69 | 0 | 0 | 0.83 | 48.84 | 0 | 0
2025-03-03 13:00 | 46.58 | 25.12 | 25.12 | 5.9 | 0 | 15.57 | 32.45 | 0 | 0
2025-03-03 14:00 | 45.79 | 37.92 | 37.92 | 7.87 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 15:00 | 46.02 | 24.56 | 24.56 | 21.45 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 16:00 | 45.52 | 54.9 | 54.9 | 0 | 9.38 | 0 | 41.36 | 0 | 0
2025-03-03 17:00 | 46.16 | 15.77 | 15.77 | 21.93 | 0 | 8.47 | 32.45 | 0 | 0
2025-03-03 18:00 | 44.95 | 0 | 0 | 44.95 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 19:00 | 44.48 | 0 | 0 | 44.48 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 20:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 21:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 22:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 32.45 | 0 | 0
2025-03-03 23:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 01:00 | 39.18 | 0 | 0 | 39.18 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 02:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 03:00 | 38.25 | 0 | 0 | 38.25 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 04:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 06:00 | 38.97 | 0 | 0 | 38.97 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 07:00 | 40.95 | 7.99 | 7.99 | 32.96 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 08:00 | 41.19 | 39.13 | 39.13 | 2.07 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 09:00 | 43.65 | 85.24 | 85.24 | 0 | 41.59 | 0 | 71.96 | 0 | 0
2025-03-04 10:00 | 44.66 | 40.85 | 40.85 | 0 | 0 | 3.82 | 67.94 | 0 | 0
2025-03-04 11:00 | 45.44 | 50.67 | 50.67 | 0 | 5.24 | 0 | 72.92 | 0 | 0
2025-03-04 12:00 | 46.35 | 53.82 | 53.82 | 0 | 7.46 | 0 | 80.01 | 0 | 0
2025-03-04 13:00 | 46.93 | 61.45 | 61.45 | 0 | 14.52 | 0 | 93.8 | 0 | 0
2025-03-04 14:00 | 47.85 | 97.16 | 97.16 | 0 | 49.3 | 0 | 140.64 | 0 | 0
2025-03-04 15:00 | 47.49 | 76.36 | 76.36 | 0 | 28.87 | 0 | 168.06 | 0 | 0
2025-03-04 16:00 | 47.63 | 47.32 | 47.32 | 0 | 0 | 0.31 | 167.73 | 0 | 0
2025-03-04 17:00 | 47.47 | 10.34 | 10.34 | 0 | 0 | 37.13 | 128.65 | 0 | 0
2025-03-04 18:00 | 45.99 | 0 | 0 | 0 | 0 | 45.99 | 80.23 | 0 | 0
2025-03-04 19:00 | 44.98 | 0 | 0 | 0 | 0 | 44.98 | 32.88 | 0 | 0
2025-03-04 20:00 | 43.56 | 0 | 0 | 43.15 | 0 | 0.41 | 32.45 | 0 | 0
2025-03-04 21:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 22:00 | 40.82 | 0 | 0 | 40.82 | 0 | 0 | 32.45 | 0 | 0
2025-03-04 23:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 01:00 | 39.75 | 0 | 0 | 39.75 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 03:00 | 38.78 | 0 | 0 | 38.78 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 04:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 05:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 06:00 | 39.84 | 0 | 0 | 39.84 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 07:00 | 39.77 | 9.62 | 9.62 | 30.16 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 08:00 | 42.09 | 97.11 | 97.11 | 0 | 55.02 | 0 | 84.72 | 0 | 0
2025-03-05 09:00 | 42.72 | 100.21 | 100.21 | 0 | 57.48 | 0 | 139.33 | 0 | 0
2025-03-05 10:00 | 44.69 | 87.68 | 87.68 | 0 | 42.99 | 0 | 180.17 | 0 | 0
2025-03-05 11:00 | 45.08 | 71.89 | 71.89 | 0 | 26.81 | 0 | 205.64 | 0 | 0
2025-03-05 12:00 | 47.24 | 54.23 | 54.23 | 0 | 6.99 | 0 | 212.28 | 0 | 0
2025-03-05 13:00 | 48.35 | 45.76 | 45.76 | 0 | 0 | 2.59 | 209.56 | 0 | 0
2025-03-05 14:00 | 48 | 42.47 | 42.47 | 0 | 0 | 5.53 | 203.74 | 0 | 0
2025-03-05 15:00 | 48.01 | 38.32 | 38.32 | 0 | 0 | 9.69 | 193.54 | 0 | 0
2025-03-05 16:00 | 47.31 | 25.29 | 25.29 | 0 | 0 | 22.03 | 170.35 | 0 | 0
2025-03-05 17:00 | 47.71 | 3.62 | 3.62 | 0 | 0 | 44.09 | 123.95 | 0 | 0
2025-03-05 18:00 | 46.68 | 0 | 0 | 0 | 0 | 46.68 | 74.81 | 0 | 0
2025-03-05 19:00 | 45.08 | 0 | 0 | 4.84 | 0 | 40.24 | 32.45 | 0 | 0
2025-03-05 20:00 | 44.82 | 0 | 0 | 44.82 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 21:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 22:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 32.45 | 0 | 0
2025-03-05 23:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 | 40.43 | 0 | 0 | 40.43 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 01:00 | 39.43 | 0 | 0 | 39.43 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 02:00 | 38.59 | 0 | 0 | 38.59 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 03:00 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 04:00 | 38.08 | 0 | 0 | 38.08 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 06:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 07:00 | 40.67 | 12.98 | 12.98 | 27.69 | 0 | 0 | 32.45 | 0 | 0
2025-03-06 08:00 | 42.33 | 74.38 | 74.38 | 0 | 32.04 | 0 | 62.89 | 0 | 0
2025-03-06 09:00 | 43.07 | 88.67 | 88.67 | 0 | 45.61 | 0 | 106.22 | 0 | 0
2025-03-06 10:00 | 45.09 | 86.36 | 86.36 | 0 | 41.27 | 0 | 145.42 | 0 | 0
2025-03-06 11:00 | 46.43 | 84.74 | 84.74 | 0 | 38.3 | 0 | 181.81 | 0 | 0
2025-03-06 12:00 | 45.86 | 81.76 | 81.76 | 0 | 35.9 | 0 | 215.91 | 0 | 0
2025-03-06 13:00 | 48.82 | 86.9 | 86.9 | 0 | 38.08 | 0 | 252.08 | 0 | 0
2025-03-06 14:00 | 47.29 | 95.31 | 89.36 | 0 | 42.07 | 0 | 292.05 | 5.95 | 0
2025-03-06 15:00 | 48.7 | 94.48 | 48.7 | 0 | 0 | 0 | 292.05 | 45.78 | 0
2025-03-06 16:00 | 49.32 | 83.23 | 49.32 | 0 | 0 | 0 | 292.05 | 33.91 | 0
2025-03-06 17:00 | 48.07 | 31.2 | 31.2 | 0 | 0 | 16.87 | 274.29 | 0 | 0
2025-03-06 18:00 | 46.59 | 0 | 0 | 0 | 0 | 46.59 | 225.25 | 0 | 0
2025-03-06 19:00 | 45.61 | 0 | 0 | 0 | 0 | 45.61 | 177.24 | 0 | 0
2025-03-06 20:00 | 45.35 | 0 | 0 | 0 | 0 | 45.35 | 129.51 | 0 | 0
2025-03-06 21:00 | 42.5 | 0 | 0 | 0 | 0 | 42.5 | 84.77 | 0 | 0
2025-03-06 22:00 | 42.68 | 0 | 0 | 0 | 0 | 42.68 | 39.85 | 0 | 0
2025-03-06 23:00 | 40.88 | 0 | 0 | 33.85 | 0 | 7.03 | 32.45 | 0 | 0
2025-03-07 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 32.45 | 0 | 0
2025-03-07 01:00 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 32.45 | 0 | 0
2025-03-07 02:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 32.45 | 0 | 0
2025-03-07 03:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 32.45 | 0 | 0
2025-03-07 04:00 | 39.11 | 0 | 0 | 39.11 | 0 | 0 | 32.45 | 0 | 0
2025-03-07 05:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 32.45 | 0 | 0
2025-03-07 06:00 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 32.45 | 0 | 0
2025-03-07 07:00 | 40.6 | 19.12 | 19.12 | 21.48 | 0 | 0 | 32.45 | 0 | 0
2025-03-07 08:00 | 42.92 | 85.22 | 85.22 | 0 | 42.31 | 0 | 72.64 | 0 | 0
2025-03-07 09:00 | 42.97 | 92.76 | 92.76 | 0 | 49.79 | 0 | 119.94 | 0 | 0
2025-03-07 10:00 | 45.86 | 92.32 | 92.32 | 0 | 46.46 | 0 | 164.08 | 0 | 0
2025-03-07 11:00 | 46.41 | 85.91 | 85.91 | 0 | 39.51 | 0 | 201.61 | 0 | 0
2025-03-07 12:00 | 47.04 | 77.75 | 77.75 | 0 | 30.71 | 0 | 230.78 | 0 | 0
2025-03-07 13:00 | 48.23 | 79.15 | 79.15 | 0 | 30.92 | 0 | 260.15 | 0 | 0
2025-03-07 14:00 | 48.77 | 80 | 80 | 0 | 31.23 | 0 | 289.82 | 0 | 0
2025-03-07 15:00 | 48.74 | 80.55 | 51.08 | 0 | 2.34 | 0 | 292.05 | 29.47 | 0
2025-03-07 16:00 | 49.21 | 82.72 | 49.21 | 0 | 0 | 0 | 292.05 | 33.51 | 0
2025-03-07 17:00 | 47.95 | 32.93 | 32.93 | 0 | 0 | 15.02 | 276.24 | 0 | 0
2025-03-07 18:00 | 46.53 | 0 | 0 | 0 | 0 | 46.53 | 227.25 | 0 | 0
2025-03-07 19:00 | 46.23 | 0 | 0 | 0 | 0 | 46.23 | 178.59 | 0 | 0
2025-03-07 20:00 | 44.16 | 0 | 0 | 0 | 0 | 44.16 | 132.1 | 0 | 0
2025-03-07 21:00 | 43.27 | 0 | 0 | 0 | 0 | 43.27 | 86.56 | 0 | 0
2025-03-07 22:00 | 41.81 | 0 | 0 | 0 | 0 | 41.81 | 42.54 | 0 | 0
2025-03-07 23:00 | 40.59 | 0 | 0 | 31 | 0 | 9.59 | 32.45 | 0 | 0
2025-03-08 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 32.45 | 0 | 0
2025-03-08 01:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 32.45 | 0 | 0
2025-03-08 02:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 32.45 | 0 | 0
2025-03-08 03:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 32.45 | 0 | 0
2025-03-08 04:00 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 32.45 | 0 | 0
2025-03-08 05:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 32.45 | 0 | 0
2025-03-08 06:00 | 39.55 | 0 | 0 | 39.55 | 0 | 0 | 32.45 | 0 | 0
2025-03-08 07:00 | 41.48 | 20.12 | 20.12 | 21.36 | 0 | 0 | 32.45 | 0 | 0
2025-03-08 08:00 | 41.53 | 75.45 | 75.45 | 0 | 33.92 | 0 | 64.67 | 0 | 0
2025-03-08 09:00 | 43.16 | 89.27 | 89.27 | 0 | 46.11 | 0 | 108.48 | 0 | 0
2025-03-08 10:00 | 44.16 | 87.98 | 87.98 | 0 | 43.82 | 0 | 150.11 | 0 | 0
2025-03-08 11:00 | 45.59 | 83.92 | 83.92 | 0 | 38.33 | 0 | 186.52 | 0 | 0
2025-03-08 12:00 | 46.08 | 82.02 | 82.02 | 0 | 35.94 | 0 | 220.67 | 0 | 0
2025-03-08 13:00 | 46.94 | 83.58 | 83.58 | 0 | 36.64 | 0 | 255.48 | 0 | 0
2025-03-08 14:00 | 47.38 | 84.11 | 84.11 | 0 | 36.74 | 0 | 290.37 | 0 | 0
2025-03-08 15:00 | 47.27 | 89.17 | 49.03 | 0 | 1.76 | 0 | 292.05 | 40.13 | 0
2025-03-08 16:00 | 47.74 | 86.84 | 47.74 | 0 | 0 | 0 | 292.05 | 39.1 | 0
2025-03-08 17:00 | 47.19 | 34.87 | 34.87 | 0 | 0 | 12.33 | 279.07 | 0 | 0
2025-03-08 18:00 | 46.36 | 0 | 0 | 0 | 0 | 46.36 | 230.28 | 0 | 0
2025-03-08 19:00 | 45.29 | 0 | 0 | 0 | 0 | 45.29 | 182.6 | 0 | 0
2025-03-08 20:00 | 44.85 | 0 | 0 | 0 | 0 | 44.85 | 135.39 | 0 | 0
2025-03-08 21:00 | 43.19 | 0 | 0 | 0 | 0 | 43.19 | 89.93 | 0 | 0
2025-03-08 22:00 | 41.98 | 0 | 0 | 0 | 0 | 41.98 | 45.74 | 0 | 0
2025-03-08 23:00 | 41.08 | 0 | 0 | 28.46 | 0 | 12.62 | 32.45 | 0 | 0
2025-03-09 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 32.45 | 0 | 0
2025-03-09 01:00 | 38.74 | 0 | 0 | 38.74 | 0 | 0 | 32.45 | 0 | 0
2025-03-09 02:00 | 39.31 | 0 | 0 | 39.31 | 0 | 0 | 32.45 | 0 | 0
2025-03-09 03:00 | 37.82 | 0 | 0 | 37.82 | 0 | 0 | 32.45 | 0 | 0
2025-03-09 04:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 32.45 | 0 | 0
2025-03-09 05:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 32.45 | 0 | 0
2025-03-09 06:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 32.45 | 0 | 0
2025-03-09 07:00 | 41.22 | 22.18 | 22.18 | 19.03 | 0 | 0 | 32.45 | 0 | 0
2025-03-09 08:00 | 41.96 | 80.47 | 80.47 | 0 | 38.51 | 0 | 69.03 | 0 | 0
2025-03-09 09:00 | 43.42 | 94.87 | 94.87 | 0 | 51.45 | 0 | 117.91 | 0 | 0
2025-03-09 10:00 | 44.42 | 91.81 | 91.81 | 0 | 47.39 | 0 | 162.93 | 0 | 0
2025-03-09 11:00 | 45.18 | 86.48 | 86.48 | 0 | 41.29 | 0 | 202.16 | 0 | 0
2025-03-09 12:00 | 46.3 | 83.19 | 83.19 | 0 | 36.89 | 0 | 237.2 | 0 | 0
2025-03-09 13:00 | 47.2 | 84.31 | 84.31 | 0 | 37.1 | 0 | 272.45 | 0 | 0
2025-03-09 14:00 | 47.13 | 85.11 | 67.76 | 0 | 20.63 | 0 | 292.05 | 17.35 | 0
2025-03-09 15:00 | 47.24 | 86.96 | 47.24 | 0 | 0 | 0 | 292.05 | 39.72 | 0
2025-03-09 16:00 | 46.83 | 72.75 | 46.83 | 0 | 0 | 0 | 292.05 | 25.92 | 0
2025-03-09 17:00 | 47.3 | 34.04 | 34.04 | 0 | 0 | 13.25 | 278.1 | 0 | 0
2025-03-09 18:00 | 46.72 | 0 | 0 | 0 | 0 | 46.72 | 228.92 | 0 | 0
2025-03-09 19:00 | 45.69 | 0 | 0 | 0 | 0 | 45.69 | 180.82 | 0 | 0
2025-03-09 20:00 | 45.02 | 0 | 0 | 0 | 0 | 45.02 | 133.43 | 0 | 0
2025-03-09 21:00 | 43.45 | 0 | 0 | 0 | 0 | 43.45 | 87.69 | 0 | 0
2025-03-09 22:00 | 42.44 | 0 | 0 | 0 | 0 | 42.44 | 43.02 | 0 | 0
2025-03-09 23:00 | 41.29 | 0 | 0 | 31.25 | 0 | 10.04 | 32.45 | 0 | 0
2025-03-10 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 01:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 02:00 | 40.13 | 0 | 0 | 40.13 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 03:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 04:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 05:00 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 06:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 07:00 | 40.7 | 23.9 | 23.9 | 16.8 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 08:00 | 43.26 | 75.89 | 75.89 | 0 | 32.63 | 0 | 63.45 | 0 | 0
2025-03-10 09:00 | 44.1 | 81.14 | 81.14 | 0 | 37.05 | 0 | 98.64 | 0 | 0
2025-03-10 10:00 | 45.08 | 96.37 | 96.37 | 0 | 51.29 | 0 | 147.37 | 0 | 0
2025-03-10 11:00 | 47.67 | 86.26 | 86.26 | 0 | 38.59 | 0 | 184.03 | 0 | 0
2025-03-10 12:00 | 48.66 | 76.34 | 76.34 | 0 | 27.68 | 0 | 210.32 | 0 | 0
2025-03-10 13:00 | 48.71 | 79.31 | 79.31 | 0 | 30.61 | 0 | 239.4 | 0 | 0
2025-03-10 14:00 | 50.86 | 77.72 | 77.72 | 0 | 26.85 | 0 | 264.91 | 0 | 0
2025-03-10 15:00 | 50.52 | 63.51 | 63.51 | 0 | 12.99 | 0 | 277.25 | 0 | 0
2025-03-10 16:00 | 49.97 | 33.47 | 33.47 | 0 | 0 | 16.5 | 259.88 | 0 | 0
2025-03-10 17:00 | 50.13 | 5.56 | 5.56 | 0 | 0 | 44.58 | 212.96 | 0 | 0
2025-03-10 18:00 | 48.42 | 0 | 0 | 0 | 0 | 48.42 | 161.99 | 0 | 0
2025-03-10 19:00 | 47.06 | 0 | 0 | 0 | 0 | 47.06 | 112.45 | 0 | 0
2025-03-10 20:00 | 45.31 | 0 | 0 | 0 | 0 | 45.31 | 64.76 | 0 | 0
2025-03-10 21:00 | 44.43 | 0 | 0 | 13.74 | 0 | 30.7 | 32.45 | 0 | 0
2025-03-10 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 32.45 | 0 | 0
2025-03-10 23:00 | 41.41 | 0 | 0 | 41.41 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 | 40 | 0 | 0 | 40 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 01:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 02:00 | 39.08 | 0 | 0 | 39.08 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 03:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 04:00 | 38.38 | 0 | 0 | 38.38 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 05:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 06:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 07:00 | 41.51 | 8.45 | 8.45 | 33.07 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 08:00 | 42.35 | 16.52 | 16.52 | 25.83 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 09:00 | 44.49 | 46.23 | 46.23 | 0 | 1.74 | 0 | 34.1 | 0 | 0
2025-03-11 10:00 | 44.83 | 70.45 | 70.45 | 0 | 25.62 | 0 | 58.44 | 0 | 0
2025-03-11 11:00 | 46.55 | 69.4 | 69.4 | 0 | 22.85 | 0 | 80.16 | 0 | 0
2025-03-11 12:00 | 46.99 | 79.68 | 79.68 | 0 | 32.69 | 0 | 111.21 | 0 | 0
2025-03-11 13:00 | 47.99 | 83.11 | 83.11 | 0 | 35.12 | 0 | 144.57 | 0 | 0
2025-03-11 14:00 | 48.77 | 87.94 | 87.94 | 0 | 39.18 | 0 | 181.79 | 0 | 0
2025-03-11 15:00 | 48.33 | 78.28 | 78.28 | 0 | 29.95 | 0 | 210.24 | 0 | 0
2025-03-11 16:00 | 48.9 | 63.85 | 63.85 | 0 | 14.95 | 0 | 224.45 | 0 | 0
2025-03-11 17:00 | 47.44 | 34.13 | 34.13 | 0 | 0 | 13.31 | 210.44 | 0 | 0
2025-03-11 18:00 | 47.34 | 0 | 0 | 0 | 0 | 47.34 | 160.61 | 0 | 0
2025-03-11 19:00 | 46.68 | 0 | 0 | 0 | 0 | 46.68 | 111.47 | 0 | 0
2025-03-11 20:00 | 45.4 | 0 | 0 | 0 | 0 | 45.4 | 63.68 | 0 | 0
2025-03-11 21:00 | 44.79 | 0 | 0 | 15.13 | 0 | 29.66 | 32.45 | 0 | 0
2025-03-11 22:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 32.45 | 0 | 0
2025-03-11 23:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 01:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 02:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 03:00 | 39.09 | 0 | 0 | 39.09 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 04:00 | 38.65 | 0 | 0 | 38.65 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 05:00 | 40.09 | 0 | 0 | 40.09 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 06:00 | 39.85 | 0 | 0 | 39.85 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 07:00 | 42 | 18.83 | 18.83 | 23.16 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 08:00 | 43.89 | 65.3 | 65.3 | 0 | 21.41 | 0 | 52.79 | 0 | 0
2025-03-12 09:00 | 43.69 | 85.82 | 85.82 | 0 | 42.14 | 0 | 92.82 | 0 | 0
2025-03-12 10:00 | 44.76 | 59.03 | 59.03 | 0 | 14.26 | 0 | 106.37 | 0 | 0
2025-03-12 11:00 | 45.06 | 70 | 70 | 0 | 24.94 | 0 | 130.06 | 0 | 0
2025-03-12 12:00 | 45.06 | 60.39 | 60.39 | 0 | 15.33 | 0 | 144.63 | 0 | 0
2025-03-12 13:00 | 46.13 | 74.88 | 74.88 | 0 | 28.75 | 0 | 171.94 | 0 | 0
2025-03-12 14:00 | 46.17 | 68.25 | 68.25 | 0 | 22.08 | 0 | 192.92 | 0 | 0
2025-03-12 15:00 | 46.09 | 61.31 | 61.31 | 0 | 15.23 | 0 | 207.38 | 0 | 0
2025-03-12 16:00 | 47.58 | 66.9 | 66.9 | 0 | 19.32 | 0 | 225.74 | 0 | 0
2025-03-12 17:00 | 46.57 | 36.2 | 36.2 | 0 | 0 | 10.38 | 214.81 | 0 | 0
2025-03-12 18:00 | 46.15 | 0 | 0 | 0 | 0 | 46.15 | 166.23 | 0 | 0
2025-03-12 19:00 | 45.15 | 0 | 0 | 0 | 0 | 45.15 | 118.71 | 0 | 0
2025-03-12 20:00 | 44.38 | 0 | 0 | 0 | 0 | 44.38 | 71.99 | 0 | 0
2025-03-12 21:00 | 43.99 | 0 | 0 | 6.42 | 0 | 37.56 | 32.45 | 0 | 0
2025-03-12 22:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-12 23:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 01:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 02:00 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 03:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 04:00 | 39.17 | 0 | 0 | 39.17 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 05:00 | 39.84 | 0 | 0 | 39.84 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 06:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 07:00 | 41.54 | 1.76 | 1.76 | 39.78 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 08:00 | 42.66 | 11.73 | 11.73 | 30.94 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 09:00 | 42.65 | 17.85 | 17.85 | 24.8 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 10:00 | 44.29 | 33.1 | 33.1 | 11.19 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 11:00 | 45.83 | 46.65 | 46.65 | 0 | 0.82 | 0 | 33.23 | 0 | 0
2025-03-13 12:00 | 46.54 | 62.44 | 62.44 | 0 | 15.91 | 0 | 48.34 | 0 | 0
2025-03-13 13:00 | 46.28 | 70.32 | 70.32 | 0 | 24.04 | 0 | 71.17 | 0 | 0
2025-03-13 14:00 | 47.25 | 69.23 | 69.23 | 0 | 21.98 | 0 | 92.05 | 0 | 0
2025-03-13 15:00 | 47.78 | 86.84 | 86.84 | 0 | 39.06 | 0 | 129.16 | 0 | 0
2025-03-13 16:00 | 47.56 | 103.26 | 103.26 | 0 | 55.7 | 0 | 182.07 | 0 | 0
2025-03-13 17:00 | 46.81 | 38.09 | 38.09 | 0 | 0 | 8.72 | 172.89 | 0 | 0
2025-03-13 18:00 | 46.11 | 0 | 0 | 0 | 0 | 46.11 | 124.36 | 0 | 0
2025-03-13 19:00 | 45.32 | 0 | 0 | 0 | 0 | 45.32 | 76.66 | 0 | 0
2025-03-13 20:00 | 44.98 | 0 | 0 | 2.98 | 0 | 42 | 32.45 | 0 | 0
2025-03-13 21:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 22:00 | 42.95 | 0 | 0 | 42.95 | 0 | 0 | 32.45 | 0 | 0
2025-03-13 23:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 | 41.12 | 0 | 0 | 41.12 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 01:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 02:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 03:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 04:00 | 39 | 0 | 0 | 39 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 05:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 06:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 07:00 | 41.84 | 44.95 | 44.95 | 0 | 3.1 | 0 | 35.4 | 0 | 0
2025-03-14 08:00 | 41.98 | 103.66 | 103.66 | 0 | 61.68 | 0 | 94 | 0 | 0
2025-03-14 09:00 | 43.63 | 75.11 | 75.11 | 0 | 31.49 | 0 | 123.91 | 0 | 0
2025-03-14 10:00 | 45.46 | 59.69 | 59.69 | 0 | 14.23 | 0 | 137.43 | 0 | 0
2025-03-14 11:00 | 45.9 | 78.51 | 78.51 | 0 | 32.61 | 0 | 168.41 | 0 | 0
2025-03-14 12:00 | 46.57 | 102.98 | 102.98 | 0 | 56.4 | 0 | 221.99 | 0 | 0
2025-03-14 13:00 | 48.11 | 92.12 | 92.12 | 0 | 44.01 | 0 | 263.8 | 0 | 0
2025-03-14 14:00 | 47.24 | 48.56 | 48.56 | 0 | 1.32 | 0 | 265.06 | 0 | 0
2025-03-14 15:00 | 47.48 | 3.65 | 3.65 | 0 | 0 | 43.83 | 218.92 | 0 | 0
2025-03-14 16:00 | 47.87 | 20.84 | 20.84 | 0 | 0 | 27.03 | 190.47 | 0 | 0
2025-03-14 17:00 | 47.6 | 2.91 | 2.91 | 0 | 0 | 44.69 | 143.42 | 0 | 0
2025-03-14 18:00 | 47.08 | 0 | 0 | 0 | 0 | 47.08 | 93.87 | 0 | 0
2025-03-14 19:00 | 46.5 | 0 | 0 | 0 | 0 | 46.5 | 44.93 | 0 | 0
2025-03-14 20:00 | 45.17 | 0 | 0 | 33.32 | 0 | 11.85 | 32.45 | 0 | 0
2025-03-14 21:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 22:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 32.45 | 0 | 0
2025-03-14 23:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 | 40.94 | 0 | 0 | 40.94 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 01:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 02:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 03:00 | 39.6 | 0 | 0 | 39.6 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 04:00 | 39.53 | 0 | 0 | 39.53 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 05:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 06:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 07:00 | 42 | 3.34 | 3.34 | 38.65 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 08:00 | 43.45 | 8.38 | 8.38 | 35.06 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 09:00 | 45.92 | 12.94 | 12.94 | 32.98 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 10:00 | 46.05 | 12.96 | 12.96 | 33.1 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 11:00 | 47.95 | 6.48 | 6.48 | 41.47 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 12:00 | 49.52 | 24.1 | 24.1 | 25.42 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 13:00 | 50 | 32.89 | 32.89 | 17.11 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 14:00 | 51.73 | 42.88 | 42.88 | 8.86 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 15:00 | 50.59 | 38.92 | 38.92 | 11.66 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 16:00 | 50.73 | 56.03 | 56.03 | 0 | 5.31 | 0 | 37.49 | 0 | 0
2025-03-15 17:00 | 49.55 | 35.18 | 35.18 | 9.59 | 0 | 4.79 | 32.45 | 0 | 0
2025-03-15 18:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 19:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 20:00 | 46.74 | 0 | 0 | 46.74 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 21:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 22:00 | 43.98 | 0 | 0 | 43.98 | 0 | 0 | 32.45 | 0 | 0
2025-03-15 23:00 | 41.96 | 0 | 0 | 41.96 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 | 40.83 | 0 | 0 | 40.83 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 01:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 02:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 04:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 05:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 06:00 | 41.46 | 0 | 0 | 41.46 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 07:00 | 41.92 | 14.95 | 14.95 | 26.97 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 08:00 | 43.48 | 21.45 | 21.45 | 22.03 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 09:00 | 44.79 | 32.26 | 32.26 | 12.53 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 10:00 | 46.6 | 31.93 | 31.93 | 14.67 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 11:00 | 47.14 | 38.63 | 38.63 | 8.52 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 12:00 | 48.18 | 31.11 | 31.11 | 17.07 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 13:00 | 49.71 | 19.71 | 19.71 | 30.01 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 14:00 | 50.46 | 13.27 | 13.27 | 37.19 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 15:00 | 50.52 | 15.26 | 15.26 | 35.26 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 16:00 | 49.76 | 10.85 | 10.85 | 38.9 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 17:00 | 49.94 | 4.07 | 4.07 | 45.87 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 18:00 | 48.35 | 0 | 0 | 48.35 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 19:00 | 47.31 | 0 | 0 | 47.31 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 20:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 21:00 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 22:00 | 43.73 | 0 | 0 | 43.73 | 0 | 0 | 32.45 | 0 | 0
2025-03-16 23:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 | 41.76 | 0 | 0 | 41.76 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 01:00 | 41.66 | 0 | 0 | 41.66 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 02:00 | 38.86 | 0 | 0 | 38.86 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 03:00 | 39.16 | 0 | 0 | 39.16 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 04:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 05:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 06:00 | 40.6 | 0 | 0 | 40.6 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 07:00 | 42.16 | 0 | 0 | 42.16 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 08:00 | 43.1 | 2.45 | 2.45 | 40.65 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 09:00 | 45.43 | 4.31 | 4.31 | 41.12 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 10:00 | 46.88 | 5.16 | 5.16 | 41.72 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 11:00 | 48.62 | 7.18 | 7.18 | 41.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 12:00 | 49.97 | 7.39 | 7.39 | 42.59 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 13:00 | 51.07 | 62.54 | 62.54 | 0 | 11.47 | 0 | 43.34 | 0 | 0
2025-03-17 14:00 | 51.25 | 57.12 | 57.12 | 0 | 5.87 | 0 | 48.92 | 0 | 0
2025-03-17 15:00 | 52.73 | 51.99 | 51.99 | 0 | 0 | 0.74 | 48.15 | 0 | 0
2025-03-17 16:00 | 51.55 | 40.06 | 40.06 | 0 | 0 | 11.49 | 36.05 | 0 | 0
2025-03-17 17:00 | 49.84 | 19.98 | 19.98 | 26.44 | 0 | 3.42 | 32.45 | 0 | 0
2025-03-17 18:00 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 19:00 | 47.51 | 0 | 0 | 47.51 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 20:00 | 46.86 | 0 | 0 | 46.86 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 21:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 22:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 32.45 | 0 | 0
2025-03-17 23:00 | 43.32 | 0 | 0 | 43.32 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 01:00 | 40.72 | 0 | 0 | 40.72 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 02:00 | 39.35 | 0 | 0 | 39.35 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 03:00 | 39.13 | 0 | 0 | 39.13 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 04:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 05:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 06:00 | 40.29 | 0.04 | 0.04 | 40.24 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 07:00 | 42.22 | 0.01 | 0.01 | 42.22 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 08:00 | 43.58 | 41.14 | 41.14 | 2.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 09:00 | 44.78 | 104.28 | 104.28 | 0 | 59.5 | 0 | 88.97 | 0 | 0
2025-03-18 10:00 | 45.78 | 109.1 | 109.1 | 0 | 63.33 | 0 | 149.13 | 0 | 0
2025-03-18 11:00 | 47.09 | 99.65 | 99.65 | 0 | 52.56 | 0 | 199.06 | 0 | 0
2025-03-18 12:00 | 48.27 | 100.48 | 100.48 | 0 | 52.21 | 0 | 248.66 | 0 | 0
2025-03-18 13:00 | 49.15 | 61.6 | 61.6 | 0 | 12.44 | 0 | 260.48 | 0 | 0
2025-03-18 14:00 | 49.88 | 25.46 | 25.46 | 0 | 0 | 24.41 | 234.78 | 0 | 0
2025-03-18 15:00 | 50.27 | 3.68 | 3.68 | 0 | 0 | 46.59 | 185.74 | 0 | 0
2025-03-18 16:00 | 49.43 | 1.98 | 1.98 | 0 | 0 | 47.45 | 135.79 | 0 | 0
2025-03-18 17:00 | 48.88 | 25.22 | 25.22 | 0 | 0 | 23.66 | 110.89 | 0 | 0
2025-03-18 18:00 | 48.58 | 0 | 0 | 0 | 0 | 48.58 | 59.76 | 0 | 0
2025-03-18 19:00 | 47.67 | 0 | 0 | 21.73 | 0 | 25.94 | 32.45 | 0 | 0
2025-03-18 20:00 | 45.97 | 0 | 0 | 45.97 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 21:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 22:00 | 44.06 | 0 | 0 | 44.06 | 0 | 0 | 32.45 | 0 | 0
2025-03-18 23:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 01:00 | 40.04 | 0 | 0 | 40.04 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 02:00 | 39.93 | 0 | 0 | 39.93 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 03:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 04:00 | 39.87 | 0 | 0 | 39.87 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 05:00 | 40.15 | 0 | 0 | 40.15 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 06:00 | 40.62 | 0 | 0 | 40.62 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 07:00 | 42.57 | 15.79 | 15.79 | 26.78 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 08:00 | 43.5 | 40 | 40 | 3.5 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 09:00 | 45.4 | 48.8 | 48.8 | 0 | 3.39 | 0 | 35.67 | 0 | 0
2025-03-19 10:00 | 46.44 | 80.53 | 80.53 | 0 | 34.08 | 0 | 68.05 | 0 | 0
2025-03-19 11:00 | 47.68 | 71.06 | 71.06 | 0 | 23.38 | 0 | 90.26 | 0 | 0
2025-03-19 12:00 | 49.55 | 66.07 | 66.07 | 0 | 16.52 | 0 | 105.95 | 0 | 0
2025-03-19 13:00 | 50.43 | 90.94 | 90.94 | 0 | 40.5 | 0 | 144.43 | 0 | 0
2025-03-19 14:00 | 51.23 | 94.6 | 94.6 | 0 | 43.36 | 0 | 185.63 | 0 | 0
2025-03-19 15:00 | 52.24 | 70.83 | 70.83 | 0 | 18.6 | 0 | 203.29 | 0 | 0
2025-03-19 16:00 | 51.08 | 65.82 | 65.82 | 0 | 14.74 | 0 | 217.29 | 0 | 0
2025-03-19 17:00 | 50.6 | 27.73 | 27.73 | 0 | 0 | 22.88 | 193.21 | 0 | 0
2025-03-19 18:00 | 48.89 | 0.33 | 0.33 | 0 | 0 | 48.57 | 142.09 | 0 | 0
2025-03-19 19:00 | 47.59 | 0 | 0 | 0 | 0 | 47.59 | 92 | 0 | 0
2025-03-19 20:00 | 47.63 | 0 | 0 | 0 | 0 | 47.63 | 41.86 | 0 | 0
2025-03-19 21:00 | 44.9 | 0 | 0 | 35.96 | 0 | 8.94 | 32.45 | 0 | 0
2025-03-19 22:00 | 43.36 | 0 | 0 | 43.36 | 0 | 0 | 32.45 | 0 | 0
2025-03-19 23:00 | 42.51 | 0 | 0 | 42.51 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 01:00 | 40.14 | 0 | 0 | 40.14 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 02:00 | 39.88 | 0 | 0 | 39.88 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 03:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 04:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 05:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 06:00 | 41.98 | 0.01 | 0.01 | 41.97 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 07:00 | 42.97 | 21.23 | 21.23 | 21.75 | 0 | 0 | 32.45 | 0 | 0
2025-03-20 08:00 | 43.87 | 44.86 | 44.86 | 0 | 0.99 | 0 | 33.39 | 0 | 0
2025-03-20 09:00 | 44.99 | 70.98 | 70.98 | 0 | 26 | 0 | 58.09 | 0 | 0
2025-03-20 10:00 | 47.04 | 67.15 | 67.15 | 0 | 20.11 | 0 | 77.19 | 0 | 0
2025-03-20 11:00 | 48.96 | 70.78 | 70.78 | 0 | 21.82 | 0 | 97.92 | 0 | 0
2025-03-20 12:00 | 50.94 | 79.82 | 79.82 | 0 | 28.88 | 0 | 125.36 | 0 | 0
2025-03-20 13:00 | 50.91 | 84.15 | 84.15 | 0 | 33.24 | 0 | 156.93 | 0 | 0
2025-03-20 14:00 | 52.07 | 85.22 | 85.22 | 0 | 33.15 | 0 | 188.43 | 0 | 0
2025-03-20 15:00 | 52.69 | 79.71 | 79.71 | 0 | 27.02 | 0 | 214.1 | 0 | 0
2025-03-20 16:00 | 50.92 | 97.17 | 97.17 | 0 | 46.25 | 0 | 258.03 | 0 | 0
2025-03-20 17:00 | 51.95 | 71.64 | 71.64 | 0 | 19.69 | 0 | 276.74 | 0 | 0
2025-03-20 18:00 | 49.77 | 1.24 | 1.24 | 0 | 0 | 48.53 | 225.66 | 0 | 0
2025-03-20 19:00 | 49.15 | 0 | 0 | 0 | 0 | 49.15 | 173.92 | 0 | 0
2025-03-20 20:00 | 47.54 | 0 | 0 | 0 | 0 | 47.54 | 123.88 | 0 | 0
2025-03-20 21:00 | 46.32 | 0 | 0 | 0 | 0 | 46.32 | 75.12 | 0 | 0
2025-03-20 22:00 | 44.45 | 0 | 0 | 3.92 | 0 | 40.54 | 32.45 | 0 | 0
2025-03-20 23:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 | 41.21 | 0 | 0 | 41.21 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 01:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 02:00 | 40.04 | 0 | 0 | 40.04 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 03:00 | 40.18 | 0 | 0 | 40.18 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 04:00 | 40.53 | 0 | 0 | 40.53 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 05:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 06:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 07:00 | 41.83 | 6.39 | 6.39 | 35.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 08:00 | 43.85 | 17.78 | 17.78 | 26.07 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 09:00 | 45.69 | 39.53 | 39.53 | 6.17 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 10:00 | 46.32 | 39.7 | 39.7 | 6.62 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 11:00 | 48.45 | 50.93 | 50.93 | 0 | 2.48 | 0 | 34.8 | 0 | 0
2025-03-21 12:00 | 49.66 | 49.98 | 49.98 | 0 | 0.32 | 0 | 35.11 | 0 | 0
2025-03-21 13:00 | 50.09 | 34.83 | 34.83 | 12.73 | 0 | 2.53 | 32.45 | 0 | 0
2025-03-21 14:00 | 49 | 23.98 | 23.98 | 25.02 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 15:00 | 50.07 | 12.79 | 12.79 | 37.28 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 16:00 | 51.48 | 9.36 | 9.36 | 42.12 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 17:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 18:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 19:00 | 48.75 | 0 | 0 | 48.75 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 20:00 | 46.87 | 0 | 0 | 46.87 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 21:00 | 46.04 | 0 | 0 | 46.04 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 22:00 | 44.22 | 0 | 0 | 44.22 | 0 | 0 | 32.45 | 0 | 0
2025-03-21 23:00 | 42.98 | 0 | 0 | 42.98 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 | 41.94 | 0 | 0 | 41.94 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 01:00 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 02:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 03:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 04:00 | 39.46 | 0 | 0 | 39.46 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 05:00 | 41.05 | 0 | 0 | 41.05 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 06:00 | 42.33 | 0.13 | 0.13 | 42.2 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 07:00 | 43.6 | 4.36 | 4.36 | 39.24 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 08:00 | 44.25 | 41.83 | 41.83 | 2.41 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 09:00 | 46.65 | 61.56 | 61.56 | 0 | 14.91 | 0 | 46.61 | 0 | 0
2025-03-22 10:00 | 48.16 | 56.68 | 56.68 | 0 | 8.52 | 0 | 54.71 | 0 | 0
2025-03-22 11:00 | 50.54 | 55.04 | 55.04 | 0 | 4.5 | 0 | 58.98 | 0 | 0
2025-03-22 12:00 | 50.23 | 70.72 | 70.72 | 0 | 20.49 | 0 | 78.45 | 0 | 0
2025-03-22 13:00 | 51.4 | 52.75 | 52.75 | 0 | 1.34 | 0 | 79.72 | 0 | 0
2025-03-22 14:00 | 52.17 | 69.78 | 69.78 | 0 | 17.61 | 0 | 96.45 | 0 | 0
2025-03-22 15:00 | 52.31 | 110.66 | 110.66 | 0 | 58.35 | 0 | 151.88 | 0 | 0
2025-03-22 16:00 | 51.88 | 75.8 | 75.8 | 0 | 23.92 | 0 | 174.6 | 0 | 0
2025-03-22 17:00 | 50.28 | 53.58 | 53.58 | 0 | 3.3 | 0 | 177.74 | 0 | 0
2025-03-22 18:00 | 50.39 | 0.52 | 0.52 | 0 | 0 | 49.87 | 125.25 | 0 | 0
2025-03-22 19:00 | 49.44 | 0 | 0 | 0 | 0 | 49.44 | 73.21 | 0 | 0
2025-03-22 20:00 | 47.45 | 0 | 0 | 8.73 | 0 | 38.72 | 32.45 | 0 | 0
2025-03-22 21:00 | 47.03 | 0 | 0 | 47.03 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 22:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 32.45 | 0 | 0
2025-03-22 23:00 | 43.64 | 0 | 0 | 43.64 | 0 | 0 | 32.45 | 0 | 0
2025-03-23 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 32.45 | 0 | 0
2025-03-23 01:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 32.45 | 0 | 0
2025-03-23 02:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 32.45 | 0 | 0
2025-03-23 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 32.45 | 0 | 0
2025-03-23 04:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 32.45 | 0 | 0
2025-03-23 05:00 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 32.45 | 0 | 0
2025-03-23 06:00 | 42.03 | 0.62 | 0.62 | 41.4 | 0 | 0 | 32.45 | 0 | 0
2025-03-23 07:00 | 42.86 | 47.26 | 47.26 | 0 | 4.4 | 0 | 36.63 | 0 | 0
2025-03-23 08:00 | 44.51 | 88.35 | 88.35 | 0 | 43.84 | 0 | 78.28 | 0 | 0
2025-03-23 09:00 | 46.78 | 101.35 | 101.35 | 0 | 54.56 | 0 | 130.12 | 0 | 0
2025-03-23 10:00 | 46.84 | 96.08 | 96.08 | 0 | 49.24 | 0 | 176.9 | 0 | 0
2025-03-23 11:00 | 48.37 | 91.41 | 91.41 | 0 | 43.04 | 0 | 217.79 | 0 | 0
2025-03-23 12:00 | 49.77 | 90.52 | 90.52 | 0 | 40.76 | 0 | 256.51 | 0 | 0
2025-03-23 13:00 | 50.44 | 91.85 | 87.85 | 0 | 37.41 | 0 | 292.05 | 4 | 0
2025-03-23 14:00 | 50.33 | 97.14 | 50.33 | 0 | 0 | 0 | 292.05 | 46.81 | 0
2025-03-23 15:00 | 49.28 | 96.71 | 49.28 | 0 | 0 | 0 | 292.05 | 47.43 | 0
2025-03-23 16:00 | 50.58 | 79.24 | 50.58 | 0 | 0 | 0 | 292.05 | 28.66 | 0
2025-03-23 17:00 | 48.76 | 44.7 | 44.7 | 0 | 0 | 4.06 | 287.78 | 0 | 0
2025-03-23 18:00 | 49.87 | 0.91 | 0.91 | 0 | 0 | 48.96 | 236.24 | 0 | 0
2025-03-23 19:00 | 48.24 | 0 | 0 | 0 | 0 | 48.24 | 185.46 | 0 | 0
2025-03-23 20:00 | 47.48 | 0 | 0 | 0 | 0 | 47.48 | 135.48 | 0 | 0
2025-03-23 21:00 | 45.21 | 0 | 0 | 0 | 0 | 45.21 | 87.89 | 0 | 0
2025-03-23 22:00 | 43.53 | 0 | 0 | 0 | 0 | 43.53 | 42.07 | 0 | 0
2025-03-23 23:00 | 43.13 | 0 | 0 | 33.99 | 0 | 9.14 | 32.45 | 0 | 0
2025-03-24 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 32.45 | 0 | 0
2025-03-24 01:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 32.45 | 0 | 0
2025-03-24 02:00 | 40.51 | 0 | 0 | 40.51 | 0 | 0 | 32.45 | 0 | 0
2025-03-24 03:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 32.45 | 0 | 0
2025-03-24 04:00 | 40.89 | 0 | 0 | 40.89 | 0 | 0 | 32.45 | 0 | 0
2025-03-24 05:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 32.45 | 0 | 0
2025-03-24 06:00 | 42.41 | 0.89 | 0.89 | 41.52 | 0 | 0 | 32.45 | 0 | 0
2025-03-24 07:00 | 43.93 | 70.1 | 70.1 | 0 | 26.17 | 0 | 57.31 | 0 | 0
2025-03-24 08:00 | 44.47 | 96.17 | 96.17 | 0 | 51.71 | 0 | 106.43 | 0 | 0
2025-03-24 09:00 | 44.98 | 6.15 | 6.15 | 0 | 0 | 38.83 | 65.56 | 0 | 0
2025-03-24 10:00 | 47.34 | 29.44 | 29.44 | 0 | 0 | 17.9 | 46.72 | 0 | 0
2025-03-24 11:00 | 49.14 | 22.52 | 22.52 | 13.07 | 0 | 13.55 | 32.45 | 0 | 0
2025-03-24 12:00 | 49.35 | 53.96 | 53.96 | 0 | 4.61 | 0 | 36.83 | 0 | 0
2025-03-24 13:00 | 50.58 | 107.36 | 107.36 | 0 | 56.78 | 0 | 90.77 | 0 | 0
2025-03-24 14:00 | 50.84 | 112.43 | 112.43 | 0 | 61.59 | 0 | 149.29 | 0 | 0
2025-03-24 15:00 | 52.11 | 116.21 | 116.21 | 0 | 64.1 | 0 | 210.18 | 0 | 0
2025-03-24 16:00 | 51.56 | 112.42 | 112.42 | 0 | 60.86 | 0 | 267.99 | 0 | 0
2025-03-24 17:00 | 50.99 | 75.48 | 75.48 | 0 | 24.49 | 0 | 291.26 | 0 | 0
2025-03-24 18:00 | 50.15 | 2.42 | 2.42 | 0 | 0 | 47.72 | 241.02 | 0 | 0
2025-03-24 19:00 | 48.72 | 0 | 0 | 0 | 0 | 48.72 | 189.74 | 0 | 0
2025-03-24 20:00 | 47.53 | 0 | 0 | 0 | 0 | 47.53 | 139.71 | 0 | 0
2025-03-24 21:00 | 45.42 | 0 | 0 | 0 | 0 | 45.42 | 91.9 | 0 | 0
2025-03-24 22:00 | 43.47 | 0 | 0 | 0 | 0 | 43.47 | 46.15 | 0 | 0
2025-03-24 23:00 | 43.26 | 0 | 0 | 30.25 | 0 | 13.01 | 32.45 | 0 | 0
2025-03-25 | 42.29 | 0 | 0 | 42.29 | 0 | 0 | 32.45 | 0 | 0
2025-03-25 01:00 | 41.79 | 0 | 0 | 41.79 | 0 | 0 | 32.45 | 0 | 0
2025-03-25 02:00 | 41.37 | 0 | 0 | 41.37 | 0 | 0 | 32.45 | 0 | 0
2025-03-25 03:00 | 41.16 | 0 | 0 | 41.16 | 0 | 0 | 32.45 | 0 | 0
2025-03-25 04:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 32.45 | 0 | 0
2025-03-25 05:00 | 41.01 | 0 | 0 | 41.01 | 0 | 0 | 32.45 | 0 | 0
2025-03-25 06:00 | 42.36 | 0.89 | 0.89 | 41.47 | 0 | 0 | 32.45 | 0 | 0
2025-03-25 07:00 | 44.6 | 56.07 | 56.07 | 0 | 11.47 | 0 | 43.35 | 0 | 0
2025-03-25 08:00 | 45.46 | 81.64 | 81.64 | 0 | 36.17 | 0 | 77.71 | 0 | 0
2025-03-25 09:00 | 46.75 | 100.18 | 100.18 | 0 | 53.43 | 0 | 128.47 | 0 | 0
2025-03-25 10:00 | 47.43 | 95.28 | 95.28 | 0 | 47.85 | 0 | 173.93 | 0 | 0
2025-03-25 11:00 | 48.5 | 91.9 | 91.9 | 0 | 43.41 | 0 | 215.17 | 0 | 0
2025-03-25 12:00 | 50.44 | 93.31 | 93.31 | 0 | 42.87 | 0 | 255.89 | 0 | 0
2025-03-25 13:00 | 50.33 | 70.1 | 70.1 | 0 | 19.77 | 0 | 274.67 | 0 | 0
2025-03-25 14:00 | 51.29 | 75.5 | 69.58 | 0 | 18.3 | 0 | 292.05 | 5.92 | 0
2025-03-25 15:00 | 51.52 | 68.59 | 51.52 | 0 | 0 | 0 | 292.05 | 17.06 | 0
2025-03-25 16:00 | 52.2 | 49.36 | 49.36 | 0 | 0 | 2.84 | 289.06 | 0 | 0
2025-03-25 17:00 | 50.71 | 23.19 | 23.19 | 0 | 0 | 27.51 | 260.1 | 0 | 0
2025-03-25 18:00 | 48.83 | 1.04 | 1.04 | 0 | 0 | 47.78 | 209.8 | 0 | 0
2025-03-25 19:00 | 49.19 | 0 | 0 | 0 | 0 | 49.19 | 158.02 | 0 | 0
2025-03-25 20:00 | 47.27 | 0 | 0 | 0 | 0 | 47.27 | 108.26 | 0 | 0
2025-03-25 21:00 | 46.21 | 0 | 0 | 0 | 0 | 46.21 | 59.62 | 0 | 0
2025-03-25 22:00 | 44.68 | 0 | 0 | 18.87 | 0 | 25.81 | 32.45 | 0 | 0
2025-03-25 23:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 32.45 | 0 | 0
2025-03-26 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 32.45 | 0 | 0
2025-03-26 01:00 | 40.53 | 0 | 0 | 40.53 | 0 | 0 | 32.45 | 0 | 0
2025-03-26 02:00 | 40.44 | 0 | 0 | 40.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-26 03:00 | 40.83 | 0 | 0 | 40.83 | 0 | 0 | 32.45 | 0 | 0
2025-03-26 04:00 | 40.39 | 0 | 0 | 40.39 | 0 | 0 | 32.45 | 0 | 0
2025-03-26 05:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 32.45 | 0 | 0
2025-03-26 06:00 | 42.56 | 1.32 | 1.32 | 41.23 | 0 | 0 | 32.45 | 0 | 0
2025-03-26 07:00 | 43.94 | 56.25 | 56.25 | 0 | 12.32 | 0 | 44.15 | 0 | 0
2025-03-26 08:00 | 44.63 | 89.86 | 89.86 | 0 | 45.23 | 0 | 87.12 | 0 | 0
2025-03-26 09:00 | 44.95 | 100.72 | 100.72 | 0 | 55.77 | 0 | 140.1 | 0 | 0
2025-03-26 10:00 | 47.48 | 99.55 | 99.55 | 0 | 52.07 | 0 | 189.57 | 0 | 0
2025-03-26 11:00 | 47.33 | 95.17 | 95.17 | 0 | 47.84 | 0 | 235.02 | 0 | 0
2025-03-26 12:00 | 49.14 | 91.87 | 91.87 | 0 | 42.73 | 0 | 275.61 | 0 | 0
2025-03-26 13:00 | 49.14 | 95.36 | 66.45 | 0 | 17.31 | 0 | 292.05 | 28.92 | 0
2025-03-26 14:00 | 49.36 | 97.22 | 49.36 | 0 | 0 | 0 | 292.05 | 47.86 | 0
2025-03-26 15:00 | 49.84 | 100.8 | 49.84 | 0 | 0 | 0 | 292.05 | 50.96 | 0
2025-03-26 16:00 | 49.85 | 90.11 | 49.85 | 0 | 0 | 0 | 292.05 | 40.26 | 0
2025-03-26 17:00 | 49.26 | 59.1 | 49.26 | 0 | 0 | 0 | 292.05 | 9.84 | 0
2025-03-26 18:00 | 49.28 | 1.43 | 1.43 | 0 | 0 | 47.85 | 241.68 | 0 | 0
2025-03-26 19:00 | 47.94 | 0 | 0 | 0 | 0 | 47.94 | 191.22 | 0 | 0
2025-03-26 20:00 | 47.61 | 0 | 0 | 0 | 0 | 47.61 | 141.1 | 0 | 0
2025-03-26 21:00 | 46.07 | 0 | 0 | 0 | 0 | 46.07 | 92.61 | 0 | 0
2025-03-26 22:00 | 44.3 | 0 | 0 | 0 | 0 | 44.3 | 45.97 | 0 | 0
2025-03-26 23:00 | 42.94 | 0 | 0 | 30.09 | 0 | 12.85 | 32.45 | 0 | 0
2025-03-27 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 32.45 | 0 | 0
2025-03-27 01:00 | 41.58 | 0 | 0 | 41.58 | 0 | 0 | 32.45 | 0 | 0
2025-03-27 02:00 | 40.64 | 0 | 0 | 40.64 | 0 | 0 | 32.45 | 0 | 0
2025-03-27 03:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 32.45 | 0 | 0
2025-03-27 04:00 | 40.55 | 0 | 0 | 40.55 | 0 | 0 | 32.45 | 0 | 0
2025-03-27 05:00 | 40.99 | 0 | 0 | 40.99 | 0 | 0 | 32.45 | 0 | 0
2025-03-27 06:00 | 43.22 | 1.32 | 1.32 | 41.91 | 0 | 0 | 32.45 | 0 | 0
2025-03-27 07:00 | 42.91 | 55.68 | 55.68 | 0 | 12.77 | 0 | 44.58 | 0 | 0
2025-03-27 08:00 | 44.61 | 93.66 | 93.66 | 0 | 49.05 | 0 | 91.18 | 0 | 0
2025-03-27 09:00 | 47.61 | 106.18 | 106.18 | 0 | 58.58 | 0 | 146.83 | 0 | 0
2025-03-27 10:00 | 49.49 | 107.81 | 107.81 | 0 | 58.32 | 0 | 202.23 | 0 | 0
2025-03-27 11:00 | 50.11 | 87.49 | 87.49 | 0 | 37.38 | 0 | 237.75 | 0 | 0
2025-03-27 12:00 | 51.62 | 76.58 | 76.58 | 0 | 24.96 | 0 | 261.46 | 0 | 0
2025-03-27 13:00 | 53.38 | 80.81 | 80.81 | 0 | 27.42 | 0 | 287.51 | 0 | 0
2025-03-27 14:00 | 52.63 | 93.62 | 57.41 | 0 | 4.78 | 0 | 292.05 | 36.2 | 0
2025-03-27 15:00 | 53.11 | 75.08 | 53.11 | 0 | 0 | 0 | 292.05 | 21.97 | 0
2025-03-27 16:00 | 53.65 | 37.82 | 37.82 | 0 | 0 | 15.84 | 275.38 | 0 | 0
2025-03-27 17:00 | 53.85 | 25.65 | 25.65 | 0 | 0 | 28.2 | 245.7 | 0 | 0
2025-03-27 18:00 | 51.72 | 1.4 | 1.4 | 0 | 0 | 50.32 | 192.73 | 0 | 0
2025-03-27 19:00 | 50.53 | 0 | 0 | 0 | 0 | 50.53 | 139.54 | 0 | 0
2025-03-27 20:00 | 49.38 | 0 | 0 | 0 | 0 | 49.38 | 87.56 | 0 | 0
2025-03-27 21:00 | 48.11 | 0 | 0 | 0 | 0 | 48.11 | 36.92 | 0 | 0
2025-03-27 22:00 | 45.04 | 0 | 0 | 40.79 | 0 | 4.25 | 32.45 | 0 | 0
2025-03-27 23:00 | 43.75 | 0 | 0 | 43.75 | 0 | 0 | 32.45 | 0 | 0
2025-03-28 | 43.44 | 0 | 0 | 43.44 | 0 | 0 | 32.45 | 0 | 0
2025-03-28 01:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 32.45 | 0 | 0
2025-03-28 02:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 32.45 | 0 | 0
2025-03-28 03:00 | 40.21 | 0 | 0 | 40.21 | 0 | 0 | 32.45 | 0 | 0
2025-03-28 04:00 | 40.98 | 0 | 0 | 40.98 | 0 | 0 | 32.45 | 0 | 0
2025-03-28 05:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 32.45 | 0 | 0
2025-03-28 06:00 | 42.05 | 2.6 | 2.6 | 39.45 | 0 | 0 | 32.45 | 0 | 0
2025-03-28 07:00 | 43.29 | 79.14 | 79.14 | 0 | 35.85 | 0 | 66.51 | 0 | 0
2025-03-28 08:00 | 45.35 | 111.12 | 111.12 | 0 | 65.77 | 0 | 128.99 | 0 | 0
2025-03-28 09:00 | 47.21 | 114.7 | 114.7 | 0 | 67.49 | 0 | 193.1 | 0 | 0
2025-03-28 10:00 | 48.12 | 111.79 | 111.79 | 0 | 63.67 | 0 | 253.59 | 0 | 0
2025-03-28 11:00 | 49.55 | 106.32 | 90.03 | 0 | 40.49 | 0 | 292.05 | 16.29 | 0
2025-03-28 12:00 | 50.92 | 102.67 | 50.92 | 0 | 0 | 0 | 292.05 | 51.75 | 0
2025-03-28 13:00 | 50.99 | 105.08 | 50.99 | 0 | 0 | 0 | 292.05 | 54.08 | 0
2025-03-28 14:00 | 52.37 | 109.65 | 52.37 | 0 | 0 | 0 | 292.05 | 57.28 | 0
2025-03-28 15:00 | 52.59 | 111.58 | 52.59 | 0 | 0 | 0 | 292.05 | 58.99 | 0
2025-03-28 16:00 | 53.3 | 106.52 | 53.3 | 0 | 0 | 0 | 292.05 | 53.22 | 0
2025-03-28 17:00 | 51.29 | 73.15 | 51.29 | 0 | 0 | 0 | 292.05 | 21.86 | 0
2025-03-28 18:00 | 50.4 | 2.01 | 2.01 | 0 | 0 | 48.39 | 241.11 | 0 | 0
2025-03-28 19:00 | 49.9 | 0 | 0 | 0 | 0 | 49.9 | 188.59 | 0 | 0
2025-03-28 20:00 | 48.59 | 0 | 0 | 0 | 0 | 48.59 | 137.44 | 0 | 0
2025-03-28 21:00 | 46.45 | 0 | 0 | 0 | 0 | 46.45 | 88.55 | 0 | 0
2025-03-28 22:00 | 45.01 | 0 | 0 | 0 | 0 | 45.01 | 41.17 | 0 | 0
2025-03-28 23:00 | 44.05 | 0 | 0 | 35.77 | 0 | 8.28 | 32.45 | 0 | 0
2025-03-29 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 32.45 | 0 | 0
2025-03-29 01:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 32.45 | 0 | 0
2025-03-29 02:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 32.45 | 0 | 0
2025-03-29 03:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 32.45 | 0 | 0
2025-03-29 04:00 | 40.75 | 0 | 0 | 40.75 | 0 | 0 | 32.45 | 0 | 0
2025-03-29 05:00 | 40.76 | 0 | 0 | 40.76 | 0 | 0 | 32.45 | 0 | 0
2025-03-29 06:00 | 41.73 | 3.26 | 3.26 | 38.47 | 0 | 0 | 32.45 | 0 | 0
2025-03-29 07:00 | 43.38 | 85.91 | 85.91 | 0 | 42.53 | 0 | 72.85 | 0 | 0
2025-03-29 08:00 | 44.88 | 114.49 | 114.49 | 0 | 69.61 | 0 | 138.98 | 0 | 0
2025-03-29 09:00 | 47.11 | 117.2 | 117.2 | 0 | 70.09 | 0 | 205.57 | 0 | 0
2025-03-29 10:00 | 48.24 | 112.6 | 112.6 | 0 | 64.37 | 0 | 266.72 | 0 | 0
2025-03-29 11:00 | 50.01 | 106.35 | 76.68 | 0 | 26.66 | 0 | 292.05 | 29.67 | 0
2025-03-29 12:00 | 51.3 | 103.21 | 51.3 | 0 | 0 | 0 | 292.05 | 51.91 | 0
2025-03-29 13:00 | 52.47 | 105.29 | 52.47 | 0 | 0 | 0 | 292.05 | 52.82 | 0
2025-03-29 14:00 | 53.99 | 109.28 | 53.99 | 0 | 0 | 0 | 292.05 | 55.29 | 0
2025-03-29 15:00 | 53.88 | 111.62 | 53.88 | 0 | 0 | 0 | 292.05 | 57.74 | 0
2025-03-29 16:00 | 53.34 | 108.92 | 53.34 | 0 | 0 | 0 | 292.05 | 55.58 | 0
2025-03-29 17:00 | 52.46 | 80.28 | 52.46 | 0 | 0 | 0 | 292.05 | 27.82 | 0
2025-03-29 18:00 | 51.47 | 2.78 | 2.78 | 0 | 0 | 48.68 | 240.81 | 0 | 0
2025-03-29 19:00 | 50.53 | 0 | 0 | 0 | 0 | 50.53 | 187.62 | 0 | 0
2025-03-29 20:00 | 49.12 | 0 | 0 | 0 | 0 | 49.12 | 135.91 | 0 | 0
2025-03-29 21:00 | 46.73 | 0 | 0 | 0 | 0 | 46.73 | 86.72 | 0 | 0
2025-03-29 22:00 | 45.56 | 0 | 0 | 0 | 0 | 45.56 | 38.77 | 0 | 0
2025-03-29 23:00 | 42.99 | 0 | 0 | 36.99 | 0 | 6 | 32.45 | 0 | 0
2025-03-30 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 32.45 | 0 | 0
2025-03-30 01:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 32.45 | 0 | 0
2025-03-30 02:00 | 41.03 | 0 | 0 | 41.03 | 0 | 0 | 32.45 | 0 | 0
2025-03-30 03:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 32.45 | 0 | 0
2025-03-30 04:00 | 40.73 | 0 | 0 | 40.73 | 0 | 0 | 32.45 | 0 | 0
2025-03-30 05:00 | 41.92 | 0 | 0 | 41.92 | 0 | 0 | 32.45 | 0 | 0
2025-03-30 06:00 | 42.84 | 4.6 | 4.6 | 38.23 | 0 | 0 | 32.45 | 0 | 0
2025-03-30 07:00 | 44.18 | 85.45 | 85.45 | 0 | 41.27 | 0 | 71.65 | 0 | 0
2025-03-30 08:00 | 45.81 | 112.38 | 112.38 | 0 | 66.57 | 0 | 134.89 | 0 | 0
2025-03-30 09:00 | 47.71 | 114.91 | 114.91 | 0 | 67.2 | 0 | 198.73 | 0 | 0
2025-03-30 10:00 | 49.91 | 111.14 | 111.14 | 0 | 61.24 | 0 | 256.91 | 0 | 0
2025-03-30 11:00 | 51.9 | 105.13 | 88.9 | 0 | 36.99 | 0 | 292.05 | 16.23 | 0
2025-03-30 12:00 | 52.73 | 102.74 | 52.73 | 0 | 0 | 0 | 292.05 | 50.01 | 0
2025-03-30 13:00 | 54.32 | 103.79 | 54.32 | 0 | 0 | 0 | 292.05 | 49.47 | 0
2025-03-30 14:00 | 54.31 | 107.48 | 54.31 | 0 | 0 | 0 | 292.05 | 53.17 | 0
2025-03-30 15:00 | 55.3 | 110.5 | 55.3 | 0 | 0 | 0 | 292.05 | 55.2 | 0
2025-03-30 16:00 | 54.28 | 104.55 | 54.28 | 0 | 0 | 0 | 292.05 | 50.27 | 0
2025-03-30 17:00 | 54.46 | 75.48 | 54.46 | 0 | 0 | 0 | 292.05 | 21.02 | 0
2025-03-30 18:00 | 53.84 | 3.03 | 3.03 | 0 | 0 | 50.81 | 238.57 | 0 | 0
2025-03-30 19:00 | 51.16 | 0 | 0 | 0 | 0 | 51.16 | 184.72 | 0 | 0
2025-03-30 20:00 | 48.38 | 0 | 0 | 0 | 0 | 48.38 | 133.79 | 0 | 0
2025-03-30 21:00 | 47.38 | 0 | 0 | 0 | 0 | 47.38 | 83.92 | 0 | 0
2025-03-30 22:00 | 46.48 | 0 | 0 | 0 | 0 | 46.48 | 34.99 | 0 | 0
2025-03-30 23:00 | 44.51 | 0 | 0 | 42.1 | 0 | 2.41 | 32.45 | 0 | 0
2025-03-31 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 32.45 | 0 | 0
2025-03-31 01:00 | 42.45 | 0 | 0 | 42.45 | 0 | 0 | 32.45 | 0 | 0
2025-03-31 02:00 | 41.53 | 0 | 0 | 41.53 | 0 | 0 | 32.45 | 0 | 0
2025-03-31 03:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 32.45 | 0 | 0
2025-03-31 04:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 32.45 | 0 | 0
2025-03-31 05:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 32.45 | 0 | 0
2025-03-31 06:00 | 43.18 | 4.54 | 4.54 | 38.63 | 0 | 0 | 32.45 | 0 | 0
2025-03-31 07:00 | 44.84 | 88.76 | 88.76 | 0 | 43.92 | 0 | 74.18 | 0 | 0
2025-03-31 08:00 | 45.88 | 113.26 | 113.26 | 0 | 67.38 | 0 | 138.19 | 0 | 0
2025-03-31 09:00 | 47.54 | 115.56 | 115.56 | 0 | 68.02 | 0 | 202.81 | 0 | 0
2025-03-31 10:00 | 50.53 | 112.89 | 112.89 | 0 | 62.36 | 0 | 262.05 | 0 | 0
2025-03-31 11:00 | 51.53 | 107.98 | 83.11 | 0 | 31.58 | 0 | 292.05 | 24.87 | 0
2025-03-31 12:00 | 53.35 | 104.82 | 53.35 | 0 | 0 | 0 | 292.05 | 51.47 | 0
2025-03-31 13:00 | 54.19 | 106.99 | 54.19 | 0 | 0 | 0 | 292.05 | 52.8 | 0
2025-03-31 14:00 | 54.59 | 111.66 | 54.59 | 0 | 0 | 0 | 292.05 | 57.07 | 0
2025-03-31 15:00 | 55.14 | 114.66 | 55.14 | 0 | 0 | 0 | 292.05 | 59.52 | 0
2025-03-31 16:00 | 55.6 | 112.13 | 55.6 | 0 | 0 | 0 | 292.05 | 56.54 | 0
2025-03-31 17:00 | 54.41 | 85.18 | 54.41 | 0 | 0 | 0 | 292.05 | 30.77 | 0
2025-03-31 18:00 | 52.09 | 4.07 | 4.07 | 0 | 0 | 48.02 | 241.5 | 0 | 0
2025-03-31 19:00 | 51.32 | 0 | 0 | 0 | 0 | 51.32 | 187.49 | 0 | 0
2025-03-31 20:00 | 50.57 | 0 | 0 | 0 | 0 | 50.57 | 134.25 | 0 | 0
2025-03-31 21:00 | 47.73 | 0 | 0 | 0 | 0 | 47.73 | 84.01 | 0 | 0
2025-03-31 22:00 | 45.14 | 0 | 0 | 0 | 0 | 45.14 | 36.5 | 0 | 0
2025-03-31 23:00 | 45.34 | 0 | 0 | 41.49 | 0 | 3.84 | 32.45 | 0 | 0
2025-04-01 | 43.49 | 0 | 0 | 43.49 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 01:00 | 42.04 | 0 | 0 | 42.04 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 02:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 03:00 | 41.73 | 0 | 0 | 41.73 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 04:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 05:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 06:00 | 43.42 | 3.11 | 3.11 | 40.31 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 07:00 | 44.7 | 12.61 | 12.61 | 32.09 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 08:00 | 46.36 | 49.59 | 49.59 | 0 | 3.23 | 0 | 35.51 | 0 | 0
2025-04-01 09:00 | 48.09 | 55.41 | 55.41 | 0 | 7.32 | 0 | 42.47 | 0 | 0
2025-04-01 10:00 | 50.64 | 52.99 | 52.99 | 0 | 2.35 | 0 | 44.7 | 0 | 0
2025-04-01 11:00 | 51.54 | 70.33 | 70.33 | 0 | 18.79 | 0 | 62.56 | 0 | 0
2025-04-01 12:00 | 52.79 | 34.85 | 34.85 | 0 | 0 | 17.94 | 43.68 | 0 | 0
2025-04-01 13:00 | 55.18 | 68.41 | 68.41 | 0 | 13.23 | 0 | 56.24 | 0 | 0
2025-04-01 14:00 | 56 | 34.98 | 34.98 | 0 | 0 | 21.01 | 34.13 | 0 | 0
2025-04-01 15:00 | 56.2 | 49.87 | 49.87 | 4.74 | 0 | 1.59 | 32.45 | 0 | 0
2025-04-01 16:00 | 55.88 | 19.1 | 19.1 | 36.78 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 17:00 | 54.71 | 4.46 | 4.46 | 50.25 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 18:00 | 53.99 | 0 | 0 | 53.99 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 19:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 20:00 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 21:00 | 48.02 | 0 | 0 | 48.02 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 22:00 | 47.3 | 0 | 0 | 47.3 | 0 | 0 | 32.45 | 0 | 0
2025-04-01 23:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 | 43.51 | 0 | 0 | 43.51 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 01:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 02:00 | 41.48 | 0 | 0 | 41.48 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 03:00 | 41.09 | 0 | 0 | 41.09 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 04:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 05:00 | 42.39 | 0 | 0 | 42.39 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 06:00 | 43.07 | 0.52 | 0.52 | 42.55 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 07:00 | 43.58 | 4.07 | 4.07 | 39.51 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 08:00 | 46.64 | 9.3 | 9.3 | 37.34 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 09:00 | 48.64 | 14.88 | 14.88 | 33.76 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 10:00 | 50.37 | 23.3 | 23.3 | 27.06 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 11:00 | 51.37 | 26.41 | 26.41 | 24.96 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 12:00 | 52.56 | 25.56 | 25.56 | 27 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 13:00 | 54.23 | 21.26 | 21.26 | 32.97 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 14:00 | 55.05 | 19.85 | 19.85 | 35.2 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 15:00 | 55 | 17.83 | 17.83 | 37.17 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 16:00 | 53.74 | 11.22 | 11.22 | 42.53 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 17:00 | 53.67 | 5.12 | 5.12 | 48.55 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 18:00 | 52.76 | 0.27 | 0.27 | 52.49 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 19:00 | 50.29 | 0 | 0 | 50.29 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 20:00 | 49.86 | 0 | 0 | 49.86 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 21:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 22:00 | 46.54 | 0 | 0 | 46.54 | 0 | 0 | 32.45 | 0 | 0
2025-04-02 23:00 | 45.37 | 0 | 0 | 45.37 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 01:00 | 42.29 | 0 | 0 | 42.29 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 02:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 03:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 04:00 | 41.17 | 0 | 0 | 41.17 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 05:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 06:00 | 44.07 | 1.17 | 1.17 | 42.9 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 07:00 | 44.25 | 6.13 | 6.13 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 08:00 | 46.78 | 16.34 | 16.34 | 30.44 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 09:00 | 47.89 | 19.67 | 19.67 | 28.22 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 10:00 | 49.71 | 26.73 | 26.73 | 22.97 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 11:00 | 51.23 | 21.46 | 21.46 | 29.77 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 12:00 | 52.72 | 28.87 | 28.87 | 23.85 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 13:00 | 53.2 | 32.61 | 32.61 | 20.59 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 14:00 | 54.44 | 28.94 | 28.94 | 25.5 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 15:00 | 54.09 | 25.94 | 25.94 | 28.14 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 16:00 | 54.05 | 14.72 | 14.72 | 39.33 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 17:00 | 52.74 | 4.65 | 4.65 | 48.09 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 18:00 | 53.31 | 0.27 | 0.27 | 53.04 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 19:00 | 51.23 | 0 | 0 | 51.23 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 20:00 | 49.89 | 0 | 0 | 49.89 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 21:00 | 47.13 | 0 | 0 | 47.13 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 22:00 | 45.89 | 0 | 0 | 45.89 | 0 | 0 | 32.45 | 0 | 0
2025-04-03 23:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 01:00 | 41.5 | 0 | 0 | 41.5 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 02:00 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 03:00 | 41.27 | 0 | 0 | 41.27 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 04:00 | 42.48 | 0 | 0 | 42.48 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 05:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 06:00 | 43.65 | 9.78 | 9.78 | 33.87 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 07:00 | 45.55 | 102.33 | 102.33 | 0 | 56.78 | 0 | 86.39 | 0 | 0
2025-04-04 08:00 | 46.15 | 124.05 | 122.55 | 0 | 76.4 | 0 | 158.97 | 1.5 | 0
2025-04-04 09:00 | 47.86 | 121.2 | 121.2 | 0 | 73.34 | 0 | 228.65 | 0 | 0
2025-04-04 10:00 | 50 | 123.82 | 116.74 | 0 | 66.74 | 0 | 292.05 | 7.09 | 0
2025-04-04 11:00 | 52.13 | 88.13 | 52.13 | 0 | 0 | 0 | 292.05 | 36 | 0
2025-04-04 12:00 | 52.44 | 52.44 | 52.44 | 0 | 0 | 0 | 292.05 | 0 | 0
2025-04-04 13:00 | 53.33 | 22.17 | 22.17 | 0 | 0 | 31.16 | 259.25 | 0 | 0
2025-04-04 14:00 | 55.24 | 36.57 | 36.57 | 0 | 0 | 18.68 | 239.59 | 0 | 0
2025-04-04 15:00 | 54.76 | 28.49 | 28.49 | 0 | 0 | 26.27 | 211.94 | 0 | 0
2025-04-04 16:00 | 54.64 | 30.1 | 30.1 | 0 | 0 | 24.54 | 186.11 | 0 | 0
2025-04-04 17:00 | 53.24 | 12.32 | 12.32 | 0 | 0 | 40.92 | 143.03 | 0 | 0
2025-04-04 18:00 | 52.77 | 5.39 | 5.39 | 0 | 0 | 47.38 | 93.16 | 0 | 0
2025-04-04 19:00 | 51.71 | 0 | 0 | 0 | 0 | 51.71 | 38.72 | 0 | 0
2025-04-04 20:00 | 50.56 | 0 | 0 | 44.6 | 0 | 5.96 | 32.45 | 0 | 0
2025-04-04 21:00 | 47.97 | 0 | 0 | 47.97 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 22:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 32.45 | 0 | 0
2025-04-04 23:00 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 01:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 02:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 03:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 04:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 05:00 | 43.25 | 0 | 0 | 43.25 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 06:00 | 44.34 | 3.66 | 3.66 | 40.68 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 07:00 | 44.47 | 69.96 | 69.96 | 0 | 25.5 | 0 | 56.67 | 0 | 0
2025-04-05 08:00 | 46.21 | 93.95 | 93.95 | 0 | 47.74 | 0 | 102.03 | 0 | 0
2025-04-05 09:00 | 47.6 | 49.3 | 49.3 | 0 | 1.7 | 0 | 103.64 | 0 | 0
2025-04-05 10:00 | 48.24 | 73.96 | 73.96 | 0 | 25.72 | 0 | 128.07 | 0 | 0
2025-04-05 11:00 | 49.68 | 87.07 | 87.07 | 0 | 37.39 | 0 | 163.59 | 0 | 0
2025-04-05 12:00 | 50.45 | 56.86 | 56.86 | 0 | 6.41 | 0 | 169.68 | 0 | 0
2025-04-05 13:00 | 51.52 | 49.81 | 49.81 | 0 | 0 | 1.71 | 167.88 | 0 | 0
2025-04-05 14:00 | 51.84 | 18.98 | 18.98 | 0 | 0 | 32.86 | 133.28 | 0 | 0
2025-04-05 15:00 | 51.17 | 53.64 | 53.64 | 0 | 2.47 | 0 | 135.62 | 0 | 0
2025-04-05 16:00 | 51.13 | 82.27 | 82.27 | 0 | 31.13 | 0 | 165.2 | 0 | 0
2025-04-05 17:00 | 51.28 | 61.51 | 61.51 | 0 | 10.22 | 0 | 174.91 | 0 | 0
2025-04-05 18:00 | 50.15 | 4.54 | 4.54 | 0 | 0 | 45.62 | 126.9 | 0 | 0
2025-04-05 19:00 | 50 | 0 | 0 | 0 | 0 | 50 | 74.26 | 0 | 0
2025-04-05 20:00 | 48.69 | 0 | 0 | 8.97 | 0 | 39.72 | 32.45 | 0 | 0
2025-04-05 21:00 | 47.07 | 0 | 0 | 47.07 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 22:00 | 45.75 | 0 | 0 | 45.75 | 0 | 0 | 32.45 | 0 | 0
2025-04-05 23:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 01:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 02:00 | 41.77 | 0 | 0 | 41.77 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 03:00 | 41.93 | 0 | 0 | 41.93 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 04:00 | 43.22 | 0 | 0 | 43.22 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 05:00 | 42.18 | 0 | 0 | 42.18 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 06:00 | 42.82 | 4.61 | 4.61 | 38.21 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 07:00 | 45.72 | 20.71 | 20.71 | 25.01 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 08:00 | 46.08 | 50.81 | 50.81 | 0 | 4.73 | 0 | 36.94 | 0 | 0
2025-04-06 09:00 | 47.89 | 57.76 | 57.76 | 0 | 9.87 | 0 | 46.31 | 0 | 0
2025-04-06 10:00 | 48.9 | 64.28 | 64.28 | 0 | 15.38 | 0 | 60.93 | 0 | 0
2025-04-06 11:00 | 50.41 | 67.98 | 67.98 | 0 | 17.57 | 0 | 77.62 | 0 | 0
2025-04-06 12:00 | 50.65 | 49.64 | 49.64 | 0 | 0 | 1.01 | 76.56 | 0 | 0
2025-04-06 13:00 | 51.63 | 48.22 | 48.22 | 0 | 0 | 3.42 | 72.96 | 0 | 0
2025-04-06 14:00 | 52.3 | 47.36 | 47.36 | 0 | 0 | 4.94 | 67.77 | 0 | 0
2025-04-06 15:00 | 51.68 | 100.98 | 100.98 | 0 | 49.3 | 0 | 114.6 | 0 | 0
2025-04-06 16:00 | 51.72 | 78.76 | 78.76 | 0 | 27.04 | 0 | 140.29 | 0 | 0
2025-04-06 17:00 | 51.55 | 79.15 | 79.15 | 0 | 27.6 | 0 | 166.51 | 0 | 0
2025-04-06 18:00 | 50.41 | 11.1 | 11.1 | 0 | 0 | 39.31 | 125.13 | 0 | 0
2025-04-06 19:00 | 50.06 | 0 | 0 | 0 | 0 | 50.06 | 72.43 | 0 | 0
2025-04-06 20:00 | 49.25 | 0 | 0 | 11.26 | 0 | 37.98 | 32.45 | 0 | 0
2025-04-06 21:00 | 47.7 | 0 | 0 | 47.7 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 22:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 32.45 | 0 | 0
2025-04-06 23:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 01:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 02:00 | 42.87 | 0 | 0 | 42.87 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 03:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 04:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 05:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 06:00 | 44.11 | 3.28 | 3.28 | 40.82 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 07:00 | 46.04 | 17.34 | 17.34 | 28.7 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 08:00 | 46.98 | 39.72 | 39.72 | 7.26 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 09:00 | 47.3 | 13.38 | 13.38 | 33.91 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 10:00 | 49.76 | 14.62 | 14.62 | 35.14 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 11:00 | 51.3 | 44.81 | 44.81 | 6.49 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 12:00 | 51.48 | 56.77 | 56.77 | 0 | 5.28 | 0 | 37.47 | 0 | 0
2025-04-07 13:00 | 52.74 | 99.85 | 99.85 | 0 | 47.1 | 0 | 82.22 | 0 | 0
2025-04-07 14:00 | 52.29 | 114.26 | 114.26 | 0 | 61.97 | 0 | 141.08 | 0 | 0
2025-04-07 15:00 | 52.02 | 52.45 | 52.45 | 0 | 0.44 | 0 | 141.5 | 0 | 0
2025-04-07 16:00 | 52.7 | 103.3 | 103.3 | 0 | 50.6 | 0 | 189.57 | 0 | 0
2025-04-07 17:00 | 51.37 | 76.92 | 76.92 | 0 | 25.55 | 0 | 213.84 | 0 | 0
2025-04-07 18:00 | 51.48 | 6.85 | 6.85 | 0 | 0 | 44.62 | 166.87 | 0 | 0
2025-04-07 19:00 | 51.33 | 0 | 0 | 0 | 0 | 51.33 | 112.84 | 0 | 0
2025-04-07 20:00 | 48.58 | 0 | 0 | 0 | 0 | 48.58 | 61.71 | 0 | 0
2025-04-07 21:00 | 47.54 | 0 | 0 | 19.74 | 0 | 27.8 | 32.45 | 0 | 0
2025-04-07 22:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 32.45 | 0 | 0
2025-04-07 23:00 | 45.23 | 0 | 0 | 45.23 | 0 | 0 | 32.45 | 0 | 0
2025-04-08 | 43.91 | 0 | 0 | 43.91 | 0 | 0 | 32.45 | 0 | 0
2025-04-08 01:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 32.45 | 0 | 0
2025-04-08 02:00 | 42.76 | 0 | 0 | 42.76 | 0 | 0 | 32.45 | 0 | 0
2025-04-08 03:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 32.45 | 0 | 0
2025-04-08 04:00 | 42.35 | 0 | 0 | 42.35 | 0 | 0 | 32.45 | 0 | 0
2025-04-08 05:00 | 43.18 | 0 | 0 | 43.18 | 0 | 0 | 32.45 | 0 | 0
2025-04-08 06:00 | 43.66 | 14.91 | 14.91 | 28.74 | 0 | 0 | 32.45 | 0 | 0
2025-04-08 07:00 | 45.91 | 74.11 | 74.11 | 0 | 28.2 | 0 | 59.24 | 0 | 0
2025-04-08 08:00 | 46.47 | 96.98 | 96.98 | 0 | 50.51 | 0 | 107.23 | 0 | 0
2025-04-08 09:00 | 49.01 | 105.24 | 105.24 | 0 | 56.23 | 0 | 160.64 | 0 | 0
2025-04-08 10:00 | 50.68 | 101.39 | 101.39 | 0 | 50.72 | 0 | 208.82 | 0 | 0
2025-04-08 11:00 | 51.5 | 102.42 | 102.42 | 0 | 50.92 | 0 | 257.2 | 0 | 0
2025-04-08 12:00 | 52.37 | 102.53 | 89.06 | 0 | 36.69 | 0 | 292.05 | 13.48 | 0
2025-04-08 13:00 | 53.43 | 98.12 | 53.43 | 0 | 0 | 0 | 292.05 | 44.68 | 0
2025-04-08 14:00 | 52.28 | 96.16 | 52.28 | 0 | 0 | 0 | 292.05 | 43.88 | 0
2025-04-08 15:00 | 54.02 | 101.12 | 54.02 | 0 | 0 | 0 | 292.05 | 47.11 | 0
2025-04-08 16:00 | 53.65 | 92.8 | 53.65 | 0 | 0 | 0 | 292.05 | 39.15 | 0
2025-04-08 17:00 | 53.21 | 64.85 | 53.21 | 0 | 0 | 0 | 292.05 | 11.64 | 0
2025-04-08 18:00 | 52.81 | 10.05 | 10.05 | 0 | 0 | 42.76 | 247.04 | 0 | 0
2025-04-08 19:00 | 51.36 | 0 | 0 | 0 | 0 | 51.36 | 192.98 | 0 | 0
2025-04-08 20:00 | 49.51 | 0 | 0 | 0 | 0 | 49.51 | 140.86 | 0 | 0
2025-04-08 21:00 | 48.53 | 0 | 0 | 0 | 0 | 48.53 | 89.78 | 0 | 0
2025-04-08 22:00 | 47.06 | 0 | 0 | 0 | 0 | 47.06 | 40.25 | 0 | 0
2025-04-08 23:00 | 45.53 | 0 | 0 | 38.12 | 0 | 7.41 | 32.45 | 0 | 0
2025-04-09 | 44.4 | 0 | 0 | 44.4 | 0 | 0 | 32.45 | 0 | 0
2025-04-09 01:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 32.45 | 0 | 0
2025-04-09 02:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 32.45 | 0 | 0
2025-04-09 03:00 | 42.25 | 0 | 0 | 42.25 | 0 | 0 | 32.45 | 0 | 0
2025-04-09 04:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 32.45 | 0 | 0
2025-04-09 05:00 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 32.45 | 0 | 0
2025-04-09 06:00 | 44.41 | 18.68 | 18.68 | 25.73 | 0 | 0 | 32.45 | 0 | 0
2025-04-09 07:00 | 45.58 | 81.76 | 81.76 | 0 | 36.18 | 0 | 66.82 | 0 | 0
2025-04-09 08:00 | 47.53 | 92.74 | 92.74 | 0 | 45.22 | 0 | 109.77 | 0 | 0
2025-04-09 09:00 | 49.27 | 100.13 | 100.13 | 0 | 50.86 | 0 | 158.1 | 0 | 0
2025-04-09 10:00 | 51.68 | 98.85 | 98.85 | 0 | 47.17 | 0 | 202.91 | 0 | 0
2025-04-09 11:00 | 54.62 | 97.36 | 97.36 | 0 | 42.75 | 0 | 243.52 | 0 | 0
2025-04-09 12:00 | 54.75 | 98.62 | 98.62 | 0 | 43.87 | 0 | 285.19 | 0 | 0
2025-04-09 13:00 | 56.11 | 98.85 | 63.33 | 0 | 7.22 | 0 | 292.05 | 35.52 | 0
2025-04-09 14:00 | 56.87 | 103.87 | 56.87 | 0 | 0 | 0 | 292.05 | 47 | 0
2025-04-09 15:00 | 58.67 | 103.3 | 58.67 | 0 | 0 | 0 | 292.05 | 44.63 | 0
2025-04-09 16:00 | 57.29 | 95.73 | 57.29 | 0 | 0 | 0 | 292.05 | 38.44 | 0
2025-04-09 17:00 | 56.68 | 78.52 | 56.68 | 0 | 0 | 0 | 292.05 | 21.84 | 0
2025-04-09 18:00 | 55.18 | 11.82 | 11.82 | 0 | 0 | 43.36 | 246.41 | 0 | 0
2025-04-09 19:00 | 53.23 | 0 | 0 | 0 | 0 | 53.23 | 190.38 | 0 | 0
2025-04-09 20:00 | 51.64 | 0 | 0 | 0 | 0 | 51.64 | 136.01 | 0 | 0
2025-04-09 21:00 | 50.95 | 0 | 0 | 0 | 0 | 50.95 | 82.38 | 0 | 0
2025-04-09 22:00 | 48.41 | 0 | 0 | 0.97 | 0 | 47.44 | 32.45 | 0 | 0
2025-04-09 23:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 | 44.72 | 0 | 0 | 44.72 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 01:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 02:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 03:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 04:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 05:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 06:00 | 44.16 | 4.4 | 4.4 | 39.76 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 07:00 | 45.74 | 1.1 | 1.1 | 44.64 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 08:00 | 47.8 | 3.89 | 3.89 | 43.92 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 09:00 | 49.27 | 25.95 | 25.95 | 23.31 | 0 | 0 | 32.45 | 0 | 0
2025-04-10 10:00 | 50.43 | 110.24 | 110.24 | 0 | 59.81 | 0 | 89.27 | 0 | 0
2025-04-10 11:00 | 51.2 | 115.78 | 115.78 | 0 | 64.58 | 0 | 150.61 | 0 | 0
2025-04-10 12:00 | 53.2 | 112.86 | 112.86 | 0 | 59.66 | 0 | 207.29 | 0 | 0
2025-04-10 13:00 | 54.51 | 72.39 | 72.39 | 0 | 17.88 | 0 | 224.28 | 0 | 0
2025-04-10 14:00 | 53.88 | 56.82 | 56.82 | 0 | 2.94 | 0 | 227.07 | 0 | 0
2025-04-10 15:00 | 54.97 | 117.8 | 117.8 | 0 | 62.82 | 0 | 286.75 | 0 | 0
2025-04-10 16:00 | 54.65 | 84.24 | 60.23 | 0 | 5.58 | 0 | 292.05 | 24.01 | 0
2025-04-10 17:00 | 54.35 | 88.71 | 54.35 | 0 | 0 | 0 | 292.05 | 34.36 | 0
2025-04-10 18:00 | 53.58 | 16.08 | 16.08 | 0 | 0 | 37.5 | 252.57 | 0 | 0
2025-04-10 19:00 | 51.66 | 0 | 0 | 0 | 0 | 51.66 | 198.19 | 0 | 0
2025-04-10 20:00 | 49.82 | 0 | 0 | 0 | 0 | 49.82 | 145.75 | 0 | 0
2025-04-10 21:00 | 48.8 | 0 | 0 | 0 | 0 | 48.8 | 94.37 | 0 | 0
2025-04-10 22:00 | 47.87 | 0 | 0 | 0 | 0 | 47.87 | 43.98 | 0 | 0
2025-04-10 23:00 | 45.56 | 0 | 0 | 34.6 | 0 | 10.96 | 32.45 | 0 | 0
2025-04-11 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 32.45 | 0 | 0
2025-04-11 01:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 32.45 | 0 | 0
2025-04-11 02:00 | 43.54 | 0 | 0 | 43.54 | 0 | 0 | 32.45 | 0 | 0
2025-04-11 03:00 | 42.82 | 0 | 0 | 42.82 | 0 | 0 | 32.45 | 0 | 0
2025-04-11 04:00 | 43.05 | 0 | 0 | 43.05 | 0 | 0 | 32.45 | 0 | 0
2025-04-11 05:00 | 43.89 | 0 | 0 | 43.89 | 0 | 0 | 32.45 | 0 | 0
2025-04-11 06:00 | 44.86 | 24.54 | 24.54 | 20.33 | 0 | 0 | 32.45 | 0 | 0
2025-04-11 07:00 | 45.96 | 79.42 | 79.42 | 0 | 33.46 | 0 | 64.24 | 0 | 0
2025-04-11 08:00 | 47.73 | 105.97 | 105.97 | 0 | 58.24 | 0 | 119.56 | 0 | 0
2025-04-11 09:00 | 49.42 | 115.39 | 115.39 | 0 | 65.97 | 0 | 182.23 | 0 | 0
2025-04-11 10:00 | 52.74 | 101.85 | 101.85 | 0 | 49.11 | 0 | 228.89 | 0 | 0
2025-04-11 11:00 | 53.33 | 77.36 | 77.36 | 0 | 24.03 | 0 | 251.72 | 0 | 0
2025-04-11 12:00 | 54.2 | 82.59 | 82.59 | 0 | 28.39 | 0 | 278.69 | 0 | 0
2025-04-11 13:00 | 55.71 | 97.07 | 69.78 | 0 | 14.07 | 0 | 292.05 | 27.3 | 0
2025-04-11 14:00 | 55.62 | 80.71 | 55.62 | 0 | 0 | 0 | 292.05 | 25.08 | 0
2025-04-11 15:00 | 57.1 | 75.14 | 57.1 | 0 | 0 | 0 | 292.05 | 18.04 | 0
2025-04-11 16:00 | 55.8 | 56.58 | 55.8 | 0 | 0 | 0 | 292.05 | 0.79 | 0
2025-04-11 17:00 | 55.73 | 59.13 | 55.73 | 0 | 0 | 0 | 292.05 | 3.4 | 0
2025-04-11 18:00 | 54.97 | 11.73 | 11.73 | 0 | 0 | 43.24 | 246.53 | 0 | 0
2025-04-11 19:00 | 53.25 | 0 | 0 | 0 | 0 | 53.25 | 190.48 | 0 | 0
2025-04-11 20:00 | 51.47 | 0 | 0 | 0 | 0 | 51.47 | 136.31 | 0 | 0
2025-04-11 21:00 | 49.64 | 0 | 0 | 0 | 0 | 49.64 | 84.06 | 0 | 0
2025-04-11 22:00 | 47.78 | 0 | 0 | 0 | 0 | 47.78 | 33.76 | 0 | 0
2025-04-11 23:00 | 45.8 | 0 | 0 | 44.55 | 0 | 1.24 | 32.45 | 0 | 0
2025-04-12 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 32.45 | 0 | 0
2025-04-12 01:00 | 44.3 | 0 | 0 | 44.3 | 0 | 0 | 32.45 | 0 | 0
2025-04-12 02:00 | 42.74 | 0 | 0 | 42.74 | 0 | 0 | 32.45 | 0 | 0
2025-04-12 03:00 | 42.14 | 0 | 0 | 42.14 | 0 | 0 | 32.45 | 0 | 0
2025-04-12 04:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 32.45 | 0 | 0
2025-04-12 05:00 | 44.11 | 0 | 0 | 44.11 | 0 | 0 | 32.45 | 0 | 0
2025-04-12 06:00 | 45.16 | 20.01 | 20.01 | 25.16 | 0 | 0 | 32.45 | 0 | 0
2025-04-12 07:00 | 46.82 | 75.02 | 75.02 | 0 | 28.2 | 0 | 59.24 | 0 | 0
2025-04-12 08:00 | 48.5 | 119.78 | 119.77 | 0 | 71.27 | 0 | 126.95 | 0 | 0
2025-04-12 09:00 | 51.28 | 124.64 | 124.64 | 0 | 73.36 | 0 | 196.64 | 0 | 0
2025-04-12 10:00 | 53.14 | 122.32 | 122.32 | 0 | 69.17 | 0 | 262.35 | 0 | 0
2025-04-12 11:00 | 55.75 | 118.16 | 87.01 | 0 | 31.26 | 0 | 292.05 | 31.15 | 0
2025-04-12 12:00 | 58.52 | 115.65 | 58.52 | 0 | 0 | 0 | 292.05 | 57.13 | 0
2025-04-12 13:00 | 60.18 | 7.21 | 7.21 | 0 | 0 | 52.97 | 236.29 | 0 | 0
2025-04-12 14:00 | 60.35 | 53.97 | 53.97 | 0 | 0 | 6.37 | 229.58 | 0 | 0
2025-04-12 15:00 | 60.79 | 98.2 | 98.2 | 0 | 37.41 | 0 | 265.12 | 0 | 0
2025-04-12 16:00 | 60.89 | 118.28 | 89.24 | 0 | 28.35 | 0 | 292.05 | 29.04 | 0
2025-04-12 17:00 | 60.61 | 99.43 | 60.61 | 0 | 0 | 0 | 292.05 | 38.83 | 0
2025-04-12 18:00 | 57.08 | 20.2 | 20.2 | 0 | 0 | 36.88 | 253.22 | 0 | 0
2025-04-12 19:00 | 56.02 | 0 | 0 | 0 | 0 | 56.02 | 194.25 | 0 | 0
2025-04-12 20:00 | 52.78 | 0 | 0 | 0 | 0 | 52.78 | 138.7 | 0 | 0
2025-04-12 21:00 | 50.67 | 0 | 0 | 0 | 0 | 50.67 | 85.36 | 0 | 0
2025-04-12 22:00 | 48.45 | 0 | 0 | 0 | 0 | 48.45 | 34.36 | 0 | 0
2025-04-12 23:00 | 46.33 | 0 | 0 | 44.52 | 0 | 1.81 | 32.45 | 0 | 0
2025-04-13 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 32.45 | 0 | 0
2025-04-13 01:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 32.45 | 0 | 0
2025-04-13 02:00 | 42.65 | 0 | 0 | 42.65 | 0 | 0 | 32.45 | 0 | 0
2025-04-13 03:00 | 41.93 | 0 | 0 | 41.93 | 0 | 0 | 32.45 | 0 | 0
2025-04-13 04:00 | 43.31 | 0 | 0 | 43.31 | 0 | 0 | 32.45 | 0 | 0
2025-04-13 05:00 | 44.06 | 0 | 0 | 44.06 | 0 | 0 | 32.45 | 0 | 0
2025-04-13 06:00 | 45.3 | 30.47 | 30.47 | 14.84 | 0 | 0 | 32.45 | 0 | 0
2025-04-13 07:00 | 45.66 | 91.46 | 91.46 | 0 | 45.8 | 0 | 75.96 | 0 | 0
2025-04-13 08:00 | 48.35 | 108.65 | 108.65 | 0 | 60.3 | 0 | 133.24 | 0 | 0
2025-04-13 09:00 | 50.41 | 111.39 | 111.39 | 0 | 60.98 | 0 | 191.17 | 0 | 0
2025-04-13 10:00 | 51.4 | 108.26 | 108.26 | 0 | 56.86 | 0 | 245.18 | 0 | 0
2025-04-13 11:00 | 53.6 | 104.16 | 102.94 | 0 | 49.34 | 0 | 292.05 | 1.22 | 0
2025-04-13 12:00 | 54.97 | 104.1 | 54.97 | 0 | 0 | 0 | 292.05 | 49.13 | 0
2025-04-13 13:00 | 57.02 | 109 | 57.02 | 0 | 0 | 0 | 292.05 | 51.98 | 0
2025-04-13 14:00 | 57.73 | 112.54 | 57.73 | 0 | 0 | 0 | 292.05 | 54.8 | 0
2025-04-13 15:00 | 56.17 | 112.52 | 56.17 | 0 | 0 | 0 | 292.05 | 56.35 | 0
2025-04-13 16:00 | 58.02 | 109.05 | 58.02 | 0 | 0 | 0 | 292.05 | 51.03 | 0
2025-04-13 17:00 | 55.64 | 91.81 | 55.64 | 0 | 0 | 0 | 292.05 | 36.16 | 0
2025-04-13 18:00 | 55.51 | 18.04 | 18.04 | 0 | 0 | 37.47 | 252.61 | 0 | 0
2025-04-13 19:00 | 54.09 | 0 | 0 | 0 | 0 | 54.09 | 195.68 | 0 | 0
2025-04-13 20:00 | 51.42 | 0 | 0 | 0 | 0 | 51.42 | 141.55 | 0 | 0
2025-04-13 21:00 | 50.32 | 0 | 0 | 0 | 0 | 50.32 | 88.58 | 0 | 0
2025-04-13 22:00 | 48.15 | 0 | 0 | 0 | 0 | 48.15 | 37.9 | 0 | 0
2025-04-13 23:00 | 46.71 | 0 | 0 | 41.53 | 0 | 5.18 | 32.45 | 0 | 0
2025-04-14 | 45.22 | 0 | 0 | 45.22 | 0 | 0 | 32.45 | 0 | 0
2025-04-14 01:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 32.45 | 0 | 0
2025-04-14 02:00 | 43.09 | 0 | 0 | 43.09 | 0 | 0 | 32.45 | 0 | 0
2025-04-14 03:00 | 42.7 | 0 | 0 | 42.7 | 0 | 0 | 32.45 | 0 | 0
2025-04-14 04:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 32.45 | 0 | 0
2025-04-14 05:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 32.45 | 0 | 0
2025-04-14 06:00 | 45.47 | 16.71 | 16.71 | 28.75 | 0 | 0 | 32.45 | 0 | 0
2025-04-14 07:00 | 46.46 | 66.96 | 66.96 | 0 | 20.5 | 0 | 51.92 | 0 | 0
2025-04-14 08:00 | 48.29 | 82.55 | 82.55 | 0 | 34.26 | 0 | 84.47 | 0 | 0
2025-04-14 09:00 | 50.77 | 98.27 | 98.27 | 0 | 47.5 | 0 | 129.6 | 0 | 0
2025-04-14 10:00 | 53.05 | 105.36 | 105.36 | 0 | 52.31 | 0 | 179.29 | 0 | 0
2025-04-14 11:00 | 55.97 | 99.99 | 99.99 | 0 | 44.02 | 0 | 221.11 | 0 | 0
2025-04-14 12:00 | 58.01 | 96.77 | 96.77 | 0 | 38.76 | 0 | 257.93 | 0 | 0
2025-04-14 13:00 | 58.97 | 96.48 | 94.88 | 0 | 35.91 | 0 | 292.05 | 1.6 | 0
2025-04-14 14:00 | 60.73 | 80.36 | 60.73 | 0 | 0 | 0 | 292.05 | 19.63 | 0
2025-04-14 15:00 | 61.04 | 88.06 | 61.04 | 0 | 0 | 0 | 292.05 | 27.02 | 0
2025-04-14 16:00 | 60.14 | 63.55 | 60.14 | 0 | 0 | 0 | 292.05 | 3.41 | 0
2025-04-14 17:00 | 58.64 | 74.27 | 58.64 | 0 | 0 | 0 | 292.05 | 15.64 | 0
2025-04-14 18:00 | 58.31 | 17.53 | 17.53 | 0 | 0 | 40.78 | 249.12 | 0 | 0
2025-04-14 19:00 | 55.54 | 0 | 0 | 0 | 0 | 55.54 | 190.66 | 0 | 0
2025-04-14 20:00 | 53.42 | 0 | 0 | 0 | 0 | 53.42 | 134.42 | 0 | 0
2025-04-14 21:00 | 50.89 | 0 | 0 | 0 | 0 | 50.89 | 80.86 | 0 | 0
2025-04-14 22:00 | 48.37 | 0 | 0 | 2.39 | 0 | 45.98 | 32.45 | 0 | 0
2025-04-14 23:00 | 46.06 | 0 | 0 | 46.06 | 0 | 0 | 32.45 | 0 | 0
2025-04-15 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 32.45 | 0 | 0
2025-04-15 01:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 32.45 | 0 | 0
2025-04-15 02:00 | 44.71 | 0 | 0 | 44.71 | 0 | 0 | 32.45 | 0 | 0
2025-04-15 03:00 | 42.37 | 0 | 0 | 42.37 | 0 | 0 | 32.45 | 0 | 0
2025-04-15 04:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 32.45 | 0 | 0
2025-04-15 05:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 32.45 | 0 | 0
2025-04-15 06:00 | 45.92 | 32.3 | 32.3 | 13.62 | 0 | 0 | 32.45 | 0 | 0
2025-04-15 07:00 | 46.7 | 82.6 | 82.6 | 0 | 35.89 | 0 | 66.55 | 0 | 0
2025-04-15 08:00 | 48.65 | 97.7 | 97.7 | 0 | 49.05 | 0 | 113.15 | 0 | 0
2025-04-15 09:00 | 49.18 | 104.08 | 104.08 | 0 | 54.9 | 0 | 165.3 | 0 | 0
2025-04-15 10:00 | 51.41 | 101.77 | 101.77 | 0 | 50.36 | 0 | 213.14 | 0 | 0
2025-04-15 11:00 | 52.66 | 99.76 | 99.76 | 0 | 47.1 | 0 | 257.89 | 0 | 0
2025-04-15 12:00 | 53.44 | 100.93 | 89.39 | 0 | 35.96 | 0 | 292.05 | 11.53 | 0
2025-04-15 13:00 | 55.32 | 104.05 | 55.32 | 0 | 0 | 0 | 292.05 | 48.73 | 0
2025-04-15 14:00 | 54.67 | 106.25 | 54.67 | 0 | 0 | 0 | 292.05 | 51.59 | 0
2025-04-15 15:00 | 55.31 | 104.12 | 55.31 | 0 | 0 | 0 | 292.05 | 48.81 | 0
2025-04-15 16:00 | 55.52 | 100.34 | 55.52 | 0 | 0 | 0 | 292.05 | 44.81 | 0
2025-04-15 17:00 | 54.84 | 85.95 | 54.84 | 0 | 0 | 0 | 292.05 | 31.11 | 0
2025-04-15 18:00 | 54.58 | 19.53 | 19.53 | 0 | 0 | 35.05 | 255.15 | 0 | 0
2025-04-15 19:00 | 53.35 | 0 | 0 | 0 | 0 | 53.35 | 199 | 0 | 0
2025-04-15 20:00 | 52.19 | 0 | 0 | 0 | 0 | 52.19 | 144.06 | 0 | 0
2025-04-15 21:00 | 50.48 | 0 | 0 | 0 | 0 | 50.48 | 90.92 | 0 | 0
2025-04-15 22:00 | 48.94 | 0 | 0 | 0 | 0 | 48.94 | 39.41 | 0 | 0
2025-04-15 23:00 | 46.67 | 0 | 0 | 40.06 | 0 | 6.61 | 32.45 | 0 | 0
2025-04-16 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 01:00 | 44.36 | 0 | 0 | 44.36 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 02:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 03:00 | 42.84 | 0 | 0 | 42.84 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 04:00 | 43.14 | 0 | 0 | 43.14 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 05:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 06:00 | 45.56 | 9.12 | 9.12 | 36.44 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 07:00 | 46.93 | 19.7 | 19.7 | 27.22 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 08:00 | 48.51 | 30.65 | 30.65 | 17.86 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 09:00 | 50.5 | 53.51 | 53.51 | 0 | 3.01 | 0 | 35.31 | 0 | 0
2025-04-16 10:00 | 52.2 | 58.5 | 58.5 | 0 | 6.3 | 0 | 41.3 | 0 | 0
2025-04-16 11:00 | 55.11 | 54.2 | 54.2 | 0 | 0 | 0.91 | 40.35 | 0 | 0
2025-04-16 12:00 | 56.2 | 42.96 | 42.96 | 5.74 | 0 | 7.5 | 32.45 | 0 | 0
2025-04-16 13:00 | 56.91 | 48.5 | 48.5 | 8.41 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 14:00 | 58.48 | 46.21 | 46.21 | 12.27 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 15:00 | 58.05 | 32.68 | 32.68 | 25.37 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 16:00 | 57.38 | 17.82 | 17.82 | 39.55 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 17:00 | 57.85 | 7.45 | 7.45 | 50.4 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 18:00 | 55.9 | 0 | 0 | 55.9 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 19:00 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 20:00 | 52.82 | 0 | 0 | 52.82 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 21:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 22:00 | 48.85 | 0 | 0 | 48.85 | 0 | 0 | 32.45 | 0 | 0
2025-04-16 23:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 32.45 | 0 | 0
2025-04-17 | 45.73 | 0 | 0 | 45.73 | 0 | 0 | 32.45 | 0 | 0
2025-04-17 01:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 32.45 | 0 | 0
2025-04-17 02:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 32.45 | 0 | 0
2025-04-17 03:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 32.45 | 0 | 0
2025-04-17 04:00 | 42.32 | 0 | 0 | 42.32 | 0 | 0 | 32.45 | 0 | 0
2025-04-17 05:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 32.45 | 0 | 0
2025-04-17 06:00 | 46.43 | 45.29 | 45.29 | 1.15 | 0 | 0 | 32.45 | 0 | 0
2025-04-17 07:00 | 47.8 | 109.23 | 109.23 | 0 | 61.43 | 0 | 90.81 | 0 | 0
2025-04-17 08:00 | 49.66 | 121.48 | 121.48 | 0 | 71.83 | 0 | 159.04 | 0 | 0
2025-04-17 09:00 | 50 | 122.78 | 122.78 | 0 | 72.77 | 0 | 228.18 | 0 | 0
2025-04-17 10:00 | 52.64 | 120.02 | 119.88 | 0 | 67.23 | 0 | 292.05 | 0.14 | 0
2025-04-17 11:00 | 53.31 | 115.97 | 53.31 | 0 | 0 | 0 | 292.05 | 62.66 | 0
2025-04-17 12:00 | 54.99 | 113.86 | 54.99 | 0 | 0 | 0 | 292.05 | 58.87 | 0
2025-04-17 13:00 | 55.12 | 116.57 | 55.12 | 0 | 0 | 0 | 292.05 | 61.45 | 0
2025-04-17 14:00 | 55.98 | 119.92 | 55.98 | 0 | 0 | 0 | 292.05 | 63.94 | 0
2025-04-17 15:00 | 56.14 | 122.41 | 56.14 | 0 | 0 | 0 | 292.05 | 66.26 | 0
2025-04-17 16:00 | 56.75 | 119.24 | 56.75 | 0 | 0 | 0 | 292.05 | 62.49 | 0
2025-04-17 17:00 | 56.16 | 104.54 | 56.16 | 0 | 0 | 0 | 292.05 | 48.38 | 0
2025-04-17 18:00 | 55.01 | 28.57 | 28.57 | 0 | 0 | 26.44 | 264.22 | 0 | 0
2025-04-17 19:00 | 52.99 | 0 | 0 | 0 | 0 | 52.99 | 208.44 | 0 | 0
2025-04-17 20:00 | 52.03 | 0 | 0 | 0 | 0 | 52.03 | 153.66 | 0 | 0
2025-04-17 21:00 | 50.14 | 0 | 0 | 0 | 0 | 50.14 | 100.89 | 0 | 0
2025-04-17 22:00 | 49.18 | 0 | 0 | 0 | 0 | 49.18 | 49.12 | 0 | 0
2025-04-17 23:00 | 47.6 | 0 | 0 | 31.77 | 0 | 15.84 | 32.45 | 0 | 0
2025-04-18 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 32.45 | 0 | 0
2025-04-18 01:00 | 44 | 0 | 0 | 44 | 0 | 0 | 32.45 | 0 | 0
2025-04-18 02:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 32.45 | 0 | 0
2025-04-18 03:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 32.45 | 0 | 0
2025-04-18 04:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 32.45 | 0 | 0
2025-04-18 05:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 32.45 | 0 | 0
2025-04-18 06:00 | 45.28 | 43.09 | 43.09 | 2.19 | 0 | 0 | 32.45 | 0 | 0
2025-04-18 07:00 | 48.12 | 100.64 | 100.64 | 0 | 52.52 | 0 | 82.34 | 0 | 0
2025-04-18 08:00 | 49.81 | 114.46 | 114.46 | 0 | 64.65 | 0 | 143.76 | 0 | 0
2025-04-18 09:00 | 51.18 | 116.71 | 116.71 | 0 | 65.52 | 0 | 206.01 | 0 | 0
2025-04-18 10:00 | 52.98 | 114.77 | 114.77 | 0 | 61.79 | 0 | 264.71 | 0 | 0
2025-04-18 11:00 | 54.86 | 111.24 | 83.64 | 0 | 28.78 | 0 | 292.05 | 27.6 | 0
2025-04-18 12:00 | 56.55 | 107.8 | 56.55 | 0 | 0 | 0 | 292.05 | 51.24 | 0
2025-04-18 13:00 | 58.39 | 109.37 | 58.39 | 0 | 0 | 0 | 292.05 | 50.98 | 0
2025-04-18 14:00 | 58.52 | 112.67 | 58.52 | 0 | 0 | 0 | 292.05 | 54.16 | 0
2025-04-18 15:00 | 58.91 | 114.32 | 58.91 | 0 | 0 | 0 | 292.05 | 55.4 | 0
2025-04-18 16:00 | 58.89 | 107.97 | 58.89 | 0 | 0 | 0 | 292.05 | 49.08 | 0
2025-04-18 17:00 | 57 | 90.16 | 57 | 0 | 0 | 0 | 292.05 | 33.15 | 0
2025-04-18 18:00 | 56.82 | 25.3 | 25.3 | 0 | 0 | 31.52 | 258.87 | 0 | 0
2025-04-18 19:00 | 54.78 | 0 | 0 | 0 | 0 | 54.78 | 201.21 | 0 | 0
2025-04-18 20:00 | 51.87 | 0 | 0 | 0 | 0 | 51.87 | 146.61 | 0 | 0
2025-04-18 21:00 | 50.11 | 0 | 0 | 0 | 0 | 50.11 | 93.87 | 0 | 0
2025-04-18 22:00 | 48.67 | 0 | 0 | 0 | 0 | 48.67 | 42.63 | 0 | 0
2025-04-18 23:00 | 47.56 | 0 | 0 | 37.89 | 0 | 9.67 | 32.45 | 0 | 0
2025-04-19 | 45.94 | 0 | 0 | 45.94 | 0 | 0 | 32.45 | 0 | 0
2025-04-19 01:00 | 44.63 | 0 | 0 | 44.63 | 0 | 0 | 32.45 | 0 | 0
2025-04-19 02:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 32.45 | 0 | 0
2025-04-19 03:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 32.45 | 0 | 0
2025-04-19 04:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 32.45 | 0 | 0
2025-04-19 05:00 | 44.69 | 0 | 0 | 44.69 | 0 | 0 | 32.45 | 0 | 0
2025-04-19 06:00 | 45.52 | 16.34 | 16.34 | 29.17 | 0 | 0 | 32.45 | 0 | 0
2025-04-19 07:00 | 47.7 | 37.04 | 37.04 | 10.66 | 0 | 0 | 32.45 | 0 | 0
2025-04-19 08:00 | 49.06 | 49.3 | 49.3 | 0 | 0.24 | 0 | 32.68 | 0 | 0
2025-04-19 09:00 | 52.97 | 56.09 | 56.09 | 0 | 3.12 | 0 | 35.64 | 0 | 0
2025-04-19 10:00 | 54.41 | 86.83 | 86.83 | 0 | 32.42 | 0 | 66.44 | 0 | 0
2025-04-19 11:00 | 58.16 | 78.73 | 78.73 | 0 | 20.57 | 0 | 85.98 | 0 | 0
2025-04-19 12:00 | 59.24 | 88.4 | 88.4 | 0 | 29.16 | 0 | 113.68 | 0 | 0
2025-04-19 13:00 | 61.43 | 104.92 | 104.92 | 0 | 43.49 | 0 | 154.99 | 0 | 0
2025-04-19 14:00 | 61.95 | 108.09 | 108.09 | 0 | 46.14 | 0 | 198.82 | 0 | 0
2025-04-19 15:00 | 62.33 | 108.74 | 108.74 | 0 | 46.42 | 0 | 242.92 | 0 | 0
2025-04-19 16:00 | 61.68 | 125.09 | 113.4 | 0 | 51.72 | 0 | 292.05 | 11.69 | 0
2025-04-19 17:00 | 60.98 | 114.33 | 60.98 | 0 | 0 | 0 | 292.05 | 53.35 | 0
2025-04-19 18:00 | 59.42 | 37.37 | 37.37 | 0 | 0 | 22.05 | 268.84 | 0 | 0
2025-04-19 19:00 | 56.75 | 0 | 0 | 0 | 0 | 56.75 | 209.1 | 0 | 0
2025-04-19 20:00 | 54.69 | 0 | 0 | 0 | 0 | 54.69 | 151.53 | 0 | 0
2025-04-19 21:00 | 51.96 | 0 | 0 | 0 | 0 | 51.96 | 96.84 | 0 | 0
2025-04-19 22:00 | 51 | 0 | 0 | 0 | 0 | 51 | 43.15 | 0 | 0
2025-04-19 23:00 | 47.64 | 0 | 0 | 37.48 | 0 | 10.17 | 32.45 | 0 | 0
2025-04-20 | 46.65 | 0 | 0 | 46.65 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 01:00 | 44.55 | 0 | 0 | 44.55 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 02:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 03:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 04:00 | 43.61 | 0 | 0 | 43.61 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 05:00 | 44.75 | 0.3 | 0.3 | 44.45 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 06:00 | 46.67 | 4.54 | 4.54 | 42.12 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 07:00 | 47.5 | 74.82 | 74.82 | 0 | 27.33 | 0 | 58.41 | 0 | 0
2025-04-20 08:00 | 49.69 | 123.97 | 123.97 | 0 | 74.27 | 0 | 128.97 | 0 | 0
2025-04-20 09:00 | 50.89 | 108.04 | 108.04 | 0 | 57.15 | 0 | 183.27 | 0 | 0
2025-04-20 10:00 | 52.78 | 104.14 | 104.14 | 0 | 51.37 | 0 | 232.07 | 0 | 0
2025-04-20 11:00 | 53.08 | 38.85 | 38.85 | 0 | 0 | 14.23 | 217.08 | 0 | 0
2025-04-20 12:00 | 55.17 | 74.9 | 74.9 | 0 | 19.74 | 0 | 235.83 | 0 | 0
2025-04-20 13:00 | 54.32 | 130.93 | 113.49 | 0 | 59.18 | 0 | 292.05 | 17.44 | 0
2025-04-20 14:00 | 54.51 | 45.84 | 45.84 | 0 | 0 | 8.67 | 282.92 | 0 | 0
2025-04-20 15:00 | 54.4 | 5.91 | 5.91 | 0 | 0 | 48.49 | 231.88 | 0 | 0
2025-04-20 16:00 | 56.06 | 3.85 | 3.85 | 0 | 0 | 52.21 | 176.92 | 0 | 0
2025-04-20 17:00 | 54.97 | 1.73 | 1.73 | 0 | 0 | 53.24 | 120.88 | 0 | 0
2025-04-20 18:00 | 53.8 | 0 | 0 | 0 | 0 | 53.8 | 64.25 | 0 | 0
2025-04-20 19:00 | 53.73 | 0 | 0 | 23.53 | 0 | 30.21 | 32.45 | 0 | 0
2025-04-20 20:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 21:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 22:00 | 48.23 | 0 | 0 | 48.23 | 0 | 0 | 32.45 | 0 | 0
2025-04-20 23:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 32.45 | 0 | 0
2025-04-21 | 45.94 | 0 | 0 | 45.94 | 0 | 0 | 32.45 | 0 | 0
2025-04-21 01:00 | 43.83 | 0 | 0 | 43.83 | 0 | 0 | 32.45 | 0 | 0
2025-04-21 02:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 32.45 | 0 | 0
2025-04-21 03:00 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 32.45 | 0 | 0
2025-04-21 04:00 | 44.34 | 0 | 0 | 44.34 | 0 | 0 | 32.45 | 0 | 0
2025-04-21 05:00 | 45.99 | 0.12 | 0.12 | 45.88 | 0 | 0 | 32.45 | 0 | 0
2025-04-21 06:00 | 46 | 47.49 | 47.49 | 0 | 1.49 | 0 | 33.87 | 0 | 0
2025-04-21 07:00 | 47.76 | 100.95 | 100.95 | 0 | 53.2 | 0 | 84.4 | 0 | 0
2025-04-21 08:00 | 50.15 | 113.68 | 113.68 | 0 | 63.54 | 0 | 144.76 | 0 | 0
2025-04-21 09:00 | 52.91 | 118.91 | 118.91 | 0 | 66 | 0 | 207.46 | 0 | 0
2025-04-21 10:00 | 54.5 | 114.88 | 114.88 | 0 | 60.38 | 0 | 264.83 | 0 | 0
2025-04-21 11:00 | 56.71 | 111.38 | 85.36 | 0 | 28.66 | 0 | 292.05 | 26.01 | 0
2025-04-21 12:00 | 59.51 | 109.34 | 59.51 | 0 | 0 | 0 | 292.05 | 49.83 | 0
2025-04-21 13:00 | 60.69 | 110.78 | 60.69 | 0 | 0 | 0 | 292.05 | 50.09 | 0
2025-04-21 14:00 | 60.45 | 113.69 | 60.45 | 0 | 0 | 0 | 292.05 | 53.25 | 0
2025-04-21 15:00 | 61.18 | 116.1 | 61.18 | 0 | 0 | 0 | 292.05 | 54.92 | 0
2025-04-21 16:00 | 62.22 | 110.88 | 62.22 | 0 | 0 | 0 | 292.05 | 48.66 | 0
2025-04-21 17:00 | 60.7 | 95.24 | 60.7 | 0 | 0 | 0 | 292.05 | 34.54 | 0
2025-04-21 18:00 | 58.6 | 31.33 | 31.33 | 0 | 0 | 27.27 | 263.34 | 0 | 0
2025-04-21 19:00 | 56.94 | 0 | 0 | 0 | 0 | 56.94 | 203.41 | 0 | 0
2025-04-21 20:00 | 54.78 | 0 | 0 | 0 | 0 | 54.78 | 145.74 | 0 | 0
2025-04-21 21:00 | 52.78 | 0 | 0 | 0 | 0 | 52.78 | 90.18 | 0 | 0
2025-04-21 22:00 | 49.41 | 0 | 0 | 0 | 0 | 49.41 | 38.17 | 0 | 0
2025-04-21 23:00 | 47.54 | 0 | 0 | 42.11 | 0 | 5.44 | 32.45 | 0 | 0
2025-04-22 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 32.45 | 0 | 0
2025-04-22 01:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 32.45 | 0 | 0
2025-04-22 02:00 | 44.39 | 0 | 0 | 44.39 | 0 | 0 | 32.45 | 0 | 0
2025-04-22 03:00 | 43.2 | 0 | 0 | 43.2 | 0 | 0 | 32.45 | 0 | 0
2025-04-22 04:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 32.45 | 0 | 0
2025-04-22 05:00 | 45.5 | 0.22 | 0.22 | 45.28 | 0 | 0 | 32.45 | 0 | 0
2025-04-22 06:00 | 46.56 | 45.42 | 45.42 | 1.14 | 0 | 0 | 32.45 | 0 | 0
2025-04-22 07:00 | 48.17 | 91.78 | 91.78 | 0 | 43.6 | 0 | 73.87 | 0 | 0
2025-04-22 08:00 | 50.16 | 106.11 | 106.11 | 0 | 55.95 | 0 | 127.03 | 0 | 0
2025-04-22 09:00 | 52.07 | 112.73 | 112.73 | 0 | 60.66 | 0 | 184.66 | 0 | 0
2025-04-22 10:00 | 54.76 | 111.17 | 111.17 | 0 | 56.42 | 0 | 238.25 | 0 | 0
2025-04-22 11:00 | 57.59 | 102.94 | 102.94 | 0 | 45.35 | 0 | 281.34 | 0 | 0
2025-04-22 12:00 | 58.78 | 101.28 | 70.06 | 0 | 11.27 | 0 | 292.05 | 31.22 | 0
2025-04-22 13:00 | 59.85 | 97.88 | 59.85 | 0 | 0 | 0 | 292.05 | 38.03 | 0
2025-04-22 14:00 | 60.97 | 100.24 | 60.97 | 0 | 0 | 0 | 292.05 | 39.28 | 0
2025-04-22 15:00 | 61.63 | 96.38 | 61.63 | 0 | 0 | 0 | 292.05 | 34.76 | 0
2025-04-22 16:00 | 61.03 | 87.69 | 61.03 | 0 | 0 | 0 | 292.05 | 26.66 | 0
2025-04-22 17:00 | 60.54 | 70.73 | 60.54 | 0 | 0 | 0 | 292.05 | 10.19 | 0
2025-04-22 18:00 | 59.1 | 26.9 | 26.9 | 0 | 0 | 32.2 | 258.15 | 0 | 0
2025-04-22 19:00 | 57.41 | 0 | 0 | 0 | 0 | 57.41 | 197.72 | 0 | 0
2025-04-22 20:00 | 55.5 | 0 | 0 | 0 | 0 | 55.5 | 139.3 | 0 | 0
2025-04-22 21:00 | 52.99 | 0 | 0 | 0 | 0 | 52.99 | 83.53 | 0 | 0
2025-04-22 22:00 | 49.74 | 0 | 0 | 1.22 | 0 | 48.52 | 32.45 | 0 | 0
2025-04-22 23:00 | 47.65 | 0 | 0 | 47.65 | 0 | 0 | 32.45 | 0 | 0
2025-04-23 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 32.45 | 0 | 0
2025-04-23 01:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 32.45 | 0 | 0
2025-04-23 02:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 32.45 | 0 | 0
2025-04-23 03:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 32.45 | 0 | 0
2025-04-23 04:00 | 44 | 0 | 0 | 44 | 0 | 0 | 32.45 | 0 | 0
2025-04-23 05:00 | 44.75 | 0.55 | 0.55 | 44.2 | 0 | 0 | 32.45 | 0 | 0
2025-04-23 06:00 | 46.26 | 49.69 | 49.69 | 0 | 3.43 | 0 | 35.71 | 0 | 0
2025-04-23 07:00 | 48.71 | 79.56 | 79.56 | 0 | 30.85 | 0 | 65.02 | 0 | 0
2025-04-23 08:00 | 50.15 | 92.56 | 92.56 | 0 | 42.4 | 0 | 105.31 | 0 | 0
2025-04-23 09:00 | 53.3 | 75.06 | 75.06 | 0 | 21.76 | 0 | 125.97 | 0 | 0
2025-04-23 10:00 | 54.11 | 85.03 | 85.03 | 0 | 30.92 | 0 | 155.35 | 0 | 0
2025-04-23 11:00 | 55.64 | 98.81 | 98.81 | 0 | 43.17 | 0 | 196.36 | 0 | 0
2025-04-23 12:00 | 57.26 | 96.7 | 96.7 | 0 | 39.43 | 0 | 233.82 | 0 | 0
2025-04-23 13:00 | 58.49 | 99.07 | 99.07 | 0 | 40.57 | 0 | 272.37 | 0 | 0
2025-04-23 14:00 | 59.26 | 108.41 | 79.98 | 0 | 20.72 | 0 | 292.05 | 28.43 | 0
2025-04-23 15:00 | 60.32 | 110.96 | 60.32 | 0 | 0 | 0 | 292.05 | 50.64 | 0
2025-04-23 16:00 | 58.62 | 111.21 | 58.62 | 0 | 0 | 0 | 292.05 | 52.58 | 0
2025-04-23 17:00 | 58.79 | 81.47 | 58.79 | 0 | 0 | 0 | 292.05 | 22.68 | 0
2025-04-23 18:00 | 57.36 | 21.24 | 21.24 | 0 | 0 | 36.13 | 254.02 | 0 | 0
2025-04-23 19:00 | 55 | 0 | 0 | 0 | 0 | 55 | 196.12 | 0 | 0
2025-04-23 20:00 | 54.41 | 0 | 0 | 0 | 0 | 54.41 | 138.85 | 0 | 0
2025-04-23 21:00 | 52.7 | 0 | 0 | 0 | 0 | 52.7 | 83.38 | 0 | 0
2025-04-23 22:00 | 49.62 | 0 | 0 | 1.24 | 0 | 48.38 | 32.45 | 0 | 0
2025-04-23 23:00 | 48.12 | 0 | 0 | 48.12 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 | 45.65 | 0 | 0 | 45.65 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 01:00 | 44.58 | 0 | 0 | 44.58 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 02:00 | 44.89 | 0 | 0 | 44.89 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 03:00 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 04:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 05:00 | 45.33 | 0 | 0 | 45.33 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 06:00 | 46.25 | 13.97 | 13.97 | 32.29 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 07:00 | 47.89 | 74.62 | 74.62 | 0 | 26.72 | 0 | 57.84 | 0 | 0
2025-04-24 08:00 | 50.25 | 77.86 | 77.86 | 0 | 27.6 | 0 | 84.06 | 0 | 0
2025-04-24 09:00 | 51.04 | 48.69 | 48.69 | 0 | 0 | 2.34 | 81.59 | 0 | 0
2025-04-24 10:00 | 52.75 | 53.23 | 53.23 | 0 | 0.48 | 0 | 82.05 | 0 | 0
2025-04-24 11:00 | 54.62 | 34.9 | 34.9 | 0 | 0 | 19.72 | 61.29 | 0 | 0
2025-04-24 12:00 | 56.08 | 33.08 | 33.08 | 0 | 0 | 23 | 37.08 | 0 | 0
2025-04-24 13:00 | 56.95 | 21.18 | 21.18 | 31.37 | 0 | 4.4 | 32.45 | 0 | 0
2025-04-24 14:00 | 56.44 | 43.72 | 43.72 | 12.71 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 15:00 | 57.38 | 36.54 | 36.54 | 20.84 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 16:00 | 56.38 | 27.1 | 27.1 | 29.27 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 17:00 | 57.25 | 5.02 | 5.02 | 52.23 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 18:00 | 55.03 | 0 | 0 | 55.03 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 19:00 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 20:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 21:00 | 52.63 | 0 | 0 | 52.63 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 22:00 | 50.18 | 0 | 0 | 50.18 | 0 | 0 | 32.45 | 0 | 0
2025-04-24 23:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 | 46.51 | 0 | 0 | 46.51 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 01:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 02:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 03:00 | 44.16 | 0 | 0 | 44.16 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 04:00 | 44.52 | 0 | 0 | 44.52 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 05:00 | 45.75 | 0.08 | 0.08 | 45.67 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 06:00 | 46.84 | 8.5 | 8.5 | 38.34 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 07:00 | 47.95 | 52.54 | 52.54 | 0 | 4.58 | 0 | 36.8 | 0 | 0
2025-04-25 08:00 | 50.33 | 51.1 | 51.1 | 0 | 0.77 | 0 | 37.54 | 0 | 0
2025-04-25 09:00 | 53.15 | 29.38 | 29.38 | 18.93 | 0 | 4.83 | 32.45 | 0 | 0
2025-04-25 10:00 | 55.94 | 40.62 | 40.62 | 15.32 | 0 | 0 | 32.45 | 0 | 0
2025-04-25 11:00 | 58.29 | 91.98 | 91.98 | 0 | 33.69 | 0 | 64.45 | 0 | 0
2025-04-25 12:00 | 59.73 | 95.89 | 95.89 | 0 | 36.16 | 0 | 98.8 | 0 | 0
2025-04-25 13:00 | 60.91 | 122.74 | 122.74 | 0 | 61.83 | 0 | 157.54 | 0 | 0
2025-04-25 14:00 | 62.04 | 125.1 | 125.1 | 0 | 63.06 | 0 | 217.45 | 0 | 0
2025-04-25 15:00 | 61.64 | 125.04 | 125.04 | 0 | 63.4 | 0 | 277.68 | 0 | 0
2025-04-25 16:00 | 61.59 | 99.31 | 76.72 | 0 | 15.13 | 0 | 292.05 | 22.59 | 0
2025-04-25 17:00 | 60.36 | 101.78 | 60.36 | 0 | 0 | 0 | 292.05 | 41.42 | 0
2025-04-25 18:00 | 58.72 | 37.49 | 37.49 | 0 | 0 | 21.23 | 269.7 | 0 | 0
2025-04-25 19:00 | 57.65 | 0 | 0 | 0 | 0 | 57.65 | 209.01 | 0 | 0
2025-04-25 20:00 | 55.43 | 0 | 0 | 0 | 0 | 55.43 | 150.67 | 0 | 0
2025-04-25 21:00 | 53.37 | 0 | 0 | 0 | 0 | 53.37 | 94.49 | 0 | 0
2025-04-25 22:00 | 51.01 | 0 | 0 | 0 | 0 | 51.01 | 40.8 | 0 | 0
2025-04-25 23:00 | 48.72 | 0 | 0 | 40.79 | 0 | 7.93 | 32.45 | 0 | 0
2025-04-26 | 47.17 | 0 | 0 | 47.17 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 01:00 | 45.49 | 0 | 0 | 45.49 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 02:00 | 44.84 | 0 | 0 | 44.84 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 03:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 04:00 | 44.81 | 0 | 0 | 44.81 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 05:00 | 45.84 | 0.78 | 0.78 | 45.06 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 06:00 | 46.55 | 8.81 | 8.81 | 37.74 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 07:00 | 48.68 | 11.62 | 11.62 | 37.06 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 08:00 | 50.36 | 38.69 | 38.69 | 11.67 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 09:00 | 52.51 | 47.36 | 47.36 | 5.15 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 10:00 | 54.26 | 68.33 | 68.33 | 0 | 14.07 | 0 | 45.82 | 0 | 0
2025-04-26 11:00 | 57.31 | 101.8 | 101.8 | 0 | 44.5 | 0 | 88.09 | 0 | 0
2025-04-26 12:00 | 58.77 | 101 | 101 | 0 | 42.23 | 0 | 128.2 | 0 | 0
2025-04-26 13:00 | 59.67 | 84.31 | 84.31 | 0 | 24.64 | 0 | 151.61 | 0 | 0
2025-04-26 14:00 | 61.11 | 94.76 | 94.76 | 0 | 33.64 | 0 | 183.57 | 0 | 0
2025-04-26 15:00 | 60.28 | 86.27 | 86.27 | 0 | 25.99 | 0 | 208.26 | 0 | 0
2025-04-26 16:00 | 61.64 | 57.22 | 57.22 | 0 | 0 | 4.43 | 203.6 | 0 | 0
2025-04-26 17:00 | 59.29 | 20.34 | 20.34 | 0 | 0 | 38.95 | 162.6 | 0 | 0
2025-04-26 18:00 | 58.36 | 4.79 | 4.79 | 0 | 0 | 53.57 | 106.21 | 0 | 0
2025-04-26 19:00 | 56.48 | 0 | 0 | 0 | 0 | 56.48 | 46.76 | 0 | 0
2025-04-26 20:00 | 55.01 | 0 | 0 | 41.41 | 0 | 13.6 | 32.45 | 0 | 0
2025-04-26 21:00 | 53.19 | 0 | 0 | 53.19 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 22:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 32.45 | 0 | 0
2025-04-26 23:00 | 49.54 | 0 | 0 | 49.54 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 01:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 02:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 03:00 | 44.67 | 0 | 0 | 44.67 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 04:00 | 44.7 | 0 | 0 | 44.7 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 05:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 06:00 | 46.71 | 0.14 | 0.14 | 46.57 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 07:00 | 50.32 | 25.36 | 25.36 | 24.96 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 08:00 | 51.07 | 44.59 | 44.59 | 6.48 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 09:00 | 52.88 | 98.32 | 98.32 | 0 | 45.45 | 0 | 75.63 | 0 | 0
2025-04-27 10:00 | 55.68 | 65.37 | 65.37 | 0 | 9.69 | 0 | 84.83 | 0 | 0
2025-04-27 11:00 | 58.29 | 82.57 | 82.57 | 0 | 24.27 | 0 | 107.89 | 0 | 0
2025-04-27 12:00 | 60.57 | 59.87 | 59.87 | 0 | 0 | 0.7 | 107.15 | 0 | 0
2025-04-27 13:00 | 62.11 | 52.63 | 52.63 | 0 | 0 | 9.48 | 97.18 | 0 | 0
2025-04-27 14:00 | 63.14 | 38.83 | 38.83 | 0 | 0 | 24.3 | 71.6 | 0 | 0
2025-04-27 15:00 | 62.8 | 55.97 | 55.97 | 0 | 0 | 6.83 | 64.41 | 0 | 0
2025-04-27 16:00 | 62.97 | 57.33 | 57.33 | 0 | 0 | 5.63 | 58.48 | 0 | 0
2025-04-27 17:00 | 61.39 | 86.82 | 86.82 | 0 | 25.43 | 0 | 82.63 | 0 | 0
2025-04-27 18:00 | 59.99 | 34.56 | 34.56 | 0 | 0 | 25.43 | 55.87 | 0 | 0
2025-04-27 19:00 | 57.86 | 0 | 0 | 35.61 | 0 | 22.25 | 32.45 | 0 | 0
2025-04-27 20:00 | 55.44 | 0 | 0 | 55.44 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 21:00 | 54.14 | 0 | 0 | 54.14 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 22:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 32.45 | 0 | 0
2025-04-27 23:00 | 49.47 | 0 | 0 | 49.47 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 | 47.26 | 0 | 0 | 47.26 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 01:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 02:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 03:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 04:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 05:00 | 46.11 | 0.67 | 0.67 | 45.44 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 06:00 | 47.43 | 17.9 | 17.9 | 29.53 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 07:00 | 48.62 | 37.07 | 37.07 | 11.55 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 08:00 | 50.56 | 59.88 | 59.88 | 0 | 9.32 | 0 | 41.31 | 0 | 0
2025-04-28 09:00 | 53.3 | 100.35 | 100.35 | 0 | 47.05 | 0 | 86.01 | 0 | 0
2025-04-28 10:00 | 56.29 | 115.48 | 115.48 | 0 | 59.19 | 0 | 142.24 | 0 | 0
2025-04-28 11:00 | 58.55 | 98.48 | 98.48 | 0 | 39.93 | 0 | 180.17 | 0 | 0
2025-04-28 12:00 | 59.41 | 64.34 | 64.34 | 0 | 4.93 | 0 | 184.85 | 0 | 0
2025-04-28 13:00 | 61.05 | 60.28 | 60.28 | 0 | 0 | 0.77 | 184.05 | 0 | 0
2025-04-28 14:00 | 62.09 | 61.82 | 61.82 | 0 | 0 | 0.27 | 183.77 | 0 | 0
2025-04-28 15:00 | 62.58 | 33.16 | 33.16 | 0 | 0 | 29.43 | 152.79 | 0 | 0
2025-04-28 16:00 | 61.77 | 21.09 | 21.09 | 0 | 0 | 40.68 | 109.97 | 0 | 0
2025-04-28 17:00 | 60.83 | 1.11 | 1.11 | 0 | 0 | 59.72 | 47.11 | 0 | 0
2025-04-28 18:00 | 59.68 | 0 | 0 | 45.76 | 0 | 13.93 | 32.45 | 0 | 0
2025-04-28 19:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 20:00 | 55.42 | 0 | 0 | 55.42 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 21:00 | 53.6 | 0 | 0 | 53.6 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 22:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 32.45 | 0 | 0
2025-04-28 23:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 32.45 | 0 | 0
2025-04-29 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 32.45 | 0 | 0
2025-04-29 01:00 | 46.48 | 0 | 0 | 46.48 | 0 | 0 | 32.45 | 0 | 0
2025-04-29 02:00 | 44.82 | 0 | 0 | 44.82 | 0 | 0 | 32.45 | 0 | 0
2025-04-29 03:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 32.45 | 0 | 0
2025-04-29 04:00 | 45.61 | 0 | 0 | 45.61 | 0 | 0 | 32.45 | 0 | 0
2025-04-29 05:00 | 45.81 | 1.33 | 1.33 | 44.48 | 0 | 0 | 32.45 | 0 | 0
2025-04-29 06:00 | 48.06 | 28.37 | 28.37 | 19.69 | 0 | 0 | 32.45 | 0 | 0
2025-04-29 07:00 | 49.83 | 84.62 | 84.62 | 0 | 34.79 | 0 | 65.5 | 0 | 0
2025-04-29 08:00 | 52.05 | 46.47 | 46.47 | 0 | 0 | 5.58 | 59.63 | 0 | 0
2025-04-29 09:00 | 55.42 | 65.39 | 65.39 | 0 | 9.98 | 0 | 69.11 | 0 | 0
2025-04-29 10:00 | 58.48 | 107.99 | 107.99 | 0 | 49.52 | 0 | 116.15 | 0 | 0
2025-04-29 11:00 | 61.91 | 71.76 | 71.76 | 0 | 9.85 | 0 | 125.5 | 0 | 0
2025-04-29 12:00 | 63.9 | 96.4 | 96.4 | 0 | 32.51 | 0 | 156.39 | 0 | 0
2025-04-29 13:00 | 66.39 | 107.24 | 107.24 | 0 | 40.84 | 0 | 195.19 | 0 | 0
2025-04-29 14:00 | 67.76 | 122.04 | 122.04 | 0 | 54.28 | 0 | 246.75 | 0 | 0
2025-04-29 15:00 | 68.63 | 121.78 | 116.31 | 0 | 47.68 | 0 | 292.05 | 5.46 | 0
2025-04-29 16:00 | 67.28 | 118.85 | 67.28 | 0 | 0 | 0 | 292.05 | 51.57 | 0
2025-04-29 17:00 | 66.88 | 100.12 | 66.88 | 0 | 0 | 0 | 292.05 | 33.24 | 0
2025-04-29 18:00 | 64.4 | 40.38 | 40.38 | 0 | 0 | 24.02 | 266.76 | 0 | 0
2025-04-29 19:00 | 60.74 | 0 | 0 | 0 | 0 | 60.74 | 202.82 | 0 | 0
2025-04-29 20:00 | 58.92 | 0 | 0 | 0 | 0 | 58.92 | 140.8 | 0 | 0
2025-04-29 21:00 | 56.3 | 0 | 0 | 0 | 0 | 56.3 | 81.54 | 0 | 0
2025-04-29 22:00 | 52.72 | 0 | 0 | 6.08 | 0 | 46.64 | 32.45 | 0 | 0
2025-04-29 23:00 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 32.45 | 0 | 0
2025-04-30 | 47.58 | 0 | 0 | 47.58 | 0 | 0 | 32.45 | 0 | 0
2025-04-30 01:00 | 45.25 | 0 | 0 | 45.25 | 0 | 0 | 32.45 | 0 | 0
2025-04-30 02:00 | 44.24 | 0 | 0 | 44.24 | 0 | 0 | 32.45 | 0 | 0
2025-04-30 03:00 | 44.97 | 0 | 0 | 44.97 | 0 | 0 | 32.45 | 0 | 0
2025-04-30 04:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 32.45 | 0 | 0
2025-04-30 05:00 | 45.62 | 1.38 | 1.38 | 44.24 | 0 | 0 | 32.45 | 0 | 0
2025-04-30 06:00 | 47.5 | 30.1 | 30.1 | 17.4 | 0 | 0 | 32.45 | 0 | 0
2025-04-30 07:00 | 49.72 | 59.36 | 59.36 | 0 | 9.64 | 0 | 41.61 | 0 | 0
2025-04-30 08:00 | 50.86 | 94.24 | 94.24 | 0 | 43.38 | 0 | 82.82 | 0 | 0
2025-04-30 09:00 | 53.66 | 96.66 | 96.66 | 0 | 43 | 0 | 123.67 | 0 | 0
2025-04-30 10:00 | 56.91 | 98.46 | 98.46 | 0 | 41.55 | 0 | 163.14 | 0 | 0
2025-04-30 11:00 | 57.72 | 99.82 | 99.82 | 0 | 42.1 | 0 | 203.14 | 0 | 0
2025-04-30 12:00 | 60.47 | 101.89 | 101.89 | 0 | 41.42 | 0 | 242.49 | 0 | 0
2025-04-30 13:00 | 61.15 | 104.15 | 104.15 | 0 | 43 | 0 | 283.35 | 0 | 0
2025-04-30 14:00 | 62.51 | 97.84 | 71.67 | 0 | 9.16 | 0 | 292.05 | 26.17 | 0
2025-04-30 15:00 | 63.07 | 91.86 | 63.07 | 0 | 0 | 0 | 292.05 | 28.79 | 0
2025-04-30 16:00 | 62.61 | 62.54 | 62.54 | 0 | 0 | 0.07 | 291.97 | 0 | 0
2025-04-30 17:00 | 61.84 | 64.11 | 61.92 | 0 | 0.08 | 0 | 292.05 | 2.18 | 0
2025-04-30 18:00 | 59.46 | 35.69 | 35.69 | 0 | 0 | 23.77 | 267.03 | 0 | 0
2025-04-30 19:00 | 58.81 | 0 | 0 | 0 | 0 | 58.81 | 205.12 | 0 | 0
2025-04-30 20:00 | 55.73 | 0 | 0 | 0 | 0 | 55.73 | 146.46 | 0 | 0
2025-04-30 21:00 | 54.01 | 0 | 0 | 0 | 0 | 54.01 | 89.6 | 0 | 0
2025-04-30 22:00 | 51.71 | 0 | 0 | 0 | 0 | 51.71 | 35.17 | 0 | 0
2025-04-30 23:00 | 49.66 | 0 | 0 | 47.07 | 0 | 2.58 | 32.45 | 0 | 0
2025-05-01 | 47.8 | 0 | 0 | 47.8 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 01:00 | 45.78 | 0 | 0 | 45.78 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 02:00 | 44.61 | 0 | 0 | 44.61 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 03:00 | 45.41 | 0 | 0 | 45.41 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 04:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 05:00 | 46.78 | 0 | 0 | 46.78 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 06:00 | 47.61 | 4.29 | 4.29 | 43.32 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 07:00 | 48.72 | 5.86 | 5.86 | 42.86 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 08:00 | 51.9 | 7.5 | 7.5 | 44.4 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 09:00 | 53.26 | 16.01 | 16.01 | 37.25 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 10:00 | 55.53 | 17.46 | 17.46 | 38.07 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 11:00 | 56.71 | 22.8 | 22.8 | 33.91 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 12:00 | 59.22 | 30.33 | 30.33 | 28.89 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 13:00 | 58.95 | 39.8 | 39.8 | 19.16 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 14:00 | 59.83 | 43.18 | 43.18 | 16.65 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 15:00 | 60.25 | 59.31 | 59.31 | 0.95 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 16:00 | 59.45 | 32.24 | 32.24 | 27.21 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 17:00 | 59.56 | 33.98 | 33.98 | 25.58 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 18:00 | 59.2 | 35.76 | 35.76 | 23.45 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 19:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 20:00 | 55.55 | 0 | 0 | 55.55 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 21:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 22:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-05-01 23:00 | 49.27 | 0 | 0 | 49.27 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 | 47.46 | 0 | 0 | 47.46 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 01:00 | 46.91 | 0 | 0 | 46.91 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 02:00 | 45.26 | 0 | 0 | 45.26 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 03:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 04:00 | 45.23 | 0 | 0 | 45.23 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 05:00 | 45.41 | 0.56 | 0.56 | 44.84 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 06:00 | 47.31 | 14.56 | 14.56 | 32.75 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 07:00 | 50.33 | 14.81 | 14.81 | 35.52 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 08:00 | 51.11 | 18.51 | 18.51 | 32.61 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 09:00 | 54.29 | 6.41 | 6.41 | 47.89 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 10:00 | 57 | 26.03 | 26.03 | 30.98 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 11:00 | 60.45 | 57 | 57 | 3.45 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 12:00 | 62.02 | 69.07 | 69.07 | 0 | 7.06 | 0 | 39.16 | 0 | 0
2025-05-02 13:00 | 62.94 | 73.25 | 73.25 | 0 | 10.32 | 0 | 48.96 | 0 | 0
2025-05-02 14:00 | 64.87 | 52.82 | 52.82 | 0 | 0 | 12.05 | 36.27 | 0 | 0
2025-05-02 15:00 | 64.19 | 69.83 | 69.83 | 0 | 5.64 | 0 | 41.63 | 0 | 0
2025-05-02 16:00 | 64.72 | 43.46 | 43.46 | 12.54 | 0 | 8.72 | 32.45 | 0 | 0
2025-05-02 17:00 | 62.54 | 21.72 | 21.72 | 40.81 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 18:00 | 62.17 | 2.69 | 2.69 | 59.47 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 19:00 | 59.38 | 0 | 0 | 59.38 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 20:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 21:00 | 54.57 | 0 | 0 | 54.57 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 22:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 32.45 | 0 | 0
2025-05-02 23:00 | 49.6 | 0 | 0 | 49.6 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 | 48.31 | 0 | 0 | 48.31 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 01:00 | 46.22 | 0 | 0 | 46.22 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 02:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 03:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 04:00 | 45.52 | 0 | 0 | 45.52 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 05:00 | 46.29 | 2.88 | 2.88 | 43.41 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 06:00 | 48.11 | 59.25 | 59.25 | 0 | 11.14 | 0 | 43.04 | 0 | 0
2025-05-03 07:00 | 50.31 | 113.74 | 113.74 | 0 | 63.44 | 0 | 103.3 | 0 | 0
2025-05-03 08:00 | 53.42 | 119.36 | 119.36 | 0 | 65.94 | 0 | 165.94 | 0 | 0
2025-05-03 09:00 | 55.4 | 121.35 | 121.35 | 0 | 65.95 | 0 | 228.59 | 0 | 0
2025-05-03 10:00 | 57.99 | 121.72 | 121.72 | 0 | 63.72 | 0 | 289.13 | 0 | 0
2025-05-03 11:00 | 61.47 | 51.45 | 51.45 | 0 | 0 | 10.02 | 278.58 | 0 | 0
2025-05-03 12:00 | 62.28 | 46.45 | 46.45 | 0 | 0 | 15.83 | 261.92 | 0 | 0
2025-05-03 13:00 | 63.89 | 49.85 | 49.85 | 0 | 0 | 14.04 | 247.14 | 0 | 0
2025-05-03 14:00 | 65.02 | 52.21 | 52.21 | 0 | 0 | 12.8 | 233.66 | 0 | 0
2025-05-03 15:00 | 64.51 | 59.55 | 59.55 | 0 | 0 | 4.96 | 228.45 | 0 | 0
2025-05-03 16:00 | 64.44 | 50.54 | 50.54 | 0 | 0 | 13.91 | 213.81 | 0 | 0
2025-05-03 17:00 | 63.39 | 27.13 | 27.13 | 0 | 0 | 36.26 | 175.64 | 0 | 0
2025-05-03 18:00 | 62.35 | 10.43 | 10.43 | 0 | 0 | 51.92 | 120.99 | 0 | 0
2025-05-03 19:00 | 59.84 | 0 | 0 | 0 | 0 | 59.84 | 58 | 0 | 0
2025-05-03 20:00 | 57.58 | 0 | 0 | 33.31 | 0 | 24.27 | 32.45 | 0 | 0
2025-05-03 21:00 | 55.48 | 0 | 0 | 55.48 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 22:00 | 52.82 | 0 | 0 | 52.82 | 0 | 0 | 32.45 | 0 | 0
2025-05-03 23:00 | 49.95 | 0 | 0 | 49.95 | 0 | 0 | 32.45 | 0 | 0
2025-05-04 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 32.45 | 0 | 0
2025-05-04 01:00 | 47.23 | 0 | 0 | 47.23 | 0 | 0 | 32.45 | 0 | 0
2025-05-04 02:00 | 46.07 | 0 | 0 | 46.07 | 0 | 0 | 32.45 | 0 | 0
2025-05-04 03:00 | 44.55 | 0 | 0 | 44.55 | 0 | 0 | 32.45 | 0 | 0
2025-05-04 04:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 32.45 | 0 | 0
2025-05-04 05:00 | 46.75 | 3.76 | 3.76 | 42.99 | 0 | 0 | 32.45 | 0 | 0
2025-05-04 06:00 | 48.66 | 65.58 | 65.58 | 0 | 16.92 | 0 | 48.52 | 0 | 0
2025-05-04 07:00 | 50.91 | 83.25 | 83.25 | 0 | 32.34 | 0 | 79.24 | 0 | 0
2025-05-04 08:00 | 53.27 | 88.89 | 88.89 | 0 | 35.62 | 0 | 113.09 | 0 | 0
2025-05-04 09:00 | 56.43 | 99.04 | 99.04 | 0 | 42.61 | 0 | 153.57 | 0 | 0
2025-05-04 10:00 | 59.35 | 108.22 | 108.22 | 0 | 48.87 | 0 | 200 | 0 | 0
2025-05-04 11:00 | 62.08 | 106.64 | 106.64 | 0 | 44.57 | 0 | 242.33 | 0 | 0
2025-05-04 12:00 | 65.05 | 103.03 | 103.03 | 0 | 37.97 | 0 | 278.41 | 0 | 0
2025-05-04 13:00 | 67.39 | 103.76 | 81.75 | 0 | 14.36 | 0 | 292.05 | 22.01 | 0
2025-05-04 14:00 | 68.77 | 103.5 | 68.77 | 0 | 0 | 0 | 292.05 | 34.73 | 0
2025-05-04 15:00 | 68.33 | 105.2 | 68.33 | 0 | 0 | 0 | 292.05 | 36.87 | 0
2025-05-04 16:00 | 68.59 | 104.09 | 68.59 | 0 | 0 | 0 | 292.05 | 35.5 | 0
2025-05-04 17:00 | 67.41 | 67.57 | 67.41 | 0 | 0 | 0 | 292.05 | 0.17 | 0
2025-05-04 18:00 | 65.04 | 27.76 | 27.76 | 0 | 0 | 37.28 | 252.81 | 0 | 0
2025-05-04 19:00 | 62.29 | 0.08 | 0.08 | 0 | 0 | 62.21 | 187.32 | 0 | 0
2025-05-04 20:00 | 59.56 | 0 | 0 | 0 | 0 | 59.56 | 124.63 | 0 | 0
2025-05-04 21:00 | 55.6 | 0 | 0 | 0 | 0 | 55.6 | 66.1 | 0 | 0
2025-05-04 22:00 | 52.31 | 0 | 0 | 20.34 | 0 | 31.97 | 32.45 | 0 | 0
2025-05-04 23:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 01:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 02:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 03:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 04:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 05:00 | 46.92 | 8.83 | 8.83 | 38.09 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 06:00 | 48.48 | 86.85 | 86.85 | 0 | 38.37 | 0 | 68.91 | 0 | 0
2025-05-05 07:00 | 50.79 | 124.72 | 124.72 | 0 | 73.93 | 0 | 139.14 | 0 | 0
2025-05-05 08:00 | 52.62 | 134.3 | 129.02 | 0 | 76.4 | 0 | 211.72 | 5.29 | 0
2025-05-05 09:00 | 55.95 | 135.94 | 132.35 | 0 | 76.4 | 0 | 284.3 | 3.6 | 0
2025-05-05 10:00 | 59.06 | 132.78 | 67.22 | 0 | 8.16 | 0 | 292.05 | 65.56 | 0
2025-05-05 11:00 | 62.09 | 77.95 | 62.09 | 0 | 0 | 0 | 292.05 | 15.86 | 0
2025-05-05 12:00 | 63.77 | 68.64 | 63.77 | 0 | 0 | 0 | 292.05 | 4.87 | 0
2025-05-05 13:00 | 65.95 | 46.54 | 46.54 | 0 | 0 | 19.41 | 271.61 | 0 | 0
2025-05-05 14:00 | 66.02 | 42.22 | 42.22 | 0 | 0 | 23.8 | 246.57 | 0 | 0
2025-05-05 15:00 | 67.49 | 46.39 | 46.39 | 0 | 0 | 21.1 | 224.35 | 0 | 0
2025-05-05 16:00 | 67.11 | 36.35 | 36.35 | 0 | 0 | 30.76 | 191.97 | 0 | 0
2025-05-05 17:00 | 65.61 | 21.21 | 21.21 | 0 | 0 | 44.4 | 145.23 | 0 | 0
2025-05-05 18:00 | 64.25 | 0.11 | 0.11 | 0 | 0 | 64.14 | 77.71 | 0 | 0
2025-05-05 19:00 | 61.65 | 0 | 0 | 18.65 | 0 | 43 | 32.45 | 0 | 0
2025-05-05 20:00 | 57.72 | 0 | 0 | 57.72 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 21:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 22:00 | 52.61 | 0 | 0 | 52.61 | 0 | 0 | 32.45 | 0 | 0
2025-05-05 23:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 32.45 | 0 | 0
2025-05-06 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 32.45 | 0 | 0
2025-05-06 01:00 | 46.94 | 0 | 0 | 46.94 | 0 | 0 | 32.45 | 0 | 0
2025-05-06 02:00 | 45.8 | 0 | 0 | 45.8 | 0 | 0 | 32.45 | 0 | 0
2025-05-06 03:00 | 45.76 | 0 | 0 | 45.76 | 0 | 0 | 32.45 | 0 | 0
2025-05-06 04:00 | 46.01 | 0 | 0 | 46.01 | 0 | 0 | 32.45 | 0 | 0
2025-05-06 05:00 | 46.8 | 4.93 | 4.93 | 41.87 | 0 | 0 | 32.45 | 0 | 0
2025-05-06 06:00 | 47.74 | 65.33 | 65.33 | 0 | 17.59 | 0 | 49.16 | 0 | 0
2025-05-06 07:00 | 49.85 | 99.88 | 99.88 | 0 | 50.03 | 0 | 96.69 | 0 | 0
2025-05-06 08:00 | 52.75 | 112.09 | 112.09 | 0 | 59.34 | 0 | 153.06 | 0 | 0
2025-05-06 09:00 | 55.71 | 113.12 | 113.12 | 0 | 57.41 | 0 | 207.6 | 0 | 0
2025-05-06 10:00 | 58.13 | 112.01 | 112.01 | 0 | 53.87 | 0 | 258.78 | 0 | 0
2025-05-06 11:00 | 61.32 | 109.31 | 96.34 | 0 | 35.02 | 0 | 292.05 | 12.97 | 0
2025-05-06 12:00 | 63.1 | 108.34 | 63.1 | 0 | 0 | 0 | 292.05 | 45.24 | 0
2025-05-06 13:00 | 64.5 | 107.74 | 64.5 | 0 | 0 | 0 | 292.05 | 43.24 | 0
2025-05-06 14:00 | 65.94 | 108.46 | 65.94 | 0 | 0 | 0 | 292.05 | 42.52 | 0
2025-05-06 15:00 | 66.57 | 103.78 | 66.57 | 0 | 0 | 0 | 292.05 | 37.22 | 0
2025-05-06 16:00 | 66.24 | 93.92 | 66.24 | 0 | 0 | 0 | 292.05 | 27.68 | 0
2025-05-06 17:00 | 65.92 | 76.57 | 65.92 | 0 | 0 | 0 | 292.05 | 10.66 | 0
2025-05-06 18:00 | 62.91 | 35.38 | 35.38 | 0 | 0 | 27.53 | 263.07 | 0 | 0
2025-05-06 19:00 | 60.97 | 0.3 | 0.3 | 0 | 0 | 60.67 | 199.21 | 0 | 0
2025-05-06 20:00 | 58.65 | 0 | 0 | 0 | 0 | 58.65 | 137.47 | 0 | 0
2025-05-06 21:00 | 55.71 | 0 | 0 | 0 | 0 | 55.71 | 78.83 | 0 | 0
2025-05-06 22:00 | 52.79 | 0 | 0 | 8.73 | 0 | 44.06 | 32.45 | 0 | 0
2025-05-06 23:00 | 49.81 | 0 | 0 | 49.81 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 | 48.49 | 0 | 0 | 48.49 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 01:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 02:00 | 45.21 | 0 | 0 | 45.21 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 03:00 | 45.34 | 0 | 0 | 45.34 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 04:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 05:00 | 47.38 | 0.49 | 0.49 | 46.89 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 06:00 | 49.04 | 12.37 | 12.37 | 36.67 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 07:00 | 50.55 | 31.61 | 31.61 | 18.94 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 08:00 | 53.65 | 50.42 | 50.42 | 3.22 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 09:00 | 55.99 | 54.23 | 54.23 | 1.76 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 10:00 | 59.99 | 44.31 | 44.31 | 15.68 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 11:00 | 63.69 | 29.25 | 29.25 | 34.44 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 12:00 | 66.82 | 33.43 | 33.43 | 33.38 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 13:00 | 68.36 | 28.17 | 28.17 | 40.19 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 14:00 | 70.72 | 12.91 | 12.91 | 57.82 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 15:00 | 69.95 | 11.82 | 11.82 | 58.14 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 16:00 | 69.57 | 16.55 | 16.55 | 53.03 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 17:00 | 69.07 | 8.19 | 8.19 | 60.88 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 18:00 | 67.24 | 2.2 | 2.2 | 65.04 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 19:00 | 63.74 | 0 | 0 | 63.74 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 20:00 | 60.22 | 0 | 0 | 60.22 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 21:00 | 55.82 | 0 | 0 | 55.82 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 22:00 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 32.45 | 0 | 0
2025-05-07 23:00 | 51.07 | 0 | 0 | 51.07 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 | 48.51 | 0 | 0 | 48.51 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 01:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 02:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 03:00 | 45.92 | 0 | 0 | 45.92 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 04:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 05:00 | 47.25 | 0.17 | 0.17 | 47.08 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 06:00 | 49.31 | 3.97 | 3.97 | 45.34 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 07:00 | 50.59 | 11.5 | 11.5 | 39.09 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 08:00 | 52.61 | 17.42 | 17.42 | 35.19 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 09:00 | 55.3 | 18.51 | 18.51 | 36.79 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 10:00 | 56.24 | 36.22 | 36.22 | 20.02 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 11:00 | 59.83 | 26.55 | 26.55 | 33.28 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 12:00 | 59.97 | 29.16 | 29.16 | 30.81 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 13:00 | 60.95 | 23.11 | 23.11 | 37.84 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 14:00 | 61.61 | 43.06 | 43.06 | 18.55 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 15:00 | 62.48 | 43.45 | 43.45 | 19.04 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 16:00 | 61.74 | 42.22 | 42.22 | 19.53 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 17:00 | 59.96 | 24.57 | 24.57 | 35.39 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 18:00 | 60.48 | 5.43 | 5.43 | 55.05 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 19:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 20:00 | 56.78 | 0 | 0 | 56.78 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 21:00 | 54.13 | 0 | 0 | 54.13 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 22:00 | 52.93 | 0 | 0 | 52.93 | 0 | 0 | 32.45 | 0 | 0
2025-05-08 23:00 | 50.26 | 0 | 0 | 50.26 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 01:00 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 02:00 | 47.29 | 0 | 0 | 47.29 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 03:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 04:00 | 46.35 | 0 | 0 | 46.35 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 05:00 | 47.36 | 0.46 | 0.46 | 46.9 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 06:00 | 48.7 | 1.71 | 1.71 | 46.99 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 07:00 | 51.43 | 7.43 | 7.43 | 44 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 08:00 | 52.97 | 31.22 | 31.22 | 21.74 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 09:00 | 55.26 | 44.82 | 44.82 | 10.44 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 10:00 | 58.23 | 52.75 | 52.75 | 5.48 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 11:00 | 59.51 | 62.79 | 62.79 | 0 | 3.27 | 0 | 35.56 | 0 | 0
2025-05-09 12:00 | 61.46 | 47.49 | 47.49 | 11.02 | 0 | 2.95 | 32.45 | 0 | 0
2025-05-09 13:00 | 61.96 | 41.94 | 41.94 | 20.03 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 14:00 | 63.89 | 30.57 | 30.57 | 33.32 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 15:00 | 64.77 | 21.13 | 21.13 | 43.64 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 16:00 | 63.9 | 3.18 | 3.18 | 60.72 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 17:00 | 63.48 | 4.8 | 4.8 | 58.69 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 18:00 | 61.06 | 2.81 | 2.81 | 58.25 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 19:00 | 59.9 | 0 | 0 | 59.9 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 20:00 | 57.27 | 0 | 0 | 57.27 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 21:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 22:00 | 53.52 | 0 | 0 | 53.52 | 0 | 0 | 32.45 | 0 | 0
2025-05-09 23:00 | 50.93 | 0 | 0 | 50.93 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 | 48.31 | 0 | 0 | 48.31 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 01:00 | 46.8 | 0 | 0 | 46.8 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 02:00 | 45.77 | 0 | 0 | 45.77 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 03:00 | 46.36 | 0 | 0 | 46.36 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 04:00 | 47.49 | 0 | 0 | 47.49 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 05:00 | 48.14 | 2.42 | 2.42 | 45.72 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 06:00 | 48.07 | 68.65 | 68.65 | 0 | 20.59 | 0 | 52.01 | 0 | 0
2025-05-10 07:00 | 51.69 | 101.92 | 101.92 | 0 | 50.23 | 0 | 99.73 | 0 | 0
2025-05-10 08:00 | 53.64 | 104.06 | 104.06 | 0 | 50.41 | 0 | 147.62 | 0 | 0
2025-05-10 09:00 | 54.65 | 112.35 | 112.35 | 0 | 57.7 | 0 | 202.44 | 0 | 0
2025-05-10 10:00 | 57.4 | 121.88 | 121.88 | 0 | 64.47 | 0 | 263.69 | 0 | 0
2025-05-10 11:00 | 59.99 | 90.73 | 89.85 | 0 | 29.86 | 0 | 292.05 | 0.88 | 0
2025-05-10 12:00 | 61.26 | 91.74 | 61.26 | 0 | 0 | 0 | 292.05 | 30.48 | 0
2025-05-10 13:00 | 61.46 | 45.75 | 45.75 | 0 | 0 | 15.71 | 275.51 | 0 | 0
2025-05-10 14:00 | 63.11 | 28.27 | 28.27 | 0 | 0 | 34.84 | 238.84 | 0 | 0
2025-05-10 15:00 | 61.97 | 5.1 | 5.1 | 0 | 0 | 56.87 | 178.97 | 0 | 0
2025-05-10 16:00 | 62.69 | 21.06 | 21.06 | 0 | 0 | 41.63 | 135.15 | 0 | 0
2025-05-10 17:00 | 62.68 | 12.62 | 12.62 | 0 | 0 | 50.06 | 82.45 | 0 | 0
2025-05-10 18:00 | 60.99 | 6.42 | 6.42 | 7.07 | 0 | 47.5 | 32.45 | 0 | 0
2025-05-10 19:00 | 59.19 | 0 | 0 | 59.19 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 20:00 | 58 | 0 | 0 | 58 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 21:00 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 22:00 | 53.83 | 0 | 0 | 53.83 | 0 | 0 | 32.45 | 0 | 0
2025-05-10 23:00 | 51.42 | 0 | 0 | 51.42 | 0 | 0 | 32.45 | 0 | 0
2025-05-11 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 32.45 | 0 | 0
2025-05-11 01:00 | 47.97 | 0 | 0 | 47.97 | 0 | 0 | 32.45 | 0 | 0
2025-05-11 02:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 32.45 | 0 | 0
2025-05-11 03:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 32.45 | 0 | 0
2025-05-11 04:00 | 46.47 | 0 | 0 | 46.47 | 0 | 0 | 32.45 | 0 | 0
2025-05-11 05:00 | 47 | 4.27 | 4.27 | 42.73 | 0 | 0 | 32.45 | 0 | 0
2025-05-11 06:00 | 48.73 | 50.51 | 50.51 | 0 | 1.78 | 0 | 34.14 | 0 | 0
2025-05-11 07:00 | 51.13 | 49.13 | 49.13 | 0.39 | 0 | 1.61 | 32.45 | 0 | 0
2025-05-11 08:00 | 53.75 | 63.3 | 63.3 | 0 | 9.54 | 0 | 41.51 | 0 | 0
2025-05-11 09:00 | 56.84 | 96.07 | 96.07 | 0 | 39.23 | 0 | 78.78 | 0 | 0
2025-05-11 10:00 | 58.54 | 91.37 | 91.37 | 0 | 32.83 | 0 | 109.97 | 0 | 0
2025-05-11 11:00 | 61.3 | 95.43 | 95.43 | 0 | 34.13 | 0 | 142.4 | 0 | 0
2025-05-11 12:00 | 63.22 | 86.43 | 86.43 | 0 | 23.21 | 0 | 164.45 | 0 | 0
2025-05-11 13:00 | 63.99 | 73.42 | 73.42 | 0 | 9.43 | 0 | 173.41 | 0 | 0
2025-05-11 14:00 | 65.29 | 99.07 | 99.07 | 0 | 33.78 | 0 | 205.5 | 0 | 0
2025-05-11 15:00 | 65.17 | 110.83 | 110.83 | 0 | 45.66 | 0 | 248.87 | 0 | 0
2025-05-11 16:00 | 65.65 | 105.94 | 105.94 | 0 | 40.29 | 0 | 287.15 | 0 | 0
2025-05-11 17:00 | 64.42 | 100.78 | 69.58 | 0 | 5.16 | 0 | 292.05 | 31.2 | 0
2025-05-11 18:00 | 62.08 | 58.68 | 58.68 | 0 | 0 | 3.4 | 288.47 | 0 | 0
2025-05-11 19:00 | 60.88 | 1.62 | 1.62 | 0 | 0 | 59.26 | 226.09 | 0 | 0
2025-05-11 20:00 | 59.39 | 0 | 0 | 0 | 0 | 59.39 | 163.58 | 0 | 0
2025-05-11 21:00 | 56.03 | 0 | 0 | 0 | 0 | 56.03 | 104.6 | 0 | 0
2025-05-11 22:00 | 53.86 | 0 | 0 | 0 | 0 | 53.86 | 47.9 | 0 | 0
2025-05-11 23:00 | 51.54 | 0 | 0 | 36.86 | 0 | 14.68 | 32.45 | 0 | 0
2025-05-12 | 48.76 | 0 | 0 | 48.76 | 0 | 0 | 32.45 | 0 | 0
2025-05-12 01:00 | 47.98 | 0 | 0 | 47.98 | 0 | 0 | 32.45 | 0 | 0
2025-05-12 02:00 | 46.02 | 0 | 0 | 46.02 | 0 | 0 | 32.45 | 0 | 0
2025-05-12 03:00 | 46.05 | 0 | 0 | 46.05 | 0 | 0 | 32.45 | 0 | 0
2025-05-12 04:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 32.45 | 0 | 0
2025-05-12 05:00 | 47.9 | 10.28 | 10.28 | 37.62 | 0 | 0 | 32.45 | 0 | 0
2025-05-12 06:00 | 49.13 | 78.62 | 78.62 | 0 | 29.5 | 0 | 60.47 | 0 | 0
2025-05-12 07:00 | 51.43 | 102.71 | 102.71 | 0 | 51.28 | 0 | 109.19 | 0 | 0
2025-05-12 08:00 | 53.29 | 116.09 | 116.09 | 0 | 62.8 | 0 | 168.85 | 0 | 0
2025-05-12 09:00 | 55.42 | 120.08 | 120.08 | 0 | 64.65 | 0 | 230.27 | 0 | 0
2025-05-12 10:00 | 57.67 | 117.34 | 117.34 | 0 | 59.67 | 0 | 286.96 | 0 | 0
2025-05-12 11:00 | 58.62 | 115.37 | 63.98 | 0 | 5.36 | 0 | 292.05 | 51.39 | 0
2025-05-12 12:00 | 60.29 | 113.03 | 60.29 | 0 | 0 | 0 | 292.05 | 52.74 | 0
2025-05-12 13:00 | 61.03 | 114.58 | 61.03 | 0 | 0 | 0 | 292.05 | 53.55 | 0
2025-05-12 14:00 | 60.94 | 115.3 | 60.94 | 0 | 0 | 0 | 292.05 | 54.36 | 0
2025-05-12 15:00 | 61.45 | 111.32 | 61.45 | 0 | 0 | 0 | 292.05 | 49.87 | 0
2025-05-12 16:00 | 62.51 | 105.9 | 62.51 | 0 | 0 | 0 | 292.05 | 43.39 | 0
2025-05-12 17:00 | 61.38 | 91.54 | 61.38 | 0 | 0 | 0 | 292.05 | 30.16 | 0
2025-05-12 18:00 | 59.61 | 48.47 | 48.47 | 0 | 0 | 11.14 | 280.32 | 0 | 0
2025-05-12 19:00 | 58.21 | 1.11 | 1.11 | 0 | 0 | 57.1 | 220.21 | 0 | 0
2025-05-12 20:00 | 57.29 | 0 | 0 | 0 | 0 | 57.29 | 159.91 | 0 | 0
2025-05-12 21:00 | 56.2 | 0 | 0 | 0 | 0 | 56.2 | 100.76 | 0 | 0
2025-05-12 22:00 | 53.22 | 0 | 0 | 0 | 0 | 53.22 | 44.73 | 0 | 0
2025-05-12 23:00 | 51.86 | 0 | 0 | 40.19 | 0 | 11.67 | 32.45 | 0 | 0
2025-05-13 | 49.76 | 0 | 0 | 49.76 | 0 | 0 | 32.45 | 0 | 0
2025-05-13 01:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 32.45 | 0 | 0
2025-05-13 02:00 | 46.17 | 0 | 0 | 46.17 | 0 | 0 | 32.45 | 0 | 0
2025-05-13 03:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 32.45 | 0 | 0
2025-05-13 04:00 | 46.67 | 0 | 0 | 46.67 | 0 | 0 | 32.45 | 0 | 0
2025-05-13 05:00 | 48.32 | 10.33 | 10.33 | 38 | 0 | 0 | 32.45 | 0 | 0
2025-05-13 06:00 | 49.18 | 67.57 | 67.57 | 0 | 18.39 | 0 | 49.92 | 0 | 0
2025-05-13 07:00 | 51.93 | 94.3 | 94.3 | 0 | 42.36 | 0 | 90.17 | 0 | 0
2025-05-13 08:00 | 54.71 | 109.3 | 109.3 | 0 | 54.58 | 0 | 142.02 | 0 | 0
2025-05-13 09:00 | 57.43 | 114.62 | 114.62 | 0 | 57.19 | 0 | 196.35 | 0 | 0
2025-05-13 10:00 | 60.75 | 113.63 | 113.63 | 0 | 52.88 | 0 | 246.59 | 0 | 0
2025-05-13 11:00 | 63.33 | 110.24 | 110.24 | 0 | 46.91 | 0 | 291.15 | 0 | 0
2025-05-13 12:00 | 65.69 | 108.44 | 66.64 | 0 | 0.95 | 0 | 292.05 | 41.8 | 0
2025-05-13 13:00 | 68.81 | 108.74 | 68.81 | 0 | 0 | 0 | 292.05 | 39.92 | 0
2025-05-13 14:00 | 69.8 | 110.24 | 69.8 | 0 | 0 | 0 | 292.05 | 40.43 | 0
2025-05-13 15:00 | 69.34 | 107.89 | 69.34 | 0 | 0 | 0 | 292.05 | 38.55 | 0
2025-05-13 16:00 | 69.56 | 93.92 | 69.56 | 0 | 0 | 0 | 292.05 | 24.35 | 0
2025-05-13 17:00 | 67.64 | 76.83 | 67.64 | 0 | 0 | 0 | 292.05 | 9.19 | 0
2025-05-13 18:00 | 65.42 | 43.16 | 43.16 | 0 | 0 | 22.26 | 268.61 | 0 | 0
2025-05-13 19:00 | 63.98 | 1.18 | 1.18 | 0 | 0 | 62.8 | 202.51 | 0 | 0
2025-05-13 20:00 | 59.7 | 0 | 0 | 0 | 0 | 59.7 | 139.67 | 0 | 0
2025-05-13 21:00 | 57.97 | 0 | 0 | 0 | 0 | 57.97 | 78.65 | 0 | 0
2025-05-13 22:00 | 54.41 | 0 | 0 | 10.52 | 0 | 43.89 | 32.45 | 0 | 0
2025-05-13 23:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 01:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 02:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 03:00 | 46.97 | 0 | 0 | 46.97 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 04:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 05:00 | 47.38 | 12.95 | 12.95 | 34.43 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 06:00 | 49.58 | 78.6 | 78.6 | 0 | 29.02 | 0 | 60.02 | 0 | 0
2025-05-14 07:00 | 52.5 | 99.04 | 99.04 | 0 | 46.54 | 0 | 104.23 | 0 | 0
2025-05-14 08:00 | 55.12 | 9.92 | 9.92 | 0 | 0 | 45.2 | 56.65 | 0 | 0
2025-05-14 09:00 | 57.27 | 29.56 | 29.56 | 4.72 | 0 | 22.99 | 32.45 | 0 | 0
2025-05-14 10:00 | 58.91 | 91.47 | 91.47 | 0 | 32.56 | 0 | 63.38 | 0 | 0
2025-05-14 11:00 | 62.15 | 117.51 | 117.51 | 0 | 55.36 | 0 | 115.97 | 0 | 0
2025-05-14 12:00 | 64.36 | 122.97 | 122.97 | 0 | 58.6 | 0 | 171.65 | 0 | 0
2025-05-14 13:00 | 65.85 | 100.71 | 100.71 | 0 | 34.86 | 0 | 204.76 | 0 | 0
2025-05-14 14:00 | 66.85 | 84.33 | 84.33 | 0 | 17.48 | 0 | 221.37 | 0 | 0
2025-05-14 15:00 | 66.97 | 96.84 | 96.84 | 0 | 29.87 | 0 | 249.74 | 0 | 0
2025-05-14 16:00 | 66.42 | 40.14 | 40.14 | 0 | 0 | 26.28 | 222.08 | 0 | 0
2025-05-14 17:00 | 65.19 | 11.13 | 11.13 | 0 | 0 | 54.06 | 165.17 | 0 | 0
2025-05-14 18:00 | 62.99 | 0 | 0 | 0 | 0 | 62.99 | 98.87 | 0 | 0
2025-05-14 19:00 | 62.07 | 0 | 0 | 0 | 0 | 62.07 | 33.53 | 0 | 0
2025-05-14 20:00 | 59.6 | 0 | 0 | 58.57 | 0 | 1.03 | 32.45 | 0 | 0
2025-05-14 21:00 | 57.19 | 0 | 0 | 57.19 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 22:00 | 53.61 | 0 | 0 | 53.61 | 0 | 0 | 32.45 | 0 | 0
2025-05-14 23:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 32.45 | 0 | 0
2025-05-15 | 50.74 | 0 | 0 | 50.74 | 0 | 0 | 32.45 | 0 | 0
2025-05-15 01:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 32.45 | 0 | 0
2025-05-15 02:00 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 32.45 | 0 | 0
2025-05-15 03:00 | 46.88 | 0 | 0 | 46.88 | 0 | 0 | 32.45 | 0 | 0
2025-05-15 04:00 | 48.1 | 0 | 0 | 48.1 | 0 | 0 | 32.45 | 0 | 0
2025-05-15 05:00 | 47.61 | 11.78 | 11.78 | 35.83 | 0 | 0 | 32.45 | 0 | 0
2025-05-15 06:00 | 49.81 | 67.46 | 67.46 | 0 | 17.65 | 0 | 49.22 | 0 | 0
2025-05-15 07:00 | 51.28 | 93.85 | 93.85 | 0 | 42.57 | 0 | 89.66 | 0 | 0
2025-05-15 08:00 | 53.54 | 109.56 | 109.56 | 0 | 56.02 | 0 | 142.88 | 0 | 0
2025-05-15 09:00 | 55.9 | 113.37 | 113.37 | 0 | 57.47 | 0 | 197.47 | 0 | 0
2025-05-15 10:00 | 58.52 | 114.44 | 114.44 | 0 | 55.91 | 0 | 250.59 | 0 | 0
2025-05-15 11:00 | 60.37 | 113.44 | 104.01 | 0 | 43.64 | 0 | 292.05 | 9.43 | 0
2025-05-15 12:00 | 60.96 | 112.81 | 60.96 | 0 | 0 | 0 | 292.05 | 51.85 | 0
2025-05-15 13:00 | 61.43 | 112.11 | 61.43 | 0 | 0 | 0 | 292.05 | 50.68 | 0
2025-05-15 14:00 | 63.39 | 109.64 | 63.39 | 0 | 0 | 0 | 292.05 | 46.24 | 0
2025-05-15 15:00 | 62.1 | 105.09 | 62.1 | 0 | 0 | 0 | 292.05 | 42.99 | 0
2025-05-15 16:00 | 61.86 | 92.54 | 61.86 | 0 | 0 | 0 | 292.05 | 30.68 | 0
2025-05-15 17:00 | 60.74 | 80.82 | 60.74 | 0 | 0 | 0 | 292.05 | 20.08 | 0
2025-05-15 18:00 | 61.43 | 44.28 | 44.28 | 0 | 0 | 17.16 | 273.99 | 0 | 0
2025-05-15 19:00 | 59.96 | 1.72 | 1.72 | 0 | 0 | 58.23 | 212.69 | 0 | 0
2025-05-15 20:00 | 59.06 | 0 | 0 | 0 | 0 | 59.06 | 150.53 | 0 | 0
2025-05-15 21:00 | 55.23 | 0 | 0 | 0 | 0 | 55.23 | 92.39 | 0 | 0
2025-05-15 22:00 | 54.54 | 0 | 0 | 0 | 0 | 54.54 | 34.97 | 0 | 0
2025-05-15 23:00 | 51.71 | 0 | 0 | 49.31 | 0 | 2.4 | 32.45 | 0 | 0
2025-05-16 | 50.3 | 0 | 0 | 50.3 | 0 | 0 | 32.45 | 0 | 0
2025-05-16 01:00 | 47.44 | 0 | 0 | 47.44 | 0 | 0 | 32.45 | 0 | 0
2025-05-16 02:00 | 47.95 | 0 | 0 | 47.95 | 0 | 0 | 32.45 | 0 | 0
2025-05-16 03:00 | 47.24 | 0 | 0 | 47.24 | 0 | 0 | 32.45 | 0 | 0
2025-05-16 04:00 | 47.19 | 0 | 0 | 47.19 | 0 | 0 | 32.45 | 0 | 0
2025-05-16 05:00 | 48.59 | 13.94 | 13.94 | 34.65 | 0 | 0 | 32.45 | 0 | 0
2025-05-16 06:00 | 49.51 | 73.42 | 73.42 | 0 | 23.91 | 0 | 55.16 | 0 | 0
2025-05-16 07:00 | 51.66 | 101.1 | 101.1 | 0 | 49.44 | 0 | 102.13 | 0 | 0
2025-05-16 08:00 | 54 | 98.29 | 98.29 | 0 | 44.28 | 0 | 144.2 | 0 | 0
2025-05-16 09:00 | 55.63 | 113.55 | 113.55 | 0 | 57.92 | 0 | 199.22 | 0 | 0
2025-05-16 10:00 | 59.19 | 109.66 | 109.66 | 0 | 50.47 | 0 | 247.17 | 0 | 0
2025-05-16 11:00 | 61.28 | 107.52 | 107.52 | 0 | 46.24 | 0 | 291.1 | 0 | 0
2025-05-16 12:00 | 61.9 | 106.83 | 62.9 | 0 | 1 | 0 | 292.05 | 43.93 | 0
2025-05-16 13:00 | 63.57 | 106.46 | 63.57 | 0 | 0 | 0 | 292.05 | 42.89 | 0
2025-05-16 14:00 | 63.95 | 105.6 | 63.95 | 0 | 0 | 0 | 292.05 | 41.65 | 0
2025-05-16 15:00 | 64.48 | 96.4 | 64.48 | 0 | 0 | 0 | 292.05 | 31.92 | 0
2025-05-16 16:00 | 63.77 | 80.12 | 63.77 | 0 | 0 | 0 | 292.05 | 16.34 | 0
2025-05-16 17:00 | 62.95 | 49.74 | 49.74 | 0 | 0 | 13.21 | 278.14 | 0 | 0
2025-05-16 18:00 | 62.77 | 28.88 | 28.88 | 0 | 0 | 33.9 | 242.46 | 0 | 0
2025-05-16 19:00 | 60.65 | 1.47 | 1.47 | 0 | 0 | 59.19 | 180.16 | 0 | 0
2025-05-16 20:00 | 59.77 | 0 | 0 | 0 | 0 | 59.77 | 117.25 | 0 | 0
2025-05-16 21:00 | 56.58 | 0 | 0 | 0 | 0 | 56.58 | 57.69 | 0 | 0
2025-05-16 22:00 | 53.77 | 0 | 0 | 29.79 | 0 | 23.98 | 32.45 | 0 | 0
2025-05-16 23:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 32.45 | 0 | 0
2025-05-17 | 50.47 | 0 | 0 | 50.47 | 0 | 0 | 32.45 | 0 | 0
2025-05-17 01:00 | 48.78 | 0 | 0 | 48.78 | 0 | 0 | 32.45 | 0 | 0
2025-05-17 02:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 32.45 | 0 | 0
2025-05-17 03:00 | 46.64 | 0 | 0 | 46.64 | 0 | 0 | 32.45 | 0 | 0
2025-05-17 04:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 32.45 | 0 | 0
2025-05-17 05:00 | 48.33 | 12.21 | 12.21 | 36.12 | 0 | 0 | 32.45 | 0 | 0
2025-05-17 06:00 | 49.51 | 52.04 | 52.04 | 0 | 2.53 | 0 | 34.86 | 0 | 0
2025-05-17 07:00 | 52.3 | 77.34 | 77.34 | 0 | 25.04 | 0 | 58.64 | 0 | 0
2025-05-17 08:00 | 55.79 | 89.68 | 89.68 | 0 | 33.89 | 0 | 90.84 | 0 | 0
2025-05-17 09:00 | 58.17 | 87.16 | 87.16 | 0 | 28.99 | 0 | 118.38 | 0 | 0
2025-05-17 10:00 | 60.34 | 89.8 | 89.8 | 0 | 29.46 | 0 | 146.37 | 0 | 0
2025-05-17 11:00 | 63.04 | 95 | 95 | 0 | 31.96 | 0 | 176.73 | 0 | 0
2025-05-17 12:00 | 67.08 | 103.07 | 103.07 | 0 | 35.98 | 0 | 210.92 | 0 | 0
2025-05-17 13:00 | 68.09 | 112.3 | 112.3 | 0 | 44.21 | 0 | 252.92 | 0 | 0
2025-05-17 14:00 | 69 | 113.89 | 110.19 | 0 | 41.19 | 0 | 292.05 | 3.69 | 0
2025-05-17 15:00 | 69.6 | 120.85 | 69.6 | 0 | 0 | 0 | 292.05 | 51.25 | 0
2025-05-17 16:00 | 68.59 | 112.29 | 68.59 | 0 | 0 | 0 | 292.05 | 43.7 | 0
2025-05-17 17:00 | 68.84 | 99.52 | 68.84 | 0 | 0 | 0 | 292.05 | 30.67 | 0
2025-05-17 18:00 | 66.05 | 61.6 | 61.6 | 0 | 0 | 4.45 | 287.36 | 0 | 0
2025-05-17 19:00 | 64.5 | 2.74 | 2.74 | 0 | 0 | 61.76 | 222.36 | 0 | 0
2025-05-17 20:00 | 61.04 | 0 | 0 | 0 | 0 | 61.04 | 158.1 | 0 | 0
2025-05-17 21:00 | 58.76 | 0 | 0 | 0 | 0 | 58.76 | 96.25 | 0 | 0
2025-05-17 22:00 | 55.25 | 0 | 0 | 0 | 0 | 55.25 | 38.09 | 0 | 0
2025-05-17 23:00 | 52.86 | 0 | 0 | 47.5 | 0 | 5.36 | 32.45 | 0 | 0
2025-05-18 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 32.45 | 0 | 0
2025-05-18 01:00 | 48.87 | 0 | 0 | 48.87 | 0 | 0 | 32.45 | 0 | 0
2025-05-18 02:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 32.45 | 0 | 0
2025-05-18 03:00 | 46.97 | 0 | 0 | 46.97 | 0 | 0 | 32.45 | 0 | 0
2025-05-18 04:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 32.45 | 0 | 0
2025-05-18 05:00 | 48.1 | 17.08 | 17.08 | 31.02 | 0 | 0 | 32.45 | 0 | 0
2025-05-18 06:00 | 50.34 | 88.99 | 88.99 | 0 | 38.65 | 0 | 69.17 | 0 | 0
2025-05-18 07:00 | 52.73 | 115.02 | 115.02 | 0 | 62.29 | 0 | 128.34 | 0 | 0
2025-05-18 08:00 | 55.79 | 123.53 | 123.53 | 0 | 67.74 | 0 | 192.7 | 0 | 0
2025-05-18 09:00 | 58.55 | 125.64 | 125.64 | 0 | 67.09 | 0 | 256.43 | 0 | 0
2025-05-18 10:00 | 62.22 | 124.88 | 99.71 | 0 | 37.49 | 0 | 292.05 | 25.17 | 0
2025-05-18 11:00 | 65.14 | 123.2 | 65.14 | 0 | 0 | 0 | 292.05 | 58.06 | 0
2025-05-18 12:00 | 67.22 | 121.93 | 67.22 | 0 | 0 | 0 | 292.05 | 54.71 | 0
2025-05-18 13:00 | 70.21 | 123.68 | 70.21 | 0 | 0 | 0 | 292.05 | 53.47 | 0
2025-05-18 14:00 | 71.06 | 125.51 | 71.06 | 0 | 0 | 0 | 292.05 | 54.46 | 0
2025-05-18 15:00 | 71.22 | 124.72 | 71.22 | 0 | 0 | 0 | 292.05 | 53.5 | 0
2025-05-18 16:00 | 71.67 | 120.58 | 71.67 | 0 | 0 | 0 | 292.05 | 48.91 | 0
2025-05-18 17:00 | 70.45 | 106.53 | 70.45 | 0 | 0 | 0 | 292.05 | 36.08 | 0
2025-05-18 18:00 | 68.28 | 68.43 | 68.28 | 0 | 0 | 0 | 292.05 | 0.15 | 0
2025-05-18 19:00 | 65.51 | 2.63 | 2.63 | 0 | 0 | 62.87 | 225.87 | 0 | 0
2025-05-18 20:00 | 61.09 | 0 | 0 | 0 | 0 | 61.09 | 161.56 | 0 | 0
2025-05-18 21:00 | 58.09 | 0 | 0 | 0 | 0 | 58.09 | 100.41 | 0 | 0
2025-05-18 22:00 | 56.58 | 0 | 0 | 0 | 0 | 56.58 | 40.86 | 0 | 0
2025-05-18 23:00 | 52.2 | 0 | 0 | 44.21 | 0 | 7.99 | 32.45 | 0 | 0
2025-05-19 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 32.45 | 0 | 0
2025-05-19 01:00 | 48.37 | 0 | 0 | 48.37 | 0 | 0 | 32.45 | 0 | 0
2025-05-19 02:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 32.45 | 0 | 0
2025-05-19 03:00 | 46.89 | 0 | 0 | 46.89 | 0 | 0 | 32.45 | 0 | 0
2025-05-19 04:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 32.45 | 0 | 0
2025-05-19 05:00 | 48.78 | 16.09 | 16.09 | 32.69 | 0 | 0 | 32.45 | 0 | 0
2025-05-19 06:00 | 50.36 | 71.2 | 71.2 | 0 | 20.85 | 0 | 52.25 | 0 | 0
2025-05-19 07:00 | 52.65 | 91.5 | 91.5 | 0 | 38.85 | 0 | 89.16 | 0 | 0
2025-05-19 08:00 | 56.54 | 102.38 | 102.38 | 0 | 45.84 | 0 | 132.71 | 0 | 0
2025-05-19 09:00 | 59.51 | 111.27 | 111.27 | 0 | 51.76 | 0 | 181.88 | 0 | 0
2025-05-19 10:00 | 64.32 | 113.55 | 113.55 | 0 | 49.23 | 0 | 228.65 | 0 | 0
2025-05-19 11:00 | 69.37 | 110.24 | 110.24 | 0 | 40.87 | 0 | 267.48 | 0 | 0
2025-05-19 12:00 | 72.3 | 101.37 | 98.17 | 0 | 25.87 | 0 | 292.05 | 3.2 | 0
2025-05-19 13:00 | 74.84 | 101.02 | 74.84 | 0 | 0 | 0 | 292.05 | 26.18 | 0
2025-05-19 14:00 | 76.29 | 101.36 | 76.29 | 0 | 0 | 0 | 292.05 | 25.08 | 0
2025-05-19 15:00 | 76 | 98.12 | 76 | 0 | 0 | 0 | 292.05 | 22.12 | 0
2025-05-19 16:00 | 75.67 | 77.74 | 75.67 | 0 | 0 | 0 | 292.05 | 2.08 | 0
2025-05-19 17:00 | 75.12 | 63.85 | 63.85 | 0 | 0 | 11.28 | 280.18 | 0 | 0
2025-05-19 18:00 | 71.23 | 23.14 | 23.14 | 0 | 0 | 48.09 | 229.56 | 0 | 0
2025-05-19 19:00 | 67.7 | 1.84 | 1.84 | 0 | 0 | 65.86 | 160.23 | 0 | 0
2025-05-19 20:00 | 64.02 | 0 | 0 | 0 | 0 | 64.02 | 92.84 | 0 | 0
2025-05-19 21:00 | 59.59 | 0 | 0 | 2.21 | 0 | 57.37 | 32.45 | 0 | 0
2025-05-19 22:00 | 55.79 | 0 | 0 | 55.79 | 0 | 0 | 32.45 | 0 | 0
2025-05-19 23:00 | 53.15 | 0 | 0 | 53.15 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 | 50.36 | 0 | 0 | 50.36 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 01:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 02:00 | 47.31 | 0 | 0 | 47.31 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 03:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 04:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 05:00 | 48.77 | 20.83 | 20.83 | 27.93 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 06:00 | 51.1 | 68.71 | 68.71 | 0 | 17.6 | 0 | 49.17 | 0 | 0
2025-05-20 07:00 | 53.49 | 103.75 | 103.75 | 0 | 50.26 | 0 | 96.92 | 0 | 0
2025-05-20 08:00 | 56.95 | 133.3 | 133.3 | 0 | 76.35 | 0 | 169.45 | 0 | 0
2025-05-20 09:00 | 61.48 | 92.86 | 92.86 | 0 | 31.37 | 0 | 199.26 | 0 | 0
2025-05-20 10:00 | 66.13 | 8.78 | 8.78 | 0 | 0 | 57.35 | 138.89 | 0 | 0
2025-05-20 11:00 | 70.31 | 20.68 | 20.68 | 0 | 0 | 49.62 | 86.65 | 0 | 0
2025-05-20 12:00 | 74.63 | 9.5 | 9.5 | 13.63 | 0 | 51.49 | 32.45 | 0 | 0
2025-05-20 13:00 | 77.59 | 22.58 | 22.58 | 55.01 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 14:00 | 79.76 | 8.1 | 8.1 | 71.66 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 15:00 | 81.34 | 87.11 | 87.11 | 0 | 5.77 | 0 | 37.93 | 0 | 0
2025-05-20 16:00 | 80.41 | 115.03 | 115.03 | 0 | 34.61 | 0 | 70.81 | 0 | 0
2025-05-20 17:00 | 78.21 | 29.54 | 29.54 | 12.22 | 0 | 36.45 | 32.45 | 0 | 0
2025-05-20 18:00 | 74.73 | 39.15 | 39.15 | 35.57 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 19:00 | 70.4 | 0.71 | 0.71 | 69.69 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 20:00 | 66.14 | 0 | 0 | 66.14 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 21:00 | 61.72 | 0 | 0 | 61.72 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 22:00 | 57.55 | 0 | 0 | 57.55 | 0 | 0 | 32.45 | 0 | 0
2025-05-20 23:00 | 53.51 | 0 | 0 | 53.51 | 0 | 0 | 32.45 | 0 | 0
2025-05-21 | 51.43 | 0 | 0 | 51.43 | 0 | 0 | 32.45 | 0 | 0
2025-05-21 01:00 | 49.05 | 0 | 0 | 49.05 | 0 | 0 | 32.45 | 0 | 0
2025-05-21 02:00 | 48.14 | 0 | 0 | 48.14 | 0 | 0 | 32.45 | 0 | 0
2025-05-21 03:00 | 47.58 | 0 | 0 | 47.58 | 0 | 0 | 32.45 | 0 | 0
2025-05-21 04:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 32.45 | 0 | 0
2025-05-21 05:00 | 48.57 | 7.9 | 7.9 | 40.67 | 0 | 0 | 32.45 | 0 | 0
2025-05-21 06:00 | 51.08 | 43.37 | 43.37 | 7.72 | 0 | 0 | 32.45 | 0 | 0
2025-05-21 07:00 | 54.53 | 106.15 | 106.15 | 0 | 51.62 | 0 | 81.49 | 0 | 0
2025-05-21 08:00 | 55.72 | 100.1 | 100.1 | 0 | 44.37 | 0 | 123.65 | 0 | 0
2025-05-21 09:00 | 59.01 | 117.61 | 117.61 | 0 | 58.6 | 0 | 179.32 | 0 | 0
2025-05-21 10:00 | 61.87 | 104.91 | 104.91 | 0 | 43.04 | 0 | 220.21 | 0 | 0
2025-05-21 11:00 | 64.8 | 92.48 | 92.48 | 0 | 27.68 | 0 | 246.5 | 0 | 0
2025-05-21 12:00 | 68.4 | 76.43 | 76.43 | 0 | 8.04 | 0 | 254.14 | 0 | 0
2025-05-21 13:00 | 69.29 | 69.8 | 69.8 | 0 | 0.51 | 0 | 254.62 | 0 | 0
2025-05-21 14:00 | 70.66 | 64.83 | 64.83 | 0 | 0 | 5.82 | 248.49 | 0 | 0
2025-05-21 15:00 | 70.54 | 92.07 | 92.07 | 0 | 21.53 | 0 | 268.94 | 0 | 0
2025-05-21 16:00 | 70.52 | 100.47 | 94.84 | 0 | 24.32 | 0 | 292.05 | 5.63 | 0
2025-05-21 17:00 | 68.77 | 109.57 | 68.77 | 0 | 0 | 0 | 292.05 | 40.8 | 0
2025-05-21 18:00 | 67.94 | 70.44 | 67.94 | 0 | 0 | 0 | 292.05 | 2.5 | 0
2025-05-21 19:00 | 66.45 | 2.83 | 2.83 | 0 | 0 | 63.62 | 225.08 | 0 | 0
2025-05-21 20:00 | 61.91 | 0 | 0 | 0 | 0 | 61.91 | 159.92 | 0 | 0
2025-05-21 21:00 | 58.14 | 0 | 0 | 0 | 0 | 58.14 | 98.72 | 0 | 0
2025-05-21 22:00 | 56.36 | 0 | 0 | 0 | 0 | 56.36 | 39.4 | 0 | 0
2025-05-21 23:00 | 52.74 | 0 | 0 | 46.14 | 0 | 6.6 | 32.45 | 0 | 0
2025-05-22 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-05-22 01:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 32.45 | 0 | 0
2025-05-22 02:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 32.45 | 0 | 0
2025-05-22 03:00 | 47.47 | 0 | 0 | 47.47 | 0 | 0 | 32.45 | 0 | 0
2025-05-22 04:00 | 48.32 | 0 | 0 | 48.32 | 0 | 0 | 32.45 | 0 | 0
2025-05-22 05:00 | 48.93 | 9.76 | 9.76 | 39.17 | 0 | 0 | 32.45 | 0 | 0
2025-05-22 06:00 | 50.5 | 56.87 | 56.87 | 0 | 6.36 | 0 | 38.5 | 0 | 0
2025-05-22 07:00 | 52.81 | 19.86 | 19.86 | 27.21 | 0 | 5.74 | 32.45 | 0 | 0
2025-05-22 08:00 | 54.67 | 54.59 | 54.59 | 0.08 | 0 | 0 | 32.45 | 0 | 0
2025-05-22 09:00 | 57.96 | 51.47 | 51.47 | 6.49 | 0 | 0 | 32.45 | 0 | 0
2025-05-22 10:00 | 59.18 | 105.04 | 105.04 | 0 | 45.86 | 0 | 76.02 | 0 | 0
2025-05-22 11:00 | 61.89 | 77.21 | 77.21 | 0 | 15.32 | 0 | 90.58 | 0 | 0
2025-05-22 12:00 | 64.15 | 67.51 | 67.51 | 0 | 3.36 | 0 | 93.77 | 0 | 0
2025-05-22 13:00 | 65.13 | 85.86 | 85.86 | 0 | 20.73 | 0 | 113.46 | 0 | 0
2025-05-22 14:00 | 66.01 | 91.88 | 91.88 | 0 | 25.87 | 0 | 138.04 | 0 | 0
2025-05-22 15:00 | 65.93 | 106.27 | 106.27 | 0 | 40.33 | 0 | 176.36 | 0 | 0
2025-05-22 16:00 | 66.3 | 124.45 | 124.45 | 0 | 58.14 | 0 | 231.6 | 0 | 0
2025-05-22 17:00 | 65.44 | 115.69 | 115.69 | 0 | 50.24 | 0 | 279.33 | 0 | 0
2025-05-22 18:00 | 63.99 | 82.69 | 77.38 | 0 | 13.39 | 0 | 292.05 | 5.31 | 0
2025-05-22 19:00 | 62.58 | 7.67 | 7.67 | 0 | 0 | 54.91 | 234.25 | 0 | 0
2025-05-22 20:00 | 60.45 | 0 | 0 | 0 | 0 | 60.45 | 170.62 | 0 | 0
2025-05-22 21:00 | 57.54 | 0 | 0 | 0 | 0 | 57.54 | 110.05 | 0 | 0
2025-05-22 22:00 | 54.64 | 0 | 0 | 0 | 0 | 54.64 | 52.54 | 0 | 0
2025-05-22 23:00 | 53.12 | 0 | 0 | 34.03 | 0 | 19.09 | 32.45 | 0 | 0
2025-05-23 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 32.45 | 0 | 0
2025-05-23 01:00 | 49.69 | 0 | 0 | 49.69 | 0 | 0 | 32.45 | 0 | 0
2025-05-23 02:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 32.45 | 0 | 0
2025-05-23 03:00 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 32.45 | 0 | 0
2025-05-23 04:00 | 48.28 | 0 | 0 | 48.28 | 0 | 0 | 32.45 | 0 | 0
2025-05-23 05:00 | 49.11 | 17.61 | 17.61 | 31.49 | 0 | 0 | 32.45 | 0 | 0
2025-05-23 06:00 | 49.85 | 72.37 | 72.37 | 0 | 22.53 | 0 | 53.85 | 0 | 0
2025-05-23 07:00 | 52.96 | 101.99 | 101.99 | 0 | 49.03 | 0 | 100.43 | 0 | 0
2025-05-23 08:00 | 53.92 | 110.66 | 110.66 | 0 | 56.74 | 0 | 154.33 | 0 | 0
2025-05-23 09:00 | 56.32 | 114.9 | 114.9 | 0 | 58.58 | 0 | 209.99 | 0 | 0
2025-05-23 10:00 | 59.12 | 111.7 | 111.7 | 0 | 52.58 | 0 | 259.94 | 0 | 0
2025-05-23 11:00 | 60.64 | 109.87 | 94.44 | 0 | 33.8 | 0 | 292.05 | 15.43 | 0
2025-05-23 12:00 | 60.01 | 110.26 | 60.01 | 0 | 0 | 0 | 292.05 | 50.25 | 0
2025-05-23 13:00 | 61.02 | 110.96 | 61.02 | 0 | 0 | 0 | 292.05 | 49.93 | 0
2025-05-23 14:00 | 61.5 | 110.74 | 61.5 | 0 | 0 | 0 | 292.05 | 49.23 | 0
2025-05-23 15:00 | 62.47 | 105.77 | 62.47 | 0 | 0 | 0 | 292.05 | 43.31 | 0
2025-05-23 16:00 | 61.24 | 100.43 | 61.24 | 0 | 0 | 0 | 292.05 | 39.19 | 0
2025-05-23 17:00 | 60.95 | 80.51 | 60.95 | 0 | 0 | 0 | 292.05 | 19.56 | 0
2025-05-23 18:00 | 61.4 | 53.14 | 53.14 | 0 | 0 | 8.26 | 283.36 | 0 | 0
2025-05-23 19:00 | 59.54 | 4.35 | 4.35 | 0 | 0 | 55.19 | 225.27 | 0 | 0
2025-05-23 20:00 | 58.8 | 0 | 0 | 0 | 0 | 58.8 | 163.37 | 0 | 0
2025-05-23 21:00 | 56.05 | 0 | 0 | 0 | 0 | 56.05 | 104.37 | 0 | 0
2025-05-23 22:00 | 54.76 | 0 | 0 | 0 | 0 | 54.76 | 46.73 | 0 | 0
2025-05-23 23:00 | 51.94 | 0 | 0 | 38.38 | 0 | 13.57 | 32.45 | 0 | 0
2025-05-24 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 32.45 | 0 | 0
2025-05-24 01:00 | 49.73 | 0 | 0 | 49.73 | 0 | 0 | 32.45 | 0 | 0
2025-05-24 02:00 | 48.15 | 0 | 0 | 48.15 | 0 | 0 | 32.45 | 0 | 0
2025-05-24 03:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 32.45 | 0 | 0
2025-05-24 04:00 | 47.8 | 0 | 0 | 47.8 | 0 | 0 | 32.45 | 0 | 0
2025-05-24 05:00 | 49.2 | 15.06 | 15.06 | 34.14 | 0 | 0 | 32.45 | 0 | 0
2025-05-24 06:00 | 51.29 | 39.98 | 39.98 | 11.31 | 0 | 0 | 32.45 | 0 | 0
2025-05-24 07:00 | 54.03 | 72.18 | 72.18 | 0 | 18.16 | 0 | 49.7 | 0 | 0
2025-05-24 08:00 | 55.05 | 93.46 | 93.46 | 0 | 38.42 | 0 | 86.2 | 0 | 0
2025-05-24 09:00 | 59.01 | 98.08 | 98.08 | 0 | 39.07 | 0 | 123.31 | 0 | 0
2025-05-24 10:00 | 62.6 | 110.62 | 110.62 | 0 | 48.02 | 0 | 168.93 | 0 | 0
2025-05-24 11:00 | 65.4 | 102.63 | 102.63 | 0 | 37.23 | 0 | 204.3 | 0 | 0
2025-05-24 12:00 | 68.18 | 106.46 | 106.46 | 0 | 38.28 | 0 | 240.67 | 0 | 0
2025-05-24 13:00 | 70.08 | 106.29 | 106.29 | 0 | 36.21 | 0 | 275.07 | 0 | 0
2025-05-24 14:00 | 71.03 | 111.18 | 88.9 | 0 | 17.87 | 0 | 292.05 | 22.28 | 0
2025-05-24 15:00 | 71.34 | 110.24 | 71.34 | 0 | 0 | 0 | 292.05 | 38.9 | 0
2025-05-24 16:00 | 71.06 | 94.32 | 71.06 | 0 | 0 | 0 | 292.05 | 23.26 | 0
2025-05-24 17:00 | 70.52 | 79.48 | 70.52 | 0 | 0 | 0 | 292.05 | 8.96 | 0
2025-05-24 18:00 | 67.62 | 48.39 | 48.39 | 0 | 0 | 19.22 | 271.81 | 0 | 0
2025-05-24 19:00 | 65.42 | 4.42 | 4.42 | 0 | 0 | 61 | 207.6 | 0 | 0
2025-05-24 20:00 | 62.62 | 0 | 0 | 0 | 0 | 62.62 | 141.69 | 0 | 0
2025-05-24 21:00 | 60.2 | 0 | 0 | 0 | 0 | 60.2 | 78.32 | 0 | 0
2025-05-24 22:00 | 56.21 | 0 | 0 | 12.63 | 0 | 43.58 | 32.45 | 0 | 0
2025-05-24 23:00 | 54.02 | 0 | 0 | 54.02 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 | 51.79 | 0 | 0 | 51.79 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 01:00 | 49.38 | 0 | 0 | 49.38 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 02:00 | 48.18 | 0 | 0 | 48.18 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 03:00 | 47.73 | 0 | 0 | 47.73 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 04:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 05:00 | 49.84 | 1.55 | 1.55 | 48.29 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 06:00 | 51.29 | 9.06 | 9.06 | 42.23 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 07:00 | 53.53 | 19.33 | 19.33 | 34.2 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 08:00 | 55.36 | 34 | 34 | 21.36 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 09:00 | 58.02 | 42.1 | 42.1 | 15.93 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 10:00 | 62.05 | 52.29 | 52.29 | 9.76 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 11:00 | 63.09 | 56.05 | 56.05 | 7.04 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 12:00 | 64.61 | 49.25 | 49.25 | 15.36 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 13:00 | 67.05 | 55.92 | 55.92 | 11.13 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 14:00 | 67.3 | 49.55 | 49.55 | 17.75 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 15:00 | 67.73 | 27.4 | 27.4 | 40.32 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 16:00 | 67.09 | 17.77 | 17.77 | 49.33 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 17:00 | 66.18 | 9.87 | 9.87 | 56.31 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 18:00 | 64.91 | 0 | 0 | 64.91 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 19:00 | 62.49 | 0 | 0 | 62.49 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 20:00 | 60.93 | 0 | 0 | 60.93 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 21:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 22:00 | 56.85 | 0 | 0 | 56.85 | 0 | 0 | 32.45 | 0 | 0
2025-05-25 23:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 32.45 | 0 | 0
2025-05-26 | 50.18 | 0 | 0 | 50.18 | 0 | 0 | 32.45 | 0 | 0
2025-05-26 01:00 | 49.5 | 0 | 0 | 49.5 | 0 | 0 | 32.45 | 0 | 0
2025-05-26 02:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 32.45 | 0 | 0
2025-05-26 03:00 | 48.44 | 0 | 0 | 48.44 | 0 | 0 | 32.45 | 0 | 0
2025-05-26 04:00 | 48 | 0 | 0 | 48 | 0 | 0 | 32.45 | 0 | 0
2025-05-26 05:00 | 49.84 | 20.12 | 20.12 | 29.72 | 0 | 0 | 32.45 | 0 | 0
2025-05-26 06:00 | 50.98 | 55.47 | 55.47 | 0 | 4.49 | 0 | 36.71 | 0 | 0
2025-05-26 07:00 | 52.99 | 109.28 | 109.28 | 0 | 56.29 | 0 | 90.19 | 0 | 0
2025-05-26 08:00 | 56.14 | 123.77 | 123.77 | 0 | 67.63 | 0 | 154.44 | 0 | 0
2025-05-26 09:00 | 59.15 | 121.63 | 121.63 | 0 | 62.48 | 0 | 213.8 | 0 | 0
2025-05-26 10:00 | 60.9 | 56.11 | 56.11 | 0 | 0 | 4.79 | 208.76 | 0 | 0
2025-05-26 11:00 | 63.75 | 76.42 | 76.42 | 0 | 12.67 | 0 | 220.79 | 0 | 0
2025-05-26 12:00 | 66.43 | 101.34 | 101.34 | 0 | 34.91 | 0 | 253.95 | 0 | 0
2025-05-26 13:00 | 67.81 | 125.96 | 107.91 | 0 | 40.1 | 0 | 292.05 | 18.04 | 0
2025-05-26 14:00 | 69.2 | 102.72 | 69.2 | 0 | 0 | 0 | 292.05 | 33.52 | 0
2025-05-26 15:00 | 68.73 | 125.3 | 68.73 | 0 | 0 | 0 | 292.05 | 56.57 | 0
2025-05-26 16:00 | 69.36 | 119.71 | 69.36 | 0 | 0 | 0 | 292.05 | 50.35 | 0
2025-05-26 17:00 | 67.42 | 104.21 | 67.42 | 0 | 0 | 0 | 292.05 | 36.79 | 0
2025-05-26 18:00 | 67.25 | 70.25 | 67.25 | 0 | 0 | 0 | 292.05 | 3 | 0
2025-05-26 19:00 | 63.47 | 7.79 | 7.79 | 0 | 0 | 55.68 | 233.44 | 0 | 0
2025-05-26 20:00 | 61.29 | 0 | 0 | 0 | 0 | 61.29 | 168.92 | 0 | 0
2025-05-26 21:00 | 59.31 | 0 | 0 | 0 | 0 | 59.31 | 106.49 | 0 | 0
2025-05-26 22:00 | 57.15 | 0 | 0 | 0 | 0 | 57.15 | 46.33 | 0 | 0
2025-05-26 23:00 | 53.82 | 0 | 0 | 40.63 | 0 | 13.19 | 32.45 | 0 | 0
2025-05-27 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 32.45 | 0 | 0
2025-05-27 01:00 | 49.67 | 0 | 0 | 49.67 | 0 | 0 | 32.45 | 0 | 0
2025-05-27 02:00 | 48 | 0 | 0 | 48 | 0 | 0 | 32.45 | 0 | 0
2025-05-27 03:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 32.45 | 0 | 0
2025-05-27 04:00 | 47.91 | 0 | 0 | 47.91 | 0 | 0 | 32.45 | 0 | 0
2025-05-27 05:00 | 49.02 | 22.89 | 22.89 | 26.13 | 0 | 0 | 32.45 | 0 | 0
2025-05-27 06:00 | 51.66 | 87.41 | 87.41 | 0 | 35.75 | 0 | 66.41 | 0 | 0
2025-05-27 07:00 | 53.2 | 104.75 | 104.75 | 0 | 51.55 | 0 | 115.38 | 0 | 0
2025-05-27 08:00 | 56.53 | 116.91 | 116.91 | 0 | 60.38 | 0 | 172.75 | 0 | 0
2025-05-27 09:00 | 58.43 | 110.39 | 110.39 | 0 | 51.96 | 0 | 222.11 | 0 | 0
2025-05-27 10:00 | 61.86 | 108.58 | 108.58 | 0 | 46.71 | 0 | 266.48 | 0 | 0
2025-05-27 11:00 | 63.84 | 97.62 | 90.76 | 0 | 26.91 | 0 | 292.05 | 6.86 | 0
2025-05-27 12:00 | 66.77 | 79.32 | 66.77 | 0 | 0 | 0 | 292.05 | 12.55 | 0
2025-05-27 13:00 | 67.71 | 103.04 | 67.71 | 0 | 0 | 0 | 292.05 | 35.33 | 0
2025-05-27 14:00 | 69.08 | 89.07 | 69.08 | 0 | 0 | 0 | 292.05 | 19.99 | 0
2025-05-27 15:00 | 68.4 | 60.62 | 60.62 | 0 | 0 | 7.77 | 283.87 | 0 | 0
2025-05-27 16:00 | 68.49 | 56.28 | 56.28 | 0 | 0 | 12.21 | 271.01 | 0 | 0
2025-05-27 17:00 | 67.06 | 32.8 | 32.8 | 0 | 0 | 34.25 | 234.95 | 0 | 0
2025-05-27 18:00 | 65.86 | 19.16 | 19.16 | 0 | 0 | 46.7 | 185.8 | 0 | 0
2025-05-27 19:00 | 63.96 | 1.93 | 1.93 | 0 | 0 | 62.03 | 120.5 | 0 | 0
2025-05-27 20:00 | 61.35 | 0 | 0 | 0 | 0 | 61.35 | 55.92 | 0 | 0
2025-05-27 21:00 | 58.48 | 0 | 0 | 36.18 | 0 | 22.3 | 32.45 | 0 | 0
2025-05-27 22:00 | 55.66 | 0 | 0 | 55.66 | 0 | 0 | 32.45 | 0 | 0
2025-05-27 23:00 | 52.59 | 0 | 0 | 52.59 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 | 51.11 | 0 | 0 | 51.11 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 01:00 | 50.1 | 0 | 0 | 50.1 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 02:00 | 47.83 | 0 | 0 | 47.83 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 03:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 04:00 | 49.52 | 0 | 0 | 49.52 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 05:00 | 49.47 | 0.66 | 0.66 | 48.82 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 06:00 | 51.8 | 32.98 | 32.98 | 18.82 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 07:00 | 54.36 | 28.37 | 28.37 | 25.99 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 08:00 | 57.14 | 37.02 | 37.02 | 20.12 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 09:00 | 59 | 83.94 | 83.94 | 0 | 24.94 | 0 | 56.14 | 0 | 0
2025-05-28 10:00 | 62.59 | 89.2 | 89.2 | 0 | 26.61 | 0 | 81.42 | 0 | 0
2025-05-28 11:00 | 64.61 | 106.7 | 106.7 | 0 | 42.09 | 0 | 121.41 | 0 | 0
2025-05-28 12:00 | 68.97 | 97.14 | 97.14 | 0 | 28.17 | 0 | 148.17 | 0 | 0
2025-05-28 13:00 | 68.72 | 116.42 | 116.42 | 0 | 47.7 | 0 | 193.48 | 0 | 0
2025-05-28 14:00 | 70.1 | 61.31 | 61.31 | 0 | 0 | 8.8 | 184.22 | 0 | 0
2025-05-28 15:00 | 70.48 | 64.78 | 64.78 | 0 | 0 | 5.71 | 178.22 | 0 | 0
2025-05-28 16:00 | 69.88 | 64.64 | 64.64 | 0 | 0 | 5.24 | 172.71 | 0 | 0
2025-05-28 17:00 | 70.19 | 63.42 | 63.42 | 0 | 0 | 6.77 | 165.58 | 0 | 0
2025-05-28 18:00 | 68.95 | 52.32 | 52.32 | 0 | 0 | 16.63 | 148.07 | 0 | 0
2025-05-28 19:00 | 65.18 | 2.46 | 2.46 | 0 | 0 | 62.73 | 82.04 | 0 | 0
2025-05-28 20:00 | 62.04 | 0 | 0 | 14.93 | 0 | 47.11 | 32.45 | 0 | 0
2025-05-28 21:00 | 58.65 | 0 | 0 | 58.65 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 22:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 32.45 | 0 | 0
2025-05-28 23:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 32.45 | 0 | 0
2025-05-29 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 32.45 | 0 | 0
2025-05-29 01:00 | 50.04 | 0 | 0 | 50.04 | 0 | 0 | 32.45 | 0 | 0
2025-05-29 02:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 32.45 | 0 | 0
2025-05-29 03:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 32.45 | 0 | 0
2025-05-29 04:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 32.45 | 0 | 0
2025-05-29 05:00 | 49.38 | 17.48 | 17.48 | 31.9 | 0 | 0 | 32.45 | 0 | 0
2025-05-29 06:00 | 52.21 | 69.15 | 69.15 | 0 | 16.94 | 0 | 48.54 | 0 | 0
2025-05-29 07:00 | 54.51 | 96.07 | 96.07 | 0 | 41.56 | 0 | 88.03 | 0 | 0
2025-05-29 08:00 | 58.12 | 108.84 | 108.84 | 0 | 50.72 | 0 | 136.21 | 0 | 0
2025-05-29 09:00 | 61.62 | 110.7 | 110.7 | 0 | 49.08 | 0 | 182.84 | 0 | 0
2025-05-29 10:00 | 64.22 | 112.65 | 112.65 | 0 | 48.43 | 0 | 228.85 | 0 | 0
2025-05-29 11:00 | 67.8 | 108.46 | 108.46 | 0 | 40.66 | 0 | 267.47 | 0 | 0
2025-05-29 12:00 | 71.33 | 102.98 | 97.2 | 0 | 25.87 | 0 | 292.05 | 5.78 | 0
2025-05-29 13:00 | 73.69 | 103.99 | 73.69 | 0 | 0 | 0 | 292.05 | 30.31 | 0
2025-05-29 14:00 | 76.2 | 98.78 | 76.2 | 0 | 0 | 0 | 292.05 | 22.58 | 0
2025-05-29 15:00 | 76.55 | 100.74 | 76.55 | 0 | 0 | 0 | 292.05 | 24.19 | 0
2025-05-29 16:00 | 76.37 | 72.29 | 72.29 | 0 | 0 | 4.08 | 287.75 | 0 | 0
2025-05-29 17:00 | 74.41 | 46.93 | 46.93 | 0 | 0 | 27.49 | 258.82 | 0 | 0
2025-05-29 18:00 | 71.81 | 24.65 | 24.65 | 0 | 0 | 47.15 | 209.18 | 0 | 0
2025-05-29 19:00 | 69.12 | 4.33 | 4.33 | 0 | 0 | 64.79 | 140.99 | 0 | 0
2025-05-29 20:00 | 65.17 | 0 | 0 | 0 | 0 | 65.17 | 72.39 | 0 | 0
2025-05-29 21:00 | 61.26 | 0 | 0 | 23.32 | 0 | 37.94 | 32.45 | 0 | 0
2025-05-29 22:00 | 58.41 | 0 | 0 | 58.41 | 0 | 0 | 32.45 | 0 | 0
2025-05-29 23:00 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 32.45 | 0 | 0
2025-05-30 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 32.45 | 0 | 0
2025-05-30 01:00 | 49.61 | 0 | 0 | 49.61 | 0 | 0 | 32.45 | 0 | 0
2025-05-30 02:00 | 49.2 | 0 | 0 | 49.2 | 0 | 0 | 32.45 | 0 | 0
2025-05-30 03:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 32.45 | 0 | 0
2025-05-30 04:00 | 48.82 | 0 | 0 | 48.82 | 0 | 0 | 32.45 | 0 | 0
2025-05-30 05:00 | 50.69 | 22.44 | 22.44 | 28.25 | 0 | 0 | 32.45 | 0 | 0
2025-05-30 06:00 | 50.94 | 75.76 | 75.76 | 0 | 24.82 | 0 | 56.03 | 0 | 0
2025-05-30 07:00 | 54.38 | 98.35 | 98.35 | 0 | 43.97 | 0 | 97.8 | 0 | 0
2025-05-30 08:00 | 57.29 | 111.32 | 111.32 | 0 | 54.03 | 0 | 149.13 | 0 | 0
2025-05-30 09:00 | 60.09 | 110.94 | 110.94 | 0 | 50.85 | 0 | 197.44 | 0 | 0
2025-05-30 10:00 | 64.8 | 112.08 | 112.08 | 0 | 47.28 | 0 | 242.35 | 0 | 0
2025-05-30 11:00 | 66.54 | 110.41 | 110.41 | 0 | 43.86 | 0 | 284.02 | 0 | 0
2025-05-30 12:00 | 68.94 | 110.79 | 77.39 | 0 | 8.45 | 0 | 292.05 | 33.4 | 0
2025-05-30 13:00 | 71.13 | 109.49 | 71.13 | 0 | 0 | 0 | 292.05 | 38.36 | 0
2025-05-30 14:00 | 71.36 | 110.84 | 71.36 | 0 | 0 | 0 | 292.05 | 39.47 | 0
2025-05-30 15:00 | 72.41 | 107.76 | 72.41 | 0 | 0 | 0 | 292.05 | 35.35 | 0
2025-05-30 16:00 | 72.86 | 104.57 | 72.86 | 0 | 0 | 0 | 292.05 | 31.72 | 0
2025-05-30 17:00 | 70.8 | 93.81 | 70.8 | 0 | 0 | 0 | 292.05 | 23.01 | 0
2025-05-30 18:00 | 68.73 | 68.75 | 68.73 | 0 | 0 | 0 | 292.05 | 0.03 | 0
2025-05-30 19:00 | 67.23 | 8.97 | 8.97 | 0 | 0 | 58.27 | 230.72 | 0 | 0
2025-05-30 20:00 | 64.28 | 0 | 0 | 0 | 0 | 64.28 | 163.05 | 0 | 0
2025-05-30 21:00 | 60.71 | 0 | 0 | 0 | 0 | 60.71 | 99.15 | 0 | 0
2025-05-30 22:00 | 57.08 | 0 | 0 | 0 | 0 | 57.08 | 39.06 | 0 | 0
2025-05-30 23:00 | 54.28 | 0 | 0 | 48.01 | 0 | 6.28 | 32.45 | 0 | 0
2025-05-31 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 32.45 | 0 | 0
2025-05-31 01:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 32.45 | 0 | 0
2025-05-31 02:00 | 48.43 | 0 | 0 | 48.43 | 0 | 0 | 32.45 | 0 | 0
2025-05-31 03:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 32.45 | 0 | 0
2025-05-31 04:00 | 48.44 | 0 | 0 | 48.44 | 0 | 0 | 32.45 | 0 | 0
2025-05-31 05:00 | 49.36 | 29.23 | 29.23 | 20.13 | 0 | 0 | 32.45 | 0 | 0
2025-05-31 06:00 | 52.13 | 92.67 | 92.67 | 0 | 40.54 | 0 | 70.96 | 0 | 0
2025-05-31 07:00 | 54.58 | 113.34 | 113.34 | 0 | 58.76 | 0 | 126.78 | 0 | 0
2025-05-31 08:00 | 58.14 | 121.03 | 121.03 | 0 | 62.89 | 0 | 186.53 | 0 | 0
2025-05-31 09:00 | 59.96 | 122.72 | 122.72 | 0 | 62.76 | 0 | 246.15 | 0 | 0
2025-05-31 10:00 | 63.43 | 121.34 | 111.74 | 0 | 48.31 | 0 | 292.05 | 9.6 | 0
2025-05-31 11:00 | 66.19 | 119.25 | 66.19 | 0 | 0 | 0 | 292.05 | 53.06 | 0
2025-05-31 12:00 | 68.27 | 117.5 | 68.27 | 0 | 0 | 0 | 292.05 | 49.24 | 0
2025-05-31 13:00 | 70.56 | 119.28 | 70.56 | 0 | 0 | 0 | 292.05 | 48.72 | 0
2025-05-31 14:00 | 71.7 | 120.63 | 71.7 | 0 | 0 | 0 | 292.05 | 48.93 | 0
2025-05-31 15:00 | 71.86 | 119.35 | 71.86 | 0 | 0 | 0 | 292.05 | 47.49 | 0
2025-05-31 16:00 | 71.19 | 115.02 | 71.19 | 0 | 0 | 0 | 292.05 | 43.83 | 0
2025-05-31 17:00 | 70.01 | 100.58 | 70.01 | 0 | 0 | 0 | 292.05 | 30.56 | 0
2025-05-31 18:00 | 67.71 | 74.6 | 67.71 | 0 | 0 | 0 | 292.05 | 6.89 | 0
2025-05-31 19:00 | 65.64 | 8.12 | 8.12 | 0 | 0 | 57.51 | 231.51 | 0 | 0
2025-05-31 20:00 | 62.97 | 0 | 0 | 0 | 0 | 62.97 | 165.23 | 0 | 0
2025-05-31 21:00 | 59.73 | 0 | 0 | 0 | 0 | 59.73 | 102.35 | 0 | 0
2025-05-31 22:00 | 57.51 | 0 | 0 | 0 | 0 | 57.51 | 41.82 | 0 | 0
2025-05-31 23:00 | 55.06 | 0 | 0 | 46.16 | 0 | 8.9 | 32.45 | 0 | 0
2025-06-01 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 32.45 | 0 | 0
2025-06-01 01:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 32.45 | 0 | 0
2025-06-01 02:00 | 48.54 | 0 | 0 | 48.54 | 0 | 0 | 32.45 | 0 | 0
2025-06-01 03:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 32.45 | 0 | 0
2025-06-01 04:00 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 32.45 | 0 | 0
2025-06-01 05:00 | 50.54 | 30.5 | 30.5 | 20.05 | 0 | 0 | 32.45 | 0 | 0
2025-06-01 06:00 | 51.73 | 93.28 | 93.28 | 0 | 41.56 | 0 | 71.93 | 0 | 0
2025-06-01 07:00 | 54.87 | 113.48 | 113.48 | 0 | 58.6 | 0 | 127.6 | 0 | 0
2025-06-01 08:00 | 56.8 | 121.91 | 121.91 | 0 | 65.11 | 0 | 189.45 | 0 | 0
2025-06-01 09:00 | 59.2 | 124.1 | 124.1 | 0 | 64.9 | 0 | 251.11 | 0 | 0
2025-06-01 10:00 | 61.35 | 122.98 | 104.45 | 0 | 43.1 | 0 | 292.05 | 18.53 | 0
2025-06-01 11:00 | 64.25 | 121 | 64.25 | 0 | 0 | 0 | 292.05 | 56.75 | 0
2025-06-01 12:00 | 66.31 | 119.56 | 66.31 | 0 | 0 | 0 | 292.05 | 53.25 | 0
2025-06-01 13:00 | 67.27 | 120.29 | 67.27 | 0 | 0 | 0 | 292.05 | 53.02 | 0
2025-06-01 14:00 | 69.03 | 120.92 | 69.03 | 0 | 0 | 0 | 292.05 | 51.9 | 0
2025-06-01 15:00 | 68.88 | 120.48 | 68.88 | 0 | 0 | 0 | 292.05 | 51.6 | 0
2025-06-01 16:00 | 67.75 | 115.21 | 67.75 | 0 | 0 | 0 | 292.05 | 47.46 | 0
2025-06-01 17:00 | 66.98 | 104.89 | 66.98 | 0 | 0 | 0 | 292.05 | 37.91 | 0
2025-06-01 18:00 | 66.1 | 79.57 | 66.1 | 0 | 0 | 0 | 292.05 | 13.47 | 0
2025-06-01 19:00 | 63.7 | 8.44 | 8.44 | 0 | 0 | 55.26 | 233.88 | 0 | 0
2025-06-01 20:00 | 62.56 | 0 | 0 | 0 | 0 | 62.56 | 168.03 | 0 | 0
2025-06-01 21:00 | 59.71 | 0 | 0 | 0 | 0 | 59.71 | 105.18 | 0 | 0
2025-06-01 22:00 | 57.05 | 0 | 0 | 0 | 0 | 57.05 | 45.12 | 0 | 0
2025-06-01 23:00 | 54.71 | 0 | 0 | 42.67 | 0 | 12.04 | 32.45 | 0 | 0
2025-06-02 | 53 | 0 | 0 | 53 | 0 | 0 | 32.45 | 0 | 0
2025-06-02 01:00 | 50.42 | 0 | 0 | 50.42 | 0 | 0 | 32.45 | 0 | 0
2025-06-02 02:00 | 49.11 | 0 | 0 | 49.11 | 0 | 0 | 32.45 | 0 | 0
2025-06-02 03:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 32.45 | 0 | 0
2025-06-02 04:00 | 49.65 | 0 | 0 | 49.65 | 0 | 0 | 32.45 | 0 | 0
2025-06-02 05:00 | 50.18 | 28.22 | 28.22 | 21.96 | 0 | 0 | 32.45 | 0 | 0
2025-06-02 06:00 | 52.14 | 85.54 | 85.54 | 0 | 33.41 | 0 | 64.19 | 0 | 0
2025-06-02 07:00 | 54.43 | 105.29 | 105.29 | 0 | 50.86 | 0 | 112.51 | 0 | 0
2025-06-02 08:00 | 56.88 | 114.17 | 114.17 | 0 | 57.29 | 0 | 166.94 | 0 | 0
2025-06-02 09:00 | 58.32 | 116.57 | 116.57 | 0 | 58.25 | 0 | 222.27 | 0 | 0
2025-06-02 10:00 | 60.29 | 117.43 | 117.43 | 0 | 57.14 | 0 | 276.55 | 0 | 0
2025-06-02 11:00 | 62.32 | 115.6 | 78.63 | 0 | 16.31 | 0 | 292.05 | 36.97 | 0
2025-06-02 12:00 | 63.57 | 113.86 | 63.57 | 0 | 0 | 0 | 292.05 | 50.3 | 0
2025-06-02 13:00 | 64.61 | 113.78 | 64.61 | 0 | 0 | 0 | 292.05 | 49.16 | 0
2025-06-02 14:00 | 65.76 | 114.74 | 65.76 | 0 | 0 | 0 | 292.05 | 48.97 | 0
2025-06-02 15:00 | 65.53 | 112.94 | 65.53 | 0 | 0 | 0 | 292.05 | 47.41 | 0
2025-06-02 16:00 | 65.54 | 108.82 | 65.54 | 0 | 0 | 0 | 292.05 | 43.27 | 0
2025-06-02 17:00 | 64.32 | 97.42 | 64.32 | 0 | 0 | 0 | 292.05 | 33.09 | 0
2025-06-02 18:00 | 63.82 | 72.76 | 63.82 | 0 | 0 | 0 | 292.05 | 8.94 | 0
2025-06-02 19:00 | 63.05 | 8.52 | 8.52 | 0 | 0 | 54.53 | 234.65 | 0 | 0
2025-06-02 20:00 | 61.36 | 0 | 0 | 0 | 0 | 61.36 | 170.06 | 0 | 0
2025-06-02 21:00 | 58.64 | 0 | 0 | 0 | 0 | 58.64 | 108.33 | 0 | 0
2025-06-02 22:00 | 56.78 | 0 | 0 | 0 | 0 | 56.78 | 48.57 | 0 | 0
2025-06-02 23:00 | 55.43 | 0 | 0 | 40.12 | 0 | 15.31 | 32.45 | 0 | 0
2025-06-03 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 32.45 | 0 | 0
2025-06-03 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 32.45 | 0 | 0
2025-06-03 02:00 | 49.18 | 0 | 0 | 49.18 | 0 | 0 | 32.45 | 0 | 0
2025-06-03 03:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 32.45 | 0 | 0
2025-06-03 04:00 | 49.2 | 0 | 0 | 49.2 | 0 | 0 | 32.45 | 0 | 0
2025-06-03 05:00 | 50.46 | 26.46 | 26.46 | 24 | 0 | 0 | 32.45 | 0 | 0
2025-06-03 06:00 | 51.64 | 85.99 | 85.99 | 0 | 34.34 | 0 | 65.08 | 0 | 0
2025-06-03 07:00 | 54.31 | 109.48 | 109.48 | 0 | 55.17 | 0 | 117.48 | 0 | 0
2025-06-03 08:00 | 57.49 | 119.12 | 119.12 | 0 | 61.64 | 0 | 176.04 | 0 | 0
2025-06-03 09:00 | 60.38 | 121.73 | 121.73 | 0 | 61.35 | 0 | 234.32 | 0 | 0
2025-06-03 10:00 | 63.01 | 120.87 | 120.87 | 0 | 57.86 | 0 | 289.29 | 0 | 0
2025-06-03 11:00 | 65.78 | 118.83 | 68.69 | 0 | 2.91 | 0 | 292.05 | 50.14 | 0
2025-06-03 12:00 | 68.06 | 117.59 | 68.06 | 0 | 0 | 0 | 292.05 | 49.53 | 0
2025-06-03 13:00 | 70.1 | 118.27 | 70.1 | 0 | 0 | 0 | 292.05 | 48.17 | 0
2025-06-03 14:00 | 70.62 | 119.1 | 70.62 | 0 | 0 | 0 | 292.05 | 48.48 | 0
2025-06-03 15:00 | 71.21 | 117.31 | 71.21 | 0 | 0 | 0 | 292.05 | 46.1 | 0
2025-06-03 16:00 | 70.4 | 111.01 | 70.4 | 0 | 0 | 0 | 292.05 | 40.61 | 0
2025-06-03 17:00 | 69.94 | 97.52 | 69.94 | 0 | 0 | 0 | 292.05 | 27.57 | 0
2025-06-03 18:00 | 68.22 | 70.09 | 68.22 | 0 | 0 | 0 | 292.05 | 1.87 | 0
2025-06-03 19:00 | 66.3 | 9.96 | 9.96 | 0 | 0 | 56.35 | 232.74 | 0 | 0
2025-06-03 20:00 | 63.65 | 0 | 0 | 0 | 0 | 63.65 | 165.74 | 0 | 0
2025-06-03 21:00 | 60.76 | 0 | 0 | 0 | 0 | 60.76 | 101.78 | 0 | 0
2025-06-03 22:00 | 57.51 | 0 | 0 | 0 | 0 | 57.51 | 41.24 | 0 | 0
2025-06-03 23:00 | 54.92 | 0 | 0 | 46.56 | 0 | 8.35 | 32.45 | 0 | 0
2025-06-04 | 53.06 | 0 | 0 | 53.06 | 0 | 0 | 32.45 | 0 | 0
2025-06-04 01:00 | 50.27 | 0 | 0 | 50.27 | 0 | 0 | 32.45 | 0 | 0
2025-06-04 02:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 32.45 | 0 | 0
2025-06-04 03:00 | 49.05 | 0 | 0 | 49.05 | 0 | 0 | 32.45 | 0 | 0
2025-06-04 04:00 | 49.58 | 0 | 0 | 49.58 | 0 | 0 | 32.45 | 0 | 0
2025-06-04 05:00 | 50.18 | 23.1 | 23.1 | 27.08 | 0 | 0 | 32.45 | 0 | 0
2025-06-04 06:00 | 52.49 | 77.45 | 77.45 | 0 | 24.96 | 0 | 56.16 | 0 | 0
2025-06-04 07:00 | 55 | 100.88 | 100.88 | 0 | 45.87 | 0 | 99.74 | 0 | 0
2025-06-04 08:00 | 56.87 | 111.86 | 111.86 | 0 | 54.99 | 0 | 151.98 | 0 | 0
2025-06-04 09:00 | 61 | 118.01 | 118.01 | 0 | 57.01 | 0 | 206.14 | 0 | 0
2025-06-04 10:00 | 64.16 | 117.83 | 117.83 | 0 | 53.68 | 0 | 257.13 | 0 | 0
2025-06-04 11:00 | 67.06 | 116.17 | 103.81 | 0 | 36.75 | 0 | 292.05 | 12.35 | 0
2025-06-04 12:00 | 70.34 | 115.41 | 70.34 | 0 | 0 | 0 | 292.05 | 45.07 | 0
2025-06-04 13:00 | 70.93 | 116.16 | 70.93 | 0 | 0 | 0 | 292.05 | 45.23 | 0
2025-06-04 14:00 | 72.32 | 116.11 | 72.32 | 0 | 0 | 0 | 292.05 | 43.79 | 0
2025-06-04 15:00 | 71.83 | 114.52 | 71.83 | 0 | 0 | 0 | 292.05 | 42.68 | 0
2025-06-04 16:00 | 72.49 | 107.36 | 72.49 | 0 | 0 | 0 | 292.05 | 34.86 | 0
2025-06-04 17:00 | 71.34 | 93.03 | 71.34 | 0 | 0 | 0 | 292.05 | 21.69 | 0
2025-06-04 18:00 | 69.37 | 64.81 | 64.81 | 0 | 0 | 4.56 | 287.25 | 0 | 0
2025-06-04 19:00 | 67.69 | 9.78 | 9.78 | 0 | 0 | 57.91 | 226.29 | 0 | 0
2025-06-04 20:00 | 64.66 | 0 | 0 | 0 | 0 | 64.66 | 158.22 | 0 | 0
2025-06-04 21:00 | 61.15 | 0 | 0 | 0 | 0 | 61.15 | 93.85 | 0 | 0
2025-06-04 22:00 | 57.79 | 0 | 0 | 0 | 0 | 57.79 | 33.02 | 0 | 0
2025-06-04 23:00 | 55.56 | 0 | 0 | 55.02 | 0 | 0.54 | 32.45 | 0 | 0
2025-06-05 | 52.81 | 0 | 0 | 52.81 | 0 | 0 | 32.45 | 0 | 0
2025-06-05 01:00 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 32.45 | 0 | 0
2025-06-05 02:00 | 48.62 | 0 | 0 | 48.62 | 0 | 0 | 32.45 | 0 | 0
2025-06-05 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 32.45 | 0 | 0
2025-06-05 04:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 32.45 | 0 | 0
2025-06-05 05:00 | 51.88 | 18.75 | 18.75 | 33.13 | 0 | 0 | 32.45 | 0 | 0
2025-06-05 06:00 | 52.85 | 64.49 | 64.49 | 0 | 11.64 | 0 | 43.51 | 0 | 0
2025-06-05 07:00 | 55.3 | 84.83 | 84.83 | 0 | 29.53 | 0 | 71.56 | 0 | 0
2025-06-05 08:00 | 58.64 | 106.6 | 106.6 | 0 | 47.96 | 0 | 117.12 | 0 | 0
2025-06-05 09:00 | 63.57 | 103.18 | 103.18 | 0 | 39.61 | 0 | 154.75 | 0 | 0
2025-06-05 10:00 | 66.73 | 102.33 | 102.33 | 0 | 35.6 | 0 | 188.57 | 0 | 0
2025-06-05 11:00 | 72.15 | 106.94 | 106.94 | 0 | 34.79 | 0 | 221.62 | 0 | 0
2025-06-05 12:00 | 76.12 | 103.54 | 103.54 | 0 | 27.42 | 0 | 247.67 | 0 | 0
2025-06-05 13:00 | 78.99 | 102.44 | 102.44 | 0 | 23.45 | 0 | 269.95 | 0 | 0
2025-06-05 14:00 | 80.64 | 106.76 | 103.91 | 0 | 23.27 | 0 | 292.05 | 2.85 | 0
2025-06-05 15:00 | 81.72 | 99.97 | 81.72 | 0 | 0 | 0 | 292.05 | 18.25 | 0
2025-06-05 16:00 | 80.84 | 89.19 | 80.84 | 0 | 0 | 0 | 292.05 | 8.35 | 0
2025-06-05 17:00 | 78.39 | 73.16 | 73.16 | 0 | 0 | 5.23 | 286.54 | 0 | 0
2025-06-05 18:00 | 76.64 | 52.25 | 52.25 | 0 | 0 | 24.4 | 260.86 | 0 | 0
2025-06-05 19:00 | 71.7 | 8.85 | 8.85 | 0 | 0 | 62.85 | 194.71 | 0 | 0
2025-06-05 20:00 | 68 | 0 | 0 | 0 | 0 | 68 | 123.13 | 0 | 0
2025-06-05 21:00 | 62.08 | 0 | 0 | 0 | 0 | 62.08 | 57.78 | 0 | 0
2025-06-05 22:00 | 59.87 | 0 | 0 | 35.81 | 0 | 24.06 | 32.45 | 0 | 0
2025-06-05 23:00 | 56.42 | 0 | 0 | 56.42 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 | 52.8 | 0 | 0 | 52.8 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 01:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 02:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 04:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 05:00 | 50.41 | 3.27 | 3.27 | 47.14 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 06:00 | 52.48 | 6.99 | 6.99 | 45.49 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 07:00 | 55.93 | 17.27 | 17.27 | 38.65 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 08:00 | 58.87 | 33.84 | 33.84 | 25.03 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 09:00 | 61.3 | 80.72 | 80.72 | 0 | 19.43 | 0 | 50.91 | 0 | 0
2025-06-06 10:00 | 64.56 | 129.79 | 129.79 | 0 | 65.23 | 0 | 112.87 | 0 | 0
2025-06-06 11:00 | 67.68 | 90.35 | 90.35 | 0 | 22.67 | 0 | 134.41 | 0 | 0
2025-06-06 12:00 | 71.03 | 32.46 | 32.46 | 0 | 0 | 38.57 | 93.81 | 0 | 0
2025-06-06 13:00 | 72.2 | 34.49 | 34.49 | 0 | 0 | 37.71 | 54.12 | 0 | 0
2025-06-06 14:00 | 74.17 | 29.18 | 29.18 | 24.41 | 0 | 20.58 | 32.45 | 0 | 0
2025-06-06 15:00 | 74.81 | 35.39 | 35.39 | 39.42 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 16:00 | 73.95 | 3.85 | 3.85 | 70.1 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 17:00 | 73.21 | 2.16 | 2.16 | 71.05 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 18:00 | 70.51 | 0.63 | 0.63 | 69.87 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 19:00 | 67.9 | 0 | 0 | 67.9 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 20:00 | 64.44 | 0 | 0 | 64.44 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 21:00 | 62.16 | 0 | 0 | 62.16 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 22:00 | 58 | 0 | 0 | 58 | 0 | 0 | 32.45 | 0 | 0
2025-06-06 23:00 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 | 52.94 | 0 | 0 | 52.94 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 01:00 | 50.41 | 0 | 0 | 50.41 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 02:00 | 49.37 | 0 | 0 | 49.37 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 03:00 | 49.94 | 0 | 0 | 49.94 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 04:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 05:00 | 50.43 | 19.15 | 19.15 | 31.28 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 06:00 | 53.13 | 13.31 | 13.31 | 39.83 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 07:00 | 55.66 | 43.2 | 43.2 | 12.46 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 08:00 | 60.78 | 19.19 | 19.19 | 41.59 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 09:00 | 62.91 | 39.6 | 39.6 | 23.31 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 10:00 | 66.43 | 73.82 | 73.82 | 0 | 7.39 | 0 | 39.47 | 0 | 0
2025-06-07 11:00 | 71.06 | 87.76 | 87.76 | 0 | 16.7 | 0 | 55.33 | 0 | 0
2025-06-07 12:00 | 72.73 | 122.07 | 122.07 | 0 | 49.34 | 0 | 102.2 | 0 | 0
2025-06-07 13:00 | 76.3 | 99.16 | 99.16 | 0 | 22.87 | 0 | 123.92 | 0 | 0
2025-06-07 14:00 | 78.91 | 108.31 | 108.31 | 0 | 29.4 | 0 | 151.85 | 0 | 0
2025-06-07 15:00 | 78.43 | 101.03 | 101.03 | 0 | 22.61 | 0 | 173.33 | 0 | 0
2025-06-07 16:00 | 77.05 | 96.24 | 96.24 | 0 | 19.19 | 0 | 191.56 | 0 | 0
2025-06-07 17:00 | 76.05 | 32.92 | 32.92 | 0 | 0 | 43.13 | 146.16 | 0 | 0
2025-06-07 18:00 | 74.38 | 27.11 | 27.11 | 0 | 0 | 47.27 | 96.4 | 0 | 0
2025-06-07 19:00 | 70.54 | 4.56 | 4.56 | 5.22 | 0 | 60.76 | 32.45 | 0 | 0
2025-06-07 20:00 | 66.2 | 0 | 0 | 66.2 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 21:00 | 62.42 | 0 | 0 | 62.42 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 22:00 | 58.78 | 0 | 0 | 58.78 | 0 | 0 | 32.45 | 0 | 0
2025-06-07 23:00 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 | 53.62 | 0 | 0 | 53.62 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 01:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 02:00 | 50 | 0 | 0 | 50 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 03:00 | 48.68 | 0 | 0 | 48.68 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 04:00 | 49.1 | 0 | 0 | 49.1 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 05:00 | 51.27 | 18.5 | 18.5 | 32.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 06:00 | 52.28 | 18.04 | 18.04 | 34.24 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 07:00 | 55.33 | 75.48 | 75.48 | 0 | 20.15 | 0 | 51.59 | 0 | 0
2025-06-08 08:00 | 58.44 | 94.84 | 94.84 | 0 | 36.39 | 0 | 86.16 | 0 | 0
2025-06-08 09:00 | 60.7 | 98.08 | 98.08 | 0 | 37.38 | 0 | 121.68 | 0 | 0
2025-06-08 10:00 | 63.66 | 91.39 | 91.39 | 0 | 27.72 | 0 | 148.02 | 0 | 0
2025-06-08 11:00 | 66.77 | 73.79 | 73.79 | 0 | 7.03 | 0 | 154.69 | 0 | 0
2025-06-08 12:00 | 69.28 | 36.52 | 36.52 | 0 | 0 | 32.75 | 120.21 | 0 | 0
2025-06-08 13:00 | 71.22 | 60.03 | 60.03 | 0 | 0 | 11.19 | 108.43 | 0 | 0
2025-06-08 14:00 | 72.03 | 95.12 | 95.12 | 0 | 23.09 | 0 | 130.37 | 0 | 0
2025-06-08 15:00 | 72.11 | 82.69 | 82.69 | 0 | 10.58 | 0 | 140.42 | 0 | 0
2025-06-08 16:00 | 71.35 | 62.59 | 62.59 | 0 | 0 | 8.76 | 131.19 | 0 | 0
2025-06-08 17:00 | 70.16 | 52.11 | 52.11 | 0 | 0 | 18.04 | 112.2 | 0 | 0
2025-06-08 18:00 | 68.77 | 64.21 | 64.21 | 0 | 0 | 4.56 | 107.4 | 0 | 0
2025-06-08 19:00 | 67.02 | 9.76 | 9.76 | 0 | 0 | 57.26 | 47.13 | 0 | 0
2025-06-08 20:00 | 64.34 | 0 | 0 | 50.4 | 0 | 13.94 | 32.45 | 0 | 0
2025-06-08 21:00 | 60.22 | 0 | 0 | 60.22 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 22:00 | 57.9 | 0 | 0 | 57.9 | 0 | 0 | 32.45 | 0 | 0
2025-06-08 23:00 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 32.45 | 0 | 0
2025-06-09 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 32.45 | 0 | 0
2025-06-09 01:00 | 50.39 | 0 | 0 | 50.39 | 0 | 0 | 32.45 | 0 | 0
2025-06-09 02:00 | 51.04 | 0 | 0 | 51.04 | 0 | 0 | 32.45 | 0 | 0
2025-06-09 03:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 32.45 | 0 | 0
2025-06-09 04:00 | 50.05 | 0 | 0 | 50.05 | 0 | 0 | 32.45 | 0 | 0
2025-06-09 05:00 | 51.29 | 24.58 | 24.58 | 26.72 | 0 | 0 | 32.45 | 0 | 0
2025-06-09 06:00 | 52.81 | 79.03 | 79.03 | 0 | 26.22 | 0 | 57.36 | 0 | 0
2025-06-09 07:00 | 55.02 | 103.01 | 103.01 | 0 | 48 | 0 | 102.96 | 0 | 0
2025-06-09 08:00 | 59.07 | 112.22 | 112.22 | 0 | 53.15 | 0 | 153.45 | 0 | 0
2025-06-09 09:00 | 61.15 | 116.22 | 116.22 | 0 | 55.07 | 0 | 205.76 | 0 | 0
2025-06-09 10:00 | 63.53 | 118.83 | 118.83 | 0 | 55.3 | 0 | 258.3 | 0 | 0
2025-06-09 11:00 | 65.54 | 116.54 | 101.07 | 0 | 35.53 | 0 | 292.05 | 15.47 | 0
2025-06-09 12:00 | 66.46 | 115.36 | 66.46 | 0 | 0 | 0 | 292.05 | 48.89 | 0
2025-06-09 13:00 | 68.84 | 115.39 | 68.84 | 0 | 0 | 0 | 292.05 | 46.55 | 0
2025-06-09 14:00 | 68.52 | 114.89 | 68.52 | 0 | 0 | 0 | 292.05 | 46.37 | 0
2025-06-09 15:00 | 69.33 | 113.16 | 69.33 | 0 | 0 | 0 | 292.05 | 43.83 | 0
2025-06-09 16:00 | 68.12 | 107.98 | 68.12 | 0 | 0 | 0 | 292.05 | 39.85 | 0
2025-06-09 17:00 | 67.18 | 95.84 | 67.18 | 0 | 0 | 0 | 292.05 | 28.66 | 0
2025-06-09 18:00 | 67.13 | 70.03 | 67.13 | 0 | 0 | 0 | 292.05 | 2.9 | 0
2025-06-09 19:00 | 64.85 | 12.74 | 12.74 | 0 | 0 | 52.11 | 237.19 | 0 | 0
2025-06-09 20:00 | 62.12 | 0 | 0 | 0 | 0 | 62.12 | 171.8 | 0 | 0
2025-06-09 21:00 | 60.92 | 0 | 0 | 0 | 0 | 60.92 | 107.67 | 0 | 0
2025-06-09 22:00 | 59.07 | 0 | 0 | 0 | 0 | 59.07 | 45.5 | 0 | 0
2025-06-09 23:00 | 56.07 | 0 | 0 | 43.68 | 0 | 12.39 | 32.45 | 0 | 0
2025-06-10 | 53 | 0 | 0 | 53 | 0 | 0 | 32.45 | 0 | 0
2025-06-10 01:00 | 51.2 | 0 | 0 | 51.2 | 0 | 0 | 32.45 | 0 | 0
2025-06-10 02:00 | 50.4 | 0 | 0 | 50.4 | 0 | 0 | 32.45 | 0 | 0
2025-06-10 03:00 | 50.09 | 0 | 0 | 50.09 | 0 | 0 | 32.45 | 0 | 0
2025-06-10 04:00 | 49.78 | 0 | 0 | 49.78 | 0 | 0 | 32.45 | 0 | 0
2025-06-10 05:00 | 51.22 | 20.67 | 20.67 | 30.55 | 0 | 0 | 32.45 | 0 | 0
2025-06-10 06:00 | 53.28 | 65.83 | 65.83 | 0 | 12.55 | 0 | 44.37 | 0 | 0
2025-06-10 07:00 | 55.84 | 68.69 | 68.69 | 0 | 12.85 | 0 | 56.58 | 0 | 0
2025-06-10 08:00 | 58.21 | 91.61 | 91.61 | 0 | 33.4 | 0 | 88.31 | 0 | 0
2025-06-10 09:00 | 60.99 | 98.19 | 98.19 | 0 | 37.2 | 0 | 123.65 | 0 | 0
2025-06-10 10:00 | 64.37 | 104.41 | 104.41 | 0 | 40.04 | 0 | 161.69 | 0 | 0
2025-06-10 11:00 | 66.6 | 105.08 | 105.08 | 0 | 38.48 | 0 | 198.24 | 0 | 0
2025-06-10 12:00 | 68.12 | 106.76 | 106.76 | 0 | 38.64 | 0 | 234.95 | 0 | 0
2025-06-10 13:00 | 70.12 | 111.06 | 111.06 | 0 | 40.94 | 0 | 273.84 | 0 | 0
2025-06-10 14:00 | 69.91 | 111.34 | 89.08 | 0 | 19.17 | 0 | 292.05 | 22.26 | 0
2025-06-10 15:00 | 71.19 | 103.69 | 71.19 | 0 | 0 | 0 | 292.05 | 32.49 | 0
2025-06-10 16:00 | 70.37 | 106.29 | 70.37 | 0 | 0 | 0 | 292.05 | 35.92 | 0
2025-06-10 17:00 | 70.9 | 88.93 | 70.9 | 0 | 0 | 0 | 292.05 | 18.03 | 0
2025-06-10 18:00 | 67.28 | 58.76 | 58.76 | 0 | 0 | 8.53 | 283.07 | 0 | 0
2025-06-10 19:00 | 65.65 | 11.54 | 11.54 | 0 | 0 | 54.1 | 226.12 | 0 | 0
2025-06-10 20:00 | 63.89 | 0 | 0 | 0 | 0 | 63.89 | 158.87 | 0 | 0
2025-06-10 21:00 | 61.25 | 0 | 0 | 0 | 0 | 61.25 | 94.4 | 0 | 0
2025-06-10 22:00 | 59.25 | 0 | 0 | 0.4 | 0 | 58.85 | 32.45 | 0 | 0
2025-06-10 23:00 | 55.23 | 0 | 0 | 55.23 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 | 53.71 | 0 | 0 | 53.71 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 01:00 | 51.88 | 0 | 0 | 51.88 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 02:00 | 50.4 | 0 | 0 | 50.4 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 03:00 | 49.14 | 0 | 0 | 49.14 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 04:00 | 50.75 | 0 | 0 | 50.75 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 05:00 | 51.92 | 25.02 | 25.02 | 26.89 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 06:00 | 53.56 | 67.06 | 67.06 | 0 | 13.5 | 0 | 45.28 | 0 | 0
2025-06-11 07:00 | 55.85 | 88.62 | 88.62 | 0 | 32.77 | 0 | 76.4 | 0 | 0
2025-06-11 08:00 | 58.68 | 119.08 | 119.08 | 0 | 60.41 | 0 | 133.79 | 0 | 0
2025-06-11 09:00 | 61.43 | 128.89 | 128.89 | 0 | 67.45 | 0 | 197.87 | 0 | 0
2025-06-11 10:00 | 64.59 | 129.16 | 129.16 | 0 | 64.57 | 0 | 259.21 | 0 | 0
2025-06-11 11:00 | 66.8 | 85.62 | 85.62 | 0 | 18.82 | 0 | 277.1 | 0 | 0
2025-06-11 12:00 | 68.44 | 65.97 | 65.97 | 0 | 0 | 2.46 | 274.51 | 0 | 0
2025-06-11 13:00 | 69.88 | 67.34 | 67.34 | 0 | 0 | 2.54 | 271.84 | 0 | 0
2025-06-11 14:00 | 70.98 | 47.51 | 47.51 | 0 | 0 | 23.47 | 247.13 | 0 | 0
2025-06-11 15:00 | 71.79 | 23.87 | 23.87 | 0 | 0 | 47.91 | 196.7 | 0 | 0
2025-06-11 16:00 | 71.34 | 17.39 | 17.39 | 0 | 0 | 53.95 | 139.91 | 0 | 0
2025-06-11 17:00 | 70.51 | 5.43 | 5.43 | 0 | 0 | 65.08 | 71.4 | 0 | 0
2025-06-11 18:00 | 69.11 | 0.76 | 0.76 | 31.35 | 0 | 37 | 32.45 | 0 | 0
2025-06-11 19:00 | 66.47 | 0 | 0 | 66.47 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 20:00 | 65.01 | 0 | 0 | 65.01 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 21:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 22:00 | 58.35 | 0 | 0 | 58.35 | 0 | 0 | 32.45 | 0 | 0
2025-06-11 23:00 | 55.99 | 0 | 0 | 55.99 | 0 | 0 | 32.45 | 0 | 0
2025-06-12 | 52.73 | 0 | 0 | 52.73 | 0 | 0 | 32.45 | 0 | 0
2025-06-12 01:00 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 32.45 | 0 | 0
2025-06-12 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 32.45 | 0 | 0
2025-06-12 03:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 32.45 | 0 | 0
2025-06-12 04:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 32.45 | 0 | 0
2025-06-12 05:00 | 52.21 | 23.48 | 23.48 | 28.73 | 0 | 0 | 32.45 | 0 | 0
2025-06-12 06:00 | 53.46 | 71.72 | 71.72 | 0 | 18.25 | 0 | 49.79 | 0 | 0
2025-06-12 07:00 | 56.84 | 98.38 | 98.38 | 0 | 41.55 | 0 | 89.26 | 0 | 0
2025-06-12 08:00 | 61.06 | 106.83 | 106.83 | 0 | 45.78 | 0 | 132.75 | 0 | 0
2025-06-12 09:00 | 64.66 | 110.99 | 110.99 | 0 | 46.33 | 0 | 176.76 | 0 | 0
2025-06-12 10:00 | 70.06 | 115.39 | 115.39 | 0 | 45.33 | 0 | 219.83 | 0 | 0
2025-06-12 11:00 | 73.99 | 113.4 | 113.4 | 0 | 39.41 | 0 | 257.27 | 0 | 0
2025-06-12 12:00 | 78.35 | 113.32 | 113.32 | 0 | 34.97 | 0 | 290.49 | 0 | 0
2025-06-12 13:00 | 81.6 | 111.26 | 83.24 | 0 | 1.64 | 0 | 292.05 | 28.02 | 0
2025-06-12 14:00 | 84.38 | 111.27 | 84.38 | 0 | 0 | 0 | 292.05 | 26.89 | 0
2025-06-12 15:00 | 85.55 | 109.98 | 85.55 | 0 | 0 | 0 | 292.05 | 24.43 | 0
2025-06-12 16:00 | 84.12 | 108.16 | 84.12 | 0 | 0 | 0 | 292.05 | 24.05 | 0
2025-06-12 17:00 | 81.36 | 86.01 | 81.36 | 0 | 0 | 0 | 292.05 | 4.65 | 0
2025-06-12 18:00 | 78.04 | 60.74 | 60.74 | 0 | 0 | 17.3 | 273.84 | 0 | 0
2025-06-12 19:00 | 74.52 | 14.14 | 14.14 | 0 | 0 | 60.38 | 210.28 | 0 | 0
2025-06-12 20:00 | 70.54 | 0 | 0 | 0 | 0 | 70.54 | 136.02 | 0 | 0
2025-06-12 21:00 | 65.09 | 0 | 0 | 0 | 0 | 65.09 | 67.5 | 0 | 0
2025-06-12 22:00 | 60.3 | 0 | 0 | 27 | 0 | 33.3 | 32.45 | 0 | 0
2025-06-12 23:00 | 57.07 | 0 | 0 | 57.07 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 01:00 | 51.3 | 0 | 0 | 51.3 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 02:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 03:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 04:00 | 48.96 | 0 | 0 | 48.96 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 05:00 | 51.89 | 22.46 | 22.46 | 29.43 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 06:00 | 53.23 | 19.46 | 19.46 | 33.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 07:00 | 55.75 | 53.32 | 53.32 | 2.44 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 08:00 | 59.61 | 23.47 | 23.47 | 36.14 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 09:00 | 61.3 | 63.45 | 63.45 | 0 | 2.15 | 0 | 34.49 | 0 | 0
2025-06-13 10:00 | 64.08 | 92.13 | 92.13 | 0 | 28.05 | 0 | 61.14 | 0 | 0
2025-06-13 11:00 | 66.81 | 86.6 | 86.6 | 0 | 19.79 | 0 | 79.94 | 0 | 0
2025-06-13 12:00 | 69.11 | 16.89 | 16.89 | 7.1 | 0 | 45.12 | 32.45 | 0 | 0
2025-06-13 13:00 | 70.18 | 76.48 | 76.48 | 0 | 6.31 | 0 | 38.44 | 0 | 0
2025-06-13 14:00 | 70.53 | 76.07 | 76.07 | 0 | 5.54 | 0 | 43.71 | 0 | 0
2025-06-13 15:00 | 71.19 | 41.92 | 41.92 | 18.58 | 0 | 10.69 | 32.45 | 0 | 0
2025-06-13 16:00 | 71.96 | 49.33 | 49.33 | 22.63 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 17:00 | 70.44 | 5.93 | 5.93 | 64.5 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 18:00 | 69.13 | 59.11 | 59.11 | 10.02 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 19:00 | 66.75 | 1.14 | 1.14 | 65.6 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 20:00 | 64.09 | 0 | 0 | 64.09 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 21:00 | 62.49 | 0 | 0 | 62.49 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 22:00 | 58.67 | 0 | 0 | 58.67 | 0 | 0 | 32.45 | 0 | 0
2025-06-13 23:00 | 55.74 | 0 | 0 | 55.74 | 0 | 0 | 32.45 | 0 | 0
2025-06-14 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 32.45 | 0 | 0
2025-06-14 01:00 | 51.26 | 0 | 0 | 51.26 | 0 | 0 | 32.45 | 0 | 0
2025-06-14 02:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 32.45 | 0 | 0
2025-06-14 03:00 | 49.88 | 0 | 0 | 49.88 | 0 | 0 | 32.45 | 0 | 0
2025-06-14 04:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 32.45 | 0 | 0
2025-06-14 05:00 | 51.75 | 27.39 | 27.39 | 24.35 | 0 | 0 | 32.45 | 0 | 0
2025-06-14 06:00 | 54.77 | 65.14 | 65.14 | 0 | 10.36 | 0 | 42.3 | 0 | 0
2025-06-14 07:00 | 56.72 | 96.14 | 96.14 | 0 | 39.42 | 0 | 79.74 | 0 | 0
2025-06-14 08:00 | 58.76 | 86.57 | 86.57 | 0 | 27.8 | 0 | 106.16 | 0 | 0
2025-06-14 09:00 | 63.88 | 60.74 | 60.74 | 0 | 0 | 3.15 | 102.85 | 0 | 0
2025-06-14 10:00 | 67.64 | 71.66 | 71.66 | 0 | 4.02 | 0 | 106.67 | 0 | 0
2025-06-14 11:00 | 71.39 | 123.15 | 123.15 | 0 | 51.76 | 0 | 155.84 | 0 | 0
2025-06-14 12:00 | 74.8 | 104.69 | 104.69 | 0 | 29.89 | 0 | 184.23 | 0 | 0
2025-06-14 13:00 | 77.26 | 60.72 | 60.72 | 0 | 0 | 16.55 | 166.81 | 0 | 0
2025-06-14 14:00 | 78.91 | 63.53 | 63.53 | 0 | 0 | 15.38 | 150.63 | 0 | 0
2025-06-14 15:00 | 79.81 | 104.97 | 104.97 | 0 | 25.16 | 0 | 174.53 | 0 | 0
2025-06-14 16:00 | 78.66 | 122.41 | 122.41 | 0 | 43.74 | 0 | 216.08 | 0 | 0
2025-06-14 17:00 | 76.8 | 111.53 | 111.53 | 0 | 34.73 | 0 | 249.07 | 0 | 0
2025-06-14 18:00 | 76.19 | 85.52 | 85.52 | 0 | 9.32 | 0 | 257.93 | 0 | 0
2025-06-14 19:00 | 71.01 | 18.72 | 18.72 | 0 | 0 | 52.29 | 202.88 | 0 | 0
2025-06-14 20:00 | 67.67 | 0 | 0 | 0 | 0 | 67.67 | 131.65 | 0 | 0
2025-06-14 21:00 | 62.97 | 0 | 0 | 0 | 0 | 62.97 | 65.37 | 0 | 0
2025-06-14 22:00 | 60.01 | 0 | 0 | 28.73 | 0 | 31.27 | 32.45 | 0 | 0
2025-06-14 23:00 | 56.09 | 0 | 0 | 56.09 | 0 | 0 | 32.45 | 0 | 0
2025-06-15 | 53.43 | 0 | 0 | 53.43 | 0 | 0 | 32.45 | 0 | 0
2025-06-15 01:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 32.45 | 0 | 0
2025-06-15 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 32.45 | 0 | 0
2025-06-15 03:00 | 50.24 | 0 | 0 | 50.24 | 0 | 0 | 32.45 | 0 | 0
2025-06-15 04:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 32.45 | 0 | 0
2025-06-15 05:00 | 52.59 | 24.19 | 24.19 | 28.4 | 0 | 0 | 32.45 | 0 | 0
2025-06-15 06:00 | 53.06 | 47.97 | 47.97 | 5.09 | 0 | 0 | 32.45 | 0 | 0
2025-06-15 07:00 | 56.93 | 94.91 | 94.91 | 0 | 37.99 | 0 | 68.54 | 0 | 0
2025-06-15 08:00 | 59.48 | 68.88 | 68.88 | 0 | 9.4 | 0 | 77.47 | 0 | 0
2025-06-15 09:00 | 62.13 | 105.04 | 105.04 | 0 | 42.91 | 0 | 118.23 | 0 | 0
2025-06-15 10:00 | 64.15 | 90.88 | 90.88 | 0 | 26.74 | 0 | 143.64 | 0 | 0
2025-06-15 11:00 | 67.07 | 103.41 | 103.41 | 0 | 36.34 | 0 | 178.16 | 0 | 0
2025-06-15 12:00 | 68.74 | 105.96 | 105.96 | 0 | 37.22 | 0 | 213.52 | 0 | 0
2025-06-15 13:00 | 70.45 | 112.26 | 112.26 | 0 | 41.81 | 0 | 253.25 | 0 | 0
2025-06-15 14:00 | 71.2 | 106.18 | 106.18 | 0 | 34.98 | 0 | 286.48 | 0 | 0
2025-06-15 15:00 | 70.6 | 81.22 | 76.46 | 0 | 5.86 | 0 | 292.05 | 4.75 | 0
2025-06-15 16:00 | 71.88 | 80.12 | 71.88 | 0 | 0 | 0 | 292.05 | 8.24 | 0
2025-06-15 17:00 | 70.39 | 67.17 | 67.17 | 0 | 0 | 3.22 | 288.66 | 0 | 0
2025-06-15 18:00 | 68.73 | 56.61 | 56.61 | 0 | 0 | 12.12 | 275.91 | 0 | 0
2025-06-15 19:00 | 66.71 | 20.37 | 20.37 | 0 | 0 | 46.34 | 227.13 | 0 | 0
2025-06-15 20:00 | 64.75 | 0 | 0 | 0 | 0 | 64.75 | 158.97 | 0 | 0
2025-06-15 21:00 | 61.39 | 0 | 0 | 0 | 0 | 61.39 | 94.34 | 0 | 0
2025-06-15 22:00 | 57.84 | 0 | 0 | 0 | 0 | 57.84 | 33.46 | 0 | 0
2025-06-15 23:00 | 56.37 | 0 | 0 | 55.4 | 0 | 0.96 | 32.45 | 0 | 0
2025-06-16 | 54.2 | 0 | 0 | 54.2 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 01:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 02:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 03:00 | 50.08 | 0 | 0 | 50.08 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 04:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 05:00 | 51.29 | 33.48 | 33.48 | 17.81 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 06:00 | 53.56 | 108.26 | 108.26 | 0 | 54.69 | 0 | 84.41 | 0 | 0
2025-06-16 07:00 | 57.23 | 128.84 | 128.84 | 0 | 71.61 | 0 | 152.44 | 0 | 0
2025-06-16 08:00 | 60.08 | 137.15 | 136.49 | 0 | 76.4 | 0 | 225.02 | 0.66 | 0
2025-06-16 09:00 | 63.9 | 134.32 | 134.32 | 0 | 70.42 | 0 | 291.92 | 0 | 0
2025-06-16 10:00 | 69.1 | 121.64 | 69.23 | 0 | 0.14 | 0 | 292.05 | 52.4 | 0
2025-06-16 11:00 | 72.15 | 99.58 | 72.15 | 0 | 0 | 0 | 292.05 | 27.43 | 0
2025-06-16 12:00 | 75.56 | 86.85 | 75.56 | 0 | 0 | 0 | 292.05 | 11.29 | 0
2025-06-16 13:00 | 77.89 | 81.28 | 77.89 | 0 | 0 | 0 | 292.05 | 3.39 | 0
2025-06-16 14:00 | 79.49 | 67.11 | 67.11 | 0 | 0 | 12.38 | 279.02 | 0 | 0
2025-06-16 15:00 | 79.28 | 38.57 | 38.57 | 0 | 0 | 40.72 | 236.16 | 0 | 0
2025-06-16 16:00 | 80.27 | 29.7 | 29.7 | 0 | 0 | 50.57 | 182.93 | 0 | 0
2025-06-16 17:00 | 78.3 | 16.19 | 16.19 | 0 | 0 | 62.11 | 117.55 | 0 | 0
2025-06-16 18:00 | 75.3 | 7.39 | 7.39 | 0 | 0 | 67.91 | 46.07 | 0 | 0
2025-06-16 19:00 | 71.91 | 0 | 0 | 58.97 | 0 | 12.93 | 32.45 | 0 | 0
2025-06-16 20:00 | 68.49 | 0 | 0 | 68.49 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 21:00 | 63.34 | 0 | 0 | 63.34 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 22:00 | 59.97 | 0 | 0 | 59.97 | 0 | 0 | 32.45 | 0 | 0
2025-06-16 23:00 | 56.24 | 0 | 0 | 56.24 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 | 54.86 | 0 | 0 | 54.86 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 01:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 02:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 03:00 | 49.36 | 0 | 0 | 49.36 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 04:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 05:00 | 51.64 | 2.53 | 2.53 | 49.11 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 06:00 | 53.32 | 7.82 | 7.82 | 45.5 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 07:00 | 57.73 | 54.5 | 54.5 | 3.23 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 08:00 | 60.19 | 65.83 | 65.83 | 0 | 5.63 | 0 | 37.8 | 0 | 0
2025-06-17 09:00 | 63.86 | 91.73 | 91.73 | 0 | 27.88 | 0 | 64.29 | 0 | 0
2025-06-17 10:00 | 66.91 | 71.58 | 71.58 | 0 | 4.66 | 0 | 68.72 | 0 | 0
2025-06-17 11:00 | 71.07 | 61.89 | 61.89 | 0 | 0 | 9.18 | 59.05 | 0 | 0
2025-06-17 12:00 | 73.52 | 58.06 | 58.06 | 0 | 0 | 15.46 | 42.78 | 0 | 0
2025-06-17 13:00 | 75.9 | 36.21 | 36.21 | 29.87 | 0 | 9.81 | 32.45 | 0 | 0
2025-06-17 14:00 | 77.82 | 34.42 | 34.42 | 43.4 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 15:00 | 77.21 | 50.88 | 50.88 | 26.33 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 16:00 | 78.32 | 110.84 | 110.84 | 0 | 32.52 | 0 | 63.34 | 0 | 0
2025-06-17 17:00 | 76.13 | 58.92 | 58.92 | 0 | 0 | 17.21 | 45.23 | 0 | 0
2025-06-17 18:00 | 74.35 | 74.35 | 74.35 | 0 | 0 | 0 | 45.22 | 0 | 0
2025-06-17 19:00 | 70.17 | 20.47 | 20.47 | 37.56 | 0 | 12.14 | 32.45 | 0 | 0
2025-06-17 20:00 | 66.8 | 0 | 0 | 66.8 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 21:00 | 63.04 | 0 | 0 | 63.04 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 22:00 | 60.16 | 0 | 0 | 60.16 | 0 | 0 | 32.45 | 0 | 0
2025-06-17 23:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 | 53.79 | 0 | 0 | 53.79 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 01:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 02:00 | 50.01 | 0 | 0 | 50.01 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 03:00 | 50.17 | 0 | 0 | 50.17 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 04:00 | 50.41 | 0 | 0 | 50.41 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 05:00 | 51.61 | 24.19 | 24.19 | 27.42 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 06:00 | 54.79 | 82.69 | 82.69 | 0 | 27.9 | 0 | 58.95 | 0 | 0
2025-06-18 07:00 | 56.66 | 89.71 | 89.71 | 0 | 33.05 | 0 | 90.35 | 0 | 0
2025-06-18 08:00 | 60.44 | 76.48 | 76.48 | 0 | 16.03 | 0 | 105.58 | 0 | 0
2025-06-18 09:00 | 62.85 | 126.23 | 126.23 | 0 | 63.38 | 0 | 165.79 | 0 | 0
2025-06-18 10:00 | 66.52 | 114.39 | 114.39 | 0 | 47.87 | 0 | 211.27 | 0 | 0
2025-06-18 11:00 | 69.41 | 113.42 | 113.42 | 0 | 44 | 0 | 253.07 | 0 | 0
2025-06-18 12:00 | 71.18 | 91.99 | 91.99 | 0 | 20.82 | 0 | 272.85 | 0 | 0
2025-06-18 13:00 | 74.72 | 97.81 | 94.94 | 0 | 20.21 | 0 | 292.05 | 2.87 | 0
2025-06-18 14:00 | 75.18 | 74.44 | 74.44 | 0 | 0 | 0.74 | 291.28 | 0 | 0
2025-06-18 15:00 | 76.04 | 49.89 | 49.89 | 0 | 0 | 26.15 | 263.75 | 0 | 0
2025-06-18 16:00 | 74.87 | 35.37 | 35.37 | 0 | 0 | 39.5 | 222.17 | 0 | 0
2025-06-18 17:00 | 73.92 | 26.15 | 26.15 | 0 | 0 | 47.77 | 171.89 | 0 | 0
2025-06-18 18:00 | 71.6 | 1.53 | 1.53 | 0 | 0 | 70.07 | 98.13 | 0 | 0
2025-06-18 19:00 | 70.06 | 0.26 | 0.26 | 7.4 | 0 | 62.4 | 32.45 | 0 | 0
2025-06-18 20:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 21:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 22:00 | 60.49 | 0 | 0 | 60.49 | 0 | 0 | 32.45 | 0 | 0
2025-06-18 23:00 | 57.28 | 0 | 0 | 57.28 | 0 | 0 | 32.45 | 0 | 0
2025-06-19 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 32.45 | 0 | 0
2025-06-19 01:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 32.45 | 0 | 0
2025-06-19 02:00 | 50.37 | 0 | 0 | 50.37 | 0 | 0 | 32.45 | 0 | 0
2025-06-19 03:00 | 49.77 | 0 | 0 | 49.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-19 04:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 32.45 | 0 | 0
2025-06-19 05:00 | 52.12 | 11.85 | 11.85 | 40.27 | 0 | 0 | 32.45 | 0 | 0
2025-06-19 06:00 | 53.43 | 55.3 | 55.3 | 0 | 1.87 | 0 | 34.23 | 0 | 0
2025-06-19 07:00 | 56.74 | 90.86 | 90.86 | 0 | 34.11 | 0 | 66.63 | 0 | 0
2025-06-19 08:00 | 59.25 | 112.68 | 112.68 | 0 | 53.43 | 0 | 117.39 | 0 | 0
2025-06-19 09:00 | 63.36 | 113.8 | 113.8 | 0 | 50.44 | 0 | 165.31 | 0 | 0
2025-06-19 10:00 | 65.93 | 109.24 | 109.24 | 0 | 43.3 | 0 | 206.45 | 0 | 0
2025-06-19 11:00 | 70.17 | 103.82 | 103.82 | 0 | 33.65 | 0 | 238.41 | 0 | 0
2025-06-19 12:00 | 72.78 | 101.62 | 101.62 | 0 | 28.84 | 0 | 265.81 | 0 | 0
2025-06-19 13:00 | 75.61 | 103.29 | 103.23 | 0 | 27.62 | 0 | 292.05 | 0.06 | 0
2025-06-19 14:00 | 76.38 | 98.56 | 76.38 | 0 | 0 | 0 | 292.05 | 22.18 | 0
2025-06-19 15:00 | 76.19 | 90.87 | 76.19 | 0 | 0 | 0 | 292.05 | 14.68 | 0
2025-06-19 16:00 | 76.37 | 78.14 | 76.37 | 0 | 0 | 0 | 292.05 | 1.77 | 0
2025-06-19 17:00 | 73.96 | 54.17 | 54.17 | 0 | 0 | 19.79 | 271.22 | 0 | 0
2025-06-19 18:00 | 72.11 | 33.87 | 33.87 | 0 | 0 | 38.25 | 230.96 | 0 | 0
2025-06-19 19:00 | 70.07 | 8.45 | 8.45 | 0 | 0 | 61.62 | 166.09 | 0 | 0
2025-06-19 20:00 | 65.68 | 0 | 0 | 0 | 0 | 65.68 | 96.95 | 0 | 0
2025-06-19 21:00 | 63.36 | 0 | 0 | 2.09 | 0 | 61.28 | 32.45 | 0 | 0
2025-06-19 22:00 | 59.49 | 0 | 0 | 59.49 | 0 | 0 | 32.45 | 0 | 0
2025-06-19 23:00 | 56.89 | 0 | 0 | 56.89 | 0 | 0 | 32.45 | 0 | 0
2025-06-20 | 53.61 | 0 | 0 | 53.61 | 0 | 0 | 32.45 | 0 | 0
2025-06-20 01:00 | 52.31 | 0 | 0 | 52.31 | 0 | 0 | 32.45 | 0 | 0
2025-06-20 02:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 32.45 | 0 | 0
2025-06-20 03:00 | 51.05 | 0 | 0 | 51.05 | 0 | 0 | 32.45 | 0 | 0
2025-06-20 04:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 32.45 | 0 | 0
2025-06-20 05:00 | 51.72 | 25.01 | 25.01 | 26.71 | 0 | 0 | 32.45 | 0 | 0
2025-06-20 06:00 | 54.03 | 81.65 | 81.65 | 0 | 27.63 | 0 | 58.7 | 0 | 0
2025-06-20 07:00 | 56.09 | 108.1 | 108.1 | 0 | 52.02 | 0 | 108.11 | 0 | 0
2025-06-20 08:00 | 59.91 | 120.57 | 120.57 | 0 | 60.66 | 0 | 165.74 | 0 | 0
2025-06-20 09:00 | 63.08 | 124.42 | 124.42 | 0 | 61.34 | 0 | 224.01 | 0 | 0
2025-06-20 10:00 | 66.98 | 124.96 | 124.96 | 0 | 57.98 | 0 | 279.09 | 0 | 0
2025-06-20 11:00 | 68.1 | 123.57 | 81.74 | 0 | 13.64 | 0 | 292.05 | 41.83 | 0
2025-06-20 12:00 | 70.5 | 122.57 | 70.5 | 0 | 0 | 0 | 292.05 | 52.07 | 0
2025-06-20 13:00 | 72 | 109.1 | 72 | 0 | 0 | 0 | 292.05 | 37.1 | 0
2025-06-20 14:00 | 73.42 | 42.5 | 42.5 | 0 | 0 | 30.92 | 259.5 | 0 | 0
2025-06-20 15:00 | 73.85 | 47.09 | 47.09 | 0 | 0 | 26.76 | 231.34 | 0 | 0
2025-06-20 16:00 | 73.29 | 41.03 | 41.03 | 0 | 0 | 32.25 | 197.39 | 0 | 0
2025-06-20 17:00 | 72.83 | 98.21 | 98.21 | 0 | 25.38 | 0 | 221.5 | 0 | 0
2025-06-20 18:00 | 70.32 | 74.96 | 74.96 | 0 | 4.64 | 0 | 225.9 | 0 | 0
2025-06-20 19:00 | 68.91 | 17.57 | 17.57 | 0 | 0 | 51.34 | 171.86 | 0 | 0
2025-06-20 20:00 | 66.01 | 0 | 0 | 0 | 0 | 66.01 | 102.37 | 0 | 0
2025-06-20 21:00 | 62.77 | 0 | 0 | 0 | 0 | 62.77 | 36.29 | 0 | 0
2025-06-20 22:00 | 59.55 | 0 | 0 | 55.91 | 0 | 3.65 | 32.45 | 0 | 0
2025-06-20 23:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 32.45 | 0 | 0
2025-06-21 | 53.94 | 0 | 0 | 53.94 | 0 | 0 | 32.45 | 0 | 0
2025-06-21 01:00 | 52.35 | 0 | 0 | 52.35 | 0 | 0 | 32.45 | 0 | 0
2025-06-21 02:00 | 50.5 | 0 | 0 | 50.5 | 0 | 0 | 32.45 | 0 | 0
2025-06-21 03:00 | 51.31 | 0 | 0 | 51.31 | 0 | 0 | 32.45 | 0 | 0
2025-06-21 04:00 | 51.31 | 0 | 0 | 51.31 | 0 | 0 | 32.45 | 0 | 0
2025-06-21 05:00 | 51.87 | 13.05 | 13.05 | 38.82 | 0 | 0 | 32.45 | 0 | 0
2025-06-21 06:00 | 54.61 | 61.58 | 61.58 | 0 | 6.98 | 0 | 39.08 | 0 | 0
2025-06-21 07:00 | 57.31 | 96.5 | 96.5 | 0 | 39.18 | 0 | 76.3 | 0 | 0
2025-06-21 08:00 | 60.28 | 109.14 | 109.14 | 0 | 48.86 | 0 | 122.72 | 0 | 0
2025-06-21 09:00 | 64.59 | 119.79 | 119.79 | 0 | 55.2 | 0 | 175.15 | 0 | 0
2025-06-21 10:00 | 68.16 | 119.38 | 119.38 | 0 | 51.22 | 0 | 223.81 | 0 | 0
2025-06-21 11:00 | 71.62 | 109.79 | 109.79 | 0 | 38.17 | 0 | 260.08 | 0 | 0
2025-06-21 12:00 | 74.59 | 94.08 | 94.08 | 0 | 19.49 | 0 | 278.59 | 0 | 0
2025-06-21 13:00 | 77.24 | 106.55 | 91.41 | 0 | 14.17 | 0 | 292.05 | 15.14 | 0
2025-06-21 14:00 | 78.67 | 122.68 | 78.67 | 0 | 0 | 0 | 292.05 | 44.02 | 0
2025-06-21 15:00 | 79.11 | 126.38 | 79.11 | 0 | 0 | 0 | 292.05 | 47.27 | 0
2025-06-21 16:00 | 78.23 | 121.83 | 78.23 | 0 | 0 | 0 | 292.05 | 43.6 | 0
2025-06-21 17:00 | 77.87 | 110.23 | 77.87 | 0 | 0 | 0 | 292.05 | 32.36 | 0
2025-06-21 18:00 | 74.09 | 84.98 | 74.09 | 0 | 0 | 0 | 292.05 | 10.88 | 0
2025-06-21 19:00 | 71.73 | 20.53 | 20.53 | 0 | 0 | 51.2 | 238.16 | 0 | 0
2025-06-21 20:00 | 67.8 | 0 | 0 | 0 | 0 | 67.8 | 166.79 | 0 | 0
2025-06-21 21:00 | 65.1 | 0 | 0 | 0 | 0 | 65.1 | 98.27 | 0 | 0
2025-06-21 22:00 | 60.09 | 0 | 0 | 0 | 0 | 60.09 | 35.02 | 0 | 0
2025-06-21 23:00 | 56.82 | 0 | 0 | 54.38 | 0 | 2.44 | 32.45 | 0 | 0
2025-06-22 | 53.86 | 0 | 0 | 53.86 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 01:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 02:00 | 50.26 | 0 | 0 | 50.26 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 03:00 | 50.25 | 0 | 0 | 50.25 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 04:00 | 49.87 | 0 | 0 | 49.87 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 05:00 | 52.38 | 8.82 | 8.82 | 43.56 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 06:00 | 54.09 | 49.29 | 49.29 | 4.81 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 07:00 | 56.27 | 27.74 | 27.74 | 28.53 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 08:00 | 60.6 | 62.99 | 62.99 | 0 | 2.39 | 0 | 34.72 | 0 | 0
2025-06-22 09:00 | 62.61 | 92.17 | 92.17 | 0 | 29.56 | 0 | 62.81 | 0 | 0
2025-06-22 10:00 | 66.79 | 91.21 | 91.21 | 0 | 24.42 | 0 | 86.01 | 0 | 0
2025-06-22 11:00 | 68.89 | 97.39 | 97.39 | 0 | 28.5 | 0 | 113.08 | 0 | 0
2025-06-22 12:00 | 72.43 | 92.7 | 92.7 | 0 | 20.27 | 0 | 132.34 | 0 | 0
2025-06-22 13:00 | 73.81 | 96.58 | 96.58 | 0 | 22.77 | 0 | 153.97 | 0 | 0
2025-06-22 14:00 | 74.06 | 108.73 | 108.73 | 0 | 34.67 | 0 | 186.91 | 0 | 0
2025-06-22 15:00 | 74.48 | 79.6 | 79.6 | 0 | 5.12 | 0 | 191.78 | 0 | 0
2025-06-22 16:00 | 74.86 | 88.4 | 88.4 | 0 | 13.54 | 0 | 204.64 | 0 | 0
2025-06-22 17:00 | 73.31 | 63.14 | 63.14 | 0 | 0 | 10.17 | 193.94 | 0 | 0
2025-06-22 18:00 | 71.55 | 11.07 | 11.07 | 0 | 0 | 60.47 | 130.28 | 0 | 0
2025-06-22 19:00 | 69.87 | 2.67 | 2.67 | 0 | 0 | 67.2 | 59.54 | 0 | 0
2025-06-22 20:00 | 66.01 | 0 | 0 | 40.27 | 0 | 25.74 | 32.45 | 0 | 0
2025-06-22 21:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 22:00 | 60.54 | 0 | 0 | 60.54 | 0 | 0 | 32.45 | 0 | 0
2025-06-22 23:00 | 57.41 | 0 | 0 | 57.41 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 | 54.27 | 0 | 0 | 54.27 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 01:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 02:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 03:00 | 50.03 | 0 | 0 | 50.03 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 04:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 05:00 | 52.25 | 8.74 | 8.74 | 43.52 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 06:00 | 54.38 | 39.08 | 39.08 | 15.3 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 07:00 | 57.39 | 57.81 | 57.81 | 0 | 0.42 | 0 | 32.85 | 0 | 0
2025-06-23 08:00 | 59.06 | 61.35 | 61.35 | 0 | 2.29 | 0 | 35.02 | 0 | 0
2025-06-23 09:00 | 62.33 | 74.41 | 74.41 | 0 | 12.08 | 0 | 46.5 | 0 | 0
2025-06-23 10:00 | 65.14 | 108.2 | 108.2 | 0 | 43.05 | 0 | 87.4 | 0 | 0
2025-06-23 11:00 | 66.94 | 115.94 | 115.94 | 0 | 49 | 0 | 133.95 | 0 | 0
2025-06-23 12:00 | 69.79 | 116.05 | 116.05 | 0 | 46.25 | 0 | 177.89 | 0 | 0
2025-06-23 13:00 | 70.82 | 99.38 | 99.38 | 0 | 28.56 | 0 | 205.03 | 0 | 0
2025-06-23 14:00 | 71.28 | 97.38 | 97.38 | 0 | 26.1 | 0 | 229.82 | 0 | 0
2025-06-23 15:00 | 72.29 | 92.9 | 92.9 | 0 | 20.61 | 0 | 249.4 | 0 | 0
2025-06-23 16:00 | 70.38 | 55.51 | 55.51 | 0 | 0 | 14.88 | 233.74 | 0 | 0
2025-06-23 17:00 | 70.36 | 50.25 | 50.25 | 0 | 0 | 20.11 | 212.57 | 0 | 0
2025-06-23 18:00 | 69.26 | 20.26 | 20.26 | 0 | 0 | 49 | 160.99 | 0 | 0
2025-06-23 19:00 | 66.83 | 6.24 | 6.24 | 0 | 0 | 60.59 | 97.21 | 0 | 0
2025-06-23 20:00 | 65.2 | 0 | 0 | 3.67 | 0 | 61.53 | 32.45 | 0 | 0
2025-06-23 21:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 22:00 | 60 | 0 | 0 | 60 | 0 | 0 | 32.45 | 0 | 0
2025-06-23 23:00 | 57.4 | 0 | 0 | 57.4 | 0 | 0 | 32.45 | 0 | 0
2025-06-24 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 32.45 | 0 | 0
2025-06-24 01:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 32.45 | 0 | 0
2025-06-24 02:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 32.45 | 0 | 0
2025-06-24 03:00 | 50.91 | 0 | 0 | 50.91 | 0 | 0 | 32.45 | 0 | 0
2025-06-24 04:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 32.45 | 0 | 0
2025-06-24 05:00 | 51.05 | 21.29 | 21.29 | 29.76 | 0 | 0 | 32.45 | 0 | 0
2025-06-24 06:00 | 55.04 | 73.65 | 73.65 | 0 | 18.61 | 0 | 50.13 | 0 | 0
2025-06-24 07:00 | 57.01 | 92.31 | 92.31 | 0 | 35.3 | 0 | 83.66 | 0 | 0
2025-06-24 08:00 | 59.31 | 102.51 | 102.51 | 0 | 43.2 | 0 | 124.71 | 0 | 0
2025-06-24 09:00 | 62.99 | 107.06 | 107.06 | 0 | 44.06 | 0 | 166.56 | 0 | 0
2025-06-24 10:00 | 64.73 | 103.39 | 103.39 | 0 | 38.66 | 0 | 203.29 | 0 | 0
2025-06-24 11:00 | 66.93 | 102.34 | 102.34 | 0 | 35.41 | 0 | 236.93 | 0 | 0
2025-06-24 12:00 | 69.21 | 103.38 | 103.38 | 0 | 34.17 | 0 | 269.4 | 0 | 0
2025-06-24 13:00 | 71.17 | 102.41 | 95.02 | 0 | 23.85 | 0 | 292.05 | 7.39 | 0
2025-06-24 14:00 | 71.84 | 106.34 | 71.84 | 0 | 0 | 0 | 292.05 | 34.5 | 0
2025-06-24 15:00 | 71.46 | 110.41 | 71.46 | 0 | 0 | 0 | 292.05 | 38.95 | 0
2025-06-24 16:00 | 71.26 | 96.48 | 71.26 | 0 | 0 | 0 | 292.05 | 25.22 | 0
2025-06-24 17:00 | 70.68 | 77.93 | 70.68 | 0 | 0 | 0 | 292.05 | 7.25 | 0
2025-06-24 18:00 | 68.4 | 64.02 | 64.02 | 0 | 0 | 4.38 | 287.44 | 0 | 0
2025-06-24 19:00 | 67.6 | 12.92 | 12.92 | 0 | 0 | 54.68 | 229.89 | 0 | 0
2025-06-24 20:00 | 64.7 | 0 | 0 | 0 | 0 | 64.7 | 161.78 | 0 | 0
2025-06-24 21:00 | 62.65 | 0 | 0 | 0 | 0 | 62.65 | 95.83 | 0 | 0
2025-06-24 22:00 | 59.6 | 0 | 0 | 0 | 0 | 59.6 | 33.09 | 0 | 0
2025-06-24 23:00 | 57.2 | 0 | 0 | 56.59 | 0 | 0.61 | 32.45 | 0 | 0
2025-06-25 | 54.71 | 0 | 0 | 54.71 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 01:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 02:00 | 51.24 | 0 | 0 | 51.24 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 03:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 04:00 | 51.37 | 0 | 0 | 51.37 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 05:00 | 52.44 | 2.55 | 2.55 | 49.9 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 06:00 | 55.47 | 9.48 | 9.48 | 45.99 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 07:00 | 57.63 | 22.43 | 22.43 | 35.19 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 08:00 | 61 | 30.7 | 30.7 | 30.3 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 09:00 | 64.88 | 36.5 | 36.5 | 28.38 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 10:00 | 68.14 | 38.23 | 38.23 | 29.91 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 11:00 | 70.9 | 40.85 | 40.85 | 30.05 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 12:00 | 73.06 | 59.97 | 59.97 | 13.08 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 13:00 | 76.3 | 55.71 | 55.71 | 20.58 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 14:00 | 78.34 | 45.82 | 45.82 | 32.52 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 15:00 | 78.27 | 82.1 | 82.1 | 0 | 3.83 | 0 | 36.09 | 0 | 0
2025-06-25 16:00 | 78.36 | 66 | 66 | 8.9 | 0 | 3.46 | 32.45 | 0 | 0
2025-06-25 17:00 | 76.61 | 70.2 | 70.2 | 6.41 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 18:00 | 74.92 | 80.9 | 80.9 | 0 | 5.98 | 0 | 38.13 | 0 | 0
2025-06-25 19:00 | 71.2 | 24.3 | 24.3 | 41.5 | 0 | 5.4 | 32.45 | 0 | 0
2025-06-25 20:00 | 68.2 | 0 | 0 | 68.2 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 21:00 | 64.61 | 0 | 0 | 64.61 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 22:00 | 61.53 | 0 | 0 | 61.53 | 0 | 0 | 32.45 | 0 | 0
2025-06-25 23:00 | 56.62 | 0 | 0 | 56.62 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 01:00 | 53.02 | 0 | 0 | 53.02 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 02:00 | 51.99 | 0 | 0 | 51.99 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 03:00 | 50.87 | 0 | 0 | 50.87 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 04:00 | 51.07 | 0 | 0 | 51.07 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 05:00 | 52.97 | 3.21 | 3.21 | 49.76 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 06:00 | 55.31 | 13.27 | 13.27 | 42.03 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 07:00 | 57.8 | 24.88 | 24.88 | 32.93 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 08:00 | 61.98 | 41.01 | 41.01 | 20.97 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 09:00 | 66.77 | 46.1 | 46.1 | 20.66 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 10:00 | 71.74 | 59.35 | 59.35 | 12.39 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 11:00 | 75.7 | 73.27 | 73.27 | 2.43 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 12:00 | 79.42 | 55.26 | 55.26 | 24.16 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 13:00 | 82.61 | 45.37 | 45.37 | 37.24 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 14:00 | 85 | 52.88 | 52.88 | 32.12 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 15:00 | 85.38 | 42.62 | 42.62 | 42.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 16:00 | 84.82 | 21.94 | 21.94 | 62.88 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 17:00 | 82.11 | 12.1 | 12.1 | 70.01 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 18:00 | 80.05 | 5.22 | 5.22 | 74.83 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 19:00 | 74.76 | 0 | 0 | 74.76 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 20:00 | 70.58 | 0 | 0 | 70.58 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 21:00 | 66.22 | 0 | 0 | 66.22 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 22:00 | 62.81 | 0 | 0 | 62.81 | 0 | 0 | 32.45 | 0 | 0
2025-06-26 23:00 | 57.77 | 0 | 0 | 57.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-27 | 54.46 | 0 | 0 | 54.46 | 0 | 0 | 32.45 | 0 | 0
2025-06-27 01:00 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 32.45 | 0 | 0
2025-06-27 02:00 | 52.1 | 0 | 0 | 52.1 | 0 | 0 | 32.45 | 0 | 0
2025-06-27 03:00 | 49.41 | 0 | 0 | 49.41 | 0 | 0 | 32.45 | 0 | 0
2025-06-27 04:00 | 50.77 | 0 | 0 | 50.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-27 05:00 | 54 | 30.67 | 30.67 | 23.32 | 0 | 0 | 32.45 | 0 | 0
2025-06-27 06:00 | 55.09 | 89.48 | 89.48 | 0 | 34.39 | 0 | 65.12 | 0 | 0
2025-06-27 07:00 | 57.08 | 111.4 | 111.4 | 0 | 54.32 | 0 | 116.73 | 0 | 0
2025-06-27 08:00 | 60.94 | 119.75 | 119.75 | 0 | 58.81 | 0 | 172.6 | 0 | 0
2025-06-27 09:00 | 64.59 | 120.52 | 120.52 | 0 | 55.93 | 0 | 225.73 | 0 | 0
2025-06-27 10:00 | 68.6 | 120.22 | 120.22 | 0 | 51.62 | 0 | 274.78 | 0 | 0
2025-06-27 11:00 | 72.5 | 117.71 | 90.68 | 0 | 18.18 | 0 | 292.05 | 27.03 | 0
2025-06-27 12:00 | 74.71 | 115.41 | 74.71 | 0 | 0 | 0 | 292.05 | 40.7 | 0
2025-06-27 13:00 | 76.51 | 116.03 | 76.51 | 0 | 0 | 0 | 292.05 | 39.53 | 0
2025-06-27 14:00 | 78.6 | 116.62 | 78.6 | 0 | 0 | 0 | 292.05 | 38.03 | 0
2025-06-27 15:00 | 78.34 | 116.12 | 78.34 | 0 | 0 | 0 | 292.05 | 37.77 | 0
2025-06-27 16:00 | 77.69 | 113.85 | 77.69 | 0 | 0 | 0 | 292.05 | 36.16 | 0
2025-06-27 17:00 | 75.9 | 100.84 | 75.9 | 0 | 0 | 0 | 292.05 | 24.95 | 0
2025-06-27 18:00 | 73.73 | 78.94 | 73.73 | 0 | 0 | 0 | 292.05 | 5.21 | 0
2025-06-27 19:00 | 71.13 | 20.66 | 20.66 | 0 | 0 | 50.47 | 238.92 | 0 | 0
2025-06-27 20:00 | 67.59 | 0 | 0 | 0 | 0 | 67.59 | 167.78 | 0 | 0
2025-06-27 21:00 | 64.71 | 0 | 0 | 0 | 0 | 64.71 | 99.66 | 0 | 0
2025-06-27 22:00 | 60.36 | 0 | 0 | 0 | 0 | 60.36 | 36.12 | 0 | 0
2025-06-27 23:00 | 56.06 | 0 | 0 | 52.58 | 0 | 3.48 | 32.45 | 0 | 0
2025-06-28 | 54.32 | 0 | 0 | 54.32 | 0 | 0 | 32.45 | 0 | 0
2025-06-28 01:00 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 32.45 | 0 | 0
2025-06-28 02:00 | 51.03 | 0 | 0 | 51.03 | 0 | 0 | 32.45 | 0 | 0
2025-06-28 03:00 | 51.63 | 0 | 0 | 51.63 | 0 | 0 | 32.45 | 0 | 0
2025-06-28 04:00 | 51.03 | 0 | 0 | 51.03 | 0 | 0 | 32.45 | 0 | 0
2025-06-28 05:00 | 53.13 | 33.71 | 33.71 | 19.42 | 0 | 0 | 32.45 | 0 | 0
2025-06-28 06:00 | 54.83 | 86.86 | 86.86 | 0 | 32.03 | 0 | 62.88 | 0 | 0
2025-06-28 07:00 | 57.61 | 108.02 | 108.02 | 0 | 50.41 | 0 | 110.76 | 0 | 0
2025-06-28 08:00 | 60.45 | 113.88 | 113.88 | 0 | 53.43 | 0 | 161.52 | 0 | 0
2025-06-28 09:00 | 64.29 | 82.11 | 82.11 | 0 | 17.82 | 0 | 178.45 | 0 | 0
2025-06-28 10:00 | 67.37 | 11.75 | 11.75 | 0 | 0 | 55.62 | 119.9 | 0 | 0
2025-06-28 11:00 | 71.02 | 31.07 | 31.07 | 0 | 0 | 39.95 | 77.85 | 0 | 0
2025-06-28 12:00 | 73.53 | 48.46 | 48.46 | 0 | 0 | 25.08 | 51.45 | 0 | 0
2025-06-28 13:00 | 75.26 | 55.63 | 55.63 | 1.57 | 0 | 18.05 | 32.45 | 0 | 0
2025-06-28 14:00 | 77.53 | 104.32 | 104.32 | 0 | 26.79 | 0 | 57.9 | 0 | 0
2025-06-28 15:00 | 77.69 | 86.45 | 86.45 | 0 | 8.76 | 0 | 66.23 | 0 | 0
2025-06-28 16:00 | 76.81 | 122.89 | 122.89 | 0 | 46.09 | 0 | 110.01 | 0 | 0
2025-06-28 17:00 | 75.8 | 125.64 | 125.64 | 0 | 49.84 | 0 | 157.36 | 0 | 0
2025-06-28 18:00 | 73.61 | 103.5 | 103.5 | 0 | 29.89 | 0 | 185.75 | 0 | 0
2025-06-28 19:00 | 70.5 | 21.41 | 21.41 | 0 | 0 | 49.09 | 134.08 | 0 | 0
2025-06-28 20:00 | 67.79 | 0 | 0 | 0 | 0 | 67.79 | 62.73 | 0 | 0
2025-06-28 21:00 | 64.01 | 0 | 0 | 35.24 | 0 | 28.76 | 32.45 | 0 | 0
2025-06-28 22:00 | 60.39 | 0 | 0 | 60.39 | 0 | 0 | 32.45 | 0 | 0
2025-06-28 23:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 32.45 | 0 | 0
2025-06-29 | 54.77 | 0 | 0 | 54.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-29 01:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 32.45 | 0 | 0
2025-06-29 02:00 | 51.05 | 0 | 0 | 51.05 | 0 | 0 | 32.45 | 0 | 0
2025-06-29 03:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 32.45 | 0 | 0
2025-06-29 04:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 32.45 | 0 | 0
2025-06-29 05:00 | 53.41 | 30.43 | 30.43 | 22.99 | 0 | 0 | 32.45 | 0 | 0
2025-06-29 06:00 | 55.35 | 91.12 | 91.12 | 0 | 35.77 | 0 | 66.43 | 0 | 0
2025-06-29 07:00 | 58.76 | 111.16 | 111.16 | 0 | 52.41 | 0 | 116.22 | 0 | 0
2025-06-29 08:00 | 60.83 | 120.18 | 120.18 | 0 | 59.35 | 0 | 172.6 | 0 | 0
2025-06-29 09:00 | 63.63 | 121.68 | 121.68 | 0 | 58.05 | 0 | 227.74 | 0 | 0
2025-06-29 10:00 | 68.42 | 119.62 | 119.62 | 0 | 51.2 | 0 | 276.39 | 0 | 0
2025-06-29 11:00 | 72.45 | 118.28 | 88.93 | 0 | 16.49 | 0 | 292.05 | 29.34 | 0
2025-06-29 12:00 | 75.3 | 116 | 75.3 | 0 | 0 | 0 | 292.05 | 40.7 | 0
2025-06-29 13:00 | 77.73 | 117.48 | 77.73 | 0 | 0 | 0 | 292.05 | 39.75 | 0
2025-06-29 14:00 | 79.75 | 118.1 | 79.75 | 0 | 0 | 0 | 292.05 | 38.35 | 0
2025-06-29 15:00 | 79.79 | 118.03 | 79.79 | 0 | 0 | 0 | 292.05 | 38.24 | 0
2025-06-29 16:00 | 79.48 | 113.45 | 79.48 | 0 | 0 | 0 | 292.05 | 33.97 | 0
2025-06-29 17:00 | 77.12 | 104.38 | 77.12 | 0 | 0 | 0 | 292.05 | 27.26 | 0
2025-06-29 18:00 | 74.68 | 84.08 | 74.68 | 0 | 0 | 0 | 292.05 | 9.4 | 0
2025-06-29 19:00 | 72.97 | 21.36 | 21.36 | 0 | 0 | 51.61 | 237.72 | 0 | 0
2025-06-29 20:00 | 68.7 | 0 | 0 | 0 | 0 | 68.7 | 165.41 | 0 | 0
2025-06-29 21:00 | 64.6 | 0 | 0 | 0 | 0 | 64.6 | 97.41 | 0 | 0
2025-06-29 22:00 | 60.91 | 0 | 0 | 0 | 0 | 60.91 | 33.29 | 0 | 0
2025-06-29 23:00 | 57.51 | 0 | 0 | 56.71 | 0 | 0.8 | 32.45 | 0 | 0
2025-06-30 | 54.77 | 0 | 0 | 54.77 | 0 | 0 | 32.45 | 0 | 0
2025-06-30 01:00 | 52.2 | 0 | 0 | 52.2 | 0 | 0 | 32.45 | 0 | 0
2025-06-30 02:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 32.45 | 0 | 0
2025-06-30 03:00 | 50.89 | 0 | 0 | 50.89 | 0 | 0 | 32.45 | 0 | 0
2025-06-30 04:00 | 51.15 | 0 | 0 | 51.15 | 0 | 0 | 32.45 | 0 | 0
2025-06-30 05:00 | 53.4 | 24.92 | 24.92 | 28.48 | 0 | 0 | 32.45 | 0 | 0
2025-06-30 06:00 | 55.27 | 87.22 | 87.22 | 0 | 31.95 | 0 | 62.8 | 0 | 0
2025-06-30 07:00 | 58.35 | 100.18 | 100.18 | 0 | 41.82 | 0 | 102.53 | 0 | 0
2025-06-30 08:00 | 61.63 | 119.41 | 119.41 | 0 | 57.78 | 0 | 157.42 | 0 | 0
2025-06-30 09:00 | 66.2 | 140.67 | 140.67 | 0 | 74.47 | 0 | 228.17 | 0 | 0
2025-06-30 10:00 | 70.92 | 133.34 | 133.34 | 0 | 62.42 | 0 | 287.47 | 0 | 0
2025-06-30 11:00 | 75.47 | 81.76 | 80.29 | 0 | 4.83 | 0 | 292.05 | 1.47 | 0
2025-06-30 12:00 | 78.96 | 79.1 | 78.96 | 0 | 0 | 0 | 292.05 | 0.14 | 0
2025-06-30 13:00 | 82.63 | 61.87 | 61.87 | 0 | 0 | 20.76 | 270.2 | 0 | 0
2025-06-30 14:00 | 84.08 | 70.99 | 70.99 | 0 | 0 | 13.09 | 256.42 | 0 | 0
2025-06-30 15:00 | 85.15 | 66.72 | 66.72 | 0 | 0 | 18.43 | 237.01 | 0 | 0
2025-06-30 16:00 | 83.83 | 56.76 | 56.76 | 0 | 0 | 27.07 | 208.52 | 0 | 0
2025-06-30 17:00 | 81.19 | 47.29 | 47.29 | 0 | 0 | 33.9 | 172.84 | 0 | 0
2025-06-30 18:00 | 79.14 | 20.78 | 20.78 | 0 | 0 | 58.37 | 111.4 | 0 | 0
2025-06-30 19:00 | 75.47 | 5.22 | 5.22 | 0 | 0 | 70.25 | 37.45 | 0 | 0
2025-06-30 20:00 | 71.03 | 0 | 0 | 66.28 | 0 | 4.75 | 32.45 | 0 | 0
2025-06-30 21:00 | 66.47 | 0 | 0 | 66.47 | 0 | 0 | 32.45 | 0 | 0
2025-06-30 22:00 | 61.82 | 0 | 0 | 61.82 | 0 | 0 | 32.45 | 0 | 0
2025-06-30 23:00 | 57.82 | 0 | 0 | 57.82 | 0 | 0 | 32.45 | 0 | 0
2025-07-01 | 55.35 | 0 | 0 | 55.35 | 0 | 0 | 32.45 | 0 | 0
2025-07-01 01:00 | 53.09 | 0 | 0 | 53.09 | 0 | 0 | 32.45 | 0 | 0
2025-07-01 02:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 32.45 | 0 | 0
2025-07-01 03:00 | 51.59 | 0 | 0 | 51.59 | 0 | 0 | 32.45 | 0 | 0
2025-07-01 04:00 | 51.06 | 0 | 0 | 51.06 | 0 | 0 | 32.45 | 0 | 0
2025-07-01 05:00 | 52.59 | 20.34 | 20.34 | 32.25 | 0 | 0 | 32.45 | 0 | 0
2025-07-01 06:00 | 55.89 | 37.41 | 37.41 | 18.48 | 0 | 0 | 32.45 | 0 | 0
2025-07-01 07:00 | 58.39 | 71.05 | 71.05 | 0 | 12.65 | 0 | 44.47 | 0 | 0
2025-07-01 08:00 | 61.17 | 89.48 | 89.48 | 0 | 28.31 | 0 | 71.37 | 0 | 0
2025-07-01 09:00 | 65.16 | 107.57 | 107.57 | 0 | 42.41 | 0 | 111.66 | 0 | 0
2025-07-01 10:00 | 68.8 | 108.89 | 108.89 | 0 | 40.09 | 0 | 149.75 | 0 | 0
2025-07-01 11:00 | 70.84 | 112.96 | 112.96 | 0 | 42.12 | 0 | 189.76 | 0 | 0
2025-07-01 12:00 | 74.78 | 102.5 | 102.5 | 0 | 27.72 | 0 | 216.1 | 0 | 0
2025-07-01 13:00 | 77.54 | 112.8 | 112.8 | 0 | 35.26 | 0 | 249.6 | 0 | 0
2025-07-01 14:00 | 78.86 | 114.77 | 114.77 | 0 | 35.91 | 0 | 283.72 | 0 | 0
2025-07-01 15:00 | 79.66 | 123.8 | 88.44 | 0 | 8.77 | 0 | 292.05 | 35.37 | 0
2025-07-01 16:00 | 79.6 | 124.96 | 79.6 | 0 | 0 | 0 | 292.05 | 45.36 | 0
2025-07-01 17:00 | 77.4 | 120.71 | 77.4 | 0 | 0 | 0 | 292.05 | 43.31 | 0
2025-07-01 18:00 | 74.7 | 100.34 | 74.7 | 0 | 0 | 0 | 292.05 | 25.63 | 0
2025-07-01 19:00 | 72.37 | 27.1 | 27.1 | 0 | 0 | 45.27 | 244.4 | 0 | 0
2025-07-01 20:00 | 68.56 | 0 | 0 | 0 | 0 | 68.56 | 172.23 | 0 | 0
2025-07-01 21:00 | 64.94 | 0 | 0 | 0 | 0 | 64.94 | 103.87 | 0 | 0
2025-07-01 22:00 | 61.2 | 0 | 0 | 0 | 0 | 61.2 | 39.45 | 0 | 0
2025-07-01 23:00 | 59.08 | 0 | 0 | 52.43 | 0 | 6.65 | 32.45 | 0 | 0
2025-07-02 | 53.95 | 0 | 0 | 53.95 | 0 | 0 | 32.45 | 0 | 0
2025-07-02 01:00 | 52.72 | 0 | 0 | 52.72 | 0 | 0 | 32.45 | 0 | 0
2025-07-02 02:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 32.45 | 0 | 0
2025-07-02 03:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 32.45 | 0 | 0
2025-07-02 04:00 | 52 | 0 | 0 | 52 | 0 | 0 | 32.45 | 0 | 0
2025-07-02 05:00 | 53.33 | 30.42 | 30.42 | 22.9 | 0 | 0 | 32.45 | 0 | 0
2025-07-02 06:00 | 55.05 | 96.84 | 96.84 | 0 | 41.79 | 0 | 72.15 | 0 | 0
2025-07-02 07:00 | 57.7 | 118.62 | 118.62 | 0 | 60.92 | 0 | 130.03 | 0 | 0
2025-07-02 08:00 | 60.94 | 128.52 | 128.52 | 0 | 67.58 | 0 | 194.23 | 0 | 0
2025-07-02 09:00 | 64.27 | 130.92 | 130.92 | 0 | 66.65 | 0 | 257.55 | 0 | 0
2025-07-02 10:00 | 67.55 | 130.13 | 103.87 | 0 | 36.32 | 0 | 292.05 | 26.26 | 0
2025-07-02 11:00 | 70.47 | 128.14 | 70.47 | 0 | 0 | 0 | 292.05 | 57.67 | 0
2025-07-02 12:00 | 73.2 | 96.02 | 73.2 | 0 | 0 | 0 | 292.05 | 22.82 | 0
2025-07-02 13:00 | 75.35 | 84.02 | 75.35 | 0 | 0 | 0 | 292.05 | 8.68 | 0
2025-07-02 14:00 | 75.53 | 123.56 | 75.53 | 0 | 0 | 0 | 292.05 | 48.02 | 0
2025-07-02 15:00 | 76.02 | 111.71 | 76.02 | 0 | 0 | 0 | 292.05 | 35.69 | 0
2025-07-02 16:00 | 75.27 | 124.52 | 75.27 | 0 | 0 | 0 | 292.05 | 49.25 | 0
2025-07-02 17:00 | 75.4 | 114.56 | 75.4 | 0 | 0 | 0 | 292.05 | 39.15 | 0
2025-07-02 18:00 | 73.2 | 83.57 | 73.2 | 0 | 0 | 0 | 292.05 | 10.37 | 0
2025-07-02 19:00 | 70.82 | 17.3 | 17.3 | 0 | 0 | 53.52 | 235.72 | 0 | 0
2025-07-02 20:00 | 66.87 | 0 | 0 | 0 | 0 | 66.87 | 165.33 | 0 | 0
2025-07-02 21:00 | 65.22 | 0 | 0 | 0 | 0 | 65.22 | 96.67 | 0 | 0
2025-07-02 22:00 | 60.69 | 0 | 0 | 0 | 0 | 60.69 | 32.79 | 0 | 0
2025-07-02 23:00 | 57.92 | 0 | 0 | 57.6 | 0 | 0.32 | 32.45 | 0 | 0
2025-07-03 | 55.72 | 0 | 0 | 55.72 | 0 | 0 | 32.45 | 0 | 0
2025-07-03 01:00 | 52.51 | 0 | 0 | 52.51 | 0 | 0 | 32.45 | 0 | 0
2025-07-03 02:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 32.45 | 0 | 0
2025-07-03 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 32.45 | 0 | 0
2025-07-03 04:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 32.45 | 0 | 0
2025-07-03 05:00 | 53.16 | 26.82 | 26.82 | 26.33 | 0 | 0 | 32.45 | 0 | 0
2025-07-03 06:00 | 56.09 | 87.85 | 87.85 | 0 | 31.75 | 0 | 62.62 | 0 | 0
2025-07-03 07:00 | 58.97 | 109.3 | 109.3 | 0 | 50.32 | 0 | 110.43 | 0 | 0
2025-07-03 08:00 | 62.29 | 118.65 | 118.65 | 0 | 56.36 | 0 | 163.97 | 0 | 0
2025-07-03 09:00 | 65.8 | 120.39 | 120.39 | 0 | 54.59 | 0 | 215.83 | 0 | 0
2025-07-03 10:00 | 71.19 | 120.48 | 120.48 | 0 | 49.29 | 0 | 262.66 | 0 | 0
2025-07-03 11:00 | 74.15 | 118.63 | 105.09 | 0 | 30.94 | 0 | 292.05 | 13.54 | 0
2025-07-03 12:00 | 79.46 | 116.22 | 79.46 | 0 | 0 | 0 | 292.05 | 36.76 | 0
2025-07-03 13:00 | 81.73 | 116.89 | 81.73 | 0 | 0 | 0 | 292.05 | 35.16 | 0
2025-07-03 14:00 | 82.21 | 118.15 | 82.21 | 0 | 0 | 0 | 292.05 | 35.94 | 0
2025-07-03 15:00 | 84.02 | 117.56 | 84.02 | 0 | 0 | 0 | 292.05 | 33.54 | 0
2025-07-03 16:00 | 83.86 | 114.26 | 83.86 | 0 | 0 | 0 | 292.05 | 30.4 | 0
2025-07-03 17:00 | 81.51 | 103.72 | 81.51 | 0 | 0 | 0 | 292.05 | 22.21 | 0
2025-07-03 18:00 | 79.02 | 82.43 | 79.02 | 0 | 0 | 0 | 292.05 | 3.41 | 0
2025-07-03 19:00 | 74.47 | 20.04 | 20.04 | 0 | 0 | 54.44 | 234.75 | 0 | 0
2025-07-03 20:00 | 70.01 | 0 | 0 | 0 | 0 | 70.01 | 161.06 | 0 | 0
2025-07-03 21:00 | 66.26 | 0 | 0 | 0 | 0 | 66.26 | 91.31 | 0 | 0
2025-07-03 22:00 | 62.12 | 0 | 0 | 6.2 | 0 | 55.92 | 32.45 | 0 | 0
2025-07-03 23:00 | 58.2 | 0 | 0 | 58.2 | 0 | 0 | 32.45 | 0 | 0
2025-07-04 | 55.89 | 0 | 0 | 55.89 | 0 | 0 | 32.45 | 0 | 0
2025-07-04 01:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 32.45 | 0 | 0
2025-07-04 02:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 32.45 | 0 | 0
2025-07-04 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 32.45 | 0 | 0
2025-07-04 04:00 | 50.87 | 0 | 0 | 50.87 | 0 | 0 | 32.45 | 0 | 0
2025-07-04 05:00 | 52.38 | 21.79 | 21.79 | 30.6 | 0 | 0 | 32.45 | 0 | 0
2025-07-04 06:00 | 55.28 | 75.2 | 75.2 | 0 | 19.92 | 0 | 51.38 | 0 | 0
2025-07-04 07:00 | 59.21 | 99.26 | 99.26 | 0 | 40.04 | 0 | 89.42 | 0 | 0
2025-07-04 08:00 | 62.01 | 110.72 | 110.72 | 0 | 48.71 | 0 | 135.69 | 0 | 0
2025-07-04 09:00 | 64.67 | 117.28 | 117.28 | 0 | 52.62 | 0 | 185.67 | 0 | 0
2025-07-04 10:00 | 67.86 | 117.04 | 117.04 | 0 | 49.17 | 0 | 232.39 | 0 | 0
2025-07-04 11:00 | 73.47 | 112.27 | 112.27 | 0 | 38.79 | 0 | 269.24 | 0 | 0
2025-07-04 12:00 | 76.27 | 111.41 | 100.28 | 0 | 24.01 | 0 | 292.05 | 11.13 | 0
2025-07-04 13:00 | 79.39 | 111.17 | 79.39 | 0 | 0 | 0 | 292.05 | 31.78 | 0
2025-07-04 14:00 | 79.96 | 110.18 | 79.96 | 0 | 0 | 0 | 292.05 | 30.21 | 0
2025-07-04 15:00 | 81.12 | 107.73 | 81.12 | 0 | 0 | 0 | 292.05 | 26.61 | 0
2025-07-04 16:00 | 80.83 | 102.02 | 80.83 | 0 | 0 | 0 | 292.05 | 21.19 | 0
2025-07-04 17:00 | 78.6 | 93.09 | 78.6 | 0 | 0 | 0 | 292.05 | 14.49 | 0
2025-07-04 18:00 | 76.11 | 64.7 | 64.7 | 0 | 0 | 11.41 | 280.04 | 0 | 0
2025-07-04 19:00 | 73.12 | 16.37 | 16.37 | 0 | 0 | 56.75 | 220.3 | 0 | 0
2025-07-04 20:00 | 69.69 | 0 | 0 | 0 | 0 | 69.69 | 146.94 | 0 | 0
2025-07-04 21:00 | 65.52 | 0 | 0 | 0 | 0 | 65.52 | 77.97 | 0 | 0
2025-07-04 22:00 | 62.2 | 0 | 0 | 18.96 | 0 | 43.24 | 32.45 | 0 | 0
2025-07-04 23:00 | 57.99 | 0 | 0 | 57.99 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 | 54.78 | 0 | 0 | 54.78 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 01:00 | 54.1 | 0 | 0 | 54.1 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 02:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 03:00 | 50.94 | 0 | 0 | 50.94 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 04:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 05:00 | 53.15 | 1.6 | 1.6 | 51.55 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 06:00 | 55.25 | 38.61 | 38.61 | 16.64 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 07:00 | 58.62 | 39.13 | 39.13 | 19.49 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 08:00 | 62.52 | 38.64 | 38.64 | 23.89 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 09:00 | 67.08 | 57.27 | 57.27 | 9.81 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 10:00 | 70.51 | 75.94 | 75.94 | 0 | 5.43 | 0 | 37.61 | 0 | 0
2025-07-05 11:00 | 77.25 | 93.21 | 93.21 | 0 | 15.96 | 0 | 52.77 | 0 | 0
2025-07-05 12:00 | 80.37 | 105.11 | 105.11 | 0 | 24.73 | 0 | 76.27 | 0 | 0
2025-07-05 13:00 | 84.02 | 115.43 | 115.43 | 0 | 31.41 | 0 | 106.11 | 0 | 0
2025-07-05 14:00 | 85.16 | 67.77 | 67.77 | 0 | 0 | 17.39 | 87.8 | 0 | 0
2025-07-05 15:00 | 86.34 | 63.96 | 63.96 | 0 | 0 | 22.39 | 64.24 | 0 | 0
2025-07-05 16:00 | 85.51 | 81.43 | 81.43 | 0 | 0 | 4.09 | 59.94 | 0 | 0
2025-07-05 17:00 | 84.47 | 58.47 | 58.47 | 0 | 0 | 26 | 32.57 | 0 | 0
2025-07-05 18:00 | 80.15 | 3.54 | 3.54 | 76.49 | 0 | 0.12 | 32.45 | 0 | 0
2025-07-05 19:00 | 76.69 | 1.92 | 1.92 | 74.77 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 20:00 | 71.37 | 0 | 0 | 71.37 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 21:00 | 66.76 | 0 | 0 | 66.76 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 22:00 | 62.42 | 0 | 0 | 62.42 | 0 | 0 | 32.45 | 0 | 0
2025-07-05 23:00 | 59.27 | 0 | 0 | 59.27 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 | 54.41 | 0 | 0 | 54.41 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 01:00 | 52.47 | 0 | 0 | 52.47 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 02:00 | 50.77 | 0 | 0 | 50.77 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 03:00 | 50.72 | 0 | 0 | 50.72 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 04:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 05:00 | 52.33 | 24.8 | 24.8 | 27.52 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 06:00 | 54.99 | 91.6 | 91.6 | 0 | 36.61 | 0 | 67.23 | 0 | 0
2025-07-06 07:00 | 57.26 | 106.19 | 106.19 | 0 | 48.93 | 0 | 113.72 | 0 | 0
2025-07-06 08:00 | 61.17 | 109.66 | 109.66 | 0 | 48.48 | 0 | 159.78 | 0 | 0
2025-07-06 09:00 | 65.98 | 83.41 | 83.41 | 0 | 17.43 | 0 | 176.34 | 0 | 0
2025-07-06 10:00 | 69.3 | 62.04 | 62.04 | 0 | 0 | 7.27 | 168.69 | 0 | 0
2025-07-06 11:00 | 72.7 | 83.31 | 83.31 | 0 | 10.61 | 0 | 178.77 | 0 | 0
2025-07-06 12:00 | 75.13 | 55.54 | 55.54 | 0 | 0 | 19.59 | 158.15 | 0 | 0
2025-07-06 13:00 | 77.2 | 59.91 | 59.91 | 0 | 0 | 17.29 | 139.95 | 0 | 0
2025-07-06 14:00 | 78.87 | 86.98 | 86.98 | 0 | 8.11 | 0 | 147.66 | 0 | 0
2025-07-06 15:00 | 79.92 | 88.53 | 88.53 | 0 | 8.61 | 0 | 155.84 | 0 | 0
2025-07-06 16:00 | 79.87 | 79.43 | 79.43 | 0 | 0 | 0.44 | 155.37 | 0 | 0
2025-07-06 17:00 | 78.42 | 68.97 | 68.97 | 0 | 0 | 9.44 | 145.43 | 0 | 0
2025-07-06 18:00 | 75.94 | 61.51 | 61.51 | 0 | 0 | 14.44 | 130.23 | 0 | 0
2025-07-06 19:00 | 72.23 | 20.65 | 20.65 | 0 | 0 | 51.59 | 75.93 | 0 | 0
2025-07-06 20:00 | 69.12 | 0 | 0 | 27.81 | 0 | 41.31 | 32.45 | 0 | 0
2025-07-06 21:00 | 65.22 | 0 | 0 | 65.22 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 22:00 | 61.58 | 0 | 0 | 61.58 | 0 | 0 | 32.45 | 0 | 0
2025-07-06 23:00 | 59.28 | 0 | 0 | 59.28 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 | 54.37 | 0 | 0 | 54.37 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 01:00 | 53.03 | 0 | 0 | 53.03 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 02:00 | 52.39 | 0 | 0 | 52.39 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 03:00 | 50.58 | 0 | 0 | 50.58 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 04:00 | 51.46 | 0 | 0 | 51.46 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 05:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 06:00 | 55.14 | 10.02 | 10.02 | 45.12 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 07:00 | 57.08 | 26.98 | 26.98 | 30.1 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 08:00 | 61.07 | 36.2 | 36.2 | 24.88 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 09:00 | 64.02 | 42.95 | 42.95 | 21.07 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 10:00 | 66.64 | 43.59 | 43.59 | 23.05 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 11:00 | 68.29 | 60.61 | 60.61 | 7.68 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 12:00 | 70.63 | 90.38 | 90.38 | 0 | 19.74 | 0 | 51.21 | 0 | 0
2025-07-07 13:00 | 71.48 | 122.54 | 122.54 | 0 | 51.07 | 0 | 99.72 | 0 | 0
2025-07-07 14:00 | 72.56 | 118.81 | 118.81 | 0 | 46.24 | 0 | 143.65 | 0 | 0
2025-07-07 15:00 | 74.07 | 109.64 | 109.64 | 0 | 35.57 | 0 | 177.44 | 0 | 0
2025-07-07 16:00 | 72.78 | 116.84 | 116.84 | 0 | 44.07 | 0 | 219.31 | 0 | 0
2025-07-07 17:00 | 71.33 | 50.87 | 50.87 | 0 | 0 | 20.46 | 197.77 | 0 | 0
2025-07-07 18:00 | 70.68 | 29.85 | 29.85 | 0 | 0 | 40.83 | 154.8 | 0 | 0
2025-07-07 19:00 | 68.05 | 11.12 | 11.12 | 0 | 0 | 56.93 | 94.87 | 0 | 0
2025-07-07 20:00 | 65.79 | 0 | 0 | 6.49 | 0 | 59.3 | 32.45 | 0 | 0
2025-07-07 21:00 | 63.17 | 0 | 0 | 63.17 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 22:00 | 60.55 | 0 | 0 | 60.55 | 0 | 0 | 32.45 | 0 | 0
2025-07-07 23:00 | 58.35 | 0 | 0 | 58.35 | 0 | 0 | 32.45 | 0 | 0
2025-07-08 | 55.57 | 0 | 0 | 55.57 | 0 | 0 | 32.45 | 0 | 0
2025-07-08 01:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 32.45 | 0 | 0
2025-07-08 02:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 32.45 | 0 | 0
2025-07-08 03:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 32.45 | 0 | 0
2025-07-08 04:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 32.45 | 0 | 0
2025-07-08 05:00 | 52.87 | 20.87 | 20.87 | 32 | 0 | 0 | 32.45 | 0 | 0
2025-07-08 06:00 | 55.14 | 82.04 | 82.04 | 0 | 26.9 | 0 | 58 | 0 | 0
2025-07-08 07:00 | 58.11 | 109.06 | 109.06 | 0 | 50.95 | 0 | 106.41 | 0 | 0
2025-07-08 08:00 | 60.56 | 121.36 | 121.36 | 0 | 60.81 | 0 | 164.17 | 0 | 0
2025-07-08 09:00 | 63.68 | 124.07 | 124.07 | 0 | 60.39 | 0 | 221.54 | 0 | 0
2025-07-08 10:00 | 66.97 | 119.53 | 119.53 | 0 | 52.56 | 0 | 271.47 | 0 | 0
2025-07-08 11:00 | 68.3 | 7.29 | 7.29 | 0 | 0 | 61.02 | 207.24 | 0 | 0
2025-07-08 12:00 | 70.73 | 93.7 | 93.7 | 0 | 22.98 | 0 | 229.07 | 0 | 0
2025-07-08 13:00 | 71.66 | 123.66 | 123.66 | 0 | 52 | 0 | 278.47 | 0 | 0
2025-07-08 14:00 | 71.38 | 6.52 | 6.52 | 0 | 0 | 64.86 | 210.21 | 0 | 0
2025-07-08 15:00 | 71.8 | 119.8 | 119.8 | 0 | 48 | 0 | 255.81 | 0 | 0
2025-07-08 16:00 | 71.7 | 120.51 | 109.85 | 0 | 38.15 | 0 | 292.05 | 10.66 | 0
2025-07-08 17:00 | 70.95 | 107.59 | 70.95 | 0 | 0 | 0 | 292.05 | 36.64 | 0
2025-07-08 18:00 | 70.09 | 80.46 | 70.09 | 0 | 0 | 0 | 292.05 | 10.37 | 0
2025-07-08 19:00 | 68.7 | 17.89 | 17.89 | 0 | 0 | 50.8 | 238.57 | 0 | 0
2025-07-08 20:00 | 66.8 | 0 | 0 | 0 | 0 | 66.8 | 168.26 | 0 | 0
2025-07-08 21:00 | 63.72 | 0 | 0 | 0 | 0 | 63.72 | 101.18 | 0 | 0
2025-07-08 22:00 | 60.51 | 0 | 0 | 0 | 0 | 60.51 | 37.48 | 0 | 0
2025-07-08 23:00 | 56.85 | 0 | 0 | 52.06 | 0 | 4.78 | 32.45 | 0 | 0
2025-07-09 | 55.69 | 0 | 0 | 55.69 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 01:00 | 53.3 | 0 | 0 | 53.3 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 03:00 | 52.44 | 0 | 0 | 52.44 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 04:00 | 52.48 | 0 | 0 | 52.48 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 05:00 | 53.68 | 10.75 | 10.75 | 42.93 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 06:00 | 55.17 | 64.79 | 64.79 | 0 | 9.61 | 0 | 41.58 | 0 | 0
2025-07-09 07:00 | 58.63 | 98.08 | 98.08 | 0 | 39.45 | 0 | 79.06 | 0 | 0
2025-07-09 08:00 | 62.82 | 90.46 | 90.46 | 0 | 27.64 | 0 | 105.32 | 0 | 0
2025-07-09 09:00 | 67.03 | 100.18 | 100.18 | 0 | 33.15 | 0 | 136.81 | 0 | 0
2025-07-09 10:00 | 72.5 | 119.47 | 119.47 | 0 | 46.97 | 0 | 181.43 | 0 | 0
2025-07-09 11:00 | 77.17 | 109.21 | 109.21 | 0 | 32.04 | 0 | 211.87 | 0 | 0
2025-07-09 12:00 | 80.72 | 102.1 | 102.1 | 0 | 21.38 | 0 | 232.18 | 0 | 0
2025-07-09 13:00 | 85.26 | 87.94 | 87.94 | 0 | 2.68 | 0 | 234.72 | 0 | 0
2025-07-09 14:00 | 86.9 | 76.35 | 76.35 | 0 | 0 | 10.55 | 223.62 | 0 | 0
2025-07-09 15:00 | 86.74 | 56.23 | 56.23 | 0 | 0 | 30.51 | 191.5 | 0 | 0
2025-07-09 16:00 | 86.83 | 56.84 | 56.84 | 0 | 0 | 29.98 | 159.93 | 0 | 0
2025-07-09 17:00 | 84.8 | 48.59 | 48.59 | 0 | 0 | 36.21 | 121.82 | 0 | 0
2025-07-09 18:00 | 81.75 | 12.03 | 12.03 | 0 | 0 | 69.72 | 48.43 | 0 | 0
2025-07-09 19:00 | 76.83 | 1.01 | 1.01 | 60.64 | 0 | 15.18 | 32.45 | 0 | 0
2025-07-09 20:00 | 72.66 | 0 | 0 | 72.66 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 21:00 | 67.52 | 0 | 0 | 67.52 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 22:00 | 62.22 | 0 | 0 | 62.22 | 0 | 0 | 32.45 | 0 | 0
2025-07-09 23:00 | 58.18 | 0 | 0 | 58.18 | 0 | 0 | 32.45 | 0 | 0
2025-07-10 | 56.26 | 0 | 0 | 56.26 | 0 | 0 | 32.45 | 0 | 0
2025-07-10 01:00 | 53.93 | 0 | 0 | 53.93 | 0 | 0 | 32.45 | 0 | 0
2025-07-10 02:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 32.45 | 0 | 0
2025-07-10 03:00 | 52.17 | 0 | 0 | 52.17 | 0 | 0 | 32.45 | 0 | 0
2025-07-10 04:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 32.45 | 0 | 0
2025-07-10 05:00 | 53.67 | 15.9 | 15.9 | 37.77 | 0 | 0 | 32.45 | 0 | 0
2025-07-10 06:00 | 55.24 | 70.16 | 70.16 | 0 | 14.91 | 0 | 46.62 | 0 | 0
2025-07-10 07:00 | 59.82 | 97.88 | 97.88 | 0 | 38.05 | 0 | 82.77 | 0 | 0
2025-07-10 08:00 | 63.24 | 107.27 | 107.27 | 0 | 44.03 | 0 | 124.6 | 0 | 0
2025-07-10 09:00 | 67.38 | 105.47 | 105.47 | 0 | 38.09 | 0 | 160.78 | 0 | 0
2025-07-10 10:00 | 72.13 | 109.26 | 109.26 | 0 | 37.13 | 0 | 196.06 | 0 | 0
2025-07-10 11:00 | 77.41 | 108.47 | 108.47 | 0 | 31.06 | 0 | 225.57 | 0 | 0
2025-07-10 12:00 | 80.78 | 107.02 | 107.02 | 0 | 26.23 | 0 | 250.49 | 0 | 0
2025-07-10 13:00 | 85.42 | 108.99 | 108.99 | 0 | 23.57 | 0 | 272.88 | 0 | 0
2025-07-10 14:00 | 86.82 | 109.97 | 107.01 | 0 | 20.18 | 0 | 292.05 | 2.97 | 0
2025-07-10 15:00 | 88.26 | 109.52 | 88.26 | 0 | 0 | 0 | 292.05 | 21.26 | 0
2025-07-10 16:00 | 87.04 | 102.26 | 87.04 | 0 | 0 | 0 | 292.05 | 15.22 | 0
2025-07-10 17:00 | 84.94 | 81.87 | 81.87 | 0 | 0 | 3.07 | 288.82 | 0 | 0
2025-07-10 18:00 | 81.24 | 61 | 61 | 0 | 0 | 20.24 | 267.51 | 0 | 0
2025-07-10 19:00 | 77.2 | 15.27 | 15.27 | 0 | 0 | 61.93 | 202.32 | 0 | 0
2025-07-10 20:00 | 73.41 | 0 | 0 | 0 | 0 | 73.41 | 125.04 | 0 | 0
2025-07-10 21:00 | 68.27 | 0 | 0 | 0 | 0 | 68.27 | 53.18 | 0 | 0
2025-07-10 22:00 | 63.15 | 0 | 0 | 43.46 | 0 | 19.7 | 32.45 | 0 | 0
2025-07-10 23:00 | 58.94 | 0 | 0 | 58.94 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 | 55.96 | 0 | 0 | 55.96 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 01:00 | 53.89 | 0 | 0 | 53.89 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 02:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 03:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 04:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 05:00 | 53.88 | 1.51 | 1.51 | 52.38 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 06:00 | 56.57 | 10.44 | 10.44 | 46.13 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 07:00 | 58.44 | 12.22 | 12.22 | 46.22 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 08:00 | 60.65 | 26.25 | 26.25 | 34.4 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 09:00 | 65.54 | 43.08 | 43.08 | 22.46 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 10:00 | 68.28 | 49.52 | 49.52 | 18.76 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 11:00 | 71.62 | 52.27 | 52.27 | 19.36 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 12:00 | 75.02 | 73.95 | 73.95 | 1.07 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 13:00 | 76.93 | 78.18 | 78.18 | 0 | 1.25 | 0 | 33.64 | 0 | 0
2025-07-11 14:00 | 77.87 | 53.67 | 53.67 | 23.08 | 0 | 1.13 | 32.45 | 0 | 0
2025-07-11 15:00 | 78.24 | 26.63 | 26.63 | 51.61 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 16:00 | 78.18 | 4.22 | 4.22 | 73.96 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 17:00 | 76.6 | 3.12 | 3.12 | 73.48 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 18:00 | 74.15 | 8.42 | 8.42 | 65.74 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 19:00 | 71.79 | 1.32 | 1.32 | 70.47 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 20:00 | 68.9 | 0 | 0 | 68.9 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 21:00 | 65.15 | 0 | 0 | 65.15 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 22:00 | 61 | 0 | 0 | 61 | 0 | 0 | 32.45 | 0 | 0
2025-07-11 23:00 | 58.89 | 0 | 0 | 58.89 | 0 | 0 | 32.45 | 0 | 0
2025-07-12 | 54.18 | 0 | 0 | 54.18 | 0 | 0 | 32.45 | 0 | 0
2025-07-12 01:00 | 53.13 | 0 | 0 | 53.13 | 0 | 0 | 32.45 | 0 | 0
2025-07-12 02:00 | 51.65 | 0 | 0 | 51.65 | 0 | 0 | 32.45 | 0 | 0
2025-07-12 03:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 32.45 | 0 | 0
2025-07-12 04:00 | 52.24 | 0 | 0 | 52.24 | 0 | 0 | 32.45 | 0 | 0
2025-07-12 05:00 | 53.91 | 18.4 | 18.4 | 35.51 | 0 | 0 | 32.45 | 0 | 0
2025-07-12 06:00 | 55.19 | 77.63 | 77.63 | 0 | 22.44 | 0 | 53.77 | 0 | 0
2025-07-12 07:00 | 58.67 | 91.5 | 91.5 | 0 | 32.83 | 0 | 84.96 | 0 | 0
2025-07-12 08:00 | 61.71 | 105.15 | 105.15 | 0 | 43.44 | 0 | 126.23 | 0 | 0
2025-07-12 09:00 | 64.17 | 108.86 | 108.86 | 0 | 44.69 | 0 | 168.68 | 0 | 0
2025-07-12 10:00 | 69.33 | 111.08 | 111.08 | 0 | 41.75 | 0 | 208.34 | 0 | 0
2025-07-12 11:00 | 70.72 | 109.46 | 109.46 | 0 | 38.74 | 0 | 245.14 | 0 | 0
2025-07-12 12:00 | 74.23 | 106.16 | 106.16 | 0 | 31.93 | 0 | 275.48 | 0 | 0
2025-07-12 13:00 | 76.17 | 107.32 | 93.62 | 0 | 17.45 | 0 | 292.05 | 13.71 | 0
2025-07-12 14:00 | 77.33 | 108.22 | 77.33 | 0 | 0 | 0 | 292.05 | 30.88 | 0
2025-07-12 15:00 | 77.36 | 101.46 | 77.36 | 0 | 0 | 0 | 292.05 | 24.1 | 0
2025-07-12 16:00 | 77.61 | 96.32 | 77.61 | 0 | 0 | 0 | 292.05 | 18.71 | 0
2025-07-12 17:00 | 75.2 | 85.72 | 75.2 | 0 | 0 | 0 | 292.05 | 10.52 | 0
2025-07-12 18:00 | 73.99 | 75.41 | 73.99 | 0 | 0 | 0 | 292.05 | 1.42 | 0
2025-07-12 19:00 | 71.16 | 15.51 | 15.51 | 0 | 0 | 55.65 | 233.47 | 0 | 0
2025-07-12 20:00 | 68.04 | 0 | 0 | 0 | 0 | 68.04 | 161.85 | 0 | 0
2025-07-12 21:00 | 65.24 | 0 | 0 | 0 | 0 | 65.24 | 93.18 | 0 | 0
2025-07-12 22:00 | 62.15 | 0 | 0 | 4.46 | 0 | 57.69 | 32.45 | 0 | 0
2025-07-12 23:00 | 58.2 | 0 | 0 | 58.2 | 0 | 0 | 32.45 | 0 | 0
2025-07-13 | 56.17 | 0 | 0 | 56.17 | 0 | 0 | 32.45 | 0 | 0
2025-07-13 01:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 32.45 | 0 | 0
2025-07-13 02:00 | 51.54 | 0 | 0 | 51.54 | 0 | 0 | 32.45 | 0 | 0
2025-07-13 03:00 | 51.38 | 0 | 0 | 51.38 | 0 | 0 | 32.45 | 0 | 0
2025-07-13 04:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 32.45 | 0 | 0
2025-07-13 05:00 | 53.08 | 17.9 | 17.9 | 35.18 | 0 | 0 | 32.45 | 0 | 0
2025-07-13 06:00 | 56 | 81.16 | 81.16 | 0 | 25.16 | 0 | 56.35 | 0 | 0
2025-07-13 07:00 | 59.11 | 105.58 | 105.58 | 0 | 46.47 | 0 | 100.5 | 0 | 0
2025-07-13 08:00 | 62.14 | 115.26 | 115.26 | 0 | 53.12 | 0 | 150.96 | 0 | 0
2025-07-13 09:00 | 66.58 | 118.5 | 118.5 | 0 | 51.92 | 0 | 200.29 | 0 | 0
2025-07-13 10:00 | 72.34 | 118.46 | 118.46 | 0 | 46.12 | 0 | 244.1 | 0 | 0
2025-07-13 11:00 | 76.34 | 115.63 | 115.63 | 0 | 39.29 | 0 | 281.43 | 0 | 0
2025-07-13 12:00 | 81.03 | 114.14 | 92.21 | 0 | 11.18 | 0 | 292.05 | 21.93 | 0
2025-07-13 13:00 | 84.55 | 115.4 | 84.55 | 0 | 0 | 0 | 292.05 | 30.85 | 0
2025-07-13 14:00 | 85.64 | 115.11 | 85.64 | 0 | 0 | 0 | 292.05 | 29.47 | 0
2025-07-13 15:00 | 86.3 | 114.6 | 86.3 | 0 | 0 | 0 | 292.05 | 28.3 | 0
2025-07-13 16:00 | 87.11 | 109.53 | 87.11 | 0 | 0 | 0 | 292.05 | 22.42 | 0
2025-07-13 17:00 | 84.34 | 94.03 | 84.34 | 0 | 0 | 0 | 292.05 | 9.69 | 0
2025-07-13 18:00 | 80.67 | 68.65 | 68.65 | 0 | 0 | 12.02 | 279.4 | 0 | 0
2025-07-13 19:00 | 76.28 | 13.55 | 13.55 | 0 | 0 | 62.73 | 213.37 | 0 | 0
2025-07-13 20:00 | 71.87 | 0 | 0 | 0 | 0 | 71.87 | 137.71 | 0 | 0
2025-07-13 21:00 | 66.81 | 0 | 0 | 0 | 0 | 66.81 | 67.39 | 0 | 0
2025-07-13 22:00 | 63.38 | 0 | 0 | 30.19 | 0 | 33.19 | 32.45 | 0 | 0
2025-07-13 23:00 | 58.61 | 0 | 0 | 58.61 | 0 | 0 | 32.45 | 0 | 0
2025-07-14 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 32.45 | 0 | 0
2025-07-14 01:00 | 53.19 | 0 | 0 | 53.19 | 0 | 0 | 32.45 | 0 | 0
2025-07-14 02:00 | 51.49 | 0 | 0 | 51.49 | 0 | 0 | 32.45 | 0 | 0
2025-07-14 03:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 32.45 | 0 | 0
2025-07-14 04:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 32.45 | 0 | 0
2025-07-14 05:00 | 53.33 | 17.51 | 17.51 | 35.82 | 0 | 0 | 32.45 | 0 | 0
2025-07-14 06:00 | 55.45 | 76.77 | 76.77 | 0 | 21.32 | 0 | 52.71 | 0 | 0
2025-07-14 07:00 | 58.63 | 95.94 | 95.94 | 0 | 37.31 | 0 | 88.15 | 0 | 0
2025-07-14 08:00 | 60.25 | 107.74 | 107.74 | 0 | 47.49 | 0 | 133.27 | 0 | 0
2025-07-14 09:00 | 64.78 | 112.55 | 112.55 | 0 | 47.77 | 0 | 178.65 | 0 | 0
2025-07-14 10:00 | 67.43 | 114.01 | 114.01 | 0 | 46.58 | 0 | 222.89 | 0 | 0
2025-07-14 11:00 | 70.11 | 112.24 | 112.24 | 0 | 42.13 | 0 | 262.92 | 0 | 0
2025-07-14 12:00 | 71.44 | 112.96 | 102.11 | 0 | 30.67 | 0 | 292.05 | 10.86 | 0
2025-07-14 13:00 | 73.41 | 114.59 | 73.41 | 0 | 0 | 0 | 292.05 | 41.18 | 0
2025-07-14 14:00 | 73.04 | 118.09 | 73.04 | 0 | 0 | 0 | 292.05 | 45.05 | 0
2025-07-14 15:00 | 74.42 | 120.46 | 74.42 | 0 | 0 | 0 | 292.05 | 46.04 | 0
2025-07-14 16:00 | 73.39 | 117.68 | 73.39 | 0 | 0 | 0 | 292.05 | 44.29 | 0
2025-07-14 17:00 | 72.08 | 109.92 | 72.08 | 0 | 0 | 0 | 292.05 | 37.84 | 0
2025-07-14 18:00 | 70.9 | 91.74 | 70.9 | 0 | 0 | 0 | 292.05 | 20.84 | 0
2025-07-14 19:00 | 69.49 | 19.59 | 19.59 | 0 | 0 | 49.89 | 239.53 | 0 | 0
2025-07-14 20:00 | 66.61 | 0 | 0 | 0 | 0 | 66.61 | 169.42 | 0 | 0
2025-07-14 21:00 | 64.39 | 0 | 0 | 0 | 0 | 64.39 | 101.64 | 0 | 0
2025-07-14 22:00 | 60.29 | 0 | 0 | 0 | 0 | 60.29 | 38.18 | 0 | 0
2025-07-14 23:00 | 57.15 | 0 | 0 | 51.71 | 0 | 5.44 | 32.45 | 0 | 0
2025-07-15 | 56.27 | 0 | 0 | 56.27 | 0 | 0 | 32.45 | 0 | 0
2025-07-15 01:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 32.45 | 0 | 0
2025-07-15 02:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 32.45 | 0 | 0
2025-07-15 03:00 | 51.55 | 0 | 0 | 51.55 | 0 | 0 | 32.45 | 0 | 0
2025-07-15 04:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 32.45 | 0 | 0
2025-07-15 05:00 | 53.63 | 15.52 | 15.52 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-07-15 06:00 | 55.66 | 76.23 | 76.23 | 0 | 20.57 | 0 | 51.99 | 0 | 0
2025-07-15 07:00 | 58.86 | 99.21 | 99.21 | 0 | 40.35 | 0 | 90.32 | 0 | 0
2025-07-15 08:00 | 61.01 | 112.53 | 112.53 | 0 | 51.52 | 0 | 139.27 | 0 | 0
2025-07-15 09:00 | 64.52 | 115.29 | 115.29 | 0 | 50.77 | 0 | 187.5 | 0 | 0
2025-07-15 10:00 | 67.48 | 116.91 | 116.91 | 0 | 49.43 | 0 | 234.45 | 0 | 0
2025-07-15 11:00 | 70 | 116.37 | 116.37 | 0 | 46.37 | 0 | 278.51 | 0 | 0
2025-07-15 12:00 | 72.1 | 115.64 | 86.36 | 0 | 14.26 | 0 | 292.05 | 29.28 | 0
2025-07-15 13:00 | 73.93 | 116.96 | 73.93 | 0 | 0 | 0 | 292.05 | 43.03 | 0
2025-07-15 14:00 | 74.88 | 116.46 | 74.88 | 0 | 0 | 0 | 292.05 | 41.58 | 0
2025-07-15 15:00 | 74.67 | 115.88 | 74.67 | 0 | 0 | 0 | 292.05 | 41.21 | 0
2025-07-15 16:00 | 75.27 | 110.2 | 75.27 | 0 | 0 | 0 | 292.05 | 34.94 | 0
2025-07-15 17:00 | 73.4 | 95.62 | 73.4 | 0 | 0 | 0 | 292.05 | 22.21 | 0
2025-07-15 18:00 | 72.19 | 75.88 | 72.19 | 0 | 0 | 0 | 292.05 | 3.69 | 0
2025-07-15 19:00 | 69.99 | 14.69 | 14.69 | 0 | 0 | 55.3 | 233.84 | 0 | 0
2025-07-15 20:00 | 67.67 | 0 | 0 | 0 | 0 | 67.67 | 162.61 | 0 | 0
2025-07-15 21:00 | 63.45 | 0 | 0 | 0 | 0 | 63.45 | 95.82 | 0 | 0
2025-07-15 22:00 | 61.82 | 0 | 0 | 1.61 | 0 | 60.2 | 32.45 | 0 | 0
2025-07-15 23:00 | 57.98 | 0 | 0 | 57.98 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 | 56.39 | 0 | 0 | 56.39 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 01:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 02:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 03:00 | 52.53 | 0 | 0 | 52.53 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 04:00 | 51.92 | 0 | 0 | 51.92 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 05:00 | 54.1 | 10.09 | 10.09 | 44.01 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 06:00 | 55.8 | 22 | 22 | 33.8 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 07:00 | 59.04 | 37.18 | 37.18 | 21.86 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 08:00 | 62.51 | 70.97 | 70.97 | 0 | 8.46 | 0 | 40.48 | 0 | 0
2025-07-16 09:00 | 66.92 | 122.33 | 122.33 | 0 | 55.41 | 0 | 93.13 | 0 | 0
2025-07-16 10:00 | 70.28 | 89 | 89 | 0 | 18.72 | 0 | 110.91 | 0 | 0
2025-07-16 11:00 | 74.08 | 96.06 | 96.06 | 0 | 21.98 | 0 | 131.8 | 0 | 0
2025-07-16 12:00 | 77.71 | 101.3 | 101.3 | 0 | 23.59 | 0 | 154.21 | 0 | 0
2025-07-16 13:00 | 80.78 | 104.37 | 104.37 | 0 | 23.59 | 0 | 176.62 | 0 | 0
2025-07-16 14:00 | 82.34 | 85.66 | 85.66 | 0 | 3.32 | 0 | 179.77 | 0 | 0
2025-07-16 15:00 | 83.4 | 83.84 | 83.84 | 0 | 0.43 | 0 | 180.19 | 0 | 0
2025-07-16 16:00 | 83.11 | 64.15 | 64.15 | 0 | 0 | 18.95 | 160.23 | 0 | 0
2025-07-16 17:00 | 80.25 | 15.72 | 15.72 | 0 | 0 | 64.53 | 92.31 | 0 | 0
2025-07-16 18:00 | 77.66 | 10.6 | 10.6 | 10.2 | 0 | 56.86 | 32.45 | 0 | 0
2025-07-16 19:00 | 73.85 | 1.34 | 1.34 | 72.51 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 20:00 | 71.64 | 0 | 0 | 71.64 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 21:00 | 66.65 | 0 | 0 | 66.65 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 22:00 | 62.72 | 0 | 0 | 62.72 | 0 | 0 | 32.45 | 0 | 0
2025-07-16 23:00 | 58.16 | 0 | 0 | 58.16 | 0 | 0 | 32.45 | 0 | 0
2025-07-17 | 55.69 | 0 | 0 | 55.69 | 0 | 0 | 32.45 | 0 | 0
2025-07-17 01:00 | 53.73 | 0 | 0 | 53.73 | 0 | 0 | 32.45 | 0 | 0
2025-07-17 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 32.45 | 0 | 0
2025-07-17 03:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 32.45 | 0 | 0
2025-07-17 04:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 32.45 | 0 | 0
2025-07-17 05:00 | 53 | 10.28 | 10.28 | 42.73 | 0 | 0 | 32.45 | 0 | 0
2025-07-17 06:00 | 55.18 | 48.68 | 48.68 | 6.5 | 0 | 0 | 32.45 | 0 | 0
2025-07-17 07:00 | 58.09 | 89.81 | 89.81 | 0 | 31.72 | 0 | 62.59 | 0 | 0
2025-07-17 08:00 | 62.59 | 79.56 | 79.56 | 0 | 16.97 | 0 | 78.71 | 0 | 0
2025-07-17 09:00 | 65.73 | 96.06 | 96.06 | 0 | 30.33 | 0 | 107.53 | 0 | 0
2025-07-17 10:00 | 68.5 | 101.09 | 101.09 | 0 | 32.59 | 0 | 138.49 | 0 | 0
2025-07-17 11:00 | 71.66 | 109.39 | 109.39 | 0 | 37.73 | 0 | 174.33 | 0 | 0
2025-07-17 12:00 | 73.82 | 96.28 | 96.28 | 0 | 22.45 | 0 | 195.66 | 0 | 0
2025-07-17 13:00 | 76.63 | 97.83 | 97.83 | 0 | 21.2 | 0 | 215.79 | 0 | 0
2025-07-17 14:00 | 77.22 | 101.76 | 101.76 | 0 | 24.54 | 0 | 239.11 | 0 | 0
2025-07-17 15:00 | 77.69 | 88.57 | 88.57 | 0 | 10.88 | 0 | 249.44 | 0 | 0
2025-07-17 16:00 | 77.71 | 91 | 91 | 0 | 13.29 | 0 | 262.06 | 0 | 0
2025-07-17 17:00 | 76.1 | 86.47 | 86.47 | 0 | 10.37 | 0 | 271.92 | 0 | 0
2025-07-17 18:00 | 74.11 | 76.18 | 76.18 | 0 | 2.07 | 0 | 273.88 | 0 | 0
2025-07-17 19:00 | 71.65 | 11.17 | 11.17 | 0 | 0 | 60.48 | 210.23 | 0 | 0
2025-07-17 20:00 | 68.97 | 0 | 0 | 0 | 0 | 68.97 | 137.63 | 0 | 0
2025-07-17 21:00 | 66.03 | 0 | 0 | 0 | 0 | 66.03 | 68.12 | 0 | 0
2025-07-17 22:00 | 62.07 | 0 | 0 | 28.19 | 0 | 33.89 | 32.45 | 0 | 0
2025-07-17 23:00 | 58.93 | 0 | 0 | 58.93 | 0 | 0 | 32.45 | 0 | 0
2025-07-18 | 55.65 | 0 | 0 | 55.65 | 0 | 0 | 32.45 | 0 | 0
2025-07-18 01:00 | 53.15 | 0 | 0 | 53.15 | 0 | 0 | 32.45 | 0 | 0
2025-07-18 02:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 32.45 | 0 | 0
2025-07-18 03:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 32.45 | 0 | 0
2025-07-18 04:00 | 51.38 | 0 | 0 | 51.38 | 0 | 0 | 32.45 | 0 | 0
2025-07-18 05:00 | 53.34 | 12.91 | 12.91 | 40.43 | 0 | 0 | 32.45 | 0 | 0
2025-07-18 06:00 | 55.71 | 76.14 | 76.14 | 0 | 20.43 | 0 | 51.86 | 0 | 0
2025-07-18 07:00 | 58.42 | 97.39 | 97.39 | 0 | 38.97 | 0 | 88.88 | 0 | 0
2025-07-18 08:00 | 62.82 | 110.96 | 110.96 | 0 | 48.14 | 0 | 134.61 | 0 | 0
2025-07-18 09:00 | 65.97 | 113.72 | 113.72 | 0 | 47.74 | 0 | 179.97 | 0 | 0
2025-07-18 10:00 | 70.07 | 114.14 | 114.14 | 0 | 44.07 | 0 | 221.84 | 0 | 0
2025-07-18 11:00 | 72.92 | 114.88 | 114.88 | 0 | 41.96 | 0 | 261.69 | 0 | 0
2025-07-18 12:00 | 75.75 | 112.98 | 107.7 | 0 | 31.95 | 0 | 292.05 | 5.28 | 0
2025-07-18 13:00 | 77.48 | 115.3 | 77.48 | 0 | 0 | 0 | 292.05 | 37.81 | 0
2025-07-18 14:00 | 79.37 | 115.89 | 79.37 | 0 | 0 | 0 | 292.05 | 36.52 | 0
2025-07-18 15:00 | 79.85 | 114.02 | 79.85 | 0 | 0 | 0 | 292.05 | 34.17 | 0
2025-07-18 16:00 | 78.68 | 107.69 | 78.68 | 0 | 0 | 0 | 292.05 | 29.02 | 0
2025-07-18 17:00 | 77.68 | 94.82 | 77.68 | 0 | 0 | 0 | 292.05 | 17.13 | 0
2025-07-18 18:00 | 75.55 | 68.09 | 68.09 | 0 | 0 | 7.46 | 284.2 | 0 | 0
2025-07-18 19:00 | 73 | 11.85 | 11.85 | 0 | 0 | 61.15 | 219.83 | 0 | 0
2025-07-18 20:00 | 69.62 | 0 | 0 | 0 | 0 | 69.62 | 146.55 | 0 | 0
2025-07-18 21:00 | 65.44 | 0 | 0 | 0 | 0 | 65.44 | 77.67 | 0 | 0
2025-07-18 22:00 | 62.31 | 0 | 0 | 19.36 | 0 | 42.96 | 32.45 | 0 | 0
2025-07-18 23:00 | 58.58 | 0 | 0 | 58.58 | 0 | 0 | 32.45 | 0 | 0
2025-07-19 | 54.32 | 0 | 0 | 54.32 | 0 | 0 | 32.45 | 0 | 0
2025-07-19 01:00 | 53.27 | 0 | 0 | 53.27 | 0 | 0 | 32.45 | 0 | 0
2025-07-19 02:00 | 52.65 | 0 | 0 | 52.65 | 0 | 0 | 32.45 | 0 | 0
2025-07-19 03:00 | 50.79 | 0 | 0 | 50.79 | 0 | 0 | 32.45 | 0 | 0
2025-07-19 04:00 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 32.45 | 0 | 0
2025-07-19 05:00 | 54.31 | 11.78 | 11.78 | 42.53 | 0 | 0 | 32.45 | 0 | 0
2025-07-19 06:00 | 55.37 | 72.05 | 72.05 | 0 | 16.68 | 0 | 48.29 | 0 | 0
2025-07-19 07:00 | 58.64 | 97.88 | 97.88 | 0 | 39.24 | 0 | 85.57 | 0 | 0
2025-07-19 08:00 | 61.34 | 111.66 | 111.66 | 0 | 50.32 | 0 | 133.37 | 0 | 0
2025-07-19 09:00 | 66.37 | 117.26 | 117.26 | 0 | 50.89 | 0 | 181.72 | 0 | 0
2025-07-19 10:00 | 69.05 | 117.77 | 117.77 | 0 | 48.72 | 0 | 228.01 | 0 | 0
2025-07-19 11:00 | 72.39 | 115.41 | 115.41 | 0 | 43.02 | 0 | 268.88 | 0 | 0
2025-07-19 12:00 | 75.83 | 116.32 | 100.23 | 0 | 24.39 | 0 | 292.05 | 16.1 | 0
2025-07-19 13:00 | 77.61 | 116.04 | 77.61 | 0 | 0 | 0 | 292.05 | 38.43 | 0
2025-07-19 14:00 | 78.18 | 116.36 | 78.18 | 0 | 0 | 0 | 292.05 | 38.18 | 0
2025-07-19 15:00 | 78.75 | 116.51 | 78.75 | 0 | 0 | 0 | 292.05 | 37.77 | 0
2025-07-19 16:00 | 78.86 | 113.79 | 78.86 | 0 | 0 | 0 | 292.05 | 34.93 | 0
2025-07-19 17:00 | 76.97 | 103.88 | 76.97 | 0 | 0 | 0 | 292.05 | 26.9 | 0
2025-07-19 18:00 | 74.1 | 77.99 | 74.1 | 0 | 0 | 0 | 292.05 | 3.9 | 0
2025-07-19 19:00 | 72.34 | 12.55 | 12.55 | 0 | 0 | 59.79 | 229.12 | 0 | 0
2025-07-19 20:00 | 68.35 | 0 | 0 | 0 | 0 | 68.35 | 157.16 | 0 | 0
2025-07-19 21:00 | 66.37 | 0 | 0 | 0 | 0 | 66.37 | 87.31 | 0 | 0
2025-07-19 22:00 | 62.08 | 0 | 0 | 9.97 | 0 | 52.11 | 32.45 | 0 | 0
2025-07-19 23:00 | 58.19 | 0 | 0 | 58.19 | 0 | 0 | 32.45 | 0 | 0
2025-07-20 | 55.47 | 0 | 0 | 55.47 | 0 | 0 | 32.45 | 0 | 0
2025-07-20 01:00 | 52.6 | 0 | 0 | 52.6 | 0 | 0 | 32.45 | 0 | 0
2025-07-20 02:00 | 51.57 | 0 | 0 | 51.57 | 0 | 0 | 32.45 | 0 | 0
2025-07-20 03:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 32.45 | 0 | 0
2025-07-20 04:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 32.45 | 0 | 0
2025-07-20 05:00 | 53.9 | 12.13 | 12.13 | 41.78 | 0 | 0 | 32.45 | 0 | 0
2025-07-20 06:00 | 55.77 | 76.65 | 76.65 | 0 | 20.88 | 0 | 52.28 | 0 | 0
2025-07-20 07:00 | 58.6 | 101.3 | 101.3 | 0 | 42.7 | 0 | 92.85 | 0 | 0
2025-07-20 08:00 | 61.88 | 114.14 | 114.14 | 0 | 52.26 | 0 | 142.49 | 0 | 0
2025-07-20 09:00 | 67.24 | 116.53 | 116.53 | 0 | 49.29 | 0 | 189.32 | 0 | 0
2025-07-20 10:00 | 70.03 | 116.92 | 116.92 | 0 | 46.89 | 0 | 233.87 | 0 | 0
2025-07-20 11:00 | 74.88 | 114.67 | 114.67 | 0 | 39.78 | 0 | 271.66 | 0 | 0
2025-07-20 12:00 | 77.74 | 113.78 | 99.2 | 0 | 21.46 | 0 | 292.05 | 14.58 | 0
2025-07-20 13:00 | 78.66 | 114.47 | 78.66 | 0 | 0 | 0 | 292.05 | 35.81 | 0
2025-07-20 14:00 | 80.78 | 115.82 | 80.78 | 0 | 0 | 0 | 292.05 | 35.04 | 0
2025-07-20 15:00 | 81.32 | 114.5 | 81.32 | 0 | 0 | 0 | 292.05 | 33.19 | 0
2025-07-20 16:00 | 81.07 | 110.93 | 81.07 | 0 | 0 | 0 | 292.05 | 29.85 | 0
2025-07-20 17:00 | 79.5 | 97.36 | 79.5 | 0 | 0 | 0 | 292.05 | 17.85 | 0
2025-07-20 18:00 | 78.54 | 70.65 | 70.65 | 0 | 0 | 7.89 | 283.75 | 0 | 0
2025-07-20 19:00 | 73.29 | 11.16 | 11.16 | 0 | 0 | 62.12 | 218.35 | 0 | 0
2025-07-20 20:00 | 70.24 | 0 | 0 | 0 | 0 | 70.24 | 144.41 | 0 | 0
2025-07-20 21:00 | 66.52 | 0 | 0 | 0 | 0 | 66.52 | 74.39 | 0 | 0
2025-07-20 22:00 | 62.36 | 0 | 0 | 22.52 | 0 | 39.84 | 32.45 | 0 | 0
2025-07-20 23:00 | 58.88 | 0 | 0 | 58.88 | 0 | 0 | 32.45 | 0 | 0
2025-07-21 | 55.43 | 0 | 0 | 55.43 | 0 | 0 | 32.45 | 0 | 0
2025-07-21 01:00 | 53.63 | 0 | 0 | 53.63 | 0 | 0 | 32.45 | 0 | 0
2025-07-21 02:00 | 52.39 | 0 | 0 | 52.39 | 0 | 0 | 32.45 | 0 | 0
2025-07-21 03:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 32.45 | 0 | 0
2025-07-21 04:00 | 52.42 | 0 | 0 | 52.42 | 0 | 0 | 32.45 | 0 | 0
2025-07-21 05:00 | 54.28 | 10.48 | 10.48 | 43.8 | 0 | 0 | 32.45 | 0 | 0
2025-07-21 06:00 | 56.42 | 66.4 | 66.4 | 0 | 9.98 | 0 | 41.94 | 0 | 0
2025-07-21 07:00 | 59.21 | 90.83 | 90.83 | 0 | 31.62 | 0 | 71.98 | 0 | 0
2025-07-21 08:00 | 62.54 | 107.84 | 107.84 | 0 | 45.3 | 0 | 115.01 | 0 | 0
2025-07-21 09:00 | 67.3 | 110.26 | 110.26 | 0 | 42.96 | 0 | 155.82 | 0 | 0
2025-07-21 10:00 | 72.2 | 114.16 | 114.16 | 0 | 41.96 | 0 | 195.68 | 0 | 0
2025-07-21 11:00 | 77.04 | 111.88 | 111.88 | 0 | 34.85 | 0 | 228.79 | 0 | 0
2025-07-21 12:00 | 80.8 | 111.03 | 111.03 | 0 | 30.23 | 0 | 257.51 | 0 | 0
2025-07-21 13:00 | 83.84 | 111.56 | 111.56 | 0 | 27.72 | 0 | 283.84 | 0 | 0
2025-07-21 14:00 | 85.81 | 109.78 | 94.45 | 0 | 8.64 | 0 | 292.05 | 15.34 | 0
2025-07-21 15:00 | 86.3 | 105.19 | 86.3 | 0 | 0 | 0 | 292.05 | 18.88 | 0
2025-07-21 16:00 | 86.29 | 97.47 | 86.29 | 0 | 0 | 0 | 292.05 | 11.18 | 0
2025-07-21 17:00 | 83.57 | 81.36 | 81.36 | 0 | 0 | 2.21 | 289.73 | 0 | 0
2025-07-21 18:00 | 80.54 | 58.34 | 58.34 | 0 | 0 | 22.19 | 266.36 | 0 | 0
2025-07-21 19:00 | 76.72 | 9.35 | 9.35 | 0 | 0 | 67.37 | 195.45 | 0 | 0
2025-07-21 20:00 | 71.64 | 0 | 0 | 0 | 0 | 71.64 | 120.04 | 0 | 0
2025-07-21 21:00 | 67.79 | 0 | 0 | 0 | 0 | 67.79 | 48.69 | 0 | 0
2025-07-21 22:00 | 63.49 | 0 | 0 | 48.07 | 0 | 15.42 | 32.45 | 0 | 0
2025-07-21 23:00 | 58.9 | 0 | 0 | 58.9 | 0 | 0 | 32.45 | 0 | 0
2025-07-22 | 55.59 | 0 | 0 | 55.59 | 0 | 0 | 32.45 | 0 | 0
2025-07-22 01:00 | 53.82 | 0 | 0 | 53.82 | 0 | 0 | 32.45 | 0 | 0
2025-07-22 02:00 | 51.78 | 0 | 0 | 51.78 | 0 | 0 | 32.45 | 0 | 0
2025-07-22 03:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 32.45 | 0 | 0
2025-07-22 04:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 32.45 | 0 | 0
2025-07-22 05:00 | 54 | 9.79 | 9.79 | 44.21 | 0 | 0 | 32.45 | 0 | 0
2025-07-22 06:00 | 56.11 | 62.41 | 62.41 | 0 | 6.29 | 0 | 38.43 | 0 | 0
2025-07-22 07:00 | 59.23 | 85.18 | 85.18 | 0 | 25.96 | 0 | 63.09 | 0 | 0
2025-07-22 08:00 | 61.23 | 104.86 | 104.86 | 0 | 43.63 | 0 | 104.54 | 0 | 0
2025-07-22 09:00 | 66.61 | 108.84 | 108.84 | 0 | 42.23 | 0 | 144.66 | 0 | 0
2025-07-22 10:00 | 69.86 | 109.91 | 109.91 | 0 | 40.05 | 0 | 182.71 | 0 | 0
2025-07-22 11:00 | 73.66 | 104.89 | 104.89 | 0 | 31.23 | 0 | 212.37 | 0 | 0
2025-07-22 12:00 | 76.36 | 102.65 | 102.65 | 0 | 26.29 | 0 | 237.35 | 0 | 0
2025-07-22 13:00 | 78.5 | 103.8 | 103.8 | 0 | 25.3 | 0 | 261.38 | 0 | 0
2025-07-22 14:00 | 79.8 | 104.84 | 104.84 | 0 | 25.03 | 0 | 285.16 | 0 | 0
2025-07-22 15:00 | 80.62 | 102.73 | 87.87 | 0 | 7.25 | 0 | 292.05 | 14.86 | 0
2025-07-22 16:00 | 79.78 | 91.61 | 79.78 | 0 | 0 | 0 | 292.05 | 11.83 | 0
2025-07-22 17:00 | 78.91 | 77.74 | 77.74 | 0 | 0 | 1.18 | 290.81 | 0 | 0
2025-07-22 18:00 | 75.37 | 56.05 | 56.05 | 0 | 0 | 19.33 | 270.47 | 0 | 0
2025-07-22 19:00 | 72.89 | 8.94 | 8.94 | 0 | 0 | 63.95 | 203.15 | 0 | 0
2025-07-22 20:00 | 70.69 | 0 | 0 | 0 | 0 | 70.69 | 128.75 | 0 | 0
2025-07-22 21:00 | 65.62 | 0 | 0 | 0 | 0 | 65.62 | 59.68 | 0 | 0
2025-07-22 22:00 | 62.1 | 0 | 0 | 36.23 | 0 | 25.87 | 32.45 | 0 | 0
2025-07-22 23:00 | 58.32 | 0 | 0 | 58.32 | 0 | 0 | 32.45 | 0 | 0
2025-07-23 | 56.05 | 0 | 0 | 56.05 | 0 | 0 | 32.45 | 0 | 0
2025-07-23 01:00 | 53.21 | 0 | 0 | 53.21 | 0 | 0 | 32.45 | 0 | 0
2025-07-23 02:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 32.45 | 0 | 0
2025-07-23 03:00 | 52.09 | 0 | 0 | 52.09 | 0 | 0 | 32.45 | 0 | 0
2025-07-23 04:00 | 51.8 | 0 | 0 | 51.8 | 0 | 0 | 32.45 | 0 | 0
2025-07-23 05:00 | 53.97 | 8.99 | 8.99 | 44.98 | 0 | 0 | 32.45 | 0 | 0
2025-07-23 06:00 | 56.29 | 64.98 | 64.98 | 0 | 8.69 | 0 | 40.7 | 0 | 0
2025-07-23 07:00 | 59.48 | 92.82 | 92.82 | 0 | 33.34 | 0 | 72.38 | 0 | 0
2025-07-23 08:00 | 62.68 | 107.68 | 107.68 | 0 | 45 | 0 | 115.13 | 0 | 0
2025-07-23 09:00 | 68.27 | 113.52 | 113.52 | 0 | 45.25 | 0 | 158.12 | 0 | 0
2025-07-23 10:00 | 71.32 | 115.36 | 115.36 | 0 | 44.04 | 0 | 199.96 | 0 | 0
2025-07-23 11:00 | 74.92 | 114.39 | 114.39 | 0 | 39.47 | 0 | 237.46 | 0 | 0
2025-07-23 12:00 | 77.8 | 112.57 | 112.57 | 0 | 34.78 | 0 | 270.5 | 0 | 0
2025-07-23 13:00 | 80.9 | 113.31 | 103.59 | 0 | 22.69 | 0 | 292.05 | 9.72 | 0
2025-07-23 14:00 | 83.39 | 114.04 | 83.39 | 0 | 0 | 0 | 292.05 | 30.65 | 0
2025-07-23 15:00 | 84.13 | 112.66 | 84.13 | 0 | 0 | 0 | 292.05 | 28.54 | 0
2025-07-23 16:00 | 83.42 | 105.26 | 83.42 | 0 | 0 | 0 | 292.05 | 21.84 | 0
2025-07-23 17:00 | 81.34 | 91.44 | 81.34 | 0 | 0 | 0 | 292.05 | 10.1 | 0
2025-07-23 18:00 | 77.6 | 65.4 | 65.4 | 0 | 0 | 12.21 | 279.2 | 0 | 0
2025-07-23 19:00 | 75 | 8.54 | 8.54 | 0 | 0 | 66.46 | 209.24 | 0 | 0
2025-07-23 20:00 | 70.17 | 0 | 0 | 0 | 0 | 70.17 | 135.37 | 0 | 0
2025-07-23 21:00 | 65.9 | 0 | 0 | 0 | 0 | 65.9 | 66 | 0 | 0
2025-07-23 22:00 | 62.73 | 0 | 0 | 30.85 | 0 | 31.88 | 32.45 | 0 | 0
2025-07-23 23:00 | 59.21 | 0 | 0 | 59.21 | 0 | 0 | 32.45 | 0 | 0
2025-07-24 | 56.04 | 0 | 0 | 56.04 | 0 | 0 | 32.45 | 0 | 0
2025-07-24 01:00 | 53.76 | 0 | 0 | 53.76 | 0 | 0 | 32.45 | 0 | 0
2025-07-24 02:00 | 52.41 | 0 | 0 | 52.41 | 0 | 0 | 32.45 | 0 | 0
2025-07-24 03:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 32.45 | 0 | 0
2025-07-24 04:00 | 52.09 | 0 | 0 | 52.09 | 0 | 0 | 32.45 | 0 | 0
2025-07-24 05:00 | 52.76 | 6.73 | 6.73 | 46.03 | 0 | 0 | 32.45 | 0 | 0
2025-07-24 06:00 | 54.59 | 60.36 | 60.36 | 0 | 5.77 | 0 | 37.94 | 0 | 0
2025-07-24 07:00 | 58.46 | 87.78 | 87.78 | 0 | 29.32 | 0 | 65.78 | 0 | 0
2025-07-24 08:00 | 60.35 | 101.23 | 101.23 | 0 | 40.88 | 0 | 104.62 | 0 | 0
2025-07-24 09:00 | 63.65 | 105.31 | 105.31 | 0 | 41.65 | 0 | 144.19 | 0 | 0
2025-07-24 10:00 | 65.91 | 108.4 | 108.4 | 0 | 42.5 | 0 | 184.56 | 0 | 0
2025-07-24 11:00 | 66.72 | 104.11 | 104.11 | 0 | 37.38 | 0 | 220.08 | 0 | 0
2025-07-24 12:00 | 68.53 | 100.8 | 100.8 | 0 | 32.27 | 0 | 250.74 | 0 | 0
2025-07-24 13:00 | 68.67 | 101.92 | 101.92 | 0 | 33.26 | 0 | 282.33 | 0 | 0
2025-07-24 14:00 | 68.49 | 106.57 | 78.72 | 0 | 10.23 | 0 | 292.05 | 27.85 | 0
2025-07-24 15:00 | 69.6 | 103.99 | 69.6 | 0 | 0 | 0 | 292.05 | 34.38 | 0
2025-07-24 16:00 | 69.18 | 95.65 | 69.18 | 0 | 0 | 0 | 292.05 | 26.47 | 0
2025-07-24 17:00 | 68.78 | 83.98 | 68.78 | 0 | 0 | 0 | 292.05 | 15.21 | 0
2025-07-24 18:00 | 69.22 | 62.72 | 62.72 | 0 | 0 | 6.5 | 285.21 | 0 | 0
2025-07-24 19:00 | 66.27 | 7.61 | 7.61 | 0 | 0 | 58.66 | 223.47 | 0 | 0
2025-07-24 20:00 | 65.55 | 0 | 0 | 0 | 0 | 65.55 | 154.47 | 0 | 0
2025-07-24 21:00 | 62.72 | 0 | 0 | 0 | 0 | 62.72 | 88.45 | 0 | 0
2025-07-24 22:00 | 61.18 | 0 | 0 | 7.99 | 0 | 53.2 | 32.45 | 0 | 0
2025-07-24 23:00 | 58.24 | 0 | 0 | 58.24 | 0 | 0 | 32.45 | 0 | 0
2025-07-25 | 56 | 0 | 0 | 56 | 0 | 0 | 32.45 | 0 | 0
2025-07-25 01:00 | 53.09 | 0 | 0 | 53.09 | 0 | 0 | 32.45 | 0 | 0
2025-07-25 02:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 32.45 | 0 | 0
2025-07-25 03:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 32.45 | 0 | 0
2025-07-25 04:00 | 53.04 | 0 | 0 | 53.04 | 0 | 0 | 32.45 | 0 | 0
2025-07-25 05:00 | 53.8 | 8.71 | 8.71 | 45.09 | 0 | 0 | 32.45 | 0 | 0
2025-07-25 06:00 | 55.36 | 78.4 | 78.4 | 0 | 23.04 | 0 | 54.33 | 0 | 0
2025-07-25 07:00 | 58.9 | 106.63 | 106.63 | 0 | 47.72 | 0 | 99.67 | 0 | 0
2025-07-25 08:00 | 63.35 | 119.37 | 119.37 | 0 | 56.02 | 0 | 152.89 | 0 | 0
2025-07-25 09:00 | 65.82 | 120.68 | 120.68 | 0 | 54.86 | 0 | 205.01 | 0 | 0
2025-07-25 10:00 | 70.13 | 120.73 | 120.73 | 0 | 50.6 | 0 | 253.08 | 0 | 0
2025-07-25 11:00 | 72.41 | 118.24 | 113.43 | 0 | 41.03 | 0 | 292.05 | 4.81 | 0
2025-07-25 12:00 | 75.65 | 116.39 | 75.65 | 0 | 0 | 0 | 292.05 | 40.74 | 0
2025-07-25 13:00 | 78.2 | 117.4 | 78.2 | 0 | 0 | 0 | 292.05 | 39.2 | 0
2025-07-25 14:00 | 79.48 | 118.64 | 79.48 | 0 | 0 | 0 | 292.05 | 39.17 | 0
2025-07-25 15:00 | 79.37 | 119.6 | 79.37 | 0 | 0 | 0 | 292.05 | 40.23 | 0
2025-07-25 16:00 | 78.87 | 116.75 | 78.87 | 0 | 0 | 0 | 292.05 | 37.88 | 0
2025-07-25 17:00 | 78.38 | 105.49 | 78.38 | 0 | 0 | 0 | 292.05 | 27.11 | 0
2025-07-25 18:00 | 76.27 | 78.95 | 76.27 | 0 | 0 | 0 | 292.05 | 2.69 | 0
2025-07-25 19:00 | 73.53 | 8.2 | 8.2 | 0 | 0 | 65.34 | 223.27 | 0 | 0
2025-07-25 20:00 | 70.3 | 0 | 0 | 0 | 0 | 70.3 | 149.27 | 0 | 0
2025-07-25 21:00 | 65.84 | 0 | 0 | 0 | 0 | 65.84 | 79.97 | 0 | 0
2025-07-25 22:00 | 61.98 | 0 | 0 | 16.83 | 0 | 45.14 | 32.45 | 0 | 0
2025-07-25 23:00 | 59.41 | 0 | 0 | 59.41 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 01:00 | 53.05 | 0 | 0 | 53.05 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 02:00 | 51.63 | 0 | 0 | 51.63 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 03:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 04:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 05:00 | 53.53 | 9.93 | 9.93 | 43.6 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 06:00 | 56.26 | 8.9 | 8.9 | 47.36 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 07:00 | 58.86 | 55.83 | 55.83 | 3.03 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 08:00 | 62.24 | 95.9 | 95.9 | 0 | 33.66 | 0 | 64.43 | 0 | 0
2025-07-26 09:00 | 63.79 | 111.69 | 111.69 | 0 | 47.9 | 0 | 109.93 | 0 | 0
2025-07-26 10:00 | 67.92 | 104.11 | 104.11 | 0 | 36.19 | 0 | 144.31 | 0 | 0
2025-07-26 11:00 | 70.84 | 85.09 | 85.09 | 0 | 14.25 | 0 | 157.84 | 0 | 0
2025-07-26 12:00 | 71.95 | 45.58 | 45.58 | 0 | 0 | 26.37 | 130.09 | 0 | 0
2025-07-26 13:00 | 74.03 | 26.67 | 26.67 | 0 | 0 | 47.36 | 80.24 | 0 | 0
2025-07-26 14:00 | 74.94 | 111.76 | 111.76 | 0 | 36.82 | 0 | 115.22 | 0 | 0
2025-07-26 15:00 | 75.71 | 42.52 | 42.52 | 0 | 0 | 33.18 | 80.29 | 0 | 0
2025-07-26 16:00 | 76.17 | 36.28 | 36.28 | 0 | 0 | 39.9 | 38.29 | 0 | 0
2025-07-26 17:00 | 75.37 | 18.04 | 18.04 | 51.78 | 0 | 5.55 | 32.45 | 0 | 0
2025-07-26 18:00 | 72.31 | 0.85 | 0.85 | 71.46 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 19:00 | 70.76 | 10.68 | 10.68 | 60.08 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 20:00 | 68.07 | 0 | 0 | 68.07 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 21:00 | 64.95 | 0 | 0 | 64.95 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 22:00 | 61.77 | 0 | 0 | 61.77 | 0 | 0 | 32.45 | 0 | 0
2025-07-26 23:00 | 58.63 | 0 | 0 | 58.63 | 0 | 0 | 32.45 | 0 | 0
2025-07-27 | 56.52 | 0 | 0 | 56.52 | 0 | 0 | 32.45 | 0 | 0
2025-07-27 01:00 | 54.08 | 0 | 0 | 54.08 | 0 | 0 | 32.45 | 0 | 0
2025-07-27 02:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 32.45 | 0 | 0
2025-07-27 03:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 32.45 | 0 | 0
2025-07-27 04:00 | 52.59 | 0 | 0 | 52.59 | 0 | 0 | 32.45 | 0 | 0
2025-07-27 05:00 | 53.69 | 7.23 | 7.23 | 46.46 | 0 | 0 | 32.45 | 0 | 0
2025-07-27 06:00 | 56.24 | 74.55 | 74.55 | 0 | 18.3 | 0 | 49.84 | 0 | 0
2025-07-27 07:00 | 58.45 | 102.17 | 102.17 | 0 | 43.72 | 0 | 91.38 | 0 | 0
2025-07-27 08:00 | 61.41 | 112.7 | 112.7 | 0 | 51.29 | 0 | 140.1 | 0 | 0
2025-07-27 09:00 | 64.33 | 116.54 | 116.54 | 0 | 52.21 | 0 | 189.7 | 0 | 0
2025-07-27 10:00 | 66.02 | 116.2 | 116.2 | 0 | 50.18 | 0 | 237.37 | 0 | 0
2025-07-27 11:00 | 69.37 | 113.6 | 113.6 | 0 | 44.23 | 0 | 279.39 | 0 | 0
2025-07-27 12:00 | 70.98 | 111.26 | 84.31 | 0 | 13.33 | 0 | 292.05 | 26.95 | 0
2025-07-27 13:00 | 72.09 | 112.72 | 72.09 | 0 | 0 | 0 | 292.05 | 40.64 | 0
2025-07-27 14:00 | 74.22 | 114.53 | 74.22 | 0 | 0 | 0 | 292.05 | 40.31 | 0
2025-07-27 15:00 | 74.03 | 115.06 | 74.03 | 0 | 0 | 0 | 292.05 | 41.03 | 0
2025-07-27 16:00 | 73.49 | 112.18 | 73.49 | 0 | 0 | 0 | 292.05 | 38.7 | 0
2025-07-27 17:00 | 72.4 | 102.36 | 72.4 | 0 | 0 | 0 | 292.05 | 29.96 | 0
2025-07-27 18:00 | 71.46 | 76.27 | 71.46 | 0 | 0 | 0 | 292.05 | 4.81 | 0
2025-07-27 19:00 | 69.91 | 6.88 | 6.88 | 0 | 0 | 63.03 | 225.7 | 0 | 0
2025-07-27 20:00 | 66.62 | 0 | 0 | 0 | 0 | 66.62 | 155.58 | 0 | 0
2025-07-27 21:00 | 64.27 | 0 | 0 | 0 | 0 | 64.27 | 87.93 | 0 | 0
2025-07-27 22:00 | 61.74 | 0 | 0 | 9.04 | 0 | 52.7 | 32.45 | 0 | 0
2025-07-27 23:00 | 57.39 | 0 | 0 | 57.39 | 0 | 0 | 32.45 | 0 | 0
2025-07-28 | 55.68 | 0 | 0 | 55.68 | 0 | 0 | 32.45 | 0 | 0
2025-07-28 01:00 | 53.32 | 0 | 0 | 53.32 | 0 | 0 | 32.45 | 0 | 0
2025-07-28 02:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 32.45 | 0 | 0
2025-07-28 03:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 32.45 | 0 | 0
2025-07-28 04:00 | 52.21 | 0 | 0 | 52.21 | 0 | 0 | 32.45 | 0 | 0
2025-07-28 05:00 | 54.5 | 1.76 | 1.76 | 52.74 | 0 | 0 | 32.45 | 0 | 0
2025-07-28 06:00 | 55.55 | 34.42 | 34.42 | 21.12 | 0 | 0 | 32.45 | 0 | 0
2025-07-28 07:00 | 58.6 | 72.48 | 72.48 | 0 | 13.88 | 0 | 45.63 | 0 | 0
2025-07-28 08:00 | 62.53 | 104.53 | 104.53 | 0 | 41.99 | 0 | 85.53 | 0 | 0
2025-07-28 09:00 | 64.42 | 107.54 | 107.54 | 0 | 43.12 | 0 | 126.49 | 0 | 0
2025-07-28 10:00 | 68.61 | 90.78 | 90.78 | 0 | 22.17 | 0 | 147.55 | 0 | 0
2025-07-28 11:00 | 70.38 | 92.16 | 92.16 | 0 | 21.78 | 0 | 168.24 | 0 | 0
2025-07-28 12:00 | 73.46 | 69.64 | 69.64 | 0 | 0 | 3.82 | 164.22 | 0 | 0
2025-07-28 13:00 | 74.56 | 67.42 | 67.42 | 0 | 0 | 7.14 | 156.7 | 0 | 0
2025-07-28 14:00 | 75.32 | 70.45 | 70.45 | 0 | 0 | 4.87 | 151.58 | 0 | 0
2025-07-28 15:00 | 75.47 | 88.94 | 88.94 | 0 | 13.48 | 0 | 164.38 | 0 | 0
2025-07-28 16:00 | 74.86 | 110.59 | 110.59 | 0 | 35.73 | 0 | 198.32 | 0 | 0
2025-07-28 17:00 | 74.22 | 116.87 | 116.87 | 0 | 42.65 | 0 | 238.84 | 0 | 0
2025-07-28 18:00 | 73.02 | 92.69 | 92.69 | 0 | 19.68 | 0 | 257.54 | 0 | 0
2025-07-28 19:00 | 70.37 | 10.98 | 10.98 | 0 | 0 | 59.39 | 195.02 | 0 | 0
2025-07-28 20:00 | 67.55 | 0 | 0 | 0 | 0 | 67.55 | 123.91 | 0 | 0
2025-07-28 21:00 | 64.57 | 0 | 0 | 0 | 0 | 64.57 | 55.94 | 0 | 0
2025-07-28 22:00 | 62.03 | 0 | 0 | 39.71 | 0 | 22.32 | 32.45 | 0 | 0
2025-07-28 23:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 | 55.42 | 0 | 0 | 55.42 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 01:00 | 53.2 | 0 | 0 | 53.2 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 02:00 | 52.32 | 0 | 0 | 52.32 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 03:00 | 52.41 | 0 | 0 | 52.41 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 04:00 | 52.7 | 0 | 0 | 52.7 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 05:00 | 52.91 | 0.87 | 0.87 | 52.04 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 06:00 | 55.63 | 55.55 | 55.55 | 0.07 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 07:00 | 58.15 | 115.14 | 115.14 | 0 | 56.99 | 0 | 86.59 | 0 | 0
2025-07-29 08:00 | 61.77 | 117.4 | 117.4 | 0 | 55.63 | 0 | 139.43 | 0 | 0
2025-07-29 09:00 | 66.18 | 90.38 | 90.38 | 0 | 24.2 | 0 | 162.42 | 0 | 0
2025-07-29 10:00 | 68.08 | 87.19 | 87.19 | 0 | 19.11 | 0 | 180.58 | 0 | 0
2025-07-29 11:00 | 71.11 | 66.03 | 66.03 | 0 | 0 | 5.08 | 175.22 | 0 | 0
2025-07-29 12:00 | 74.16 | 87.75 | 87.75 | 0 | 13.59 | 0 | 188.14 | 0 | 0
2025-07-29 13:00 | 76.72 | 20.34 | 20.34 | 0 | 0 | 56.38 | 128.79 | 0 | 0
2025-07-29 14:00 | 78.14 | 7.29 | 7.29 | 0 | 0 | 70.85 | 54.21 | 0 | 0
2025-07-29 15:00 | 78.47 | 21.16 | 21.16 | 36.64 | 0 | 20.67 | 32.45 | 0 | 0
2025-07-29 16:00 | 78.42 | 4.23 | 4.23 | 74.19 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 17:00 | 75.7 | 2.37 | 2.37 | 73.32 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 18:00 | 75.16 | 0.72 | 0.72 | 74.44 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 19:00 | 71.77 | 0 | 0 | 71.77 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 20:00 | 69.16 | 0 | 0 | 69.16 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 21:00 | 64.72 | 0 | 0 | 64.72 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 22:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 32.45 | 0 | 0
2025-07-29 23:00 | 58.74 | 0 | 0 | 58.74 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 | 56.46 | 0 | 0 | 56.46 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 01:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 02:00 | 52.14 | 0 | 0 | 52.14 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 03:00 | 51.1 | 0 | 0 | 51.1 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 04:00 | 52.38 | 0 | 0 | 52.38 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 05:00 | 53.94 | 0.02 | 0.02 | 53.93 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 06:00 | 56.53 | 15.89 | 15.89 | 40.63 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 07:00 | 58.74 | 9.34 | 9.34 | 49.4 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 08:00 | 63.23 | 64.1 | 64.1 | 0 | 0.87 | 0 | 33.28 | 0 | 0
2025-07-30 09:00 | 67.63 | 68.63 | 68.63 | 0 | 1 | 0 | 34.23 | 0 | 0
2025-07-30 10:00 | 70.47 | 14.56 | 14.56 | 54.22 | 0 | 1.69 | 32.45 | 0 | 0
2025-07-30 11:00 | 75.79 | 7.51 | 7.51 | 68.28 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 12:00 | 79.67 | 39.52 | 39.52 | 40.15 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 13:00 | 81.97 | 94.27 | 94.27 | 0 | 12.3 | 0 | 44.13 | 0 | 0
2025-07-30 14:00 | 83.35 | 93.09 | 93.09 | 0 | 9.74 | 0 | 53.39 | 0 | 0
2025-07-30 15:00 | 85.07 | 5.87 | 5.87 | 59.31 | 0 | 19.89 | 32.45 | 0 | 0
2025-07-30 16:00 | 83.36 | 88.06 | 88.06 | 0 | 4.7 | 0 | 36.91 | 0 | 0
2025-07-30 17:00 | 82.01 | 96.7 | 96.7 | 0 | 14.69 | 0 | 50.87 | 0 | 0
2025-07-30 18:00 | 79.17 | 59.22 | 59.22 | 2.45 | 0 | 17.5 | 32.45 | 0 | 0
2025-07-30 19:00 | 75.84 | 2.83 | 2.83 | 73.01 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 20:00 | 70.98 | 0 | 0 | 70.98 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 21:00 | 66.61 | 0 | 0 | 66.61 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 22:00 | 62.81 | 0 | 0 | 62.81 | 0 | 0 | 32.45 | 0 | 0
2025-07-30 23:00 | 59.51 | 0 | 0 | 59.51 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 | 56.77 | 0 | 0 | 56.77 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 01:00 | 52.74 | 0 | 0 | 52.74 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 02:00 | 52.26 | 0 | 0 | 52.26 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 03:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 04:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 05:00 | 53.02 | 8.51 | 8.51 | 44.51 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 06:00 | 55.29 | 82.69 | 82.69 | 0 | 27.41 | 0 | 58.49 | 0 | 0
2025-07-31 07:00 | 57.98 | 105.96 | 105.96 | 0 | 47.98 | 0 | 104.07 | 0 | 0
2025-07-31 08:00 | 61.14 | 130.17 | 130.17 | 0 | 69.03 | 0 | 169.65 | 0 | 0
2025-07-31 09:00 | 64.24 | 132.89 | 132.89 | 0 | 68.65 | 0 | 234.87 | 0 | 0
2025-07-31 10:00 | 66.99 | 131.21 | 127.18 | 0 | 60.19 | 0 | 292.05 | 4.03 | 0
2025-07-31 11:00 | 69.03 | 93.86 | 69.03 | 0 | 0 | 0 | 292.05 | 24.82 | 0
2025-07-31 12:00 | 70.18 | 59.59 | 59.59 | 0 | 0 | 10.59 | 280.9 | 0 | 0
2025-07-31 13:00 | 72.5 | 68.13 | 68.13 | 0 | 0 | 4.36 | 276.31 | 0 | 0
2025-07-31 14:00 | 72.87 | 53.84 | 53.84 | 0 | 0 | 19.04 | 256.27 | 0 | 0
2025-07-31 15:00 | 73.73 | 53.47 | 53.47 | 0 | 0 | 20.26 | 234.94 | 0 | 0
2025-07-31 16:00 | 72.54 | 13.78 | 13.78 | 0 | 0 | 58.76 | 173.09 | 0 | 0
2025-07-31 17:00 | 71.33 | 6.93 | 6.93 | 0 | 0 | 64.4 | 105.3 | 0 | 0
2025-07-31 18:00 | 70.83 | 0.78 | 0.78 | 0.84 | 0 | 69.2 | 32.45 | 0 | 0
2025-07-31 19:00 | 69.68 | 0 | 0 | 69.68 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 20:00 | 66.83 | 0 | 0 | 66.83 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 21:00 | 63.98 | 0 | 0 | 63.98 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 22:00 | 60.74 | 0 | 0 | 60.74 | 0 | 0 | 32.45 | 0 | 0
2025-07-31 23:00 | 59.15 | 0 | 0 | 59.15 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 | 55.24 | 0 | 0 | 55.24 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 01:00 | 53.14 | 0 | 0 | 53.14 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 02:00 | 52.38 | 0 | 0 | 52.38 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 03:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 04:00 | 52.73 | 0 | 0 | 52.73 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 05:00 | 53.82 | 0.03 | 0.03 | 53.78 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 06:00 | 56.2 | 9.5 | 9.5 | 46.7 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 07:00 | 58.96 | 30.39 | 30.39 | 28.58 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 08:00 | 62.02 | 64.65 | 64.65 | 0 | 2.62 | 0 | 34.94 | 0 | 0
2025-08-01 09:00 | 65.25 | 55.41 | 55.41 | 7.47 | 0 | 2.37 | 32.45 | 0 | 0
2025-08-01 10:00 | 69.39 | 48.7 | 48.7 | 20.69 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 11:00 | 72.4 | 41.39 | 41.39 | 31.02 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 12:00 | 76.09 | 8.05 | 8.05 | 68.04 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 13:00 | 78.51 | 8.05 | 8.05 | 70.47 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 14:00 | 80.27 | 20.11 | 20.11 | 60.16 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 15:00 | 80.21 | 24.2 | 24.2 | 56.01 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 16:00 | 80 | 14.48 | 14.48 | 65.52 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 17:00 | 77.96 | 11.6 | 11.6 | 66.36 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 18:00 | 75.6 | 2.03 | 2.03 | 73.57 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 19:00 | 73.13 | 0 | 0 | 73.13 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 20:00 | 69.26 | 0 | 0 | 69.26 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 21:00 | 65.91 | 0 | 0 | 65.91 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 22:00 | 61.57 | 0 | 0 | 61.57 | 0 | 0 | 32.45 | 0 | 0
2025-08-01 23:00 | 58.24 | 0 | 0 | 58.24 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 | 56 | 0 | 0 | 56 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 01:00 | 53.92 | 0 | 0 | 53.92 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 02:00 | 51.58 | 0 | 0 | 51.58 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 03:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 04:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 05:00 | 53.48 | 1.68 | 1.68 | 51.81 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 06:00 | 56.39 | 20.79 | 20.79 | 35.6 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 07:00 | 58.9 | 38.09 | 38.09 | 20.82 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 08:00 | 62.12 | 72.48 | 72.48 | 0 | 10.36 | 0 | 42.3 | 0 | 0
2025-08-02 09:00 | 66.05 | 101.7 | 101.7 | 0 | 35.65 | 0 | 76.16 | 0 | 0
2025-08-02 10:00 | 68.04 | 106.4 | 106.4 | 0 | 38.36 | 0 | 112.6 | 0 | 0
2025-08-02 11:00 | 70.89 | 88.94 | 88.94 | 0 | 18.04 | 0 | 129.74 | 0 | 0
2025-08-02 12:00 | 73.54 | 86.72 | 86.72 | 0 | 13.18 | 0 | 142.27 | 0 | 0
2025-08-02 13:00 | 75.67 | 87.77 | 87.77 | 0 | 12.11 | 0 | 153.77 | 0 | 0
2025-08-02 14:00 | 75.79 | 100.46 | 100.46 | 0 | 24.67 | 0 | 177.21 | 0 | 0
2025-08-02 15:00 | 77.26 | 69.25 | 69.25 | 0 | 0 | 8.01 | 168.78 | 0 | 0
2025-08-02 16:00 | 76.7 | 57.18 | 57.18 | 0 | 0 | 19.51 | 148.24 | 0 | 0
2025-08-02 17:00 | 76.19 | 38.14 | 38.14 | 0 | 0 | 38.04 | 108.19 | 0 | 0
2025-08-02 18:00 | 74.08 | 27.25 | 27.25 | 0 | 0 | 46.82 | 58.9 | 0 | 0
2025-08-02 19:00 | 71.08 | 2.48 | 2.48 | 43.48 | 0 | 25.13 | 32.45 | 0 | 0
2025-08-02 20:00 | 68.68 | 0 | 0 | 68.68 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 21:00 | 65.46 | 0 | 0 | 65.46 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 22:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 32.45 | 0 | 0
2025-08-02 23:00 | 58.25 | 0 | 0 | 58.25 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 | 54.56 | 0 | 0 | 54.56 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 01:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 02:00 | 51.69 | 0 | 0 | 51.69 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 03:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 04:00 | 51.58 | 0 | 0 | 51.58 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 05:00 | 53.2 | 3.55 | 3.55 | 49.65 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 06:00 | 55.06 | 71.57 | 71.57 | 0 | 16.51 | 0 | 48.14 | 0 | 0
2025-08-03 07:00 | 58.61 | 113.33 | 113.33 | 0 | 54.72 | 0 | 100.12 | 0 | 0
2025-08-03 08:00 | 62.01 | 126.72 | 126.72 | 0 | 64.71 | 0 | 161.6 | 0 | 0
2025-08-03 09:00 | 65.46 | 124.76 | 124.76 | 0 | 59.3 | 0 | 217.93 | 0 | 0
2025-08-03 10:00 | 68.68 | 116.48 | 116.48 | 0 | 47.81 | 0 | 263.35 | 0 | 0
2025-08-03 11:00 | 71.02 | 55.64 | 55.64 | 0 | 0 | 15.38 | 247.15 | 0 | 0
2025-08-03 12:00 | 74.13 | 75.94 | 75.94 | 0 | 1.82 | 0 | 248.88 | 0 | 0
2025-08-03 13:00 | 76.24 | 75.27 | 75.27 | 0 | 0 | 0.97 | 247.86 | 0 | 0
2025-08-03 14:00 | 77.49 | 65.24 | 65.24 | 0 | 0 | 12.25 | 234.97 | 0 | 0
2025-08-03 15:00 | 78.15 | 64.68 | 64.68 | 0 | 0 | 13.48 | 220.78 | 0 | 0
2025-08-03 16:00 | 78.4 | 47.8 | 47.8 | 0 | 0 | 30.6 | 188.57 | 0 | 0
2025-08-03 17:00 | 76.85 | 32.05 | 32.05 | 0 | 0 | 44.8 | 141.42 | 0 | 0
2025-08-03 18:00 | 73.94 | 16.1 | 16.1 | 0 | 0 | 57.84 | 80.53 | 0 | 0
2025-08-03 19:00 | 72.13 | 1.2 | 1.2 | 25.26 | 0 | 45.67 | 32.45 | 0 | 0
2025-08-03 20:00 | 68.99 | 0 | 0 | 68.99 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 21:00 | 64.86 | 0 | 0 | 64.86 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 22:00 | 62.22 | 0 | 0 | 62.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-03 23:00 | 58.44 | 0 | 0 | 58.44 | 0 | 0 | 32.45 | 0 | 0
2025-08-04 | 55.09 | 0 | 0 | 55.09 | 0 | 0 | 32.45 | 0 | 0
2025-08-04 01:00 | 53.69 | 0 | 0 | 53.69 | 0 | 0 | 32.45 | 0 | 0
2025-08-04 02:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 32.45 | 0 | 0
2025-08-04 03:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 32.45 | 0 | 0
2025-08-04 04:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 32.45 | 0 | 0
2025-08-04 05:00 | 53.11 | 2.68 | 2.68 | 50.43 | 0 | 0 | 32.45 | 0 | 0
2025-08-04 06:00 | 56.1 | 57.25 | 57.25 | 0 | 1.16 | 0 | 33.55 | 0 | 0
2025-08-04 07:00 | 58.9 | 91.65 | 91.65 | 0 | 32.75 | 0 | 64.66 | 0 | 0
2025-08-04 08:00 | 62.78 | 103.52 | 103.52 | 0 | 40.74 | 0 | 103.36 | 0 | 0
2025-08-04 09:00 | 67.09 | 111.52 | 111.52 | 0 | 44.43 | 0 | 145.57 | 0 | 0
2025-08-04 10:00 | 70.73 | 110.2 | 110.2 | 0 | 39.48 | 0 | 183.07 | 0 | 0
2025-08-04 11:00 | 75.1 | 111.82 | 111.82 | 0 | 36.73 | 0 | 217.96 | 0 | 0
2025-08-04 12:00 | 78.2 | 108.56 | 108.56 | 0 | 30.35 | 0 | 246.8 | 0 | 0
2025-08-04 13:00 | 82.55 | 106.04 | 106.04 | 0 | 23.49 | 0 | 269.11 | 0 | 0
2025-08-04 14:00 | 83.56 | 105.9 | 105.9 | 0 | 22.34 | 0 | 290.34 | 0 | 0
2025-08-04 15:00 | 84.88 | 104.83 | 86.68 | 0 | 1.8 | 0 | 292.05 | 18.15 | 0
2025-08-04 16:00 | 84.35 | 103.73 | 84.35 | 0 | 0 | 0 | 292.05 | 19.39 | 0
2025-08-04 17:00 | 82.57 | 82.17 | 82.17 | 0 | 0 | 0.4 | 291.63 | 0 | 0
2025-08-04 18:00 | 78.71 | 49.7 | 49.7 | 0 | 0 | 29.01 | 261.09 | 0 | 0
2025-08-04 19:00 | 75.51 | 2.49 | 2.49 | 0 | 0 | 73.02 | 184.22 | 0 | 0
2025-08-04 20:00 | 72.14 | 0 | 0 | 0 | 0 | 72.14 | 108.29 | 0 | 0
2025-08-04 21:00 | 67.77 | 0 | 0 | 0 | 0 | 67.77 | 36.95 | 0 | 0
2025-08-04 22:00 | 63.19 | 0 | 0 | 58.91 | 0 | 4.28 | 32.45 | 0 | 0
2025-08-04 23:00 | 59.09 | 0 | 0 | 59.09 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 01:00 | 53.79 | 0 | 0 | 53.79 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 02:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 03:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 04:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 05:00 | 53.34 | 1.82 | 1.82 | 51.52 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 06:00 | 55.79 | 48.65 | 48.65 | 7.14 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 07:00 | 58.86 | 81.38 | 81.38 | 0 | 22.51 | 0 | 53.84 | 0 | 0
2025-08-05 08:00 | 62.58 | 94.12 | 94.12 | 0 | 31.53 | 0 | 83.8 | 0 | 0
2025-08-05 09:00 | 65.99 | 99.43 | 99.43 | 0 | 33.43 | 0 | 115.56 | 0 | 0
2025-08-05 10:00 | 69.65 | 104.29 | 104.29 | 0 | 34.64 | 0 | 148.47 | 0 | 0
2025-08-05 11:00 | 74.98 | 104.69 | 104.69 | 0 | 29.71 | 0 | 176.69 | 0 | 0
2025-08-05 12:00 | 78.78 | 101.65 | 101.65 | 0 | 22.87 | 0 | 198.42 | 0 | 0
2025-08-05 13:00 | 80.38 | 103.22 | 103.22 | 0 | 22.83 | 0 | 220.11 | 0 | 0
2025-08-05 14:00 | 81.16 | 105.53 | 105.53 | 0 | 24.37 | 0 | 243.26 | 0 | 0
2025-08-05 15:00 | 82.01 | 106.68 | 106.68 | 0 | 24.67 | 0 | 266.69 | 0 | 0
2025-08-05 16:00 | 82.08 | 95.23 | 95.23 | 0 | 13.15 | 0 | 279.18 | 0 | 0
2025-08-05 17:00 | 80.83 | 75.42 | 75.42 | 0 | 0 | 5.41 | 273.48 | 0 | 0
2025-08-05 18:00 | 76.93 | 38.1 | 38.1 | 0 | 0 | 38.83 | 232.61 | 0 | 0
2025-08-05 19:00 | 74.11 | 1.83 | 1.83 | 0 | 0 | 72.28 | 156.52 | 0 | 0
2025-08-05 20:00 | 70.42 | 0 | 0 | 0 | 0 | 70.42 | 82.39 | 0 | 0
2025-08-05 21:00 | 66.72 | 0 | 0 | 19.27 | 0 | 47.45 | 32.45 | 0 | 0
2025-08-05 22:00 | 62.16 | 0 | 0 | 62.16 | 0 | 0 | 32.45 | 0 | 0
2025-08-05 23:00 | 57.96 | 0 | 0 | 57.96 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 01:00 | 53.98 | 0 | 0 | 53.98 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 02:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 03:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 04:00 | 51.75 | 0 | 0 | 51.75 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 05:00 | 53 | 3.05 | 3.05 | 49.95 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 06:00 | 56.28 | 71.84 | 71.84 | 0 | 15.56 | 0 | 47.23 | 0 | 0
2025-08-06 07:00 | 59.15 | 114.68 | 114.68 | 0 | 55.53 | 0 | 99.99 | 0 | 0
2025-08-06 08:00 | 63.1 | 125.67 | 125.67 | 0 | 62.57 | 0 | 159.44 | 0 | 0
2025-08-06 09:00 | 68 | 127.84 | 127.84 | 0 | 59.84 | 0 | 216.29 | 0 | 0
2025-08-06 10:00 | 71.35 | 126.04 | 126.04 | 0 | 54.69 | 0 | 268.24 | 0 | 0
2025-08-06 11:00 | 76.11 | 119.86 | 101.17 | 0 | 25.06 | 0 | 292.05 | 18.69 | 0
2025-08-06 12:00 | 80.5 | 121.21 | 80.5 | 0 | 0 | 0 | 292.05 | 40.7 | 0
2025-08-06 13:00 | 83.34 | 122.61 | 83.34 | 0 | 0 | 0 | 292.05 | 39.28 | 0
2025-08-06 14:00 | 86.06 | 76.11 | 76.11 | 0 | 0 | 9.95 | 281.58 | 0 | 0
2025-08-06 15:00 | 86.28 | 26.62 | 26.62 | 0 | 0 | 59.66 | 218.78 | 0 | 0
2025-08-06 16:00 | 85.17 | 108.05 | 108.05 | 0 | 22.88 | 0 | 240.51 | 0 | 0
2025-08-06 17:00 | 83.65 | 60.44 | 60.44 | 0 | 0 | 23.21 | 216.09 | 0 | 0
2025-08-06 18:00 | 80.51 | 44.02 | 44.02 | 0 | 0 | 36.48 | 177.68 | 0 | 0
2025-08-06 19:00 | 76.86 | 4.46 | 4.46 | 0 | 0 | 72.4 | 101.47 | 0 | 0
2025-08-06 20:00 | 72.07 | 0 | 0 | 6.5 | 0 | 65.57 | 32.45 | 0 | 0
2025-08-06 21:00 | 67.48 | 0 | 0 | 67.48 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 22:00 | 63.01 | 0 | 0 | 63.01 | 0 | 0 | 32.45 | 0 | 0
2025-08-06 23:00 | 58.86 | 0 | 0 | 58.86 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 | 55.21 | 0 | 0 | 55.21 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 01:00 | 53.5 | 0 | 0 | 53.5 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 02:00 | 51.79 | 0 | 0 | 51.79 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 03:00 | 52.32 | 0 | 0 | 52.32 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 04:00 | 52.63 | 0 | 0 | 52.63 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 05:00 | 53.67 | 1.34 | 1.34 | 52.33 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 06:00 | 55.76 | 35.2 | 35.2 | 20.56 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 07:00 | 58.4 | 82.91 | 82.91 | 0 | 24.5 | 0 | 55.73 | 0 | 0
2025-08-07 08:00 | 61.14 | 101.54 | 101.54 | 0 | 40.39 | 0 | 94.1 | 0 | 0
2025-08-07 09:00 | 65.21 | 105.79 | 105.79 | 0 | 40.58 | 0 | 132.65 | 0 | 0
2025-08-07 10:00 | 68.88 | 107.88 | 107.88 | 0 | 39 | 0 | 169.7 | 0 | 0
2025-08-07 11:00 | 72.2 | 102.86 | 102.86 | 0 | 30.66 | 0 | 198.82 | 0 | 0
2025-08-07 12:00 | 75.1 | 95.51 | 95.51 | 0 | 20.41 | 0 | 218.22 | 0 | 0
2025-08-07 13:00 | 77.44 | 94.52 | 94.52 | 0 | 17.08 | 0 | 234.44 | 0 | 0
2025-08-07 14:00 | 77.96 | 96.74 | 96.74 | 0 | 18.78 | 0 | 252.28 | 0 | 0
2025-08-07 15:00 | 78.42 | 78.55 | 78.55 | 0 | 0.13 | 0 | 252.4 | 0 | 0
2025-08-07 16:00 | 79.04 | 77.44 | 77.44 | 0 | 0 | 1.6 | 250.72 | 0 | 0
2025-08-07 17:00 | 77.37 | 64.61 | 64.61 | 0 | 0 | 12.76 | 237.29 | 0 | 0
2025-08-07 18:00 | 74.67 | 35.99 | 35.99 | 0 | 0 | 38.68 | 196.58 | 0 | 0
2025-08-07 19:00 | 72.03 | 1.14 | 1.14 | 0 | 0 | 70.89 | 121.96 | 0 | 0
2025-08-07 20:00 | 68.78 | 0 | 0 | 0 | 0 | 68.78 | 49.55 | 0 | 0
2025-08-07 21:00 | 65.33 | 0 | 0 | 49.08 | 0 | 16.25 | 32.45 | 0 | 0
2025-08-07 22:00 | 62.01 | 0 | 0 | 62.01 | 0 | 0 | 32.45 | 0 | 0
2025-08-07 23:00 | 59.71 | 0 | 0 | 59.71 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 | 55.57 | 0 | 0 | 55.57 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 01:00 | 53.64 | 0 | 0 | 53.64 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 02:00 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 03:00 | 51.21 | 0 | 0 | 51.21 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 04:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 05:00 | 53.51 | 2.9 | 2.9 | 50.62 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 06:00 | 53.28 | 32.28 | 32.28 | 21 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 07:00 | 58.57 | 29.11 | 29.11 | 29.46 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 08:00 | 62.31 | 55.4 | 55.4 | 6.91 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 09:00 | 63.58 | 107.68 | 107.68 | 0 | 44.09 | 0 | 74.34 | 0 | 0
2025-08-08 10:00 | 68.46 | 134.54 | 134.54 | 0 | 66.08 | 0 | 137.11 | 0 | 0
2025-08-08 11:00 | 69.1 | 119.27 | 119.27 | 0 | 50.17 | 0 | 184.77 | 0 | 0
2025-08-08 12:00 | 73.28 | 54.22 | 54.22 | 0 | 0 | 19.06 | 164.71 | 0 | 0
2025-08-08 13:00 | 74.53 | 9.08 | 9.08 | 0 | 0 | 65.45 | 95.81 | 0 | 0
2025-08-08 14:00 | 74.43 | 8.18 | 8.18 | 6.05 | 0 | 60.19 | 32.45 | 0 | 0
2025-08-08 15:00 | 76.18 | 17.96 | 17.96 | 58.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 16:00 | 76.18 | 53.71 | 53.71 | 22.46 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 17:00 | 74.72 | 62.09 | 62.09 | 12.63 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 18:00 | 73.1 | 63.25 | 63.25 | 9.85 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 19:00 | 70.28 | 2.28 | 2.28 | 68 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 20:00 | 66.76 | 0 | 0 | 66.76 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 21:00 | 64.93 | 0 | 0 | 64.93 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 22:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 32.45 | 0 | 0
2025-08-08 23:00 | 58.8 | 0 | 0 | 58.8 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 01:00 | 52.53 | 0 | 0 | 52.53 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 02:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 03:00 | 50.62 | 0 | 0 | 50.62 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 04:00 | 51.92 | 0 | 0 | 51.92 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 05:00 | 53.48 | 0.06 | 0.06 | 53.43 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 06:00 | 54.78 | 7.34 | 7.34 | 47.44 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 07:00 | 58.73 | 11.16 | 11.16 | 47.57 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 08:00 | 61.93 | 17.12 | 17.12 | 44.81 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 09:00 | 64.85 | 37.63 | 37.63 | 27.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 10:00 | 68.49 | 66.1 | 66.1 | 2.39 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 11:00 | 70.79 | 44.63 | 44.63 | 26.16 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 12:00 | 74.31 | 54.55 | 54.55 | 19.75 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 13:00 | 76.54 | 63.43 | 63.43 | 13.11 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 14:00 | 77.91 | 59.23 | 59.23 | 18.68 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 15:00 | 78.45 | 45.1 | 45.1 | 33.35 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 16:00 | 77.95 | 22.63 | 22.63 | 55.32 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 17:00 | 76.4 | 9.81 | 9.81 | 66.6 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 18:00 | 74.62 | 0 | 0 | 74.62 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 19:00 | 72.27 | 0 | 0 | 72.27 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 20:00 | 68.53 | 0 | 0 | 68.53 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 21:00 | 65.28 | 0 | 0 | 65.28 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 22:00 | 61.54 | 0 | 0 | 61.54 | 0 | 0 | 32.45 | 0 | 0
2025-08-09 23:00 | 58.02 | 0 | 0 | 58.02 | 0 | 0 | 32.45 | 0 | 0
2025-08-10 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 32.45 | 0 | 0
2025-08-10 01:00 | 52.98 | 0 | 0 | 52.98 | 0 | 0 | 32.45 | 0 | 0
2025-08-10 02:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 32.45 | 0 | 0
2025-08-10 03:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-08-10 04:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 32.45 | 0 | 0
2025-08-10 05:00 | 53.1 | 1.02 | 1.02 | 52.08 | 0 | 0 | 32.45 | 0 | 0
2025-08-10 06:00 | 55.25 | 66.56 | 66.56 | 0 | 11.32 | 0 | 43.2 | 0 | 0
2025-08-10 07:00 | 57.62 | 111.57 | 111.57 | 0 | 53.95 | 0 | 94.46 | 0 | 0
2025-08-10 08:00 | 62.09 | 121.92 | 121.92 | 0 | 59.83 | 0 | 151.29 | 0 | 0
2025-08-10 09:00 | 65.77 | 123.12 | 123.12 | 0 | 57.35 | 0 | 205.78 | 0 | 0
2025-08-10 10:00 | 69.87 | 120.86 | 120.86 | 0 | 50.99 | 0 | 254.22 | 0 | 0
2025-08-10 11:00 | 72.75 | 117.57 | 112.57 | 0 | 39.82 | 0 | 292.05 | 5 | 0
2025-08-10 12:00 | 77.05 | 115.54 | 77.05 | 0 | 0 | 0 | 292.05 | 38.48 | 0
2025-08-10 13:00 | 78.31 | 116.64 | 78.31 | 0 | 0 | 0 | 292.05 | 38.33 | 0
2025-08-10 14:00 | 79.57 | 119.19 | 79.57 | 0 | 0 | 0 | 292.05 | 39.62 | 0
2025-08-10 15:00 | 80.03 | 120.22 | 80.03 | 0 | 0 | 0 | 292.05 | 40.19 | 0
2025-08-10 16:00 | 79.14 | 118.19 | 79.14 | 0 | 0 | 0 | 292.05 | 39.05 | 0
2025-08-10 17:00 | 79.27 | 107.48 | 79.27 | 0 | 0 | 0 | 292.05 | 28.21 | 0
2025-08-10 18:00 | 76.79 | 62.66 | 62.66 | 0 | 0 | 14.13 | 277.18 | 0 | 0
2025-08-10 19:00 | 73.31 | 0.89 | 0.89 | 0 | 0 | 72.42 | 200.94 | 0 | 0
2025-08-10 20:00 | 68.99 | 0 | 0 | 0 | 0 | 68.99 | 128.32 | 0 | 0
2025-08-10 21:00 | 66.56 | 0 | 0 | 0 | 0 | 66.56 | 58.26 | 0 | 0
2025-08-10 22:00 | 61.72 | 0 | 0 | 37.21 | 0 | 24.52 | 32.45 | 0 | 0
2025-08-10 23:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 32.45 | 0 | 0
2025-08-11 | 56.17 | 0 | 0 | 56.17 | 0 | 0 | 32.45 | 0 | 0
2025-08-11 01:00 | 53.55 | 0 | 0 | 53.55 | 0 | 0 | 32.45 | 0 | 0
2025-08-11 02:00 | 52.92 | 0 | 0 | 52.92 | 0 | 0 | 32.45 | 0 | 0
2025-08-11 03:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 32.45 | 0 | 0
2025-08-11 04:00 | 51.62 | 0 | 0 | 51.62 | 0 | 0 | 32.45 | 0 | 0
2025-08-11 05:00 | 52.91 | 0.92 | 0.92 | 51.99 | 0 | 0 | 32.45 | 0 | 0
2025-08-11 06:00 | 54.52 | 47.79 | 47.79 | 6.74 | 0 | 0 | 32.45 | 0 | 0
2025-08-11 07:00 | 58.23 | 65.95 | 65.95 | 0 | 7.72 | 0 | 39.78 | 0 | 0
2025-08-11 08:00 | 62.37 | 97.16 | 97.16 | 0 | 34.78 | 0 | 72.83 | 0 | 0
2025-08-11 09:00 | 65.8 | 87.26 | 87.26 | 0 | 21.45 | 0 | 93.2 | 0 | 0
2025-08-11 10:00 | 69.25 | 97.06 | 97.06 | 0 | 27.81 | 0 | 119.63 | 0 | 0
2025-08-11 11:00 | 72.25 | 111.28 | 111.28 | 0 | 39.03 | 0 | 156.71 | 0 | 0
2025-08-11 12:00 | 75.9 | 124.36 | 124.36 | 0 | 48.46 | 0 | 202.74 | 0 | 0
2025-08-11 13:00 | 78.63 | 124.52 | 124.52 | 0 | 45.89 | 0 | 246.34 | 0 | 0
2025-08-11 14:00 | 79.82 | 128.06 | 127.93 | 0 | 48.12 | 0 | 292.05 | 0.13 | 0
2025-08-11 15:00 | 80.19 | 129.49 | 80.19 | 0 | 0 | 0 | 292.05 | 49.3 | 0
2025-08-11 16:00 | 79.2 | 127.28 | 79.2 | 0 | 0 | 0 | 292.05 | 48.08 | 0
2025-08-11 17:00 | 78.56 | 116.18 | 78.56 | 0 | 0 | 0 | 292.05 | 37.62 | 0
2025-08-11 18:00 | 74.22 | 69.63 | 69.63 | 0 | 0 | 4.59 | 287.22 | 0 | 0
2025-08-11 19:00 | 72.94 | 1.86 | 1.86 | 0 | 0 | 71.09 | 212.39 | 0 | 0
2025-08-11 20:00 | 70.53 | 0 | 0 | 0 | 0 | 70.53 | 138.15 | 0 | 0
2025-08-11 21:00 | 64.75 | 0 | 0 | 0 | 0 | 64.75 | 69.99 | 0 | 0
2025-08-11 22:00 | 61.68 | 0 | 0 | 26.01 | 0 | 35.66 | 32.45 | 0 | 0
2025-08-11 23:00 | 58.37 | 0 | 0 | 58.37 | 0 | 0 | 32.45 | 0 | 0
2025-08-12 | 55.04 | 0 | 0 | 55.04 | 0 | 0 | 32.45 | 0 | 0
2025-08-12 01:00 | 53.67 | 0 | 0 | 53.67 | 0 | 0 | 32.45 | 0 | 0
2025-08-12 02:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 32.45 | 0 | 0
2025-08-12 03:00 | 51.39 | 0 | 0 | 51.39 | 0 | 0 | 32.45 | 0 | 0
2025-08-12 04:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 32.45 | 0 | 0
2025-08-12 05:00 | 53.16 | 0.77 | 0.77 | 52.39 | 0 | 0 | 32.45 | 0 | 0
2025-08-12 06:00 | 56.86 | 48.65 | 48.65 | 8.21 | 0 | 0 | 32.45 | 0 | 0
2025-08-12 07:00 | 58 | 92.58 | 92.58 | 0 | 34.58 | 0 | 65.3 | 0 | 0
2025-08-12 08:00 | 60.97 | 108.95 | 108.95 | 0 | 47.98 | 0 | 110.88 | 0 | 0
2025-08-12 09:00 | 63.01 | 113.12 | 113.12 | 0 | 50.11 | 0 | 158.49 | 0 | 0
2025-08-12 10:00 | 66.4 | 110.61 | 110.61 | 0 | 44.21 | 0 | 200.49 | 0 | 0
2025-08-12 11:00 | 69.69 | 109.43 | 109.43 | 0 | 39.74 | 0 | 238.25 | 0 | 0
2025-08-12 12:00 | 70.43 | 107.87 | 107.87 | 0 | 37.44 | 0 | 273.82 | 0 | 0
2025-08-12 13:00 | 71.46 | 108.52 | 90.65 | 0 | 19.19 | 0 | 292.05 | 17.87 | 0
2025-08-12 14:00 | 73.42 | 109.97 | 73.42 | 0 | 0 | 0 | 292.05 | 36.55 | 0
2025-08-12 15:00 | 74.38 | 111.29 | 74.38 | 0 | 0 | 0 | 292.05 | 36.91 | 0
2025-08-12 16:00 | 73.43 | 108.28 | 73.43 | 0 | 0 | 0 | 292.05 | 34.85 | 0
2025-08-12 17:00 | 72.37 | 92.48 | 72.37 | 0 | 0 | 0 | 292.05 | 20.11 | 0
2025-08-12 18:00 | 70.17 | 47.84 | 47.84 | 0 | 0 | 22.33 | 268.55 | 0 | 0
2025-08-12 19:00 | 69.34 | 0.64 | 0.64 | 0 | 0 | 68.71 | 196.23 | 0 | 0
2025-08-12 20:00 | 67 | 0 | 0 | 0 | 0 | 67 | 125.7 | 0 | 0
2025-08-12 21:00 | 62.97 | 0 | 0 | 0 | 0 | 62.97 | 59.42 | 0 | 0
2025-08-12 22:00 | 61.44 | 0 | 0 | 35.82 | 0 | 25.62 | 32.45 | 0 | 0
2025-08-12 23:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 | 55.91 | 0 | 0 | 55.91 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 01:00 | 53.42 | 0 | 0 | 53.42 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 02:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 03:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 04:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 05:00 | 52.22 | 0.62 | 0.62 | 51.61 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 06:00 | 54.59 | 13.18 | 13.18 | 41.41 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 07:00 | 57.87 | 2.23 | 2.23 | 55.64 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 08:00 | 61.55 | 21.47 | 21.47 | 40.09 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 09:00 | 65.46 | 23.96 | 23.96 | 41.5 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 10:00 | 69.08 | 44.7 | 44.7 | 24.38 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 11:00 | 72.9 | 37.2 | 37.2 | 35.7 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 12:00 | 75.87 | 81 | 81 | 0 | 5.13 | 0 | 37.33 | 0 | 0
2025-08-13 13:00 | 77.13 | 129.61 | 129.61 | 0 | 52.48 | 0 | 87.18 | 0 | 0
2025-08-13 14:00 | 79.11 | 124.17 | 124.17 | 0 | 45.06 | 0 | 129.99 | 0 | 0
2025-08-13 15:00 | 79.06 | 124.52 | 124.52 | 0 | 45.47 | 0 | 173.18 | 0 | 0
2025-08-13 16:00 | 78.9 | 99.67 | 99.67 | 0 | 20.77 | 0 | 192.91 | 0 | 0
2025-08-13 17:00 | 77.72 | 45.69 | 45.69 | 0 | 0 | 32.03 | 159.2 | 0 | 0
2025-08-13 18:00 | 73.59 | 20.63 | 20.63 | 0 | 0 | 52.96 | 103.45 | 0 | 0
2025-08-13 19:00 | 73.55 | 0.13 | 0.13 | 5.96 | 0 | 67.45 | 32.45 | 0 | 0
2025-08-13 20:00 | 69.2 | 0 | 0 | 69.2 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 21:00 | 64.96 | 0 | 0 | 64.96 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 22:00 | 62.58 | 0 | 0 | 62.58 | 0 | 0 | 32.45 | 0 | 0
2025-08-13 23:00 | 58.06 | 0 | 0 | 58.06 | 0 | 0 | 32.45 | 0 | 0
2025-08-14 | 55.37 | 0 | 0 | 55.37 | 0 | 0 | 32.45 | 0 | 0
2025-08-14 01:00 | 52.84 | 0 | 0 | 52.84 | 0 | 0 | 32.45 | 0 | 0
2025-08-14 02:00 | 52.52 | 0 | 0 | 52.52 | 0 | 0 | 32.45 | 0 | 0
2025-08-14 03:00 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 32.45 | 0 | 0
2025-08-14 04:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 32.45 | 0 | 0
2025-08-14 05:00 | 53.69 | 0.53 | 0.53 | 53.16 | 0 | 0 | 32.45 | 0 | 0
2025-08-14 06:00 | 55.6 | 55.05 | 55.05 | 0.55 | 0 | 0 | 32.45 | 0 | 0
2025-08-14 07:00 | 58.2 | 103.93 | 103.93 | 0 | 45.73 | 0 | 75.9 | 0 | 0
2025-08-14 08:00 | 62.2 | 115.2 | 115.2 | 0 | 53 | 0 | 126.24 | 0 | 0
2025-08-14 09:00 | 66.63 | 117 | 117 | 0 | 50.37 | 0 | 174.1 | 0 | 0
2025-08-14 10:00 | 69.27 | 115.36 | 115.36 | 0 | 46.09 | 0 | 217.88 | 0 | 0
2025-08-14 11:00 | 72.7 | 112.78 | 112.78 | 0 | 40.08 | 0 | 255.95 | 0 | 0
2025-08-14 12:00 | 75.78 | 110.89 | 110.89 | 0 | 35.1 | 0 | 289.3 | 0 | 0
2025-08-14 13:00 | 78.71 | 112.3 | 81.6 | 0 | 2.89 | 0 | 292.05 | 30.7 | 0
2025-08-14 14:00 | 79.25 | 114.07 | 79.25 | 0 | 0 | 0 | 292.05 | 34.82 | 0
2025-08-14 15:00 | 79.92 | 113.71 | 79.92 | 0 | 0 | 0 | 292.05 | 33.78 | 0
2025-08-14 16:00 | 78.78 | 112.54 | 78.78 | 0 | 0 | 0 | 292.05 | 33.75 | 0
2025-08-14 17:00 | 77.47 | 98.56 | 77.47 | 0 | 0 | 0 | 292.05 | 21.09 | 0
2025-08-14 18:00 | 75.44 | 50.58 | 50.58 | 0 | 0 | 24.85 | 265.89 | 0 | 0
2025-08-14 19:00 | 72.61 | 0.33 | 0.33 | 0 | 0 | 72.28 | 189.8 | 0 | 0
2025-08-14 20:00 | 69.99 | 0 | 0 | 0 | 0 | 69.99 | 116.12 | 0 | 0
2025-08-14 21:00 | 65.63 | 0 | 0 | 0 | 0 | 65.63 | 47.04 | 0 | 0
2025-08-14 22:00 | 61.19 | 0 | 0 | 47.33 | 0 | 13.86 | 32.45 | 0 | 0
2025-08-14 23:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 | 56.18 | 0 | 0 | 56.18 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 01:00 | 53.65 | 0 | 0 | 53.65 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 02:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 03:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 04:00 | 52.22 | 0 | 0 | 52.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 05:00 | 52.59 | 0.43 | 0.43 | 52.17 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 06:00 | 55.69 | 45.74 | 45.74 | 9.95 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 07:00 | 60.01 | 93.33 | 93.33 | 0 | 33.32 | 0 | 64.1 | 0 | 0
2025-08-15 08:00 | 63.24 | 107.21 | 107.21 | 0 | 43.97 | 0 | 105.87 | 0 | 0
2025-08-15 09:00 | 67.74 | 109.66 | 109.66 | 0 | 41.92 | 0 | 145.69 | 0 | 0
2025-08-15 10:00 | 73.74 | 110.22 | 110.22 | 0 | 36.48 | 0 | 180.35 | 0 | 0
2025-08-15 11:00 | 78.72 | 105.34 | 105.34 | 0 | 26.62 | 0 | 205.64 | 0 | 0
2025-08-15 12:00 | 83.19 | 103.48 | 103.48 | 0 | 20.29 | 0 | 224.92 | 0 | 0
2025-08-15 13:00 | 88.22 | 107.01 | 107.01 | 0 | 18.79 | 0 | 242.77 | 0 | 0
2025-08-15 14:00 | 91 | 109.73 | 109.73 | 0 | 18.73 | 0 | 260.57 | 0 | 0
2025-08-15 15:00 | 91.18 | 108.42 | 108.42 | 0 | 17.24 | 0 | 276.94 | 0 | 0
2025-08-15 16:00 | 90.25 | 102.98 | 102.98 | 0 | 12.73 | 0 | 289.04 | 0 | 0
2025-08-15 17:00 | 87.38 | 86.28 | 86.28 | 0 | 0 | 1.1 | 287.87 | 0 | 0
2025-08-15 18:00 | 83.82 | 38.55 | 38.55 | 0 | 0 | 45.27 | 240.22 | 0 | 0
2025-08-15 19:00 | 78.67 | 0.24 | 0.24 | 2.03 | 0 | 76.4 | 159.8 | 0 | 0
2025-08-15 20:00 | 73.03 | 0 | 0 | 0 | 0 | 73.03 | 82.93 | 0 | 0
2025-08-15 21:00 | 69.08 | 0 | 0 | 21.12 | 0 | 47.96 | 32.45 | 0 | 0
2025-08-15 22:00 | 63.38 | 0 | 0 | 63.38 | 0 | 0 | 32.45 | 0 | 0
2025-08-15 23:00 | 59.16 | 0 | 0 | 59.16 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 | 55.81 | 0 | 0 | 55.81 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 01:00 | 53.41 | 0 | 0 | 53.41 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 02:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 03:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 04:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 05:00 | 53.24 | 0.34 | 0.34 | 52.9 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 06:00 | 55.54 | 44.03 | 44.03 | 11.51 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 07:00 | 58.42 | 93.76 | 93.76 | 0 | 35.34 | 0 | 66.02 | 0 | 0
2025-08-16 08:00 | 61.96 | 104.89 | 104.89 | 0 | 42.93 | 0 | 106.81 | 0 | 0
2025-08-16 09:00 | 67.32 | 110.06 | 110.06 | 0 | 42.74 | 0 | 147.41 | 0 | 0
2025-08-16 10:00 | 72.07 | 105.17 | 105.17 | 0 | 33.1 | 0 | 178.86 | 0 | 0
2025-08-16 11:00 | 76.1 | 98.33 | 98.33 | 0 | 22.23 | 0 | 199.98 | 0 | 0
2025-08-16 12:00 | 81.7 | 100.72 | 100.72 | 0 | 19.02 | 0 | 218.04 | 0 | 0
2025-08-16 13:00 | 85.44 | 101.44 | 101.44 | 0 | 16 | 0 | 233.24 | 0 | 0
2025-08-16 14:00 | 88.49 | 102.03 | 102.03 | 0 | 13.54 | 0 | 246.1 | 0 | 0
2025-08-16 15:00 | 87.82 | 94.62 | 94.62 | 0 | 6.8 | 0 | 252.56 | 0 | 0
2025-08-16 16:00 | 86.96 | 87.17 | 87.17 | 0 | 0.21 | 0 | 252.77 | 0 | 0
2025-08-16 17:00 | 84.41 | 74.99 | 74.99 | 0 | 0 | 9.42 | 242.85 | 0 | 0
2025-08-16 18:00 | 81.55 | 33.37 | 33.37 | 0 | 0 | 48.18 | 192.13 | 0 | 0
2025-08-16 19:00 | 77.15 | 0.13 | 0.13 | 0.62 | 0 | 76.4 | 111.71 | 0 | 0
2025-08-16 20:00 | 71.77 | 0 | 0 | 0 | 0 | 71.77 | 36.16 | 0 | 0
2025-08-16 21:00 | 67.16 | 0 | 0 | 63.63 | 0 | 3.53 | 32.45 | 0 | 0
2025-08-16 22:00 | 61.64 | 0 | 0 | 61.64 | 0 | 0 | 32.45 | 0 | 0
2025-08-16 23:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 32.45 | 0 | 0
2025-08-17 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 32.45 | 0 | 0
2025-08-17 01:00 | 52.89 | 0 | 0 | 52.89 | 0 | 0 | 32.45 | 0 | 0
2025-08-17 02:00 | 50.84 | 0 | 0 | 50.84 | 0 | 0 | 32.45 | 0 | 0
2025-08-17 03:00 | 50.8 | 0 | 0 | 50.8 | 0 | 0 | 32.45 | 0 | 0
2025-08-17 04:00 | 51.41 | 0 | 0 | 51.41 | 0 | 0 | 32.45 | 0 | 0
2025-08-17 05:00 | 52.9 | 0.26 | 0.26 | 52.64 | 0 | 0 | 32.45 | 0 | 0
2025-08-17 06:00 | 55.26 | 40.8 | 40.8 | 14.47 | 0 | 0 | 32.45 | 0 | 0
2025-08-17 07:00 | 58.42 | 85.78 | 85.78 | 0 | 27.36 | 0 | 58.44 | 0 | 0
2025-08-17 08:00 | 61.06 | 101.54 | 101.54 | 0 | 40.48 | 0 | 96.9 | 0 | 0
2025-08-17 09:00 | 64.26 | 108.75 | 108.75 | 0 | 44.49 | 0 | 139.17 | 0 | 0
2025-08-17 10:00 | 67.44 | 109.31 | 109.31 | 0 | 41.87 | 0 | 178.94 | 0 | 0
2025-08-17 11:00 | 69.62 | 106.78 | 106.78 | 0 | 37.17 | 0 | 214.25 | 0 | 0
2025-08-17 12:00 | 71.46 | 107.25 | 107.25 | 0 | 35.79 | 0 | 248.25 | 0 | 0
2025-08-17 13:00 | 73.57 | 108.72 | 108.72 | 0 | 35.15 | 0 | 281.65 | 0 | 0
2025-08-17 14:00 | 74.57 | 110.81 | 85.52 | 0 | 10.95 | 0 | 292.05 | 25.29 | 0
2025-08-17 15:00 | 74.68 | 107.07 | 74.68 | 0 | 0 | 0 | 292.05 | 32.39 | 0
2025-08-17 16:00 | 73.31 | 98.26 | 73.31 | 0 | 0 | 0 | 292.05 | 24.96 | 0
2025-08-17 17:00 | 72.64 | 84.7 | 72.64 | 0 | 0 | 0 | 292.05 | 12.05 | 0
2025-08-17 18:00 | 71.34 | 35.13 | 35.13 | 0 | 0 | 36.21 | 253.94 | 0 | 0
2025-08-17 19:00 | 69.72 | 0 | 0 | 0 | 0 | 69.72 | 180.55 | 0 | 0
2025-08-17 20:00 | 66.71 | 0 | 0 | 0 | 0 | 66.71 | 110.33 | 0 | 0
2025-08-17 21:00 | 64.35 | 0 | 0 | 0 | 0 | 64.35 | 42.59 | 0 | 0
2025-08-17 22:00 | 61.35 | 0 | 0 | 51.72 | 0 | 9.64 | 32.45 | 0 | 0
2025-08-17 23:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 | 55.62 | 0 | 0 | 55.62 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 01:00 | 52.35 | 0 | 0 | 52.35 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 02:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 03:00 | 50.73 | 0 | 0 | 50.73 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 04:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 05:00 | 52.72 | 0.07 | 0.07 | 52.65 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 06:00 | 55.68 | 33.84 | 33.84 | 21.84 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 07:00 | 58.03 | 95.61 | 95.61 | 0 | 37.58 | 0 | 68.15 | 0 | 0
2025-08-18 08:00 | 62.01 | 116.35 | 116.35 | 0 | 54.34 | 0 | 119.77 | 0 | 0
2025-08-18 09:00 | 64.48 | 120.73 | 120.73 | 0 | 56.25 | 0 | 173.21 | 0 | 0
2025-08-18 10:00 | 68.96 | 99.4 | 99.4 | 0 | 30.44 | 0 | 202.13 | 0 | 0
2025-08-18 11:00 | 70.89 | 100.74 | 100.74 | 0 | 29.85 | 0 | 230.48 | 0 | 0
2025-08-18 12:00 | 73.42 | 77.99 | 77.99 | 0 | 4.57 | 0 | 234.83 | 0 | 0
2025-08-18 13:00 | 74.75 | 21.99 | 21.99 | 0 | 0 | 52.76 | 179.29 | 0 | 0
2025-08-18 14:00 | 77.18 | 91.35 | 91.35 | 0 | 14.17 | 0 | 192.76 | 0 | 0
2025-08-18 15:00 | 76.79 | 78.59 | 78.59 | 0 | 1.8 | 0 | 194.47 | 0 | 0
2025-08-18 16:00 | 76.3 | 113.98 | 113.98 | 0 | 37.69 | 0 | 230.28 | 0 | 0
2025-08-18 17:00 | 76.03 | 95.56 | 95.56 | 0 | 19.53 | 0 | 248.83 | 0 | 0
2025-08-18 18:00 | 73.99 | 39.38 | 39.38 | 0 | 0 | 34.6 | 212.41 | 0 | 0
2025-08-18 19:00 | 71.37 | 0.09 | 0.09 | 0 | 0 | 71.28 | 137.38 | 0 | 0
2025-08-18 20:00 | 67.55 | 0 | 0 | 0 | 0 | 67.55 | 66.27 | 0 | 0
2025-08-18 21:00 | 64.37 | 0 | 0 | 32.24 | 0 | 32.13 | 32.45 | 0 | 0
2025-08-18 22:00 | 60.97 | 0 | 0 | 60.97 | 0 | 0 | 32.45 | 0 | 0
2025-08-18 23:00 | 58.19 | 0 | 0 | 58.19 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 | 55.61 | 0 | 0 | 55.61 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 01:00 | 52.97 | 0 | 0 | 52.97 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 02:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 03:00 | 51.43 | 0 | 0 | 51.43 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 04:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 05:00 | 53.2 | 0 | 0 | 53.2 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 06:00 | 55.69 | 6.37 | 6.37 | 49.31 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 07:00 | 58.37 | 29.57 | 29.57 | 28.8 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 08:00 | 60.72 | 75.18 | 75.18 | 0 | 14.46 | 0 | 46.19 | 0 | 0
2025-08-19 09:00 | 62.87 | 70.01 | 70.01 | 0 | 7.15 | 0 | 52.98 | 0 | 0
2025-08-19 10:00 | 65.23 | 73.23 | 73.23 | 0 | 8 | 0 | 60.57 | 0 | 0
2025-08-19 11:00 | 67.73 | 88.45 | 88.45 | 0 | 20.72 | 0 | 80.26 | 0 | 0
2025-08-19 12:00 | 69.91 | 89.1 | 89.1 | 0 | 19.19 | 0 | 98.48 | 0 | 0
2025-08-19 13:00 | 70.44 | 89.57 | 89.57 | 0 | 19.13 | 0 | 116.66 | 0 | 0
2025-08-19 14:00 | 71.13 | 96.25 | 96.25 | 0 | 25.12 | 0 | 140.52 | 0 | 0
2025-08-19 15:00 | 71.15 | 67.61 | 67.61 | 0 | 0 | 3.54 | 136.79 | 0 | 0
2025-08-19 16:00 | 70.74 | 86.4 | 86.4 | 0 | 15.66 | 0 | 151.67 | 0 | 0
2025-08-19 17:00 | 70.14 | 94.62 | 94.62 | 0 | 24.47 | 0 | 174.92 | 0 | 0
2025-08-19 18:00 | 69.14 | 37.53 | 37.53 | 0 | 0 | 31.62 | 141.64 | 0 | 0
2025-08-19 19:00 | 68.3 | 0 | 0 | 0 | 0 | 68.3 | 69.75 | 0 | 0
2025-08-19 20:00 | 65.22 | 0 | 0 | 29.79 | 0 | 35.43 | 32.45 | 0 | 0
2025-08-19 21:00 | 62.88 | 0 | 0 | 62.88 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 22:00 | 59.7 | 0 | 0 | 59.7 | 0 | 0 | 32.45 | 0 | 0
2025-08-19 23:00 | 57.73 | 0 | 0 | 57.73 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 | 55.54 | 0 | 0 | 55.54 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 01:00 | 53.55 | 0 | 0 | 53.55 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 02:00 | 51.49 | 0 | 0 | 51.49 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 03:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 04:00 | 51.32 | 0 | 0 | 51.32 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 05:00 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 06:00 | 55.02 | 27.23 | 27.23 | 27.78 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 07:00 | 57.59 | 60.54 | 60.54 | 0 | 2.95 | 0 | 35.25 | 0 | 0
2025-08-20 08:00 | 60.7 | 72.78 | 72.78 | 0 | 12.08 | 0 | 46.72 | 0 | 0
2025-08-20 09:00 | 64.06 | 82.12 | 82.12 | 0 | 18.06 | 0 | 63.88 | 0 | 0
2025-08-20 10:00 | 66.79 | 92.7 | 92.7 | 0 | 25.91 | 0 | 88.49 | 0 | 0
2025-08-20 11:00 | 69.63 | 94.4 | 94.4 | 0 | 24.77 | 0 | 112.02 | 0 | 0
2025-08-20 12:00 | 72.94 | 96.22 | 96.22 | 0 | 23.28 | 0 | 134.13 | 0 | 0
2025-08-20 13:00 | 75.2 | 94.74 | 94.74 | 0 | 19.54 | 0 | 152.7 | 0 | 0
2025-08-20 14:00 | 74.33 | 101.89 | 101.89 | 0 | 27.57 | 0 | 178.89 | 0 | 0
2025-08-20 15:00 | 74.67 | 100.08 | 100.08 | 0 | 25.41 | 0 | 203.03 | 0 | 0
2025-08-20 16:00 | 74.45 | 104.43 | 104.43 | 0 | 29.98 | 0 | 231.51 | 0 | 0
2025-08-20 17:00 | 73.79 | 85.74 | 85.74 | 0 | 11.95 | 0 | 242.86 | 0 | 0
2025-08-20 18:00 | 72.54 | 30.92 | 30.92 | 0 | 0 | 41.62 | 199.06 | 0 | 0
2025-08-20 19:00 | 70.04 | 0 | 0 | 0 | 0 | 70.04 | 125.33 | 0 | 0
2025-08-20 20:00 | 67.03 | 0 | 0 | 0 | 0 | 67.03 | 54.77 | 0 | 0
2025-08-20 21:00 | 64.1 | 0 | 0 | 42.89 | 0 | 21.21 | 32.45 | 0 | 0
2025-08-20 22:00 | 60.29 | 0 | 0 | 60.29 | 0 | 0 | 32.45 | 0 | 0
2025-08-20 23:00 | 57.44 | 0 | 0 | 57.44 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 | 54.87 | 0 | 0 | 54.87 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 01:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 02:00 | 50.75 | 0 | 0 | 50.75 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 03:00 | 50.31 | 0 | 0 | 50.31 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 04:00 | 51.72 | 0 | 0 | 51.72 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 05:00 | 52.82 | 0.18 | 0.18 | 52.64 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 06:00 | 55.19 | 57.49 | 57.49 | 0 | 2.3 | 0 | 34.63 | 0 | 0
2025-08-21 07:00 | 56.84 | 118.97 | 118.97 | 0 | 62.13 | 0 | 93.65 | 0 | 0
2025-08-21 08:00 | 60.42 | 129.4 | 129.4 | 0 | 68.98 | 0 | 159.19 | 0 | 0
2025-08-21 09:00 | 65.18 | 130.71 | 130.71 | 0 | 65.53 | 0 | 221.44 | 0 | 0
2025-08-21 10:00 | 67.2 | 128.06 | 128.06 | 0 | 60.85 | 0 | 279.25 | 0 | 0
2025-08-21 11:00 | 72.74 | 124.36 | 86.21 | 0 | 13.47 | 0 | 292.05 | 38.15 | 0
2025-08-21 12:00 | 74.29 | 122.26 | 74.29 | 0 | 0 | 0 | 292.05 | 47.98 | 0
2025-08-21 13:00 | 78 | 115.29 | 78 | 0 | 0 | 0 | 292.05 | 37.29 | 0
2025-08-21 14:00 | 78.64 | 19.95 | 19.95 | 0 | 0 | 58.69 | 230.27 | 0 | 0
2025-08-21 15:00 | 80.12 | 5.51 | 5.51 | 0 | 0 | 74.62 | 151.73 | 0 | 0
2025-08-21 16:00 | 80.69 | 3.66 | 3.66 | 0.63 | 0 | 76.4 | 71.31 | 0 | 0
2025-08-21 17:00 | 76.44 | 1.77 | 1.77 | 37.75 | 0 | 36.92 | 32.45 | 0 | 0
2025-08-21 18:00 | 75.55 | 0 | 0 | 75.55 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 19:00 | 71.22 | 0 | 0 | 71.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 20:00 | 68.81 | 0 | 0 | 68.81 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 21:00 | 64.75 | 0 | 0 | 64.75 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 22:00 | 61.22 | 0 | 0 | 61.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-21 23:00 | 57.31 | 0 | 0 | 57.31 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 | 55.3 | 0 | 0 | 55.3 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 01:00 | 51.93 | 0 | 0 | 51.93 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 02:00 | 51.9 | 0 | 0 | 51.9 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 03:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 04:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 05:00 | 53.45 | 0 | 0 | 53.45 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 06:00 | 54.87 | 39.71 | 39.71 | 15.16 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 07:00 | 58.91 | 89.19 | 89.19 | 0 | 30.28 | 0 | 61.22 | 0 | 0
2025-08-22 08:00 | 62.27 | 23.77 | 23.77 | 11.17 | 0 | 27.33 | 32.45 | 0 | 0
2025-08-22 09:00 | 65.43 | 48.49 | 48.49 | 16.94 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 10:00 | 70.16 | 123.87 | 123.87 | 0 | 53.71 | 0 | 83.48 | 0 | 0
2025-08-22 11:00 | 74.51 | 96.28 | 96.28 | 0 | 21.77 | 0 | 104.16 | 0 | 0
2025-08-22 12:00 | 78.99 | 96.27 | 96.27 | 0 | 17.28 | 0 | 120.58 | 0 | 0
2025-08-22 13:00 | 81.43 | 94.9 | 94.9 | 0 | 13.46 | 0 | 133.37 | 0 | 0
2025-08-22 14:00 | 83.22 | 71.77 | 71.77 | 0 | 0 | 11.45 | 121.31 | 0 | 0
2025-08-22 15:00 | 83.69 | 9.79 | 9.79 | 0 | 0 | 73.9 | 43.52 | 0 | 0
2025-08-22 16:00 | 83.11 | 17.92 | 17.92 | 54.67 | 0 | 10.51 | 32.45 | 0 | 0
2025-08-22 17:00 | 81.87 | 3.88 | 3.88 | 77.99 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 18:00 | 78.23 | 0 | 0 | 78.23 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 19:00 | 74.25 | 0 | 0 | 74.25 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 20:00 | 69.92 | 0 | 0 | 69.92 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 21:00 | 65.55 | 0 | 0 | 65.55 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 22:00 | 60.96 | 0 | 0 | 60.96 | 0 | 0 | 32.45 | 0 | 0
2025-08-22 23:00 | 57.58 | 0 | 0 | 57.58 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 | 55.38 | 0 | 0 | 55.38 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 01:00 | 52.44 | 0 | 0 | 52.44 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 02:00 | 51.56 | 0 | 0 | 51.56 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 03:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 04:00 | 51.5 | 0 | 0 | 51.5 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 05:00 | 52.46 | 0 | 0 | 52.46 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 06:00 | 54.39 | 42.23 | 42.23 | 12.16 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 07:00 | 57.37 | 104.42 | 104.42 | 0 | 47.05 | 0 | 77.15 | 0 | 0
2025-08-23 08:00 | 60.03 | 86.74 | 86.74 | 0 | 26.72 | 0 | 102.53 | 0 | 0
2025-08-23 09:00 | 62.31 | 68.01 | 68.01 | 0 | 5.7 | 0 | 107.95 | 0 | 0
2025-08-23 10:00 | 66.81 | 116.99 | 116.99 | 0 | 50.18 | 0 | 155.62 | 0 | 0
2025-08-23 11:00 | 69.14 | 105.25 | 105.25 | 0 | 36.11 | 0 | 189.93 | 0 | 0
2025-08-23 12:00 | 71.07 | 90.29 | 90.29 | 0 | 19.23 | 0 | 208.19 | 0 | 0
2025-08-23 13:00 | 72.38 | 84.26 | 84.26 | 0 | 11.88 | 0 | 219.48 | 0 | 0
2025-08-23 14:00 | 73.14 | 80.67 | 80.67 | 0 | 7.53 | 0 | 226.63 | 0 | 0
2025-08-23 15:00 | 74.33 | 50.83 | 50.83 | 0 | 0 | 23.5 | 201.88 | 0 | 0
2025-08-23 16:00 | 74.68 | 67.71 | 67.71 | 0 | 0 | 6.98 | 194.54 | 0 | 0
2025-08-23 17:00 | 72.97 | 68.41 | 68.41 | 0 | 0 | 4.56 | 189.74 | 0 | 0
2025-08-23 18:00 | 70.53 | 29.35 | 29.35 | 0 | 0 | 41.18 | 146.4 | 0 | 0
2025-08-23 19:00 | 69.13 | 0 | 0 | 0 | 0 | 69.13 | 73.63 | 0 | 0
2025-08-23 20:00 | 66.32 | 0 | 0 | 27.2 | 0 | 39.12 | 32.45 | 0 | 0
2025-08-23 21:00 | 63.8 | 0 | 0 | 63.8 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 22:00 | 60.58 | 0 | 0 | 60.58 | 0 | 0 | 32.45 | 0 | 0
2025-08-23 23:00 | 55.79 | 0 | 0 | 55.79 | 0 | 0 | 32.45 | 0 | 0
2025-08-24 | 54.84 | 0 | 0 | 54.84 | 0 | 0 | 32.45 | 0 | 0
2025-08-24 01:00 | 51.98 | 0 | 0 | 51.98 | 0 | 0 | 32.45 | 0 | 0
2025-08-24 02:00 | 50.44 | 0 | 0 | 50.44 | 0 | 0 | 32.45 | 0 | 0
2025-08-24 03:00 | 50.59 | 0 | 0 | 50.59 | 0 | 0 | 32.45 | 0 | 0
2025-08-24 04:00 | 51.35 | 0 | 0 | 51.35 | 0 | 0 | 32.45 | 0 | 0
2025-08-24 05:00 | 51.66 | 0 | 0 | 51.66 | 0 | 0 | 32.45 | 0 | 0
2025-08-24 06:00 | 54.91 | 40.69 | 40.69 | 14.23 | 0 | 0 | 32.45 | 0 | 0
2025-08-24 07:00 | 57.6 | 99.28 | 99.28 | 0 | 41.68 | 0 | 72.04 | 0 | 0
2025-08-24 08:00 | 60.25 | 112.93 | 112.93 | 0 | 52.67 | 0 | 122.08 | 0 | 0
2025-08-24 09:00 | 62.92 | 115.57 | 115.57 | 0 | 52.65 | 0 | 172.1 | 0 | 0
2025-08-24 10:00 | 65.89 | 112.67 | 112.67 | 0 | 46.78 | 0 | 216.55 | 0 | 0
2025-08-24 11:00 | 69.61 | 109.47 | 109.47 | 0 | 39.86 | 0 | 254.42 | 0 | 0
2025-08-24 12:00 | 70.6 | 105.79 | 105.79 | 0 | 35.19 | 0 | 287.85 | 0 | 0
2025-08-24 13:00 | 73.58 | 107.74 | 78 | 0 | 4.42 | 0 | 292.05 | 29.74 | 0
2025-08-24 14:00 | 74 | 109.88 | 74 | 0 | 0 | 0 | 292.05 | 35.87 | 0
2025-08-24 15:00 | 74.39 | 107.95 | 74.39 | 0 | 0 | 0 | 292.05 | 33.56 | 0
2025-08-24 16:00 | 73.23 | 101.54 | 73.23 | 0 | 0 | 0 | 292.05 | 28.31 | 0
2025-08-24 17:00 | 72.97 | 84.4 | 72.97 | 0 | 0 | 0 | 292.05 | 11.42 | 0
2025-08-24 18:00 | 71.66 | 25.64 | 25.64 | 0 | 0 | 46.02 | 243.61 | 0 | 0
2025-08-24 19:00 | 68.43 | 0 | 0 | 0 | 0 | 68.43 | 171.58 | 0 | 0
2025-08-24 20:00 | 66.63 | 0 | 0 | 0 | 0 | 66.63 | 101.45 | 0 | 0
2025-08-24 21:00 | 63.4 | 0 | 0 | 0 | 0 | 63.4 | 34.71 | 0 | 0
2025-08-24 22:00 | 59.91 | 0 | 0 | 57.76 | 0 | 2.15 | 32.45 | 0 | 0
2025-08-24 23:00 | 57.65 | 0 | 0 | 57.65 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 01:00 | 52.55 | 0 | 0 | 52.55 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 02:00 | 51.89 | 0 | 0 | 51.89 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 03:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 04:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 05:00 | 52.22 | 0 | 0 | 52.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 06:00 | 54.01 | 8.14 | 8.14 | 45.87 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 07:00 | 56.53 | 25.2 | 25.2 | 31.33 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 08:00 | 59.41 | 44.44 | 44.44 | 14.98 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 09:00 | 61.04 | 59 | 59 | 2.04 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 10:00 | 63.78 | 55.38 | 55.38 | 8.4 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 11:00 | 65.98 | 46.07 | 46.07 | 19.91 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 12:00 | 65.94 | 40.17 | 40.17 | 25.76 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 13:00 | 65.96 | 38.68 | 38.68 | 27.27 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 14:00 | 66.3 | 20.43 | 20.43 | 45.87 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 15:00 | 67.47 | 24.53 | 24.53 | 42.94 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 16:00 | 66.94 | 15.38 | 15.38 | 51.57 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 17:00 | 67.07 | 8.02 | 8.02 | 59.04 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 18:00 | 65.7 | 0 | 0 | 65.7 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 19:00 | 65.33 | 0 | 0 | 65.33 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 20:00 | 63.32 | 0 | 0 | 63.32 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 21:00 | 61.08 | 0 | 0 | 61.08 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 22:00 | 58.94 | 0 | 0 | 58.94 | 0 | 0 | 32.45 | 0 | 0
2025-08-25 23:00 | 56.08 | 0 | 0 | 56.08 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 | 55.45 | 0 | 0 | 55.45 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 01:00 | 52.3 | 0 | 0 | 52.3 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 02:00 | 51.33 | 0 | 0 | 51.33 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 03:00 | 50.29 | 0 | 0 | 50.29 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 04:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 05:00 | 52.23 | 0 | 0 | 52.23 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 06:00 | 55.01 | 30.93 | 30.93 | 24.08 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 07:00 | 56.93 | 78.34 | 78.34 | 0 | 21.41 | 0 | 52.79 | 0 | 0
2025-08-26 08:00 | 59.92 | 17.57 | 17.57 | 23.03 | 0 | 19.33 | 32.45 | 0 | 0
2025-08-26 09:00 | 63.8 | 42.46 | 42.46 | 21.34 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 10:00 | 67.32 | 81.44 | 81.44 | 0 | 14.12 | 0 | 45.86 | 0 | 0
2025-08-26 11:00 | 70.99 | 97.95 | 97.95 | 0 | 26.96 | 0 | 71.48 | 0 | 0
2025-08-26 12:00 | 72.98 | 70.36 | 70.36 | 0 | 0 | 2.62 | 68.72 | 0 | 0
2025-08-26 13:00 | 75.14 | 63.73 | 63.73 | 0 | 0 | 11.4 | 56.71 | 0 | 0
2025-08-26 14:00 | 76.44 | 97.88 | 97.88 | 0 | 21.45 | 0 | 77.09 | 0 | 0
2025-08-26 15:00 | 75.93 | 92.38 | 92.38 | 0 | 16.45 | 0 | 92.71 | 0 | 0
2025-08-26 16:00 | 75.6 | 107.22 | 107.22 | 0 | 31.62 | 0 | 122.76 | 0 | 0
2025-08-26 17:00 | 74.27 | 83.94 | 83.94 | 0 | 9.67 | 0 | 131.94 | 0 | 0
2025-08-26 18:00 | 72.14 | 23.39 | 23.39 | 0 | 0 | 48.74 | 80.63 | 0 | 0
2025-08-26 19:00 | 70.56 | 0 | 0 | 24.79 | 0 | 45.77 | 32.45 | 0 | 0
2025-08-26 20:00 | 67.22 | 0 | 0 | 67.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 21:00 | 63.77 | 0 | 0 | 63.77 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 22:00 | 59.06 | 0 | 0 | 59.06 | 0 | 0 | 32.45 | 0 | 0
2025-08-26 23:00 | 58.22 | 0 | 0 | 58.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 | 53.83 | 0 | 0 | 53.83 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 01:00 | 53.28 | 0 | 0 | 53.28 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 02:00 | 50.22 | 0 | 0 | 50.22 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 03:00 | 50.08 | 0 | 0 | 50.08 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 04:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 05:00 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 06:00 | 53.73 | 30.22 | 30.22 | 23.51 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 07:00 | 56.29 | 106.58 | 106.58 | 0 | 50.29 | 0 | 80.23 | 0 | 0
2025-08-27 08:00 | 58.97 | 110.94 | 110.94 | 0 | 51.97 | 0 | 129.6 | 0 | 0
2025-08-27 09:00 | 62.92 | 127.06 | 127.06 | 0 | 64.14 | 0 | 190.53 | 0 | 0
2025-08-27 10:00 | 65.59 | 119.26 | 119.26 | 0 | 53.67 | 0 | 241.51 | 0 | 0
2025-08-27 11:00 | 68.5 | 7.65 | 7.65 | 0 | 0 | 60.85 | 177.46 | 0 | 0
2025-08-27 12:00 | 69.17 | 119.15 | 119.15 | 0 | 49.98 | 0 | 224.94 | 0 | 0
2025-08-27 13:00 | 71.01 | 120.28 | 120.28 | 0 | 49.27 | 0 | 271.75 | 0 | 0
2025-08-27 14:00 | 71.1 | 69.98 | 69.98 | 0 | 0 | 1.12 | 270.57 | 0 | 0
2025-08-27 15:00 | 71.86 | 34.58 | 34.58 | 0 | 0 | 37.28 | 231.33 | 0 | 0
2025-08-27 16:00 | 71.49 | 108.26 | 108.26 | 0 | 36.77 | 0 | 266.26 | 0 | 0
2025-08-27 17:00 | 71.13 | 1.44 | 1.44 | 0 | 0 | 69.7 | 192.9 | 0 | 0
2025-08-27 18:00 | 70.02 | 0 | 0 | 0 | 0 | 70.02 | 119.19 | 0 | 0
2025-08-27 19:00 | 68.09 | 0 | 0 | 0 | 0 | 68.09 | 47.52 | 0 | 0
2025-08-27 20:00 | 64.81 | 0 | 0 | 50.5 | 0 | 14.31 | 32.45 | 0 | 0
2025-08-27 21:00 | 63.03 | 0 | 0 | 63.03 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 22:00 | 59.64 | 0 | 0 | 59.64 | 0 | 0 | 32.45 | 0 | 0
2025-08-27 23:00 | 56.67 | 0 | 0 | 56.67 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 | 53.9 | 0 | 0 | 53.9 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 01:00 | 51.9 | 0 | 0 | 51.9 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 02:00 | 51.74 | 0 | 0 | 51.74 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 03:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 04:00 | 50.96 | 0 | 0 | 50.96 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 05:00 | 52.05 | 0 | 0 | 52.05 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 06:00 | 55.47 | 36.39 | 36.39 | 19.09 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 07:00 | 57.54 | 79.22 | 79.22 | 0 | 21.68 | 0 | 53.04 | 0 | 0
2025-08-28 08:00 | 59.54 | 99.28 | 99.28 | 0 | 39.74 | 0 | 90.79 | 0 | 0
2025-08-28 09:00 | 62.91 | 47.38 | 47.38 | 0 | 0 | 15.53 | 74.44 | 0 | 0
2025-08-28 10:00 | 66.01 | 119.02 | 119.02 | 0 | 53.01 | 0 | 124.8 | 0 | 0
2025-08-28 11:00 | 68.97 | 83.28 | 83.28 | 0 | 14.31 | 0 | 138.4 | 0 | 0
2025-08-28 12:00 | 70.87 | 85.22 | 85.22 | 0 | 14.34 | 0 | 152.03 | 0 | 0
2025-08-28 13:00 | 73.19 | 48.13 | 48.13 | 0 | 0 | 25.06 | 125.65 | 0 | 0
2025-08-28 14:00 | 74.78 | 61.46 | 61.46 | 0 | 0 | 13.32 | 111.63 | 0 | 0
2025-08-28 15:00 | 73.76 | 120.36 | 120.36 | 0 | 46.6 | 0 | 155.9 | 0 | 0
2025-08-28 16:00 | 73.49 | 74.92 | 74.92 | 0 | 1.44 | 0 | 157.26 | 0 | 0
2025-08-28 17:00 | 72.73 | 34.77 | 34.77 | 0 | 0 | 37.96 | 117.31 | 0 | 0
2025-08-28 18:00 | 71 | 0 | 0 | 0 | 0 | 71 | 42.57 | 0 | 0
2025-08-28 19:00 | 69.89 | 0 | 0 | 60.28 | 0 | 9.61 | 32.45 | 0 | 0
2025-08-28 20:00 | 66.62 | 0 | 0 | 66.62 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 21:00 | 63.52 | 0 | 0 | 63.52 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 22:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 32.45 | 0 | 0
2025-08-28 23:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 | 53.4 | 0 | 0 | 53.4 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 01:00 | 52.49 | 0 | 0 | 52.49 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 02:00 | 51.04 | 0 | 0 | 51.04 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 03:00 | 50.99 | 0 | 0 | 50.99 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 04:00 | 50.69 | 0 | 0 | 50.69 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 05:00 | 52.03 | 0 | 0 | 52.03 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 06:00 | 54.21 | 33.8 | 33.8 | 20.41 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 07:00 | 57.14 | 79.69 | 79.69 | 0 | 22.55 | 0 | 53.87 | 0 | 0
2025-08-29 08:00 | 58.83 | 120.22 | 120.22 | 0 | 61.39 | 0 | 112.19 | 0 | 0
2025-08-29 09:00 | 62.88 | 123.19 | 123.19 | 0 | 60.3 | 0 | 169.48 | 0 | 0
2025-08-29 10:00 | 65.32 | 118.77 | 118.77 | 0 | 53.45 | 0 | 220.26 | 0 | 0
2025-08-29 11:00 | 67.29 | 66.29 | 66.29 | 0 | 0 | 1 | 219.21 | 0 | 0
2025-08-29 12:00 | 68.82 | 66.24 | 66.24 | 0 | 0 | 2.58 | 216.49 | 0 | 0
2025-08-29 13:00 | 71.3 | 63.09 | 63.09 | 0 | 0 | 8.21 | 207.84 | 0 | 0
2025-08-29 14:00 | 73.02 | 51.11 | 51.11 | 0 | 0 | 21.91 | 184.78 | 0 | 0
2025-08-29 15:00 | 73.44 | 61.91 | 61.91 | 0 | 0 | 11.53 | 172.64 | 0 | 0
2025-08-29 16:00 | 72.47 | 35.22 | 35.22 | 0 | 0 | 37.25 | 133.43 | 0 | 0
2025-08-29 17:00 | 72.35 | 27.94 | 27.94 | 0 | 0 | 44.41 | 86.68 | 0 | 0
2025-08-29 18:00 | 69.84 | 6.98 | 6.98 | 11.34 | 0 | 51.52 | 32.45 | 0 | 0
2025-08-29 19:00 | 68.3 | 0 | 0 | 68.3 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 20:00 | 65.1 | 0 | 0 | 65.1 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 21:00 | 62.26 | 0 | 0 | 62.26 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 22:00 | 59.23 | 0 | 0 | 59.23 | 0 | 0 | 32.45 | 0 | 0
2025-08-29 23:00 | 55.66 | 0 | 0 | 55.66 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 | 54.76 | 0 | 0 | 54.76 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 01:00 | 51.71 | 0 | 0 | 51.71 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 02:00 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 03:00 | 49.68 | 0 | 0 | 49.68 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 04:00 | 50.62 | 0 | 0 | 50.62 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 05:00 | 52.92 | 0 | 0 | 52.92 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 06:00 | 55.16 | 24.11 | 24.11 | 31.05 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 07:00 | 55.99 | 83.31 | 83.31 | 0 | 27.32 | 0 | 58.4 | 0 | 0
2025-08-30 08:00 | 59.79 | 101.86 | 101.86 | 0 | 42.07 | 0 | 98.37 | 0 | 0
2025-08-30 09:00 | 62.8 | 106.67 | 106.67 | 0 | 43.87 | 0 | 140.04 | 0 | 0
2025-08-30 10:00 | 67.16 | 105.28 | 105.28 | 0 | 38.13 | 0 | 176.27 | 0 | 0
2025-08-30 11:00 | 69.9 | 104.1 | 104.1 | 0 | 34.2 | 0 | 208.75 | 0 | 0
2025-08-30 12:00 | 72.09 | 101.73 | 101.73 | 0 | 29.64 | 0 | 236.91 | 0 | 0
2025-08-30 13:00 | 74.48 | 104.41 | 104.41 | 0 | 29.93 | 0 | 265.35 | 0 | 0
2025-08-30 14:00 | 75.47 | 109.77 | 103.58 | 0 | 28.11 | 0 | 292.05 | 6.19 | 0
2025-08-30 15:00 | 76.95 | 111.25 | 76.95 | 0 | 0 | 0 | 292.05 | 34.3 | 0
2025-08-30 16:00 | 75.98 | 107.5 | 75.98 | 0 | 0 | 0 | 292.05 | 31.51 | 0
2025-08-30 17:00 | 74.77 | 87.22 | 74.77 | 0 | 0 | 0 | 292.05 | 12.44 | 0
2025-08-30 18:00 | 71.08 | 18.3 | 18.3 | 0 | 0 | 52.78 | 236.5 | 0 | 0
2025-08-30 19:00 | 69.73 | 0 | 0 | 0 | 0 | 69.73 | 163.1 | 0 | 0
2025-08-30 20:00 | 67.7 | 0 | 0 | 0 | 0 | 67.7 | 91.83 | 0 | 0
2025-08-30 21:00 | 63.98 | 0 | 0 | 7.57 | 0 | 56.41 | 32.45 | 0 | 0
2025-08-30 22:00 | 59.04 | 0 | 0 | 59.04 | 0 | 0 | 32.45 | 0 | 0
2025-08-30 23:00 | 56.67 | 0 | 0 | 56.67 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 | 53.26 | 0 | 0 | 53.26 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 01:00 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 02:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 03:00 | 49.81 | 0 | 0 | 49.81 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 04:00 | 50.66 | 0 | 0 | 50.66 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 05:00 | 50.61 | 0 | 0 | 50.61 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 06:00 | 53.31 | 0 | 0 | 53.31 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 07:00 | 56.25 | 18.63 | 18.63 | 37.61 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 08:00 | 59.19 | 36.53 | 36.53 | 22.67 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 09:00 | 60.26 | 58.13 | 58.13 | 2.13 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 10:00 | 63.22 | 61.47 | 61.47 | 1.74 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 11:00 | 65.69 | 84.31 | 84.31 | 0 | 18.61 | 0 | 50.13 | 0 | 0
2025-08-31 12:00 | 65.8 | 80.85 | 80.85 | 0 | 15.05 | 0 | 64.43 | 0 | 0
2025-08-31 13:00 | 67.55 | 78.76 | 78.76 | 0 | 11.21 | 0 | 75.08 | 0 | 0
2025-08-31 14:00 | 67.98 | 52.85 | 52.85 | 0 | 0 | 15.13 | 59.15 | 0 | 0
2025-08-31 15:00 | 68.97 | 29.01 | 29.01 | 14.59 | 0 | 25.37 | 32.45 | 0 | 0
2025-08-31 16:00 | 67.83 | 28.95 | 28.95 | 38.88 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 17:00 | 67.34 | 5.42 | 5.42 | 61.93 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 18:00 | 66.95 | 0.72 | 0.72 | 66.23 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 19:00 | 64.53 | 0 | 0 | 64.53 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 20:00 | 63.3 | 0 | 0 | 63.3 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 21:00 | 61 | 0 | 0 | 61 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 22:00 | 58.7 | 0 | 0 | 58.7 | 0 | 0 | 32.45 | 0 | 0
2025-08-31 23:00 | 56.65 | 0 | 0 | 56.65 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 | 54.07 | 0 | 0 | 54.07 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 01:00 | 51.46 | 0 | 0 | 51.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 03:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 04:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 05:00 | 51.91 | 0 | 0 | 51.91 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 06:00 | 53.7 | 9.3 | 9.3 | 44.39 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 07:00 | 56.18 | 12.15 | 12.15 | 44.03 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 08:00 | 58.03 | 35.63 | 35.63 | 22.4 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 09:00 | 62.15 | 63.49 | 63.49 | 0 | 1.34 | 0 | 33.72 | 0 | 0
2025-09-01 10:00 | 63.43 | 70.28 | 70.28 | 0 | 6.85 | 0 | 40.23 | 0 | 0
2025-09-01 11:00 | 66.33 | 69.37 | 69.37 | 0 | 3.04 | 0 | 43.12 | 0 | 0
2025-09-01 12:00 | 67.06 | 73.5 | 73.5 | 0 | 6.44 | 0 | 49.23 | 0 | 0
2025-09-01 13:00 | 68.16 | 70.81 | 70.81 | 0 | 2.65 | 0 | 51.76 | 0 | 0
2025-09-01 14:00 | 69.72 | 55.64 | 55.64 | 0 | 0 | 14.07 | 36.94 | 0 | 0
2025-09-01 15:00 | 69.82 | 87.64 | 87.64 | 0 | 17.82 | 0 | 53.87 | 0 | 0
2025-09-01 16:00 | 69.22 | 99.96 | 99.96 | 0 | 30.74 | 0 | 83.08 | 0 | 0
2025-09-01 17:00 | 68.85 | 48.13 | 48.13 | 0 | 0 | 20.72 | 61.27 | 0 | 0
2025-09-01 18:00 | 67.23 | 14.3 | 14.3 | 25.55 | 0 | 27.37 | 32.45 | 0 | 0
2025-09-01 19:00 | 65.81 | 0 | 0 | 65.81 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 20:00 | 63.48 | 0 | 0 | 63.48 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 21:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 22:00 | 58.5 | 0 | 0 | 58.5 | 0 | 0 | 32.45 | 0 | 0
2025-09-01 23:00 | 56.95 | 0 | 0 | 56.95 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 | 53.9 | 0 | 0 | 53.9 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 01:00 | 51.83 | 0 | 0 | 51.83 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 02:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 03:00 | 50.05 | 0 | 0 | 50.05 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 04:00 | 50.34 | 0 | 0 | 50.34 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 05:00 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 06:00 | 54.5 | 27.57 | 27.57 | 26.93 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 07:00 | 56.83 | 96.82 | 96.82 | 0 | 40 | 0 | 70.45 | 0 | 0
2025-09-02 08:00 | 60.97 | 114.8 | 114.8 | 0 | 53.82 | 0 | 121.58 | 0 | 0
2025-09-02 09:00 | 65.53 | 119.21 | 119.21 | 0 | 53.68 | 0 | 172.58 | 0 | 0
2025-09-02 10:00 | 70.77 | 115.88 | 115.88 | 0 | 45.1 | 0 | 215.43 | 0 | 0
2025-09-02 11:00 | 75.08 | 111.76 | 111.76 | 0 | 36.68 | 0 | 250.27 | 0 | 0
2025-09-02 12:00 | 80.38 | 103.39 | 103.39 | 0 | 23.02 | 0 | 272.14 | 0 | 0
2025-09-02 13:00 | 82.87 | 53.46 | 53.46 | 0 | 0 | 29.41 | 241.19 | 0 | 0
2025-09-02 14:00 | 85.08 | 111.59 | 111.59 | 0 | 26.51 | 0 | 266.37 | 0 | 0
2025-09-02 15:00 | 85.89 | 64.9 | 64.9 | 0 | 0 | 21 | 244.27 | 0 | 0
2025-09-02 16:00 | 84.54 | 2.35 | 2.35 | 5.79 | 0 | 76.4 | 163.85 | 0 | 0
2025-09-02 17:00 | 82.43 | 0.78 | 0.78 | 5.25 | 0 | 76.4 | 83.43 | 0 | 0
2025-09-02 18:00 | 79.21 | 0 | 0 | 30.78 | 0 | 48.43 | 32.45 | 0 | 0
2025-09-02 19:00 | 75.7 | 0 | 0 | 75.7 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 20:00 | 70.32 | 0 | 0 | 70.32 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 21:00 | 65.28 | 0 | 0 | 65.28 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 22:00 | 61.65 | 0 | 0 | 61.65 | 0 | 0 | 32.45 | 0 | 0
2025-09-02 23:00 | 57.93 | 0 | 0 | 57.93 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 | 54.24 | 0 | 0 | 54.24 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 01:00 | 51.24 | 0 | 0 | 51.24 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 02:00 | 50.15 | 0 | 0 | 50.15 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 03:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 04:00 | 50.52 | 0 | 0 | 50.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 05:00 | 51.53 | 0 | 0 | 51.53 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 06:00 | 53.98 | 24.11 | 24.11 | 29.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 07:00 | 56.55 | 86.88 | 86.88 | 0 | 30.33 | 0 | 61.26 | 0 | 0
2025-09-03 08:00 | 58.43 | 100.83 | 100.83 | 0 | 42.4 | 0 | 101.54 | 0 | 0
2025-09-03 09:00 | 61.5 | 103.78 | 103.78 | 0 | 42.28 | 0 | 141.7 | 0 | 0
2025-09-03 10:00 | 64.33 | 107.03 | 107.03 | 0 | 42.71 | 0 | 182.27 | 0 | 0
2025-09-03 11:00 | 65.4 | 101.38 | 101.38 | 0 | 35.98 | 0 | 216.45 | 0 | 0
2025-09-03 12:00 | 67.67 | 99.62 | 99.62 | 0 | 31.95 | 0 | 246.8 | 0 | 0
2025-09-03 13:00 | 68.32 | 98.89 | 98.89 | 0 | 30.57 | 0 | 275.84 | 0 | 0
2025-09-03 14:00 | 69.1 | 103.35 | 86.16 | 0 | 17.06 | 0 | 292.05 | 17.19 | 0
2025-09-03 15:00 | 69.55 | 100.8 | 69.55 | 0 | 0 | 0 | 292.05 | 31.25 | 0
2025-09-03 16:00 | 69.83 | 90.98 | 69.83 | 0 | 0 | 0 | 292.05 | 21.15 | 0
2025-09-03 17:00 | 68.71 | 68.23 | 68.23 | 0 | 0 | 0.49 | 291.54 | 0 | 0
2025-09-03 18:00 | 67.34 | 9.54 | 9.54 | 0 | 0 | 57.81 | 230.69 | 0 | 0
2025-09-03 19:00 | 66.01 | 0 | 0 | 0 | 0 | 66.01 | 161.21 | 0 | 0
2025-09-03 20:00 | 63.29 | 0 | 0 | 0 | 0 | 63.29 | 94.59 | 0 | 0
2025-09-03 21:00 | 61.61 | 0 | 0 | 2.58 | 0 | 59.03 | 32.45 | 0 | 0
2025-09-03 22:00 | 59.29 | 0 | 0 | 59.29 | 0 | 0 | 32.45 | 0 | 0
2025-09-03 23:00 | 56.01 | 0 | 0 | 56.01 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 | 53.44 | 0 | 0 | 53.44 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 01:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 02:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 03:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 04:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 06:00 | 53.48 | 25.44 | 25.44 | 28.03 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 07:00 | 56.37 | 89.22 | 89.22 | 0 | 32.85 | 0 | 63.66 | 0 | 0
2025-09-04 08:00 | 59.54 | 109.36 | 109.36 | 0 | 49.82 | 0 | 110.99 | 0 | 0
2025-09-04 09:00 | 61.96 | 110.94 | 110.94 | 0 | 48.98 | 0 | 157.52 | 0 | 0
2025-09-04 10:00 | 62.99 | 107.6 | 107.6 | 0 | 44.61 | 0 | 199.9 | 0 | 0
2025-09-04 11:00 | 66.61 | 103.09 | 103.09 | 0 | 36.49 | 0 | 234.56 | 0 | 0
2025-09-04 12:00 | 69.43 | 101.58 | 101.58 | 0 | 32.15 | 0 | 265.1 | 0 | 0
2025-09-04 13:00 | 69.78 | 102.57 | 98.15 | 0 | 28.37 | 0 | 292.05 | 4.42 | 0
2025-09-04 14:00 | 69.69 | 104.55 | 69.69 | 0 | 0 | 0 | 292.05 | 34.86 | 0
2025-09-04 15:00 | 70.68 | 104.85 | 70.68 | 0 | 0 | 0 | 292.05 | 34.17 | 0
2025-09-04 16:00 | 69.63 | 95.95 | 69.63 | 0 | 0 | 0 | 292.05 | 26.32 | 0
2025-09-04 17:00 | 70.09 | 74.41 | 70.09 | 0 | 0 | 0 | 292.05 | 4.32 | 0
2025-09-04 18:00 | 67.67 | 8.92 | 8.92 | 0 | 0 | 58.75 | 230.21 | 0 | 0
2025-09-04 19:00 | 66.36 | 0 | 0 | 0 | 0 | 66.36 | 160.35 | 0 | 0
2025-09-04 20:00 | 63.64 | 0 | 0 | 0 | 0 | 63.64 | 93.37 | 0 | 0
2025-09-04 21:00 | 61.2 | 0 | 0 | 3.33 | 0 | 57.87 | 32.45 | 0 | 0
2025-09-04 22:00 | 59.46 | 0 | 0 | 59.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-04 23:00 | 56.04 | 0 | 0 | 56.04 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 | 53.44 | 0 | 0 | 53.44 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 01:00 | 50.97 | 0 | 0 | 50.97 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 02:00 | 49.29 | 0 | 0 | 49.29 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 03:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 04:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 05:00 | 52.04 | 0 | 0 | 52.04 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 06:00 | 53.44 | 22.76 | 22.76 | 30.68 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 07:00 | 57.51 | 87.82 | 87.82 | 0 | 30.31 | 0 | 61.25 | 0 | 0
2025-09-05 08:00 | 60.09 | 107.42 | 107.42 | 0 | 47.33 | 0 | 106.21 | 0 | 0
2025-09-05 09:00 | 64.6 | 110.1 | 110.1 | 0 | 45.5 | 0 | 149.44 | 0 | 0
2025-09-05 10:00 | 68.73 | 107.97 | 107.97 | 0 | 39.24 | 0 | 186.71 | 0 | 0
2025-09-05 11:00 | 74.27 | 104.39 | 104.39 | 0 | 30.12 | 0 | 215.33 | 0 | 0
2025-09-05 12:00 | 78.88 | 101.41 | 101.41 | 0 | 22.52 | 0 | 236.73 | 0 | 0
2025-09-05 13:00 | 80.19 | 103.39 | 103.39 | 0 | 23.2 | 0 | 258.77 | 0 | 0
2025-09-05 14:00 | 82.99 | 105.68 | 105.68 | 0 | 22.68 | 0 | 280.32 | 0 | 0
2025-09-05 15:00 | 84.52 | 104.89 | 96.86 | 0 | 12.34 | 0 | 292.05 | 8.03 | 0
2025-09-05 16:00 | 82.44 | 97.7 | 82.44 | 0 | 0 | 0 | 292.05 | 15.26 | 0
2025-09-05 17:00 | 81.36 | 76.46 | 76.46 | 0 | 0 | 4.9 | 286.89 | 0 | 0
2025-09-05 18:00 | 78.44 | 7.71 | 7.71 | 0 | 0 | 70.73 | 212.44 | 0 | 0
2025-09-05 19:00 | 73.81 | 0 | 0 | 0 | 0 | 73.81 | 134.74 | 0 | 0
2025-09-05 20:00 | 69.55 | 0 | 0 | 0 | 0 | 69.55 | 61.53 | 0 | 0
2025-09-05 21:00 | 65.6 | 0 | 0 | 37.97 | 0 | 27.63 | 32.45 | 0 | 0
2025-09-05 22:00 | 61.42 | 0 | 0 | 61.42 | 0 | 0 | 32.45 | 0 | 0
2025-09-05 23:00 | 56.7 | 0 | 0 | 56.7 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 | 53.46 | 0 | 0 | 53.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 01:00 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 02:00 | 50.63 | 0 | 0 | 50.63 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 03:00 | 49.02 | 0 | 0 | 49.02 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 04:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 06:00 | 53.47 | 0.85 | 0.85 | 52.62 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 07:00 | 57.05 | 8.48 | 8.48 | 48.57 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 08:00 | 62.27 | 51.05 | 51.05 | 11.22 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 09:00 | 65.73 | 57.74 | 57.74 | 7.99 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 10:00 | 70.82 | 63.02 | 63.02 | 7.8 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 11:00 | 76.84 | 34.32 | 34.32 | 42.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 12:00 | 81.3 | 53.7 | 53.7 | 27.6 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 13:00 | 85.82 | 39.17 | 39.17 | 46.66 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 14:00 | 87.73 | 113.53 | 113.53 | 0 | 25.79 | 0 | 56.95 | 0 | 0
2025-09-06 15:00 | 88.41 | 109.47 | 109.47 | 0 | 21.06 | 0 | 76.96 | 0 | 0
2025-09-06 16:00 | 86.76 | 98.04 | 98.04 | 0 | 11.28 | 0 | 87.68 | 0 | 0
2025-09-06 17:00 | 84.29 | 42.73 | 42.73 | 0 | 0 | 41.56 | 43.93 | 0 | 0
2025-09-06 18:00 | 80.26 | 1.08 | 1.08 | 68.28 | 0 | 10.91 | 32.45 | 0 | 0
2025-09-06 19:00 | 76.52 | 0 | 0 | 76.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 20:00 | 70.35 | 0 | 0 | 70.35 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 21:00 | 66.41 | 0 | 0 | 66.41 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 22:00 | 61 | 0 | 0 | 61 | 0 | 0 | 32.45 | 0 | 0
2025-09-06 23:00 | 56.79 | 0 | 0 | 56.79 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 | 52.8 | 0 | 0 | 52.8 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 01:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 02:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 03:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 04:00 | 50.64 | 0 | 0 | 50.64 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 05:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 06:00 | 53.1 | 14.2 | 14.2 | 38.9 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 07:00 | 55.95 | 64.13 | 64.13 | 0 | 8.18 | 0 | 40.22 | 0 | 0
2025-09-07 08:00 | 58.29 | 77.38 | 77.38 | 0 | 19.09 | 0 | 58.36 | 0 | 0
2025-09-07 09:00 | 61.16 | 83.27 | 83.27 | 0 | 22.12 | 0 | 79.37 | 0 | 0
2025-09-07 10:00 | 63.06 | 75.39 | 75.39 | 0 | 12.33 | 0 | 91.08 | 0 | 0
2025-09-07 11:00 | 66.67 | 79.8 | 79.8 | 0 | 13.13 | 0 | 103.56 | 0 | 0
2025-09-07 12:00 | 67.08 | 95.54 | 95.54 | 0 | 28.45 | 0 | 130.59 | 0 | 0
2025-09-07 13:00 | 69.41 | 95.25 | 95.25 | 0 | 25.84 | 0 | 155.14 | 0 | 0
2025-09-07 14:00 | 69.29 | 99.94 | 99.94 | 0 | 30.65 | 0 | 184.26 | 0 | 0
2025-09-07 15:00 | 70.04 | 86.64 | 86.64 | 0 | 16.6 | 0 | 200.02 | 0 | 0
2025-09-07 16:00 | 69.75 | 106.64 | 106.64 | 0 | 36.88 | 0 | 235.06 | 0 | 0
2025-09-07 17:00 | 69.2 | 79.8 | 79.8 | 0 | 10.6 | 0 | 245.13 | 0 | 0
2025-09-07 18:00 | 66.95 | 9.15 | 9.15 | 0 | 0 | 57.8 | 184.28 | 0 | 0
2025-09-07 19:00 | 66.17 | 0 | 0 | 0 | 0 | 66.17 | 114.63 | 0 | 0
2025-09-07 20:00 | 64.39 | 0 | 0 | 0 | 0 | 64.39 | 46.85 | 0 | 0
2025-09-07 21:00 | 60.83 | 0 | 0 | 47.16 | 0 | 13.68 | 32.45 | 0 | 0
2025-09-07 22:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 32.45 | 0 | 0
2025-09-07 23:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 01:00 | 52.07 | 0 | 0 | 52.07 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 02:00 | 49.45 | 0 | 0 | 49.45 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 03:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 04:00 | 50.76 | 0 | 0 | 50.76 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 05:00 | 51.52 | 0 | 0 | 51.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 06:00 | 54.25 | 1.21 | 1.21 | 53.03 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 07:00 | 55.51 | 2.45 | 2.45 | 53.06 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 08:00 | 58.72 | 19.34 | 19.34 | 39.37 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 09:00 | 61.4 | 71.93 | 71.93 | 0 | 10.53 | 0 | 42.46 | 0 | 0
2025-09-08 10:00 | 64.82 | 101.38 | 101.38 | 0 | 36.55 | 0 | 77.18 | 0 | 0
2025-09-08 11:00 | 66.63 | 111.5 | 111.5 | 0 | 44.87 | 0 | 119.81 | 0 | 0
2025-09-08 12:00 | 70.2 | 100.92 | 100.92 | 0 | 30.72 | 0 | 149 | 0 | 0
2025-09-08 13:00 | 71.78 | 69.45 | 69.45 | 0 | 0 | 2.34 | 146.54 | 0 | 0
2025-09-08 14:00 | 72.69 | 10.43 | 10.43 | 0 | 0 | 62.26 | 81 | 0 | 0
2025-09-08 15:00 | 72.9 | 8.68 | 8.68 | 18.1 | 0 | 46.12 | 32.45 | 0 | 0
2025-09-08 16:00 | 72.28 | 2.34 | 2.34 | 69.93 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 17:00 | 71.99 | 0.75 | 0.75 | 71.23 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 18:00 | 69.27 | 1.49 | 1.49 | 67.78 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 19:00 | 67.77 | 0 | 0 | 67.77 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 20:00 | 65.79 | 0 | 0 | 65.79 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 21:00 | 62.47 | 0 | 0 | 62.47 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 22:00 | 57.9 | 0 | 0 | 57.9 | 0 | 0 | 32.45 | 0 | 0
2025-09-08 23:00 | 55.46 | 0 | 0 | 55.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 | 53.36 | 0 | 0 | 53.36 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 01:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 02:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 03:00 | 49.63 | 0 | 0 | 49.63 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 04:00 | 49.86 | 0 | 0 | 49.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 05:00 | 52.08 | 0 | 0 | 52.08 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 06:00 | 53.02 | 17.02 | 17.02 | 36 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 07:00 | 56.39 | 83.09 | 83.09 | 0 | 26.7 | 0 | 57.81 | 0 | 0
2025-09-09 08:00 | 58.32 | 85.11 | 85.11 | 0 | 26.79 | 0 | 83.26 | 0 | 0
2025-09-09 09:00 | 61.86 | 98.58 | 98.58 | 0 | 36.72 | 0 | 118.14 | 0 | 0
2025-09-09 10:00 | 66.21 | 98.28 | 98.28 | 0 | 32.07 | 0 | 148.61 | 0 | 0
2025-09-09 11:00 | 69.68 | 93.14 | 93.14 | 0 | 23.46 | 0 | 170.89 | 0 | 0
2025-09-09 12:00 | 71.52 | 89.32 | 89.32 | 0 | 17.8 | 0 | 187.8 | 0 | 0
2025-09-09 13:00 | 74.22 | 93.94 | 93.94 | 0 | 19.72 | 0 | 206.54 | 0 | 0
2025-09-09 14:00 | 74.92 | 98.28 | 98.28 | 0 | 23.36 | 0 | 228.74 | 0 | 0
2025-09-09 15:00 | 76 | 90.09 | 90.09 | 0 | 14.09 | 0 | 242.12 | 0 | 0
2025-09-09 16:00 | 76.03 | 87.46 | 87.46 | 0 | 11.44 | 0 | 252.99 | 0 | 0
2025-09-09 17:00 | 73.99 | 54.75 | 54.75 | 0 | 0 | 19.24 | 232.74 | 0 | 0
2025-09-09 18:00 | 71.87 | 3.21 | 3.21 | 0 | 0 | 68.66 | 160.46 | 0 | 0
2025-09-09 19:00 | 68.57 | 0 | 0 | 0 | 0 | 68.57 | 88.28 | 0 | 0
2025-09-09 20:00 | 65.53 | 0 | 0 | 12.49 | 0 | 53.04 | 32.45 | 0 | 0
2025-09-09 21:00 | 63.26 | 0 | 0 | 63.26 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 22:00 | 58.99 | 0 | 0 | 58.99 | 0 | 0 | 32.45 | 0 | 0
2025-09-09 23:00 | 55.31 | 0 | 0 | 55.31 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 | 53.01 | 0 | 0 | 53.01 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 01:00 | 50.25 | 0 | 0 | 50.25 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 02:00 | 49.26 | 0 | 0 | 49.26 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 03:00 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 04:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 05:00 | 52 | 0 | 0 | 52 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 06:00 | 53.12 | 14.61 | 14.61 | 38.51 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 07:00 | 56.06 | 61.79 | 61.79 | 0 | 5.73 | 0 | 37.9 | 0 | 0
2025-09-10 08:00 | 59.99 | 89.07 | 89.07 | 0 | 29.08 | 0 | 65.53 | 0 | 0
2025-09-10 09:00 | 62.44 | 91.68 | 91.68 | 0 | 29.24 | 0 | 93.31 | 0 | 0
2025-09-10 10:00 | 68.24 | 87.37 | 87.37 | 0 | 19.12 | 0 | 111.47 | 0 | 0
2025-09-10 11:00 | 72.42 | 96.81 | 96.81 | 0 | 24.39 | 0 | 134.64 | 0 | 0
2025-09-10 12:00 | 77.07 | 93.66 | 93.66 | 0 | 16.59 | 0 | 150.4 | 0 | 0
2025-09-10 13:00 | 79.9 | 87.58 | 87.58 | 0 | 7.69 | 0 | 157.71 | 0 | 0
2025-09-10 14:00 | 80.84 | 63.45 | 63.45 | 0 | 0 | 17.39 | 139.41 | 0 | 0
2025-09-10 15:00 | 82.71 | 47.44 | 47.44 | 0 | 0 | 35.28 | 102.27 | 0 | 0
2025-09-10 16:00 | 81.27 | 16.67 | 16.67 | 0 | 0 | 64.6 | 34.28 | 0 | 0
2025-09-10 17:00 | 78.96 | 0.2 | 0.2 | 77.03 | 0 | 1.73 | 32.45 | 0 | 0
2025-09-10 18:00 | 76.42 | 0.24 | 0.24 | 76.18 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 19:00 | 72.35 | 0 | 0 | 72.35 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 20:00 | 68.91 | 0 | 0 | 68.91 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 21:00 | 63.94 | 0 | 0 | 63.94 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 22:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 32.45 | 0 | 0
2025-09-10 23:00 | 56.52 | 0 | 0 | 56.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 01:00 | 51.28 | 0 | 0 | 51.28 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 02:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 03:00 | 49.55 | 0 | 0 | 49.55 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 04:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 05:00 | 51.51 | 0 | 0 | 51.51 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 06:00 | 52.75 | 8.89 | 8.89 | 43.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 07:00 | 55.2 | 91.62 | 91.62 | 0 | 36.42 | 0 | 67.05 | 0 | 0
2025-09-11 08:00 | 58.71 | 86.72 | 86.72 | 0 | 28.01 | 0 | 93.66 | 0 | 0
2025-09-11 09:00 | 61.38 | 63.38 | 63.38 | 0 | 2.01 | 0 | 95.57 | 0 | 0
2025-09-11 10:00 | 63.13 | 70.5 | 70.5 | 0 | 7.37 | 0 | 102.57 | 0 | 0
2025-09-11 11:00 | 65.17 | 80.74 | 80.74 | 0 | 15.57 | 0 | 117.36 | 0 | 0
2025-09-11 12:00 | 67.97 | 72.33 | 72.33 | 0 | 4.36 | 0 | 121.5 | 0 | 0
2025-09-11 13:00 | 68.98 | 82.42 | 82.42 | 0 | 13.44 | 0 | 134.27 | 0 | 0
2025-09-11 14:00 | 69.56 | 78.67 | 78.67 | 0 | 9.11 | 0 | 142.92 | 0 | 0
2025-09-11 15:00 | 69.52 | 72.18 | 72.18 | 0 | 2.67 | 0 | 145.46 | 0 | 0
2025-09-11 16:00 | 69.57 | 35.72 | 35.72 | 0 | 0 | 33.85 | 109.83 | 0 | 0
2025-09-11 17:00 | 68.57 | 11.91 | 11.91 | 0 | 0 | 56.67 | 50.18 | 0 | 0
2025-09-11 18:00 | 66.9 | 0.84 | 0.84 | 49.22 | 0 | 16.84 | 32.45 | 0 | 0
2025-09-11 19:00 | 65.46 | 0 | 0 | 65.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 20:00 | 63.27 | 0 | 0 | 63.27 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 21:00 | 60.38 | 0 | 0 | 60.38 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 22:00 | 58.3 | 0 | 0 | 58.3 | 0 | 0 | 32.45 | 0 | 0
2025-09-11 23:00 | 55.83 | 0 | 0 | 55.83 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 01:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 02:00 | 49.95 | 0 | 0 | 49.95 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 03:00 | 49.19 | 0 | 0 | 49.19 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 04:00 | 48.96 | 0 | 0 | 48.96 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 05:00 | 51.14 | 0 | 0 | 51.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 06:00 | 52.82 | 13.19 | 13.19 | 39.63 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 07:00 | 56.56 | 85.9 | 85.9 | 0 | 29.34 | 0 | 60.32 | 0 | 0
2025-09-12 08:00 | 58.89 | 105.5 | 105.5 | 0 | 46.62 | 0 | 104.61 | 0 | 0
2025-09-12 09:00 | 61.59 | 105.4 | 105.4 | 0 | 43.81 | 0 | 146.23 | 0 | 0
2025-09-12 10:00 | 64.39 | 94.96 | 94.96 | 0 | 30.56 | 0 | 175.26 | 0 | 0
2025-09-12 11:00 | 67.15 | 92.63 | 92.63 | 0 | 25.48 | 0 | 199.47 | 0 | 0
2025-09-12 12:00 | 68.94 | 92.33 | 92.33 | 0 | 23.39 | 0 | 221.69 | 0 | 0
2025-09-12 13:00 | 70.38 | 95.38 | 95.38 | 0 | 25 | 0 | 245.45 | 0 | 0
2025-09-12 14:00 | 71.95 | 96.77 | 96.77 | 0 | 24.83 | 0 | 269.03 | 0 | 0
2025-09-12 15:00 | 72.74 | 99.01 | 96.97 | 0 | 24.23 | 0 | 292.05 | 2.04 | 0
2025-09-12 16:00 | 71.33 | 92.01 | 71.33 | 0 | 0 | 0 | 292.05 | 20.68 | 0
2025-09-12 17:00 | 70.98 | 56.97 | 56.97 | 0 | 0 | 14.01 | 277.31 | 0 | 0
2025-09-12 18:00 | 69.32 | 1.58 | 1.58 | 0 | 0 | 67.74 | 206 | 0 | 0
2025-09-12 19:00 | 66.96 | 0 | 0 | 0 | 0 | 66.96 | 135.51 | 0 | 0
2025-09-12 20:00 | 63.94 | 0 | 0 | 0 | 0 | 63.94 | 68.21 | 0 | 0
2025-09-12 21:00 | 61.06 | 0 | 0 | 27.09 | 0 | 33.97 | 32.45 | 0 | 0
2025-09-12 22:00 | 59.02 | 0 | 0 | 59.02 | 0 | 0 | 32.45 | 0 | 0
2025-09-12 23:00 | 55.59 | 0 | 0 | 55.59 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 01:00 | 50.68 | 0 | 0 | 50.68 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 02:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 03:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 04:00 | 49.09 | 0 | 0 | 49.09 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 05:00 | 51.22 | 0 | 0 | 51.22 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 06:00 | 52.52 | 5.94 | 5.94 | 46.57 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 07:00 | 54.86 | 3.52 | 3.52 | 51.34 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 08:00 | 58.61 | 12.02 | 12.02 | 46.59 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 09:00 | 62.26 | 31.91 | 31.91 | 30.34 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 10:00 | 64.89 | 47.53 | 47.53 | 17.36 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 11:00 | 69.39 | 51.23 | 51.23 | 18.16 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 12:00 | 72.96 | 80.68 | 80.68 | 0 | 7.73 | 0 | 39.79 | 0 | 0
2025-09-13 13:00 | 75.19 | 74.77 | 74.77 | 0 | 0 | 0.42 | 39.35 | 0 | 0
2025-09-13 14:00 | 77.64 | 85.94 | 85.94 | 0 | 8.31 | 0 | 47.24 | 0 | 0
2025-09-13 15:00 | 77.68 | 116.18 | 116.18 | 0 | 38.5 | 0 | 83.82 | 0 | 0
2025-09-13 16:00 | 77.24 | 113.73 | 113.73 | 0 | 36.49 | 0 | 118.48 | 0 | 0
2025-09-13 17:00 | 76.36 | 70.59 | 70.59 | 0 | 0 | 5.77 | 112.4 | 0 | 0
2025-09-13 18:00 | 72.9 | 1.35 | 1.35 | 0 | 0 | 71.56 | 37.08 | 0 | 0
2025-09-13 19:00 | 69.49 | 0 | 0 | 65.1 | 0 | 4.4 | 32.45 | 0 | 0
2025-09-13 20:00 | 66.36 | 0 | 0 | 66.36 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 21:00 | 61.92 | 0 | 0 | 61.92 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 22:00 | 58.68 | 0 | 0 | 58.68 | 0 | 0 | 32.45 | 0 | 0
2025-09-13 23:00 | 55.09 | 0 | 0 | 55.09 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 | 52.77 | 0 | 0 | 52.77 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 01:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 02:00 | 49.03 | 0 | 0 | 49.03 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 03:00 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 04:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 05:00 | 49.64 | 0 | 0 | 49.64 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 06:00 | 51.85 | 6.99 | 6.99 | 44.85 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 07:00 | 54.61 | 66.16 | 66.16 | 0 | 11.55 | 0 | 43.42 | 0 | 0
2025-09-14 08:00 | 57.83 | 64.43 | 64.43 | 0 | 6.61 | 0 | 49.7 | 0 | 0
2025-09-14 09:00 | 61.85 | 112.56 | 112.56 | 0 | 50.71 | 0 | 97.87 | 0 | 0
2025-09-14 10:00 | 65.19 | 85.38 | 85.38 | 0 | 20.19 | 0 | 117.05 | 0 | 0
2025-09-14 11:00 | 68.88 | 47.66 | 47.66 | 0 | 0 | 21.22 | 94.71 | 0 | 0
2025-09-14 12:00 | 71.57 | 54 | 54 | 0 | 0 | 17.57 | 76.21 | 0 | 0
2025-09-14 13:00 | 73.94 | 37.34 | 37.34 | 0 | 0 | 36.61 | 37.68 | 0 | 0
2025-09-14 14:00 | 75.11 | 37.44 | 37.44 | 32.7 | 0 | 4.97 | 32.45 | 0 | 0
2025-09-14 15:00 | 75.39 | 35.46 | 35.46 | 39.93 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 16:00 | 75.36 | 75.48 | 75.48 | 0 | 0.12 | 0 | 32.57 | 0 | 0
2025-09-14 17:00 | 73.86 | 43.27 | 43.27 | 30.48 | 0 | 0.11 | 32.45 | 0 | 0
2025-09-14 18:00 | 71.38 | 1 | 1 | 70.38 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 19:00 | 68.98 | 0 | 0 | 68.98 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 20:00 | 63.91 | 0 | 0 | 63.91 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 21:00 | 61.5 | 0 | 0 | 61.5 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 22:00 | 58.12 | 0 | 0 | 58.12 | 0 | 0 | 32.45 | 0 | 0
2025-09-14 23:00 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 | 53.16 | 0 | 0 | 53.16 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 01:00 | 49.75 | 0 | 0 | 49.75 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 02:00 | 49.98 | 0 | 0 | 49.98 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 03:00 | 48.27 | 0 | 0 | 48.27 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 04:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 05:00 | 50.36 | 0 | 0 | 50.36 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 06:00 | 52.22 | 13.78 | 13.78 | 38.44 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 07:00 | 54.04 | 88.49 | 88.49 | 0 | 34.45 | 0 | 65.18 | 0 | 0
2025-09-15 08:00 | 57.95 | 108.03 | 108.03 | 0 | 50.08 | 0 | 112.75 | 0 | 0
2025-09-15 09:00 | 60.92 | 111.73 | 111.73 | 0 | 50.8 | 0 | 161.01 | 0 | 0
2025-09-15 10:00 | 64.01 | 107.36 | 107.36 | 0 | 43.34 | 0 | 202.19 | 0 | 0
2025-09-15 11:00 | 65.92 | 102.52 | 102.52 | 0 | 36.6 | 0 | 236.96 | 0 | 0
2025-09-15 12:00 | 68.36 | 100.36 | 100.36 | 0 | 32 | 0 | 267.36 | 0 | 0
2025-09-15 13:00 | 70.06 | 103.28 | 96.05 | 0 | 25.99 | 0 | 292.05 | 7.22 | 0
2025-09-15 14:00 | 71.97 | 105.83 | 71.97 | 0 | 0 | 0 | 292.05 | 33.86 | 0
2025-09-15 15:00 | 70.07 | 52.43 | 52.43 | 0 | 0 | 17.64 | 273.48 | 0 | 0
2025-09-15 16:00 | 70.65 | 8.44 | 8.44 | 0 | 0 | 62.21 | 208 | 0 | 0
2025-09-15 17:00 | 70.08 | 0.03 | 0.03 | 0 | 0 | 70.04 | 134.27 | 0 | 0
2025-09-15 18:00 | 67.84 | 0 | 0 | 0 | 0 | 67.84 | 62.86 | 0 | 0
2025-09-15 19:00 | 66.01 | 0 | 0 | 37.12 | 0 | 28.89 | 32.45 | 0 | 0
2025-09-15 20:00 | 63.42 | 0 | 0 | 63.42 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 21:00 | 60.26 | 0 | 0 | 60.26 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 22:00 | 57.66 | 0 | 0 | 57.66 | 0 | 0 | 32.45 | 0 | 0
2025-09-15 23:00 | 55.14 | 0 | 0 | 55.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 | 52.16 | 0 | 0 | 52.16 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 01:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 02:00 | 49.08 | 0 | 0 | 49.08 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 03:00 | 48.75 | 0 | 0 | 48.75 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 04:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 05:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 06:00 | 52.05 | 2.17 | 2.17 | 49.89 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 07:00 | 55.38 | 1.7 | 1.7 | 53.69 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 08:00 | 57.91 | 36.39 | 36.39 | 21.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 09:00 | 61.26 | 32.29 | 32.29 | 28.97 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 10:00 | 63.21 | 59.74 | 59.74 | 3.47 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 11:00 | 66.34 | 58.98 | 58.98 | 7.36 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 12:00 | 68.31 | 52.3 | 52.3 | 16.01 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 13:00 | 70.41 | 58.51 | 58.51 | 11.9 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 14:00 | 72.54 | 64.73 | 64.73 | 7.81 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 15:00 | 73.05 | 107.2 | 107.2 | 0 | 34.16 | 0 | 64.9 | 0 | 0
2025-09-16 16:00 | 71.34 | 103.44 | 103.44 | 0 | 32.1 | 0 | 95.4 | 0 | 0
2025-09-16 17:00 | 70.53 | 59.11 | 59.11 | 0 | 0 | 11.42 | 83.37 | 0 | 0
2025-09-16 18:00 | 68.89 | 1.21 | 1.21 | 19.31 | 0 | 48.38 | 32.45 | 0 | 0
2025-09-16 19:00 | 66.82 | 0 | 0 | 66.82 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 20:00 | 62.83 | 0 | 0 | 62.83 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 21:00 | 59.87 | 0 | 0 | 59.87 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 22:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-16 23:00 | 53.78 | 0 | 0 | 53.78 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 | 51.81 | 0 | 0 | 51.81 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 01:00 | 50.31 | 0 | 0 | 50.31 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 02:00 | 49.27 | 0 | 0 | 49.27 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 03:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 04:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 05:00 | 50.66 | 0 | 0 | 50.66 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 06:00 | 52.18 | 2 | 2 | 50.18 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 07:00 | 53.95 | 79.82 | 79.82 | 0 | 25.86 | 0 | 57.02 | 0 | 0
2025-09-17 08:00 | 56.74 | 55.29 | 55.29 | 0 | 0 | 1.45 | 55.49 | 0 | 0
2025-09-17 09:00 | 59.35 | 19.2 | 19.2 | 18.26 | 0 | 21.89 | 32.45 | 0 | 0
2025-09-17 10:00 | 62.25 | 56.33 | 56.33 | 5.92 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 11:00 | 63.69 | 20.16 | 20.16 | 43.53 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 12:00 | 65.4 | 27.89 | 27.89 | 37.51 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 13:00 | 65.56 | 37.07 | 37.07 | 28.49 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 14:00 | 66.23 | 85.52 | 85.52 | 0 | 19.29 | 0 | 50.77 | 0 | 0
2025-09-17 15:00 | 66.58 | 65.97 | 65.97 | 0 | 0 | 0.61 | 50.13 | 0 | 0
2025-09-17 16:00 | 66.42 | 26.07 | 26.07 | 23.56 | 0 | 16.79 | 32.45 | 0 | 0
2025-09-17 17:00 | 65.36 | 9.98 | 9.98 | 55.38 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 18:00 | 65.43 | 0 | 0 | 65.43 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 19:00 | 63.74 | 0 | 0 | 63.74 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 20:00 | 61.24 | 0 | 0 | 61.24 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 21:00 | 59.48 | 0 | 0 | 59.48 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 22:00 | 56.84 | 0 | 0 | 56.84 | 0 | 0 | 32.45 | 0 | 0
2025-09-17 23:00 | 54.64 | 0 | 0 | 54.64 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 01:00 | 50.07 | 0 | 0 | 50.07 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 02:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 03:00 | 48.86 | 0 | 0 | 48.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 04:00 | 48.64 | 0 | 0 | 48.64 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 05:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 06:00 | 51.48 | 0.68 | 0.68 | 50.8 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 07:00 | 54.41 | 3.53 | 3.53 | 50.88 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 08:00 | 57.27 | 17.23 | 17.23 | 40.05 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 09:00 | 61.05 | 65.54 | 65.54 | 0 | 4.49 | 0 | 36.72 | 0 | 0
2025-09-18 10:00 | 63.43 | 51.69 | 51.69 | 7.69 | 0 | 4.05 | 32.45 | 0 | 0
2025-09-18 11:00 | 65.89 | 81.04 | 81.04 | 0 | 15.16 | 0 | 46.85 | 0 | 0
2025-09-18 12:00 | 68.13 | 27.86 | 27.86 | 26.59 | 0 | 13.68 | 32.45 | 0 | 0
2025-09-18 13:00 | 70.45 | 20.76 | 20.76 | 49.68 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 14:00 | 70.69 | 38.88 | 38.88 | 31.81 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 15:00 | 71.29 | 3.41 | 3.41 | 67.88 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 16:00 | 70.44 | 14.17 | 14.17 | 56.28 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 17:00 | 70.6 | 11.46 | 11.46 | 59.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 18:00 | 68.34 | 0 | 0 | 68.34 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 19:00 | 65.49 | 0 | 0 | 65.49 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 20:00 | 63.09 | 0 | 0 | 63.09 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 21:00 | 60.46 | 0 | 0 | 60.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 22:00 | 57.11 | 0 | 0 | 57.11 | 0 | 0 | 32.45 | 0 | 0
2025-09-18 23:00 | 54.18 | 0 | 0 | 54.18 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 | 51.56 | 0 | 0 | 51.56 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 01:00 | 50.19 | 0 | 0 | 50.19 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 02:00 | 48.67 | 0 | 0 | 48.67 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 03:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 04:00 | 48.18 | 0 | 0 | 48.18 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 05:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 06:00 | 51.8 | 4.81 | 4.81 | 46.98 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 07:00 | 54.13 | 69.84 | 69.84 | 0 | 15.71 | 0 | 47.37 | 0 | 0
2025-09-19 08:00 | 57.16 | 80.36 | 80.36 | 0 | 23.19 | 0 | 69.4 | 0 | 0
2025-09-19 09:00 | 60.37 | 84.17 | 84.17 | 0 | 23.8 | 0 | 92.01 | 0 | 0
2025-09-19 10:00 | 63.25 | 93.04 | 93.04 | 0 | 29.8 | 0 | 120.32 | 0 | 0
2025-09-19 11:00 | 65.84 | 94.36 | 94.36 | 0 | 28.53 | 0 | 147.42 | 0 | 0
2025-09-19 12:00 | 67.71 | 77.63 | 77.63 | 0 | 9.93 | 0 | 156.85 | 0 | 0
2025-09-19 13:00 | 69.26 | 76.04 | 76.04 | 0 | 6.77 | 0 | 163.28 | 0 | 0
2025-09-19 14:00 | 70.1 | 62.65 | 62.65 | 0 | 0 | 7.45 | 155.44 | 0 | 0
2025-09-19 15:00 | 70.69 | 52.74 | 52.74 | 0 | 0 | 17.95 | 136.55 | 0 | 0
2025-09-19 16:00 | 70.63 | 31.13 | 31.13 | 0 | 0 | 39.5 | 94.97 | 0 | 0
2025-09-19 17:00 | 69.15 | 3.71 | 3.71 | 6.05 | 0 | 59.4 | 32.45 | 0 | 0
2025-09-19 18:00 | 67.87 | 0 | 0 | 67.87 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 19:00 | 65.08 | 0 | 0 | 65.08 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 20:00 | 62.07 | 0 | 0 | 62.07 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 21:00 | 60.41 | 0 | 0 | 60.41 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 22:00 | 56.82 | 0 | 0 | 56.82 | 0 | 0 | 32.45 | 0 | 0
2025-09-19 23:00 | 53.87 | 0 | 0 | 53.87 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 | 51.26 | 0 | 0 | 51.26 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 02:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 03:00 | 48.14 | 0 | 0 | 48.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 04:00 | 48.63 | 0 | 0 | 48.63 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 05:00 | 50.45 | 0 | 0 | 50.45 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 06:00 | 50.9 | 1.89 | 1.89 | 49.01 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 07:00 | 55.26 | 37.72 | 37.72 | 17.54 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 08:00 | 58.41 | 52.02 | 52.02 | 6.39 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 09:00 | 58.99 | 56.89 | 56.89 | 2.1 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 10:00 | 63.48 | 50.64 | 50.64 | 12.85 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 11:00 | 66.17 | 31.02 | 31.02 | 35.15 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 12:00 | 69 | 31.14 | 31.14 | 37.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 13:00 | 70.93 | 39.58 | 39.58 | 31.35 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 14:00 | 72.82 | 24.83 | 24.83 | 47.98 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 15:00 | 72.79 | 20.76 | 20.76 | 52.02 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 16:00 | 71.95 | 7.37 | 7.37 | 64.58 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 17:00 | 71.05 | 0.02 | 0.02 | 71.03 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 18:00 | 69.39 | 0 | 0 | 69.39 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 19:00 | 65.94 | 0 | 0 | 65.94 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 20:00 | 62.71 | 0 | 0 | 62.71 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 21:00 | 61.34 | 0 | 0 | 61.34 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 22:00 | 56.87 | 0 | 0 | 56.87 | 0 | 0 | 32.45 | 0 | 0
2025-09-20 23:00 | 54.21 | 0 | 0 | 54.21 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 01:00 | 50.06 | 0 | 0 | 50.06 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 02:00 | 49.51 | 0 | 0 | 49.51 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 03:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 04:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 05:00 | 49.09 | 0 | 0 | 49.09 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 06:00 | 51.4 | 4.9 | 4.9 | 46.5 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 07:00 | 53.79 | 84.62 | 84.62 | 0 | 30.83 | 0 | 61.74 | 0 | 0
2025-09-21 08:00 | 55.71 | 108.55 | 108.55 | 0 | 52.84 | 0 | 111.94 | 0 | 0
2025-09-21 09:00 | 59.74 | 111.65 | 111.65 | 0 | 51.91 | 0 | 161.26 | 0 | 0
2025-09-21 10:00 | 61.47 | 86.61 | 86.61 | 0 | 25.14 | 0 | 185.14 | 0 | 0
2025-09-21 11:00 | 65.19 | 86.7 | 86.7 | 0 | 21.51 | 0 | 205.58 | 0 | 0
2025-09-21 12:00 | 67.38 | 78.3 | 78.3 | 0 | 10.92 | 0 | 215.95 | 0 | 0
2025-09-21 13:00 | 67.87 | 74.34 | 74.34 | 0 | 6.46 | 0 | 222.09 | 0 | 0
2025-09-21 14:00 | 69.16 | 38.15 | 38.15 | 0 | 0 | 31.01 | 189.45 | 0 | 0
2025-09-21 15:00 | 68.64 | 18.71 | 18.71 | 0 | 0 | 49.94 | 136.88 | 0 | 0
2025-09-21 16:00 | 69.25 | 13.4 | 13.4 | 0 | 0 | 55.86 | 78.08 | 0 | 0
2025-09-21 17:00 | 67.75 | 0 | 0 | 24.4 | 0 | 43.35 | 32.45 | 0 | 0
2025-09-21 18:00 | 65.93 | 0 | 0 | 65.93 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 19:00 | 64.3 | 0 | 0 | 64.3 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 20:00 | 61.78 | 0 | 0 | 61.78 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 21:00 | 59.17 | 0 | 0 | 59.17 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 22:00 | 57.04 | 0 | 0 | 57.04 | 0 | 0 | 32.45 | 0 | 0
2025-09-21 23:00 | 53.53 | 0 | 0 | 53.53 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 | 52.43 | 0 | 0 | 52.43 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 01:00 | 49.02 | 0 | 0 | 49.02 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 02:00 | 49.32 | 0 | 0 | 49.32 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 03:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 04:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 05:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 06:00 | 51.39 | 0.08 | 0.08 | 51.31 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 07:00 | 54.45 | 1.67 | 1.67 | 52.78 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 08:00 | 57.74 | 10.92 | 10.92 | 46.82 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 09:00 | 60.81 | 13.96 | 13.96 | 46.85 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 10:00 | 63.31 | 45.95 | 45.95 | 17.36 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 11:00 | 66.73 | 68.94 | 68.94 | 0 | 2.22 | 0 | 34.56 | 0 | 0
2025-09-22 12:00 | 68.97 | 80.77 | 80.77 | 0 | 11.8 | 0 | 45.77 | 0 | 0
2025-09-22 13:00 | 70.99 | 98.68 | 98.68 | 0 | 27.68 | 0 | 72.06 | 0 | 0
2025-09-22 14:00 | 72.26 | 56.19 | 56.19 | 0 | 0 | 16.07 | 55.15 | 0 | 0
2025-09-22 15:00 | 73.08 | 37.66 | 37.66 | 13.87 | 0 | 21.56 | 32.45 | 0 | 0
2025-09-22 16:00 | 72.96 | 27.06 | 27.06 | 45.9 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 17:00 | 70.53 | 19.96 | 19.96 | 50.58 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 18:00 | 69.34 | 0 | 0 | 69.34 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 19:00 | 67.39 | 0 | 0 | 67.39 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 20:00 | 64.07 | 0 | 0 | 64.07 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 21:00 | 59.92 | 0 | 0 | 59.92 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 22:00 | 56.29 | 0 | 0 | 56.29 | 0 | 0 | 32.45 | 0 | 0
2025-09-22 23:00 | 54.28 | 0 | 0 | 54.28 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 | 50.32 | 0 | 0 | 50.32 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 01:00 | 50.13 | 0 | 0 | 50.13 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 02:00 | 48.3 | 0 | 0 | 48.3 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 03:00 | 48.92 | 0 | 0 | 48.92 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 04:00 | 47.54 | 0 | 0 | 47.54 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 05:00 | 50.03 | 0 | 0 | 50.03 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 06:00 | 51.42 | 3.23 | 3.23 | 48.2 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 07:00 | 53.87 | 37.52 | 37.52 | 16.35 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 08:00 | 56.44 | 70.44 | 70.44 | 0 | 13.99 | 0 | 45.74 | 0 | 0
2025-09-23 09:00 | 60.88 | 86.04 | 86.04 | 0 | 25.16 | 0 | 69.64 | 0 | 0
2025-09-23 10:00 | 64.52 | 89.14 | 89.14 | 0 | 24.62 | 0 | 93.04 | 0 | 0
2025-09-23 11:00 | 68.55 | 92.03 | 92.03 | 0 | 23.48 | 0 | 115.34 | 0 | 0
2025-09-23 12:00 | 71.25 | 90.28 | 90.28 | 0 | 19.03 | 0 | 133.42 | 0 | 0
2025-09-23 13:00 | 72.88 | 87.62 | 87.62 | 0 | 14.74 | 0 | 147.43 | 0 | 0
2025-09-23 14:00 | 74.23 | 89.98 | 89.98 | 0 | 15.75 | 0 | 162.39 | 0 | 0
2025-09-23 15:00 | 74.58 | 82.45 | 82.45 | 0 | 7.87 | 0 | 169.87 | 0 | 0
2025-09-23 16:00 | 75.46 | 66.38 | 66.38 | 0 | 0 | 9.08 | 160.31 | 0 | 0
2025-09-23 17:00 | 72.78 | 18.77 | 18.77 | 0 | 0 | 54.02 | 103.45 | 0 | 0
2025-09-23 18:00 | 71.49 | 0 | 0 | 4.04 | 0 | 67.45 | 32.45 | 0 | 0
2025-09-23 19:00 | 67.92 | 0 | 0 | 67.92 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 20:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 21:00 | 60.43 | 0 | 0 | 60.43 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 22:00 | 57.46 | 0 | 0 | 57.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-23 23:00 | 54.03 | 0 | 0 | 54.03 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 | 51.08 | 0 | 0 | 51.08 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 01:00 | 49.78 | 0 | 0 | 49.78 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 02:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 03:00 | 47.5 | 0 | 0 | 47.5 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 04:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 05:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 06:00 | 51.51 | 1.68 | 1.68 | 49.83 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 07:00 | 53.43 | 24.19 | 24.19 | 29.24 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 08:00 | 55.86 | 59.81 | 59.81 | 0 | 3.95 | 0 | 36.2 | 0 | 0
2025-09-24 09:00 | 60.37 | 87.49 | 87.49 | 0 | 27.12 | 0 | 61.96 | 0 | 0
2025-09-24 10:00 | 63.33 | 95.03 | 95.03 | 0 | 31.7 | 0 | 92.08 | 0 | 0
2025-09-24 11:00 | 65.87 | 81.53 | 81.53 | 0 | 15.66 | 0 | 106.96 | 0 | 0
2025-09-24 12:00 | 67.71 | 78.54 | 78.54 | 0 | 10.83 | 0 | 117.25 | 0 | 0
2025-09-24 13:00 | 69.66 | 91.04 | 91.04 | 0 | 21.38 | 0 | 137.56 | 0 | 0
2025-09-24 14:00 | 71.71 | 92.12 | 92.12 | 0 | 20.41 | 0 | 156.95 | 0 | 0
2025-09-24 15:00 | 71.25 | 68.22 | 68.22 | 0 | 0 | 3.03 | 153.76 | 0 | 0
2025-09-24 16:00 | 70.7 | 48.26 | 48.26 | 0 | 0 | 22.44 | 130.14 | 0 | 0
2025-09-24 17:00 | 70.75 | 11.91 | 11.91 | 0 | 0 | 58.84 | 68.2 | 0 | 0
2025-09-24 18:00 | 67.88 | 0 | 0 | 33.92 | 0 | 33.96 | 32.45 | 0 | 0
2025-09-24 19:00 | 66.31 | 0 | 0 | 66.31 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 20:00 | 61.86 | 0 | 0 | 61.86 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 21:00 | 59.76 | 0 | 0 | 59.76 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 22:00 | 57.5 | 0 | 0 | 57.5 | 0 | 0 | 32.45 | 0 | 0
2025-09-24 23:00 | 53.68 | 0 | 0 | 53.68 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 | 51.01 | 0 | 0 | 51.01 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 01:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 02:00 | 48.71 | 0 | 0 | 48.71 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 03:00 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 04:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 05:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 06:00 | 51.92 | 1.95 | 1.95 | 49.98 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 07:00 | 54.14 | 28.47 | 28.47 | 25.67 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 08:00 | 56.39 | 43.44 | 43.44 | 12.95 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 09:00 | 58.93 | 57.82 | 57.82 | 1.11 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 10:00 | 63.43 | 77.58 | 77.58 | 0 | 14.15 | 0 | 45.89 | 0 | 0
2025-09-25 11:00 | 65.46 | 76.12 | 76.12 | 0 | 10.66 | 0 | 56.02 | 0 | 0
2025-09-25 12:00 | 67.68 | 68.38 | 68.38 | 0 | 0.7 | 0 | 56.68 | 0 | 0
2025-09-25 13:00 | 69.36 | 82.01 | 82.01 | 0 | 12.64 | 0 | 68.69 | 0 | 0
2025-09-25 14:00 | 71.19 | 98.44 | 98.44 | 0 | 27.25 | 0 | 94.58 | 0 | 0
2025-09-25 15:00 | 71.22 | 96.93 | 96.93 | 0 | 25.71 | 0 | 119 | 0 | 0
2025-09-25 16:00 | 71.2 | 80.92 | 80.92 | 0 | 9.72 | 0 | 128.24 | 0 | 0
2025-09-25 17:00 | 70.61 | 27.44 | 27.44 | 0 | 0 | 43.18 | 82.79 | 0 | 0
2025-09-25 18:00 | 68.04 | 0 | 0 | 20.22 | 0 | 47.82 | 32.45 | 0 | 0
2025-09-25 19:00 | 65.82 | 0 | 0 | 65.82 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 20:00 | 62.3 | 0 | 0 | 62.3 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 21:00 | 59.54 | 0 | 0 | 59.54 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 22:00 | 57.37 | 0 | 0 | 57.37 | 0 | 0 | 32.45 | 0 | 0
2025-09-25 23:00 | 53.38 | 0 | 0 | 53.38 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 | 51.17 | 0 | 0 | 51.17 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 01:00 | 48.4 | 0 | 0 | 48.4 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 02:00 | 48.82 | 0 | 0 | 48.82 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 03:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 04:00 | 48.58 | 0 | 0 | 48.58 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 05:00 | 49.12 | 0 | 0 | 49.12 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 06:00 | 51.29 | 0.32 | 0.32 | 50.97 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 07:00 | 53.66 | 7.83 | 7.83 | 45.83 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 08:00 | 55.84 | 34.77 | 34.77 | 21.07 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 09:00 | 59.55 | 43.82 | 43.82 | 15.73 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 10:00 | 61.58 | 48.14 | 48.14 | 13.43 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 11:00 | 65.1 | 48.29 | 48.29 | 16.81 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 12:00 | 66.89 | 55.01 | 55.01 | 11.88 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 13:00 | 69.09 | 35.83 | 35.83 | 33.26 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 14:00 | 69.83 | 22.12 | 22.12 | 47.71 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 15:00 | 70.48 | 2.43 | 2.43 | 68.04 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 16:00 | 69.52 | 1.01 | 1.01 | 68.51 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 17:00 | 69.04 | 0.42 | 0.42 | 68.62 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 18:00 | 67.11 | 0 | 0 | 67.11 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 19:00 | 64.45 | 0 | 0 | 64.45 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 20:00 | 61.93 | 0 | 0 | 61.93 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 21:00 | 59.07 | 0 | 0 | 59.07 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 22:00 | 55.76 | 0 | 0 | 55.76 | 0 | 0 | 32.45 | 0 | 0
2025-09-26 23:00 | 53.26 | 0 | 0 | 53.26 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 | 50.33 | 0 | 0 | 50.33 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 01:00 | 50.23 | 0 | 0 | 50.23 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 02:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 03:00 | 47.69 | 0 | 0 | 47.69 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 04:00 | 48.52 | 0 | 0 | 48.52 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 05:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 06:00 | 49.56 | 0.5 | 0.5 | 49.06 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 07:00 | 52.96 | 9.5 | 9.5 | 43.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 08:00 | 55.17 | 13.31 | 13.31 | 41.85 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 09:00 | 58.64 | 31.85 | 31.85 | 26.79 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 10:00 | 61.76 | 28.66 | 28.66 | 33.1 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 11:00 | 64.82 | 22.67 | 22.67 | 42.15 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 12:00 | 66.11 | 55.31 | 55.31 | 10.8 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 13:00 | 68.65 | 76.42 | 76.42 | 0 | 7.77 | 0 | 39.83 | 0 | 0
2025-09-27 14:00 | 69.58 | 83.08 | 83.08 | 0 | 13.5 | 0 | 52.66 | 0 | 0
2025-09-27 15:00 | 70.13 | 87.86 | 87.86 | 0 | 17.73 | 0 | 69.51 | 0 | 0
2025-09-27 16:00 | 69.31 | 83.01 | 83.01 | 0 | 13.7 | 0 | 82.52 | 0 | 0
2025-09-27 17:00 | 69.15 | 26.07 | 26.07 | 0 | 0 | 43.08 | 37.18 | 0 | 0
2025-09-27 18:00 | 66.62 | 0 | 0 | 62.13 | 0 | 4.49 | 32.45 | 0 | 0
2025-09-27 19:00 | 65.24 | 0 | 0 | 65.24 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 20:00 | 61.26 | 0 | 0 | 61.26 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 21:00 | 59.13 | 0 | 0 | 59.13 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 22:00 | 55.83 | 0 | 0 | 55.83 | 0 | 0 | 32.45 | 0 | 0
2025-09-27 23:00 | 52.99 | 0 | 0 | 52.99 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 | 50.95 | 0 | 0 | 50.95 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 01:00 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 02:00 | 46.49 | 0 | 0 | 46.49 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 03:00 | 45.91 | 0 | 0 | 45.91 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 04:00 | 48.46 | 0 | 0 | 48.46 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 05:00 | 49.53 | 0 | 0 | 49.53 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 06:00 | 51.58 | 0.81 | 0.81 | 50.77 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 07:00 | 52.81 | 0.03 | 0.03 | 52.78 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 08:00 | 54.64 | 32.07 | 32.07 | 22.57 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 09:00 | 57.63 | 19.01 | 19.01 | 38.62 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 10:00 | 60.3 | 37.36 | 37.36 | 22.94 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 11:00 | 61.99 | 52.84 | 52.84 | 9.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 12:00 | 65.14 | 45.17 | 45.17 | 19.96 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 13:00 | 66.79 | 91.9 | 91.9 | 0 | 25.12 | 0 | 56.31 | 0 | 0
2025-09-28 14:00 | 66.74 | 83.23 | 83.23 | 0 | 16.49 | 0 | 71.98 | 0 | 0
2025-09-28 15:00 | 66.78 | 32.84 | 32.84 | 0 | 0 | 33.94 | 36.26 | 0 | 0
2025-09-28 16:00 | 65.86 | 58.63 | 58.63 | 3.61 | 0 | 3.62 | 32.45 | 0 | 0
2025-09-28 17:00 | 66.44 | 20.18 | 20.18 | 46.26 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 18:00 | 64.35 | 0 | 0 | 64.35 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 19:00 | 62.35 | 0 | 0 | 62.35 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 20:00 | 60.53 | 0 | 0 | 60.53 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 21:00 | 57.54 | 0 | 0 | 57.54 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 22:00 | 55.36 | 0 | 0 | 55.36 | 0 | 0 | 32.45 | 0 | 0
2025-09-28 23:00 | 52.1 | 0 | 0 | 52.1 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 | 51.13 | 0 | 0 | 51.13 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 01:00 | 48.76 | 0 | 0 | 48.76 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 02:00 | 48.28 | 0 | 0 | 48.28 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 03:00 | 47.22 | 0 | 0 | 47.22 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 04:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 05:00 | 48.2 | 0 | 0 | 48.2 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 06:00 | 50.96 | 0.92 | 0.92 | 50.04 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 07:00 | 52.48 | 50.94 | 50.94 | 1.54 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 08:00 | 55.43 | 58.8 | 58.8 | 0 | 3.37 | 0 | 35.65 | 0 | 0
2025-09-29 09:00 | 58.67 | 67.58 | 67.58 | 0 | 8.91 | 0 | 44.12 | 0 | 0
2025-09-29 10:00 | 61.77 | 70.38 | 70.38 | 0 | 8.61 | 0 | 52.3 | 0 | 0
2025-09-29 11:00 | 63.72 | 56.93 | 56.93 | 0 | 0 | 6.8 | 45.15 | 0 | 0
2025-09-29 12:00 | 66.96 | 50.46 | 50.46 | 4.44 | 0 | 12.06 | 32.45 | 0 | 0
2025-09-29 13:00 | 69.4 | 55.09 | 55.09 | 14.31 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 14:00 | 70.04 | 42.32 | 42.32 | 27.72 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 15:00 | 70.53 | 44.02 | 44.02 | 26.51 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 16:00 | 70.31 | 70.74 | 70.74 | 0 | 0.43 | 0 | 32.86 | 0 | 0
2025-09-29 17:00 | 68.94 | 23.15 | 23.15 | 45.4 | 0 | 0.39 | 32.45 | 0 | 0
2025-09-29 18:00 | 66.56 | 0 | 0 | 66.56 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 19:00 | 64.56 | 0 | 0 | 64.56 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 20:00 | 62.21 | 0 | 0 | 62.21 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 21:00 | 58.14 | 0 | 0 | 58.14 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 22:00 | 55.49 | 0 | 0 | 55.49 | 0 | 0 | 32.45 | 0 | 0
2025-09-29 23:00 | 52.23 | 0 | 0 | 52.23 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 | 50.88 | 0 | 0 | 50.88 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 01:00 | 48.63 | 0 | 0 | 48.63 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 02:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 03:00 | 47.25 | 0 | 0 | 47.25 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 04:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 05:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 06:00 | 49.68 | 1.18 | 1.18 | 48.49 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 07:00 | 52.12 | 49.43 | 49.43 | 2.69 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 08:00 | 55.95 | 64.59 | 64.59 | 0 | 8.64 | 0 | 40.66 | 0 | 0
2025-09-30 09:00 | 57.69 | 82.71 | 82.71 | 0 | 25.02 | 0 | 64.43 | 0 | 0
2025-09-30 10:00 | 61.07 | 85.65 | 85.65 | 0 | 24.58 | 0 | 87.78 | 0 | 0
2025-09-30 11:00 | 62.99 | 80.61 | 80.61 | 0 | 17.62 | 0 | 104.52 | 0 | 0
2025-09-30 12:00 | 65.99 | 77.23 | 77.23 | 0 | 11.23 | 0 | 115.19 | 0 | 0
2025-09-30 13:00 | 66.79 | 80.38 | 80.38 | 0 | 13.59 | 0 | 128.1 | 0 | 0
2025-09-30 14:00 | 68.38 | 89.78 | 89.78 | 0 | 21.4 | 0 | 148.43 | 0 | 0
2025-09-30 15:00 | 68.74 | 87.36 | 87.36 | 0 | 18.62 | 0 | 166.12 | 0 | 0
2025-09-30 16:00 | 69.52 | 68.03 | 68.03 | 0 | 0 | 1.5 | 164.54 | 0 | 0
2025-09-30 17:00 | 67.61 | 18.34 | 18.34 | 0 | 0 | 49.28 | 112.67 | 0 | 0
2025-09-30 18:00 | 65.32 | 0 | 0 | 0 | 0 | 65.32 | 43.92 | 0 | 0
2025-09-30 19:00 | 63.75 | 0 | 0 | 52.86 | 0 | 10.89 | 32.45 | 0 | 0
2025-09-30 20:00 | 61.9 | 0 | 0 | 61.9 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 21:00 | 57.24 | 0 | 0 | 57.24 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 22:00 | 54.85 | 0 | 0 | 54.85 | 0 | 0 | 32.45 | 0 | 0
2025-09-30 23:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 | 50.24 | 0 | 0 | 50.24 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 01:00 | 48.41 | 0 | 0 | 48.41 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 02:00 | 46.81 | 0 | 0 | 46.81 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 03:00 | 47.79 | 0 | 0 | 47.79 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 04:00 | 46.75 | 0 | 0 | 46.75 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 05:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 06:00 | 50.97 | 0.84 | 0.84 | 50.13 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 07:00 | 53.02 | 51.23 | 51.23 | 1.79 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 08:00 | 55.77 | 90.39 | 90.39 | 0 | 34.62 | 0 | 65.34 | 0 | 0
2025-10-01 09:00 | 59.32 | 95.21 | 95.21 | 0 | 35.88 | 0 | 99.43 | 0 | 0
2025-10-01 10:00 | 63.89 | 92.94 | 92.94 | 0 | 29.05 | 0 | 127.03 | 0 | 0
2025-10-01 11:00 | 67.6 | 86.1 | 86.1 | 0 | 18.5 | 0 | 144.6 | 0 | 0
2025-10-01 12:00 | 71.69 | 86.91 | 86.91 | 0 | 15.22 | 0 | 159.05 | 0 | 0
2025-10-01 13:00 | 73.78 | 88.57 | 88.57 | 0 | 14.79 | 0 | 173.1 | 0 | 0
2025-10-01 14:00 | 76.75 | 90.98 | 90.98 | 0 | 14.23 | 0 | 186.62 | 0 | 0
2025-10-01 15:00 | 77.05 | 87.02 | 87.02 | 0 | 9.97 | 0 | 196.09 | 0 | 0
2025-10-01 16:00 | 76.44 | 76.38 | 76.38 | 0 | 0 | 0.06 | 196.03 | 0 | 0
2025-10-01 17:00 | 75.2 | 16.36 | 16.36 | 0 | 0 | 58.84 | 134.09 | 0 | 0
2025-10-01 18:00 | 71.37 | 0 | 0 | 0 | 0 | 71.37 | 58.96 | 0 | 0
2025-10-01 19:00 | 67.62 | 0 | 0 | 42.43 | 0 | 25.19 | 32.45 | 0 | 0
2025-10-01 20:00 | 63.73 | 0 | 0 | 63.73 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 21:00 | 59.9 | 0 | 0 | 59.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 22:00 | 56.22 | 0 | 0 | 56.22 | 0 | 0 | 32.45 | 0 | 0
2025-10-01 23:00 | 52.62 | 0 | 0 | 52.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 | 49.24 | 0 | 0 | 49.24 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 01:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 02:00 | 47.52 | 0 | 0 | 47.52 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 03:00 | 47.04 | 0 | 0 | 47.04 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 04:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 05:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 06:00 | 50.64 | 0.54 | 0.54 | 50.1 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 07:00 | 53.43 | 26.33 | 26.33 | 27.1 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 08:00 | 56.18 | 79.48 | 79.48 | 0 | 23.31 | 0 | 54.59 | 0 | 0
2025-10-02 09:00 | 60.12 | 51.43 | 51.43 | 0 | 0 | 8.7 | 45.44 | 0 | 0
2025-10-02 10:00 | 63.88 | 47.89 | 47.89 | 3.64 | 0 | 12.34 | 32.45 | 0 | 0
2025-10-02 11:00 | 67.04 | 60.96 | 60.96 | 6.08 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 12:00 | 70.16 | 44.99 | 44.99 | 25.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 13:00 | 72.28 | 76.99 | 76.99 | 0 | 4.71 | 0 | 36.93 | 0 | 0
2025-10-02 14:00 | 74.03 | 54.86 | 54.86 | 14.91 | 0 | 4.25 | 32.45 | 0 | 0
2025-10-02 15:00 | 74.45 | 92.81 | 92.81 | 0 | 18.36 | 0 | 49.89 | 0 | 0
2025-10-02 16:00 | 74.36 | 66.56 | 66.56 | 0 | 0 | 7.8 | 41.69 | 0 | 0
2025-10-02 17:00 | 72.03 | 1.4 | 1.4 | 61.85 | 0 | 8.77 | 32.45 | 0 | 0
2025-10-02 18:00 | 69.71 | 0 | 0 | 69.71 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 19:00 | 65.39 | 0 | 0 | 65.39 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 20:00 | 63.81 | 0 | 0 | 63.81 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 21:00 | 59.16 | 0 | 0 | 59.16 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 22:00 | 56.02 | 0 | 0 | 56.02 | 0 | 0 | 32.45 | 0 | 0
2025-10-02 23:00 | 53.47 | 0 | 0 | 53.47 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 | 50.16 | 0 | 0 | 50.16 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 01:00 | 49.01 | 0 | 0 | 49.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 02:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 03:00 | 48.05 | 0 | 0 | 48.05 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 04:00 | 47.76 | 0 | 0 | 47.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 05:00 | 48.39 | 0 | 0 | 48.39 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 06:00 | 50.72 | 0.48 | 0.48 | 50.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 07:00 | 51.7 | 37.9 | 37.9 | 13.8 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 08:00 | 54.83 | 74.66 | 74.66 | 0 | 19.83 | 0 | 51.29 | 0 | 0
2025-10-03 09:00 | 58.63 | 92.42 | 92.42 | 0 | 33.78 | 0 | 83.39 | 0 | 0
2025-10-03 10:00 | 59.96 | 89.66 | 89.66 | 0 | 29.7 | 0 | 111.61 | 0 | 0
2025-10-03 11:00 | 64 | 83.05 | 83.05 | 0 | 19.05 | 0 | 129.71 | 0 | 0
2025-10-03 12:00 | 66.44 | 81.07 | 81.07 | 0 | 14.63 | 0 | 143.6 | 0 | 0
2025-10-03 13:00 | 69.07 | 74.46 | 74.46 | 0 | 5.4 | 0 | 148.73 | 0 | 0
2025-10-03 14:00 | 68.5 | 70.19 | 70.19 | 0 | 1.68 | 0 | 150.33 | 0 | 0
2025-10-03 15:00 | 70.51 | 65.82 | 65.82 | 0 | 0 | 4.7 | 145.38 | 0 | 0
2025-10-03 16:00 | 69.01 | 36.7 | 36.7 | 0 | 0 | 32.32 | 111.36 | 0 | 0
2025-10-03 17:00 | 67.86 | 10.22 | 10.22 | 0 | 0 | 57.64 | 50.69 | 0 | 0
2025-10-03 18:00 | 65.56 | 0 | 0 | 48.24 | 0 | 17.33 | 32.45 | 0 | 0
2025-10-03 19:00 | 63.17 | 0 | 0 | 63.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 21:00 | 57.35 | 0 | 0 | 57.35 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 22:00 | 55.34 | 0 | 0 | 55.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-03 23:00 | 51.95 | 0 | 0 | 51.95 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 | 49.16 | 0 | 0 | 49.16 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 01:00 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 02:00 | 47.26 | 0 | 0 | 47.26 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 03:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 04:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 05:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 06:00 | 50.31 | 0.09 | 0.09 | 50.23 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 07:00 | 51.69 | 25 | 25 | 26.69 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 08:00 | 53.66 | 42.57 | 42.57 | 11.09 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 09:00 | 56.64 | 15.96 | 15.96 | 40.68 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 10:00 | 59.15 | 41.47 | 41.47 | 17.69 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 11:00 | 60.26 | 48.33 | 48.33 | 11.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 12:00 | 62.26 | 65.1 | 65.1 | 0 | 2.85 | 0 | 35.15 | 0 | 0
2025-10-04 13:00 | 63.61 | 78.25 | 78.25 | 0 | 14.63 | 0 | 49.05 | 0 | 0
2025-10-04 14:00 | 64.65 | 51.04 | 51.04 | 0 | 0 | 13.61 | 34.73 | 0 | 0
2025-10-04 15:00 | 64.64 | 42.25 | 42.25 | 20.22 | 0 | 2.17 | 32.45 | 0 | 0
2025-10-04 16:00 | 65.11 | 77.17 | 77.17 | 0 | 12.06 | 0 | 43.91 | 0 | 0
2025-10-04 17:00 | 63.17 | 15.21 | 15.21 | 37.08 | 0 | 10.88 | 32.45 | 0 | 0
2025-10-04 18:00 | 61.91 | 0 | 0 | 61.91 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 19:00 | 60.82 | 0 | 0 | 60.82 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 20:00 | 58.83 | 0 | 0 | 58.83 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 21:00 | 55.87 | 0 | 0 | 55.87 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 22:00 | 53.88 | 0 | 0 | 53.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-04 23:00 | 51.65 | 0 | 0 | 51.65 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 01:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 02:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 03:00 | 47.35 | 0 | 0 | 47.35 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 04:00 | 47.21 | 0 | 0 | 47.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 05:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 06:00 | 49.64 | 0.45 | 0.45 | 49.19 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 07:00 | 51.66 | 39.65 | 39.65 | 12.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 08:00 | 54.43 | 66.65 | 66.65 | 0 | 12.23 | 0 | 44.07 | 0 | 0
2025-10-05 09:00 | 55.77 | 76.46 | 76.46 | 0 | 20.7 | 0 | 63.73 | 0 | 0
2025-10-05 10:00 | 58.56 | 79.95 | 79.95 | 0 | 21.39 | 0 | 84.05 | 0 | 0
2025-10-05 11:00 | 60.03 | 65.72 | 65.72 | 0 | 5.69 | 0 | 89.46 | 0 | 0
2025-10-05 12:00 | 62.23 | 72.82 | 72.82 | 0 | 10.59 | 0 | 99.52 | 0 | 0
2025-10-05 13:00 | 63.2 | 39.24 | 39.24 | 0 | 0 | 23.96 | 74.3 | 0 | 0
2025-10-05 14:00 | 63.3 | 42.84 | 42.84 | 0 | 0 | 20.47 | 52.75 | 0 | 0
2025-10-05 15:00 | 63.29 | 66.87 | 66.87 | 0 | 3.58 | 0 | 56.15 | 0 | 0
2025-10-05 16:00 | 63.46 | 54.37 | 54.37 | 0 | 0 | 9.09 | 46.59 | 0 | 0
2025-10-05 17:00 | 62.47 | 1.65 | 1.65 | 47.39 | 0 | 13.43 | 32.45 | 0 | 0
2025-10-05 18:00 | 62.33 | 0 | 0 | 62.33 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 19:00 | 60.05 | 0 | 0 | 60.05 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 20:00 | 57.97 | 0 | 0 | 57.97 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 21:00 | 55.84 | 0 | 0 | 55.84 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 22:00 | 53.21 | 0 | 0 | 53.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-05 23:00 | 51.88 | 0 | 0 | 51.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 01:00 | 48.45 | 0 | 0 | 48.45 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 02:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 03:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 04:00 | 47.42 | 0 | 0 | 47.42 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 05:00 | 46.82 | 0 | 0 | 46.82 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 06:00 | 50.64 | 0 | 0 | 50.64 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 07:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 08:00 | 54.9 | 2.02 | 2.02 | 52.87 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 09:00 | 58.31 | 3.7 | 3.7 | 54.61 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 10:00 | 61.74 | 11.56 | 11.56 | 50.18 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 11:00 | 64.77 | 13.91 | 13.91 | 50.86 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 12:00 | 68.03 | 11 | 11 | 57.03 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 13:00 | 70.09 | 65.33 | 65.33 | 4.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 14:00 | 72.18 | 64.61 | 64.61 | 7.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 15:00 | 72.06 | 44.34 | 44.34 | 27.72 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 16:00 | 72.28 | 27.58 | 27.58 | 44.7 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 17:00 | 70.28 | 3.7 | 3.7 | 66.58 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 18:00 | 66.63 | 0 | 0 | 66.63 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 19:00 | 65.94 | 0 | 0 | 65.94 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 20:00 | 61.09 | 0 | 0 | 61.09 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 21:00 | 58.77 | 0 | 0 | 58.77 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 22:00 | 54.84 | 0 | 0 | 54.84 | 0 | 0 | 32.45 | 0 | 0
2025-10-06 23:00 | 52.51 | 0 | 0 | 52.51 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 01:00 | 48.06 | 0 | 0 | 48.06 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 02:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 03:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 04:00 | 46.93 | 0 | 0 | 46.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 05:00 | 48.22 | 0 | 0 | 48.22 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 06:00 | 48.33 | 0.28 | 0.28 | 48.04 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 07:00 | 51.55 | 41 | 41 | 10.54 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 08:00 | 54.36 | 83.96 | 83.96 | 0 | 29.59 | 0 | 60.56 | 0 | 0
2025-10-07 09:00 | 57.05 | 93.19 | 93.19 | 0 | 36.14 | 0 | 94.89 | 0 | 0
2025-10-07 10:00 | 60.24 | 78.48 | 78.48 | 0 | 18.24 | 0 | 112.22 | 0 | 0
2025-10-07 11:00 | 62.23 | 48.21 | 48.21 | 0 | 0 | 14.02 | 97.47 | 0 | 0
2025-10-07 12:00 | 64.74 | 42.61 | 42.61 | 0 | 0 | 22.13 | 74.17 | 0 | 0
2025-10-07 13:00 | 67.09 | 64.61 | 64.61 | 0 | 0 | 2.48 | 71.56 | 0 | 0
2025-10-07 14:00 | 66.48 | 40.75 | 40.75 | 0 | 0 | 25.74 | 44.47 | 0 | 0
2025-10-07 15:00 | 68.3 | 27.14 | 27.14 | 29.75 | 0 | 11.42 | 32.45 | 0 | 0
2025-10-07 16:00 | 67.46 | 5.71 | 5.71 | 61.75 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 17:00 | 66.04 | 0.82 | 0.82 | 65.22 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 18:00 | 64.88 | 0 | 0 | 64.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 19:00 | 63.03 | 0 | 0 | 63.03 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 20:00 | 60.28 | 0 | 0 | 60.28 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 21:00 | 56.87 | 0 | 0 | 56.87 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 22:00 | 54.59 | 0 | 0 | 54.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-07 23:00 | 52.02 | 0 | 0 | 52.02 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 | 49.23 | 0 | 0 | 49.23 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 01:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 02:00 | 46.27 | 0 | 0 | 46.27 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 03:00 | 46.66 | 0 | 0 | 46.66 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 04:00 | 46.57 | 0 | 0 | 46.57 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 05:00 | 47.1 | 0 | 0 | 47.1 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 06:00 | 48.43 | 0 | 0 | 48.43 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 07:00 | 51.89 | 46.8 | 46.8 | 5.09 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 08:00 | 53.8 | 97.7 | 97.7 | 0 | 43.89 | 0 | 74.15 | 0 | 0
2025-10-08 09:00 | 57.09 | 99.25 | 99.25 | 0 | 42.16 | 0 | 114.2 | 0 | 0
2025-10-08 10:00 | 60.46 | 71.66 | 71.66 | 0 | 11.21 | 0 | 124.85 | 0 | 0
2025-10-08 11:00 | 61.95 | 21.42 | 21.42 | 0 | 0 | 40.53 | 82.18 | 0 | 0
2025-10-08 12:00 | 65 | 31.52 | 31.52 | 0 | 0 | 33.48 | 46.94 | 0 | 0
2025-10-08 13:00 | 66.81 | 60.65 | 60.65 | 0 | 0 | 6.16 | 40.46 | 0 | 0
2025-10-08 14:00 | 68.28 | 47.35 | 47.35 | 13.33 | 0 | 7.61 | 32.45 | 0 | 0
2025-10-08 15:00 | 69.12 | 58.01 | 58.01 | 11.11 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 16:00 | 67.43 | 4.57 | 4.57 | 62.86 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 17:00 | 67.18 | 0.03 | 0.03 | 67.16 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 18:00 | 65.53 | 0 | 0 | 65.53 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 19:00 | 62.51 | 0 | 0 | 62.51 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 20:00 | 59.77 | 0 | 0 | 59.77 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 21:00 | 57.14 | 0 | 0 | 57.14 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 22:00 | 54.25 | 0 | 0 | 54.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-08 23:00 | 51.76 | 0 | 0 | 51.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 | 49.23 | 0 | 0 | 49.23 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 01:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 02:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 03:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 04:00 | 46.55 | 0 | 0 | 46.55 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 05:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 06:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 07:00 | 50.89 | 0.1 | 0.1 | 50.79 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 08:00 | 52.19 | 2.92 | 2.92 | 49.27 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 09:00 | 54.49 | 4.84 | 4.84 | 49.65 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 10:00 | 55.67 | 6.71 | 6.71 | 48.96 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 11:00 | 58.06 | 8.17 | 8.17 | 49.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 12:00 | 58.89 | 8.7 | 8.7 | 50.19 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 13:00 | 58.69 | 7.48 | 7.48 | 51.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 14:00 | 60.09 | 6.13 | 6.13 | 53.96 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 15:00 | 60.02 | 3.69 | 3.69 | 56.33 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 16:00 | 60.17 | 1.57 | 1.57 | 58.6 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 17:00 | 59.32 | 0 | 0 | 59.32 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 18:00 | 58.4 | 0 | 0 | 58.4 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 19:00 | 57.37 | 0 | 0 | 57.37 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 20:00 | 56.1 | 0 | 0 | 56.1 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 21:00 | 54.68 | 0 | 0 | 54.68 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 22:00 | 52.84 | 0 | 0 | 52.84 | 0 | 0 | 32.45 | 0 | 0
2025-10-09 23:00 | 50.7 | 0 | 0 | 50.7 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 01:00 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 02:00 | 47.59 | 0 | 0 | 47.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 03:00 | 45.6 | 0 | 0 | 45.6 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 04:00 | 46.05 | 0 | 0 | 46.05 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 05:00 | 49 | 0 | 0 | 49 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 06:00 | 49.22 | 0 | 0 | 49.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 07:00 | 50.54 | 42.11 | 42.11 | 8.44 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 08:00 | 54.33 | 90.9 | 90.9 | 0 | 36.57 | 0 | 67.19 | 0 | 0
2025-10-10 09:00 | 56.44 | 68.19 | 68.19 | 0 | 11.76 | 0 | 78.36 | 0 | 0
2025-10-10 10:00 | 60.44 | 35.1 | 35.1 | 0 | 0 | 25.35 | 51.68 | 0 | 0
2025-10-10 11:00 | 62.87 | 49.11 | 49.11 | 0 | 0 | 13.76 | 37.19 | 0 | 0
2025-10-10 12:00 | 65.4 | 52.62 | 52.62 | 8.28 | 0 | 4.5 | 32.45 | 0 | 0
2025-10-10 13:00 | 68.5 | 71.3 | 71.3 | 0 | 2.8 | 0 | 35.11 | 0 | 0
2025-10-10 14:00 | 69.31 | 90.4 | 90.4 | 0 | 21.1 | 0 | 55.16 | 0 | 0
2025-10-10 15:00 | 69.97 | 94.07 | 94.07 | 0 | 24.11 | 0 | 78.06 | 0 | 0
2025-10-10 16:00 | 69.24 | 70.16 | 70.16 | 0 | 0.91 | 0 | 78.93 | 0 | 0
2025-10-10 17:00 | 67.47 | 6.84 | 6.84 | 16.48 | 0 | 44.15 | 32.45 | 0 | 0
2025-10-10 18:00 | 65.92 | 0 | 0 | 65.92 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 19:00 | 63.58 | 0 | 0 | 63.58 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 20:00 | 60.06 | 0 | 0 | 60.06 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 21:00 | 57.79 | 0 | 0 | 57.79 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 22:00 | 54.34 | 0 | 0 | 54.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-10 23:00 | 51.34 | 0 | 0 | 51.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 01:00 | 47.27 | 0 | 0 | 47.27 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 02:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 03:00 | 45.82 | 0 | 0 | 45.82 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 04:00 | 46.31 | 0 | 0 | 46.31 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 05:00 | 47 | 0 | 0 | 47 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 06:00 | 48.99 | 0 | 0 | 48.99 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 07:00 | 50.96 | 42.65 | 42.65 | 8.31 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 08:00 | 53.87 | 89.36 | 89.36 | 0 | 35.5 | 0 | 66.17 | 0 | 0
2025-10-11 09:00 | 56.58 | 93.07 | 93.07 | 0 | 36.49 | 0 | 100.84 | 0 | 0
2025-10-11 10:00 | 59.15 | 87.26 | 87.26 | 0 | 28.11 | 0 | 127.55 | 0 | 0
2025-10-11 11:00 | 61.06 | 79.52 | 79.52 | 0 | 18.46 | 0 | 145.09 | 0 | 0
2025-10-11 12:00 | 64.97 | 79.53 | 79.53 | 0 | 14.56 | 0 | 158.91 | 0 | 0
2025-10-11 13:00 | 65.82 | 85.64 | 85.64 | 0 | 19.81 | 0 | 177.73 | 0 | 0
2025-10-11 14:00 | 67.01 | 91.97 | 91.97 | 0 | 24.96 | 0 | 201.45 | 0 | 0
2025-10-11 15:00 | 67.27 | 89.87 | 89.87 | 0 | 22.6 | 0 | 222.92 | 0 | 0
2025-10-11 16:00 | 66.8 | 67.4 | 67.4 | 0 | 0.59 | 0 | 223.48 | 0 | 0
2025-10-11 17:00 | 66.67 | 2.29 | 2.29 | 0 | 0 | 64.38 | 155.72 | 0 | 0
2025-10-11 18:00 | 64.77 | 0 | 0 | 0 | 0 | 64.77 | 87.54 | 0 | 0
2025-10-11 19:00 | 61.96 | 0 | 0 | 9.63 | 0 | 52.33 | 32.45 | 0 | 0
2025-10-11 20:00 | 59.01 | 0 | 0 | 59.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 21:00 | 56.56 | 0 | 0 | 56.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 22:00 | 53.52 | 0 | 0 | 53.52 | 0 | 0 | 32.45 | 0 | 0
2025-10-11 23:00 | 50.86 | 0 | 0 | 50.86 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 | 48.72 | 0 | 0 | 48.72 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 01:00 | 46.82 | 0 | 0 | 46.82 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 02:00 | 46.2 | 0 | 0 | 46.2 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 03:00 | 45.84 | 0 | 0 | 45.84 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 04:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 05:00 | 46.73 | 0 | 0 | 46.73 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 06:00 | 48.9 | 0 | 0 | 48.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 07:00 | 49.98 | 4.67 | 4.67 | 45.3 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 08:00 | 52.23 | 35.51 | 35.51 | 16.72 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 09:00 | 54.37 | 60.46 | 60.46 | 0 | 6.09 | 0 | 38.23 | 0 | 0
2025-10-12 10:00 | 56.08 | 68.84 | 68.84 | 0 | 12.76 | 0 | 50.35 | 0 | 0
2025-10-12 11:00 | 58.85 | 63.08 | 63.08 | 0 | 4.23 | 0 | 54.38 | 0 | 0
2025-10-12 12:00 | 59.25 | 65.41 | 65.41 | 0 | 6.16 | 0 | 60.23 | 0 | 0
2025-10-12 13:00 | 60.39 | 67.91 | 67.91 | 0 | 7.52 | 0 | 67.38 | 0 | 0
2025-10-12 14:00 | 61.98 | 77.76 | 77.76 | 0 | 15.78 | 0 | 82.37 | 0 | 0
2025-10-12 15:00 | 61.27 | 97.51 | 97.51 | 0 | 36.24 | 0 | 116.8 | 0 | 0
2025-10-12 16:00 | 61.26 | 72.36 | 72.36 | 0 | 11.1 | 0 | 127.34 | 0 | 0
2025-10-12 17:00 | 60.23 | 5.11 | 5.11 | 0 | 0 | 55.12 | 69.32 | 0 | 0
2025-10-12 18:00 | 60.15 | 0 | 0 | 25.12 | 0 | 35.03 | 32.45 | 0 | 0
2025-10-12 19:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 20:00 | 56.98 | 0 | 0 | 56.98 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 21:00 | 54.9 | 0 | 0 | 54.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 22:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-12 23:00 | 50.17 | 0 | 0 | 50.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 | 48.04 | 0 | 0 | 48.04 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 01:00 | 47.56 | 0 | 0 | 47.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 02:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 03:00 | 45.26 | 0 | 0 | 45.26 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 04:00 | 45.96 | 0 | 0 | 45.96 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 05:00 | 46.76 | 0 | 0 | 46.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 06:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 07:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 08:00 | 52.43 | 1.63 | 1.63 | 50.8 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 09:00 | 54.51 | 3.15 | 3.15 | 51.36 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 10:00 | 56.54 | 4.6 | 4.6 | 51.94 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 11:00 | 58.58 | 5.91 | 5.91 | 52.67 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 12:00 | 60.93 | 6.61 | 6.61 | 54.32 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 13:00 | 62.39 | 58.31 | 58.31 | 4.08 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 14:00 | 62.82 | 57.25 | 57.25 | 5.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 15:00 | 63.86 | 53.52 | 53.52 | 10.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 16:00 | 63.22 | 37.62 | 37.62 | 25.6 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 17:00 | 62.72 | 0.88 | 0.88 | 61.85 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 18:00 | 61.02 | 0 | 0 | 61.02 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 19:00 | 58.97 | 0 | 0 | 58.97 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 20:00 | 57.34 | 0 | 0 | 57.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 21:00 | 54.36 | 0 | 0 | 54.36 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 22:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 32.45 | 0 | 0
2025-10-13 23:00 | 49.93 | 0 | 0 | 49.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 01:00 | 46.62 | 0 | 0 | 46.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 02:00 | 46.34 | 0 | 0 | 46.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 03:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 04:00 | 45.48 | 0 | 0 | 45.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 05:00 | 46.98 | 0 | 0 | 46.98 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 06:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 07:00 | 51.22 | 21.89 | 21.89 | 29.33 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 08:00 | 52.82 | 78.45 | 78.45 | 0 | 25.63 | 0 | 56.8 | 0 | 0
2025-10-14 09:00 | 56.33 | 64.9 | 64.9 | 0 | 8.57 | 0 | 64.94 | 0 | 0
2025-10-14 10:00 | 57.92 | 36.55 | 36.55 | 0 | 0 | 21.36 | 42.45 | 0 | 0
2025-10-14 11:00 | 61.1 | 52.95 | 52.95 | 0 | 0 | 8.16 | 33.87 | 0 | 0
2025-10-14 12:00 | 62.24 | 68.24 | 68.24 | 0 | 5.99 | 0 | 39.56 | 0 | 0
2025-10-14 13:00 | 64.6 | 15.24 | 15.24 | 42.6 | 0 | 6.76 | 32.45 | 0 | 0
2025-10-14 14:00 | 64.27 | 8.45 | 8.45 | 55.83 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 15:00 | 65.24 | 8.68 | 8.68 | 56.57 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 16:00 | 65.68 | 0.66 | 0.66 | 65.02 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 17:00 | 63.73 | 0 | 0 | 63.73 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 18:00 | 62.93 | 0 | 0 | 62.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 19:00 | 61.01 | 0 | 0 | 61.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 20:00 | 57.81 | 0 | 0 | 57.81 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 21:00 | 54.93 | 0 | 0 | 54.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 22:00 | 52.56 | 0 | 0 | 52.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-14 23:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 | 48.12 | 0 | 0 | 48.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 01:00 | 46.7 | 0 | 0 | 46.7 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 02:00 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 03:00 | 46.19 | 0 | 0 | 46.19 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 04:00 | 45.32 | 0 | 0 | 45.32 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 05:00 | 47.34 | 0 | 0 | 47.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 06:00 | 47.65 | 0 | 0 | 47.65 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 07:00 | 50.21 | 0 | 0 | 50.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 08:00 | 53.09 | 25.93 | 25.93 | 27.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 09:00 | 55.58 | 2.74 | 2.74 | 52.84 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 10:00 | 57.31 | 13.57 | 13.57 | 43.74 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 11:00 | 60.15 | 45.75 | 45.75 | 14.4 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 12:00 | 62.1 | 56.7 | 56.7 | 5.41 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 13:00 | 63.17 | 42.83 | 42.83 | 20.35 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 14:00 | 64.73 | 75.01 | 75.01 | 0 | 10.28 | 0 | 42.21 | 0 | 0
2025-10-15 15:00 | 65.69 | 86.08 | 86.08 | 0 | 20.39 | 0 | 61.59 | 0 | 0
2025-10-15 16:00 | 64.66 | 32.6 | 32.6 | 4.38 | 0 | 27.68 | 32.45 | 0 | 0
2025-10-15 17:00 | 63.73 | 0.78 | 0.78 | 62.95 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 18:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 19:00 | 59.14 | 0 | 0 | 59.14 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 20:00 | 57.75 | 0 | 0 | 57.75 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 21:00 | 54.5 | 0 | 0 | 54.5 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 22:00 | 52.21 | 0 | 0 | 52.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-15 23:00 | 51.25 | 0 | 0 | 51.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 01:00 | 46.13 | 0 | 0 | 46.13 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 02:00 | 46.13 | 0 | 0 | 46.13 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 03:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 04:00 | 45.33 | 0 | 0 | 45.33 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 05:00 | 47.12 | 0 | 0 | 47.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 06:00 | 48.02 | 0 | 0 | 48.02 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 07:00 | 49.14 | 8.93 | 8.93 | 40.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 08:00 | 52.42 | 36.3 | 36.3 | 16.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 09:00 | 54.3 | 54.54 | 54.54 | 0 | 0.25 | 0 | 32.68 | 0 | 0
2025-10-16 10:00 | 57.58 | 75.02 | 75.02 | 0 | 17.44 | 0 | 49.25 | 0 | 0
2025-10-16 11:00 | 58.64 | 64.46 | 64.46 | 0 | 5.82 | 0 | 54.78 | 0 | 0
2025-10-16 12:00 | 61.27 | 61.24 | 61.24 | 0 | 0 | 0.03 | 54.75 | 0 | 0
2025-10-16 13:00 | 63 | 50.54 | 50.54 | 0 | 0 | 12.46 | 41.63 | 0 | 0
2025-10-16 14:00 | 62.55 | 64.54 | 64.54 | 0 | 1.99 | 0 | 43.53 | 0 | 0
2025-10-16 15:00 | 63.16 | 80.77 | 80.77 | 0 | 17.6 | 0 | 60.25 | 0 | 0
2025-10-16 16:00 | 63.16 | 62.3 | 62.3 | 0 | 0 | 0.87 | 59.33 | 0 | 0
2025-10-16 17:00 | 61.69 | 1.59 | 1.59 | 34.56 | 0 | 25.54 | 32.45 | 0 | 0
2025-10-16 18:00 | 60.88 | 0 | 0 | 60.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 19:00 | 58.83 | 0 | 0 | 58.83 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 20:00 | 56.69 | 0 | 0 | 56.69 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 21:00 | 54.52 | 0 | 0 | 54.52 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 22:00 | 52.18 | 0 | 0 | 52.18 | 0 | 0 | 32.45 | 0 | 0
2025-10-16 23:00 | 50.01 | 0 | 0 | 50.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 | 47.55 | 0 | 0 | 47.55 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 01:00 | 46.08 | 0 | 0 | 46.08 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 02:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 03:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 04:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 05:00 | 46.52 | 0 | 0 | 46.52 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 06:00 | 46.95 | 0 | 0 | 46.95 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 07:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 08:00 | 51.9 | 3.42 | 3.42 | 48.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 09:00 | 54.01 | 7.72 | 7.72 | 46.29 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 10:00 | 57.64 | 7.61 | 7.61 | 50.03 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 11:00 | 59.05 | 4.93 | 4.93 | 54.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 12:00 | 61.02 | 8.17 | 8.17 | 52.85 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 13:00 | 62.14 | 60.45 | 60.45 | 1.69 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 14:00 | 63.28 | 61.58 | 61.58 | 1.7 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 15:00 | 62.99 | 56.82 | 56.82 | 6.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 16:00 | 63.2 | 37.69 | 37.69 | 25.52 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 17:00 | 61.91 | 0.37 | 0.37 | 61.54 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 18:00 | 60.79 | 0 | 0 | 60.79 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 19:00 | 57.76 | 0 | 0 | 57.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 20:00 | 56.26 | 0 | 0 | 56.26 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 21:00 | 55.17 | 0 | 0 | 55.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 22:00 | 52.45 | 0 | 0 | 52.45 | 0 | 0 | 32.45 | 0 | 0
2025-10-17 23:00 | 50.45 | 0 | 0 | 50.45 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 | 48.38 | 0 | 0 | 48.38 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 01:00 | 46.56 | 0 | 0 | 46.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 02:00 | 45.06 | 0 | 0 | 45.06 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 03:00 | 44.45 | 0 | 0 | 44.45 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 04:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 05:00 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 06:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 07:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 08:00 | 52.76 | 7 | 7 | 45.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 09:00 | 54.01 | 4.68 | 4.68 | 49.33 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 10:00 | 57.05 | 3.94 | 3.94 | 53.11 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 11:00 | 59.34 | 11.2 | 11.2 | 48.14 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 12:00 | 59.77 | 67.57 | 67.57 | 0 | 7.8 | 0 | 39.86 | 0 | 0
2025-10-18 13:00 | 61.41 | 83.53 | 83.53 | 0 | 22.12 | 0 | 60.87 | 0 | 0
2025-10-18 14:00 | 61.98 | 92.96 | 92.96 | 0 | 30.97 | 0 | 90.29 | 0 | 0
2025-10-18 15:00 | 62.17 | 50.53 | 50.53 | 0 | 0 | 11.64 | 78.04 | 0 | 0
2025-10-18 16:00 | 62.83 | 47.32 | 47.32 | 0 | 0 | 15.51 | 61.71 | 0 | 0
2025-10-18 17:00 | 61.55 | 0.45 | 0.45 | 33.3 | 0 | 27.8 | 32.45 | 0 | 0
2025-10-18 18:00 | 60.31 | 0 | 0 | 60.31 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 19:00 | 58.77 | 0 | 0 | 58.77 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 20:00 | 55.46 | 0 | 0 | 55.46 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 21:00 | 54.74 | 0 | 0 | 54.74 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 22:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 32.45 | 0 | 0
2025-10-18 23:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 | 47.87 | 0 | 0 | 47.87 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 01:00 | 46.77 | 0 | 0 | 46.77 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 02:00 | 45.11 | 0 | 0 | 45.11 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 03:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 04:00 | 45.19 | 0 | 0 | 45.19 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 05:00 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 06:00 | 47.04 | 0 | 0 | 47.04 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 07:00 | 49.57 | 12.74 | 12.74 | 36.83 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 08:00 | 51.58 | 14.99 | 14.99 | 36.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 09:00 | 53.54 | 54.87 | 54.87 | 0 | 1.33 | 0 | 33.72 | 0 | 0
2025-10-19 10:00 | 57.01 | 66.98 | 66.98 | 0 | 9.97 | 0 | 43.19 | 0 | 0
2025-10-19 11:00 | 58.7 | 38.35 | 38.35 | 10.15 | 0 | 10.21 | 32.45 | 0 | 0
2025-10-19 12:00 | 60.78 | 27.86 | 27.86 | 32.92 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 13:00 | 62.29 | 27.99 | 27.99 | 34.31 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 14:00 | 64.11 | 13.3 | 13.3 | 50.82 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 15:00 | 63.81 | 6.12 | 6.12 | 57.69 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 16:00 | 63.54 | 5.28 | 5.28 | 58.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 17:00 | 62.3 | 0 | 0 | 62.3 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 18:00 | 61.22 | 0 | 0 | 61.22 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 19:00 | 59.66 | 0 | 0 | 59.66 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 20:00 | 57 | 0 | 0 | 57 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 21:00 | 54.55 | 0 | 0 | 54.55 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 22:00 | 52.06 | 0 | 0 | 52.06 | 0 | 0 | 32.45 | 0 | 0
2025-10-19 23:00 | 48.8 | 0 | 0 | 48.8 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 | 47.06 | 0 | 0 | 47.06 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 01:00 | 45.86 | 0 | 0 | 45.86 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 02:00 | 44.66 | 0 | 0 | 44.66 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 03:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 04:00 | 44.09 | 0 | 0 | 44.09 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 05:00 | 45.29 | 0 | 0 | 45.29 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 06:00 | 47.37 | 0 | 0 | 47.37 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 07:00 | 49.56 | 5.55 | 5.55 | 44.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 08:00 | 51.76 | 24.88 | 24.88 | 26.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 09:00 | 55.11 | 25.46 | 25.46 | 29.65 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 10:00 | 57.93 | 23.04 | 23.04 | 34.89 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 11:00 | 61.7 | 10.22 | 10.22 | 51.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 12:00 | 63.78 | 15.31 | 15.31 | 48.47 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 13:00 | 66.35 | 23.97 | 23.97 | 42.38 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 14:00 | 67.48 | 31.36 | 31.36 | 36.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 15:00 | 67.15 | 20.94 | 20.94 | 46.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 16:00 | 67.33 | 8.59 | 8.59 | 58.74 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 17:00 | 65.38 | 0 | 0 | 65.38 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 18:00 | 63.8 | 0 | 0 | 63.8 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 19:00 | 60.79 | 0 | 0 | 60.79 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 20:00 | 58.34 | 0 | 0 | 58.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 21:00 | 54.4 | 0 | 0 | 54.4 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 22:00 | 52.17 | 0 | 0 | 52.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-20 23:00 | 49.88 | 0 | 0 | 49.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 | 47.51 | 0 | 0 | 47.51 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 01:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 02:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 03:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 04:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 05:00 | 45.02 | 0 | 0 | 45.02 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 06:00 | 46.6 | 0 | 0 | 46.6 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 07:00 | 49.99 | 4.98 | 4.98 | 45.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 08:00 | 50.01 | 19.07 | 19.07 | 30.94 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 09:00 | 50.6 | 58.02 | 58.02 | 0 | 7.42 | 0 | 39.5 | 0 | 0
2025-10-21 10:00 | 52.38 | 50.37 | 50.37 | 0 | 0 | 2 | 37.39 | 0 | 0
2025-10-21 11:00 | 52.08 | 73.81 | 73.81 | 0 | 21.74 | 0 | 58.04 | 0 | 0
2025-10-21 12:00 | 54.07 | 74.73 | 74.73 | 0 | 20.67 | 0 | 77.67 | 0 | 0
2025-10-21 13:00 | 54.6 | 80.35 | 80.35 | 0 | 25.74 | 0 | 102.13 | 0 | 0
2025-10-21 14:00 | 53.84 | 85.91 | 85.91 | 0 | 32.07 | 0 | 132.59 | 0 | 0
2025-10-21 15:00 | 54.09 | 82.72 | 82.72 | 0 | 28.63 | 0 | 159.79 | 0 | 0
2025-10-21 16:00 | 54.76 | 42.29 | 42.29 | 0 | 0 | 12.48 | 146.66 | 0 | 0
2025-10-21 17:00 | 53.32 | 0.29 | 0.29 | 0 | 0 | 53.03 | 90.84 | 0 | 0
2025-10-21 18:00 | 53.28 | 0 | 0 | 0 | 0 | 53.28 | 34.75 | 0 | 0
2025-10-21 19:00 | 53.35 | 0 | 0 | 51.16 | 0 | 2.19 | 32.45 | 0 | 0
2025-10-21 20:00 | 52.29 | 0 | 0 | 52.29 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 21:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 22:00 | 49.52 | 0 | 0 | 49.52 | 0 | 0 | 32.45 | 0 | 0
2025-10-21 23:00 | 48.7 | 0 | 0 | 48.7 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 | 46.99 | 0 | 0 | 46.99 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 01:00 | 45.93 | 0 | 0 | 45.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 02:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 03:00 | 44.56 | 0 | 0 | 44.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 04:00 | 44.04 | 0 | 0 | 44.04 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 05:00 | 45.9 | 0 | 0 | 45.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 06:00 | 46.9 | 0 | 0 | 46.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 07:00 | 48.81 | 20.67 | 20.67 | 28.13 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 08:00 | 51.52 | 77.87 | 77.87 | 0 | 26.36 | 0 | 57.49 | 0 | 0
2025-10-22 09:00 | 52.87 | 85.15 | 85.15 | 0 | 32.28 | 0 | 88.15 | 0 | 0
2025-10-22 10:00 | 56.11 | 64.39 | 64.39 | 0 | 8.29 | 0 | 96.03 | 0 | 0
2025-10-22 11:00 | 58.19 | 55.36 | 55.36 | 0 | 0 | 2.83 | 93.05 | 0 | 0
2025-10-22 12:00 | 59.57 | 54.45 | 54.45 | 0 | 0 | 5.12 | 87.66 | 0 | 0
2025-10-22 13:00 | 60.02 | 68.98 | 68.98 | 0 | 8.96 | 0 | 96.17 | 0 | 0
2025-10-22 14:00 | 60.24 | 29.66 | 29.66 | 0 | 0 | 30.58 | 63.97 | 0 | 0
2025-10-22 15:00 | 62.15 | 13.13 | 13.13 | 19.07 | 0 | 29.95 | 32.45 | 0 | 0
2025-10-22 16:00 | 61.39 | 6.26 | 6.26 | 55.13 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 17:00 | 60.14 | 0 | 0 | 60.14 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 18:00 | 59.78 | 0 | 0 | 59.78 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 19:00 | 57.04 | 0 | 0 | 57.04 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 20:00 | 55.22 | 0 | 0 | 55.22 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 21:00 | 53.49 | 0 | 0 | 53.49 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 22:00 | 50.44 | 0 | 0 | 50.44 | 0 | 0 | 32.45 | 0 | 0
2025-10-22 23:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 | 47.48 | 0 | 0 | 47.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 01:00 | 45.62 | 0 | 0 | 45.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 02:00 | 45.25 | 0 | 0 | 45.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 03:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 04:00 | 44.63 | 0 | 0 | 44.63 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 05:00 | 44.35 | 0 | 0 | 44.35 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 06:00 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 07:00 | 49.18 | 3.71 | 3.71 | 45.47 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 08:00 | 50.2 | 19.2 | 19.2 | 31 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 09:00 | 53.17 | 26.12 | 26.12 | 27.05 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 10:00 | 55.88 | 33.24 | 33.24 | 22.64 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 11:00 | 58.68 | 43.89 | 43.89 | 14.79 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 12:00 | 59.59 | 47 | 47 | 12.58 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 13:00 | 61.04 | 29.48 | 29.48 | 31.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 14:00 | 62.28 | 21.67 | 21.67 | 40.61 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 15:00 | 62.8 | 7.56 | 7.56 | 55.24 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 16:00 | 62.23 | 0 | 0 | 62.23 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 17:00 | 61.89 | 0 | 0 | 61.89 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 18:00 | 59.48 | 0 | 0 | 59.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 19:00 | 58 | 0 | 0 | 58 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 20:00 | 55.94 | 0 | 0 | 55.94 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 21:00 | 53.14 | 0 | 0 | 53.14 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 22:00 | 51.4 | 0 | 0 | 51.4 | 0 | 0 | 32.45 | 0 | 0
2025-10-23 23:00 | 48.87 | 0 | 0 | 48.87 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 | 47.18 | 0 | 0 | 47.18 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 01:00 | 45.48 | 0 | 0 | 45.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 02:00 | 44.69 | 0 | 0 | 44.69 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 03:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 04:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 05:00 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 06:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 07:00 | 48.13 | 0 | 0 | 48.13 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 08:00 | 50.92 | 10.36 | 10.36 | 40.56 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 09:00 | 52.02 | 18.85 | 18.85 | 33.16 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 10:00 | 55.33 | 8.08 | 8.08 | 47.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 11:00 | 58.36 | 4.44 | 4.44 | 53.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 12:00 | 59.79 | 11.03 | 11.03 | 48.77 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 13:00 | 61.44 | 79.97 | 79.97 | 0 | 18.53 | 0 | 50.05 | 0 | 0
2025-10-24 14:00 | 60.84 | 59.12 | 59.12 | 0 | 0 | 1.73 | 48.24 | 0 | 0
2025-10-24 15:00 | 62.48 | 32.51 | 32.51 | 14.98 | 0 | 15 | 32.45 | 0 | 0
2025-10-24 16:00 | 62.52 | 32.38 | 32.38 | 30.14 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 17:00 | 61.62 | 0 | 0 | 61.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 18:00 | 60.34 | 0 | 0 | 60.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 19:00 | 57.78 | 0 | 0 | 57.78 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 20:00 | 55.53 | 0 | 0 | 55.53 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 21:00 | 52.54 | 0 | 0 | 52.54 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 22:00 | 50.73 | 0 | 0 | 50.73 | 0 | 0 | 32.45 | 0 | 0
2025-10-24 23:00 | 48.01 | 0 | 0 | 48.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 | 45.66 | 0 | 0 | 45.66 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 01:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 02:00 | 45.12 | 0 | 0 | 45.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 03:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 04:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 05:00 | 44.97 | 0 | 0 | 44.97 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 06:00 | 45.69 | 0 | 0 | 45.69 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 07:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 08:00 | 49.26 | 7.75 | 7.75 | 41.5 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 09:00 | 52.18 | 41.01 | 41.01 | 11.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 10:00 | 54.51 | 38.7 | 38.7 | 15.81 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 11:00 | 56.55 | 38.68 | 38.68 | 17.87 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 12:00 | 57.68 | 33.97 | 33.97 | 23.71 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 13:00 | 58.34 | 33.76 | 33.76 | 24.58 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 14:00 | 59.61 | 13.37 | 13.37 | 46.24 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 15:00 | 59.89 | 1.43 | 1.43 | 58.46 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 16:00 | 59.62 | 1.86 | 1.86 | 57.77 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 17:00 | 59.74 | 0 | 0 | 59.74 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 18:00 | 57.43 | 0 | 0 | 57.43 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 19:00 | 56.59 | 0 | 0 | 56.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 20:00 | 54.62 | 0 | 0 | 54.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 21:00 | 52.94 | 0 | 0 | 52.94 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 22:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 32.45 | 0 | 0
2025-10-25 23:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 01:00 | 45.28 | 0 | 0 | 45.28 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 02:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 03:00 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 04:00 | 44.42 | 0 | 0 | 44.42 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 05:00 | 45.28 | 0 | 0 | 45.28 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 06:00 | 46.58 | 0 | 0 | 46.58 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 07:00 | 47.63 | 0 | 0 | 47.63 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 08:00 | 50.3 | 1.08 | 1.08 | 49.22 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 09:00 | 50.94 | 2.57 | 2.57 | 48.37 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 10:00 | 52.81 | 82.06 | 82.06 | 0 | 29.25 | 0 | 60.24 | 0 | 0
2025-10-26 11:00 | 54.06 | 78.47 | 78.47 | 0 | 24.41 | 0 | 83.42 | 0 | 0
2025-10-26 12:00 | 55.5 | 76.59 | 76.59 | 0 | 21.09 | 0 | 103.46 | 0 | 0
2025-10-26 13:00 | 55.08 | 83.42 | 83.42 | 0 | 28.34 | 0 | 130.38 | 0 | 0
2025-10-26 14:00 | 55.25 | 91.5 | 91.5 | 0 | 36.25 | 0 | 164.82 | 0 | 0
2025-10-26 15:00 | 54.94 | 92.98 | 92.98 | 0 | 38.04 | 0 | 200.96 | 0 | 0
2025-10-26 16:00 | 56.35 | 42.52 | 42.52 | 0 | 0 | 13.83 | 186.4 | 0 | 0
2025-10-26 17:00 | 55.45 | 0 | 0 | 0 | 0 | 55.45 | 128.03 | 0 | 0
2025-10-26 18:00 | 54.87 | 0 | 0 | 0 | 0 | 54.87 | 70.28 | 0 | 0
2025-10-26 19:00 | 55.32 | 0 | 0 | 19.39 | 0 | 35.93 | 32.45 | 0 | 0
2025-10-26 20:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 21:00 | 50.52 | 0 | 0 | 50.52 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 22:00 | 49.46 | 0 | 0 | 49.46 | 0 | 0 | 32.45 | 0 | 0
2025-10-26 23:00 | 47.41 | 0 | 0 | 47.41 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 | 46.12 | 0 | 0 | 46.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 01:00 | 44.75 | 0 | 0 | 44.75 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 02:00 | 43.81 | 0 | 0 | 43.81 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 03:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 04:00 | 44.9 | 0 | 0 | 44.9 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 05:00 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 06:00 | 46.21 | 0 | 0 | 46.21 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 07:00 | 48.5 | 0 | 0 | 48.5 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 08:00 | 50.48 | 5.14 | 5.14 | 45.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 09:00 | 52.69 | 2.6 | 2.6 | 50.09 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 10:00 | 55.24 | 3.9 | 3.9 | 51.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 11:00 | 57.18 | 4.67 | 4.67 | 52.51 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 12:00 | 59.38 | 4.78 | 4.78 | 54.6 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 13:00 | 60.91 | 68.43 | 68.43 | 0 | 7.52 | 0 | 39.59 | 0 | 0
2025-10-27 14:00 | 61.56 | 93.64 | 93.64 | 0 | 32.08 | 0 | 70.07 | 0 | 0
2025-10-27 15:00 | 61.69 | 96.07 | 96.07 | 0 | 34.38 | 0 | 102.73 | 0 | 0
2025-10-27 16:00 | 62.24 | 43.22 | 43.22 | 0 | 0 | 19.02 | 82.71 | 0 | 0
2025-10-27 17:00 | 60.3 | 0 | 0 | 12.55 | 0 | 47.75 | 32.45 | 0 | 0
2025-10-27 18:00 | 59.24 | 0 | 0 | 59.24 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 19:00 | 57.32 | 0 | 0 | 57.32 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 20:00 | 54.6 | 0 | 0 | 54.6 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 21:00 | 52.15 | 0 | 0 | 52.15 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 22:00 | 50.07 | 0 | 0 | 50.07 | 0 | 0 | 32.45 | 0 | 0
2025-10-27 23:00 | 47.88 | 0 | 0 | 47.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 | 45.53 | 0 | 0 | 45.53 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 01:00 | 44.51 | 0 | 0 | 44.51 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 02:00 | 44.1 | 0 | 0 | 44.1 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 03:00 | 44.32 | 0 | 0 | 44.32 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 04:00 | 44.25 | 0 | 0 | 44.25 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 05:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 06:00 | 46.58 | 0 | 0 | 46.58 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 07:00 | 47.93 | 10.22 | 10.22 | 37.71 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 08:00 | 50.85 | 88.4 | 88.4 | 0 | 37.54 | 0 | 68.11 | 0 | 0
2025-10-28 09:00 | 53.38 | 92.23 | 92.23 | 0 | 38.85 | 0 | 105.02 | 0 | 0
2025-10-28 10:00 | 56.23 | 83.94 | 83.94 | 0 | 27.71 | 0 | 131.34 | 0 | 0
2025-10-28 11:00 | 59.17 | 74.88 | 74.88 | 0 | 15.71 | 0 | 146.27 | 0 | 0
2025-10-28 12:00 | 61.82 | 72.43 | 72.43 | 0 | 10.62 | 0 | 156.35 | 0 | 0
2025-10-28 13:00 | 64.58 | 79.01 | 79.01 | 0 | 14.43 | 0 | 170.06 | 0 | 0
2025-10-28 14:00 | 65.24 | 86.72 | 86.72 | 0 | 21.49 | 0 | 190.48 | 0 | 0
2025-10-28 15:00 | 66.25 | 85.97 | 85.97 | 0 | 19.72 | 0 | 209.21 | 0 | 0
2025-10-28 16:00 | 65.72 | 34.71 | 34.71 | 0 | 0 | 31.01 | 176.58 | 0 | 0
2025-10-28 17:00 | 64.24 | 0 | 0 | 0 | 0 | 64.24 | 108.96 | 0 | 0
2025-10-28 18:00 | 60.94 | 0 | 0 | 0 | 0 | 60.94 | 44.81 | 0 | 0
2025-10-28 19:00 | 59.78 | 0 | 0 | 48.04 | 0 | 11.74 | 32.45 | 0 | 0
2025-10-28 20:00 | 56.1 | 0 | 0 | 56.1 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 21:00 | 53.75 | 0 | 0 | 53.75 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 22:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 32.45 | 0 | 0
2025-10-28 23:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 | 46.88 | 0 | 0 | 46.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 01:00 | 44.17 | 0 | 0 | 44.17 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 02:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 03:00 | 43.61 | 0 | 0 | 43.61 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 04:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 05:00 | 44.62 | 0 | 0 | 44.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 06:00 | 45.24 | 0 | 0 | 45.24 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 07:00 | 47.41 | 0 | 0 | 47.41 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 08:00 | 48.54 | 2.51 | 2.51 | 46.03 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 09:00 | 50.52 | 5.53 | 5.53 | 44.99 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 10:00 | 52.66 | 8.27 | 8.27 | 44.39 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 11:00 | 53.56 | 8.93 | 8.93 | 44.64 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 12:00 | 53.65 | 10.16 | 10.16 | 43.49 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 13:00 | 55.49 | 9.15 | 9.15 | 46.34 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 14:00 | 55.45 | 6.65 | 6.65 | 48.8 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 15:00 | 55.31 | 3.73 | 3.73 | 51.58 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 16:00 | 55.83 | 0.22 | 0.22 | 55.61 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 17:00 | 54.98 | 0 | 0 | 54.98 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 18:00 | 53.81 | 0 | 0 | 53.81 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 19:00 | 54.36 | 0 | 0 | 54.36 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 20:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 21:00 | 50.67 | 0 | 0 | 50.67 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 22:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 32.45 | 0 | 0
2025-10-29 23:00 | 48.01 | 0 | 0 | 48.01 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 | 45.62 | 0 | 0 | 45.62 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 01:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 02:00 | 43.37 | 0 | 0 | 43.37 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 03:00 | 44.09 | 0 | 0 | 44.09 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 04:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 05:00 | 44.41 | 0 | 0 | 44.41 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 06:00 | 46.57 | 0 | 0 | 46.57 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 07:00 | 48.07 | 9.33 | 9.33 | 38.74 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 08:00 | 49.73 | 81.6 | 81.6 | 0 | 31.87 | 0 | 62.72 | 0 | 0
2025-10-30 09:00 | 52.2 | 87.08 | 87.08 | 0 | 34.88 | 0 | 95.86 | 0 | 0
2025-10-30 10:00 | 54.94 | 76.26 | 76.26 | 0 | 21.32 | 0 | 116.11 | 0 | 0
2025-10-30 11:00 | 56.77 | 69.35 | 69.35 | 0 | 12.59 | 0 | 128.07 | 0 | 0
2025-10-30 12:00 | 59.31 | 65.61 | 65.61 | 0 | 6.3 | 0 | 134.05 | 0 | 0
2025-10-30 13:00 | 61.13 | 72.31 | 72.31 | 0 | 11.18 | 0 | 144.68 | 0 | 0
2025-10-30 14:00 | 61.2 | 77.98 | 77.98 | 0 | 16.79 | 0 | 160.62 | 0 | 0
2025-10-30 15:00 | 62.32 | 74.05 | 74.05 | 0 | 11.73 | 0 | 171.77 | 0 | 0
2025-10-30 16:00 | 61.89 | 25.5 | 25.5 | 0 | 0 | 36.39 | 133.46 | 0 | 0
2025-10-30 17:00 | 61.49 | 0 | 0 | 0 | 0 | 61.49 | 68.73 | 0 | 0
2025-10-30 18:00 | 58.39 | 0 | 0 | 23.92 | 0 | 34.47 | 32.45 | 0 | 0
2025-10-30 19:00 | 56.99 | 0 | 0 | 56.99 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 20:00 | 54.54 | 0 | 0 | 54.54 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 21:00 | 52.76 | 0 | 0 | 52.76 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 22:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 32.45 | 0 | 0
2025-10-30 23:00 | 48.59 | 0 | 0 | 48.59 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 | 45.99 | 0 | 0 | 45.99 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 01:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 02:00 | 43.69 | 0 | 0 | 43.69 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 03:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 04:00 | 44 | 0 | 0 | 44 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 05:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 06:00 | 45.24 | 0 | 0 | 45.24 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 07:00 | 47.53 | 7.4 | 7.4 | 40.12 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 08:00 | 49.8 | 73.86 | 73.86 | 0 | 24.06 | 0 | 55.31 | 0 | 0
2025-10-31 09:00 | 50.08 | 83.02 | 83.02 | 0 | 32.94 | 0 | 86.6 | 0 | 0
2025-10-31 10:00 | 53.83 | 77.12 | 77.12 | 0 | 23.29 | 0 | 108.73 | 0 | 0
2025-10-31 11:00 | 54.87 | 69.56 | 69.56 | 0 | 14.69 | 0 | 122.69 | 0 | 0
2025-10-31 12:00 | 55.52 | 67.55 | 67.55 | 0 | 12.03 | 0 | 134.11 | 0 | 0
2025-10-31 13:00 | 56.12 | 71.26 | 71.26 | 0 | 15.14 | 0 | 148.5 | 0 | 0
2025-10-31 14:00 | 57.57 | 77.76 | 77.76 | 0 | 20.19 | 0 | 167.68 | 0 | 0
2025-10-31 15:00 | 58.57 | 71.61 | 71.61 | 0 | 13.04 | 0 | 180.06 | 0 | 0
2025-10-31 16:00 | 58.3 | 24.32 | 24.32 | 0 | 0 | 33.98 | 144.3 | 0 | 0
2025-10-31 17:00 | 57.93 | 0 | 0 | 0 | 0 | 57.93 | 83.31 | 0 | 0
2025-10-31 18:00 | 56.19 | 0 | 0 | 7.87 | 0 | 48.32 | 32.45 | 0 | 0
2025-10-31 19:00 | 54.39 | 0 | 0 | 54.39 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 20:00 | 52.93 | 0 | 0 | 52.93 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 21:00 | 51.2 | 0 | 0 | 51.2 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 22:00 | 49.3 | 0 | 0 | 49.3 | 0 | 0 | 32.45 | 0 | 0
2025-10-31 23:00 | 46.9 | 0 | 0 | 46.9 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 | 45.97 | 0 | 0 | 45.97 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 01:00 | 43.93 | 0 | 0 | 43.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 02:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 03:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 04:00 | 43.98 | 0 | 0 | 43.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 05:00 | 44.18 | 0 | 0 | 44.18 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 06:00 | 45.17 | 0 | 0 | 45.17 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 07:00 | 47.64 | 8.66 | 8.66 | 38.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 08:00 | 50.17 | 78.96 | 78.96 | 0 | 28.79 | 0 | 59.8 | 0 | 0
2025-11-01 09:00 | 51.26 | 84.54 | 84.54 | 0 | 33.28 | 0 | 91.42 | 0 | 0
2025-11-01 10:00 | 53.82 | 75.31 | 75.31 | 0 | 21.48 | 0 | 111.83 | 0 | 0
2025-11-01 11:00 | 55.63 | 66.36 | 66.36 | 0 | 10.73 | 0 | 122.03 | 0 | 0
2025-11-01 12:00 | 56.44 | 64.83 | 64.83 | 0 | 8.38 | 0 | 129.99 | 0 | 0
2025-11-01 13:00 | 58.01 | 72.9 | 72.9 | 0 | 14.89 | 0 | 144.13 | 0 | 0
2025-11-01 14:00 | 58.14 | 81.99 | 81.99 | 0 | 23.85 | 0 | 166.79 | 0 | 0
2025-11-01 15:00 | 58.95 | 81.75 | 81.75 | 0 | 22.8 | 0 | 188.45 | 0 | 0
2025-11-01 16:00 | 58.47 | 25.92 | 25.92 | 0 | 0 | 32.55 | 154.18 | 0 | 0
2025-11-01 17:00 | 57.8 | 0 | 0 | 0 | 0 | 57.8 | 93.34 | 0 | 0
2025-11-01 18:00 | 56.37 | 0 | 0 | 0 | 0 | 56.37 | 34 | 0 | 0
2025-11-01 19:00 | 54.97 | 0 | 0 | 53.49 | 0 | 1.48 | 32.45 | 0 | 0
2025-11-01 20:00 | 53.47 | 0 | 0 | 53.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 21:00 | 51.09 | 0 | 0 | 51.09 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 22:00 | 48.16 | 0 | 0 | 48.16 | 0 | 0 | 32.45 | 0 | 0
2025-11-01 23:00 | 46.8 | 0 | 0 | 46.8 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 | 44.54 | 0 | 0 | 44.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 01:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 02:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 03:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 04:00 | 42.92 | 0 | 0 | 42.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 05:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 06:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 07:00 | 46.25 | 13.05 | 13.05 | 33.2 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 08:00 | 48.88 | 92.32 | 92.32 | 0 | 43.44 | 0 | 73.71 | 0 | 0
2025-11-02 09:00 | 50.64 | 97.09 | 97.09 | 0 | 46.45 | 0 | 117.84 | 0 | 0
2025-11-02 10:00 | 52.32 | 88.73 | 88.73 | 0 | 36.42 | 0 | 152.44 | 0 | 0
2025-11-02 11:00 | 52.95 | 77.86 | 77.86 | 0 | 24.91 | 0 | 176.11 | 0 | 0
2025-11-02 12:00 | 54.99 | 16.46 | 16.46 | 0 | 0 | 38.53 | 135.55 | 0 | 0
2025-11-02 13:00 | 54.99 | 42.96 | 42.96 | 0 | 0 | 12.03 | 122.89 | 0 | 0
2025-11-02 14:00 | 56.07 | 34.96 | 34.96 | 0 | 0 | 21.11 | 100.68 | 0 | 0
2025-11-02 15:00 | 55.65 | 1.17 | 1.17 | 0 | 0 | 54.48 | 43.33 | 0 | 0
2025-11-02 16:00 | 55.63 | 0 | 0 | 45.29 | 0 | 10.33 | 32.45 | 0 | 0
2025-11-02 17:00 | 54.02 | 0 | 0 | 54.02 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 18:00 | 54.25 | 0 | 0 | 54.25 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 19:00 | 53.3 | 0 | 0 | 53.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 20:00 | 51.64 | 0 | 0 | 51.64 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 21:00 | 51.1 | 0 | 0 | 51.1 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 22:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-02 23:00 | 46.54 | 0 | 0 | 46.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 | 44.74 | 0 | 0 | 44.74 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 01:00 | 43.68 | 0 | 0 | 43.68 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 02:00 | 43.7 | 0 | 0 | 43.7 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 03:00 | 43.65 | 0 | 0 | 43.65 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 04:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 05:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 06:00 | 44.61 | 0 | 0 | 44.61 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 07:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 08:00 | 49.16 | 0.9 | 0.9 | 48.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 09:00 | 50.47 | 2.13 | 2.13 | 48.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 10:00 | 51.72 | 3.34 | 3.34 | 48.37 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 11:00 | 53.5 | 4.62 | 4.62 | 48.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 12:00 | 55.7 | 5.43 | 5.43 | 50.27 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 13:00 | 57 | 53.1 | 53.1 | 3.9 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 14:00 | 56.39 | 55.58 | 55.58 | 0.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 15:00 | 57.5 | 52.71 | 52.71 | 4.78 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 16:00 | 58.23 | 17.33 | 17.33 | 40.91 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 17:00 | 56.62 | 0 | 0 | 56.62 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 18:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 19:00 | 54.48 | 0 | 0 | 54.48 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 20:00 | 51.87 | 0 | 0 | 51.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 21:00 | 50.38 | 0 | 0 | 50.38 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 22:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 32.45 | 0 | 0
2025-11-03 23:00 | 46.3 | 0 | 0 | 46.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 | 44.65 | 0 | 0 | 44.65 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 01:00 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 02:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 03:00 | 43.33 | 0 | 0 | 43.33 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 04:00 | 42.83 | 0 | 0 | 42.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 05:00 | 43.83 | 0 | 0 | 43.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 06:00 | 45.42 | 0 | 0 | 45.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 07:00 | 46.59 | 0 | 0 | 46.59 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 08:00 | 49.32 | 5.42 | 5.42 | 43.89 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 09:00 | 50.42 | 10.87 | 10.87 | 39.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 10:00 | 54.2 | 16.98 | 16.98 | 37.22 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 11:00 | 55.22 | 16.53 | 16.53 | 38.7 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 12:00 | 58.55 | 16.47 | 16.47 | 42.08 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 13:00 | 60.84 | 13.74 | 13.74 | 47.1 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 14:00 | 61.85 | 12.16 | 12.16 | 49.69 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 15:00 | 61.27 | 4.95 | 4.95 | 56.32 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 16:00 | 60.95 | 0.5 | 0.5 | 60.45 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 17:00 | 60.07 | 0 | 0 | 60.07 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 18:00 | 58.76 | 0 | 0 | 58.76 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 19:00 | 55.44 | 0 | 0 | 55.44 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 20:00 | 53.98 | 0 | 0 | 53.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 21:00 | 51.6 | 0 | 0 | 51.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 22:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 32.45 | 0 | 0
2025-11-04 23:00 | 47.15 | 0 | 0 | 47.15 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 | 45.05 | 0 | 0 | 45.05 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 01:00 | 43.42 | 0 | 0 | 43.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 02:00 | 41.95 | 0 | 0 | 41.95 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 03:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 04:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 05:00 | 43.4 | 0 | 0 | 43.4 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 06:00 | 45.18 | 0 | 0 | 45.18 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 07:00 | 47.3 | 0 | 0 | 47.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 08:00 | 48.54 | 1.4 | 1.4 | 47.14 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 09:00 | 51 | 3.46 | 3.46 | 47.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 10:00 | 52.22 | 5.29 | 5.29 | 46.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 11:00 | 55.18 | 6.75 | 6.75 | 48.43 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 12:00 | 56.88 | 6.83 | 6.83 | 50.05 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 13:00 | 58.97 | 6.08 | 6.08 | 52.89 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 14:00 | 59 | 4.48 | 4.48 | 54.52 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 15:00 | 59.47 | 2.25 | 2.25 | 57.22 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 16:00 | 59.81 | 0 | 0 | 59.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 17:00 | 58.31 | 0 | 0 | 58.31 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 18:00 | 56.36 | 0 | 0 | 56.36 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 19:00 | 56.33 | 0 | 0 | 56.33 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 20:00 | 52.4 | 0 | 0 | 52.4 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 21:00 | 50.69 | 0 | 0 | 50.69 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 22:00 | 48.73 | 0 | 0 | 48.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-05 23:00 | 46.72 | 0 | 0 | 46.72 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 | 44.76 | 0 | 0 | 44.76 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 01:00 | 43.48 | 0 | 0 | 43.48 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 02:00 | 42.68 | 0 | 0 | 42.68 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 03:00 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 04:00 | 43.87 | 0 | 0 | 43.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 05:00 | 43.46 | 0 | 0 | 43.46 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 06:00 | 45.15 | 0 | 0 | 45.15 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 07:00 | 46.45 | 0.26 | 0.26 | 46.19 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 08:00 | 48.62 | 7.19 | 7.19 | 41.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 09:00 | 51.06 | 11.84 | 11.84 | 39.22 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 10:00 | 53.16 | 13.9 | 13.9 | 39.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 11:00 | 56.46 | 17.53 | 17.53 | 38.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 12:00 | 58.69 | 16.46 | 16.46 | 42.24 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 13:00 | 61.36 | 16.65 | 16.65 | 44.71 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 14:00 | 61.38 | 12.91 | 12.91 | 48.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 15:00 | 62.11 | 9.48 | 9.48 | 52.63 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 16:00 | 61.53 | 3.8 | 3.8 | 57.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 17:00 | 61.49 | 0 | 0 | 61.49 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 18:00 | 58.46 | 0 | 0 | 58.46 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 19:00 | 56.83 | 0 | 0 | 56.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 20:00 | 54.42 | 0 | 0 | 54.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 21:00 | 51.21 | 0 | 0 | 51.21 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 22:00 | 48.1 | 0 | 0 | 48.1 | 0 | 0 | 32.45 | 0 | 0
2025-11-06 23:00 | 45.93 | 0 | 0 | 45.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 01:00 | 42.79 | 0 | 0 | 42.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 02:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 03:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 04:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 05:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 06:00 | 44.2 | 0 | 0 | 44.2 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 07:00 | 45.86 | 1.77 | 1.77 | 44.09 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 08:00 | 48.74 | 7.53 | 7.53 | 41.21 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 09:00 | 50.37 | 58.58 | 58.58 | 0 | 8.21 | 0 | 40.25 | 0 | 0
2025-11-07 10:00 | 51.7 | 57.71 | 57.71 | 0 | 6.01 | 0 | 45.96 | 0 | 0
2025-11-07 11:00 | 55.74 | 40.3 | 40.3 | 2.6 | 0 | 12.83 | 32.45 | 0 | 0
2025-11-07 12:00 | 56.97 | 51.62 | 51.62 | 5.35 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 13:00 | 59.36 | 58.44 | 58.44 | 0.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 14:00 | 60.87 | 22.09 | 22.09 | 38.78 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 15:00 | 60.55 | 38.12 | 38.12 | 22.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 16:00 | 60.67 | 0 | 0 | 60.67 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 17:00 | 59.2 | 0 | 0 | 59.2 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 18:00 | 58.28 | 0 | 0 | 58.28 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 19:00 | 54.88 | 0 | 0 | 54.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 20:00 | 53.08 | 0 | 0 | 53.08 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 21:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 22:00 | 48.29 | 0 | 0 | 48.29 | 0 | 0 | 32.45 | 0 | 0
2025-11-07 23:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 01:00 | 44.31 | 0 | 0 | 44.31 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 02:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 03:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 04:00 | 42.81 | 0 | 0 | 42.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 05:00 | 43.87 | 0 | 0 | 43.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 06:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 07:00 | 45.39 | 0.27 | 0.27 | 45.12 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 08:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 09:00 | 50.1 | 2.11 | 2.11 | 47.99 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 10:00 | 51.93 | 17.94 | 17.94 | 33.99 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 11:00 | 54.03 | 75.13 | 75.13 | 0 | 21.1 | 0 | 52.49 | 0 | 0
2025-11-08 12:00 | 54.56 | 19.7 | 19.7 | 15.82 | 0 | 19.04 | 32.45 | 0 | 0
2025-11-08 13:00 | 56.99 | 20.22 | 20.22 | 36.78 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 14:00 | 57.56 | 79.27 | 79.27 | 0 | 21.71 | 0 | 53.08 | 0 | 0
2025-11-08 15:00 | 58.69 | 16.65 | 16.65 | 22.44 | 0 | 19.6 | 32.45 | 0 | 0
2025-11-08 16:00 | 58.44 | 15.89 | 15.89 | 42.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 17:00 | 57.38 | 0 | 0 | 57.38 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 18:00 | 55.95 | 0 | 0 | 55.95 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 19:00 | 53.27 | 0 | 0 | 53.27 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 20:00 | 52.34 | 0 | 0 | 52.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 21:00 | 50.28 | 0 | 0 | 50.28 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 22:00 | 48.54 | 0 | 0 | 48.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-08 23:00 | 47.11 | 0 | 0 | 47.11 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 | 43.55 | 0 | 0 | 43.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 01:00 | 42.96 | 0 | 0 | 42.96 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 02:00 | 42.04 | 0 | 0 | 42.04 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 03:00 | 42.24 | 0 | 0 | 42.24 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 04:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 05:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 06:00 | 44.91 | 0 | 0 | 44.91 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 07:00 | 45.54 | 4.72 | 4.72 | 40.82 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 08:00 | 47.68 | 77.59 | 77.59 | 0 | 29.91 | 0 | 60.87 | 0 | 0
2025-11-09 09:00 | 50.09 | 91.38 | 91.38 | 0 | 41.29 | 0 | 100.09 | 0 | 0
2025-11-09 10:00 | 52.98 | 77.83 | 77.83 | 0 | 24.85 | 0 | 123.69 | 0 | 0
2025-11-09 11:00 | 55.07 | 22.06 | 22.06 | 0 | 0 | 33.01 | 88.95 | 0 | 0
2025-11-09 12:00 | 57.93 | 5.94 | 5.94 | 0 | 0 | 51.99 | 34.22 | 0 | 0
2025-11-09 13:00 | 59.68 | 3.17 | 3.17 | 54.83 | 0 | 1.68 | 32.45 | 0 | 0
2025-11-09 14:00 | 60.54 | 2.19 | 2.19 | 58.35 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 15:00 | 61.78 | 0.88 | 0.88 | 60.9 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 16:00 | 60.91 | 0 | 0 | 60.91 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 17:00 | 60.3 | 0 | 0 | 60.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 18:00 | 57.86 | 0 | 0 | 57.86 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 19:00 | 55.67 | 0 | 0 | 55.67 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 20:00 | 52.88 | 0 | 0 | 52.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 21:00 | 50.6 | 0 | 0 | 50.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 22:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-09 23:00 | 45.89 | 0 | 0 | 45.89 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 01:00 | 42.6 | 0 | 0 | 42.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 02:00 | 42.66 | 0 | 0 | 42.66 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 03:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 04:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 05:00 | 43.04 | 0 | 0 | 43.04 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 06:00 | 44.93 | 0 | 0 | 44.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 07:00 | 45.13 | 0 | 0 | 45.13 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 08:00 | 46.8 | 0.95 | 0.95 | 45.85 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 09:00 | 49.22 | 2.96 | 2.96 | 46.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 10:00 | 50.87 | 5.26 | 5.26 | 45.61 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 11:00 | 52.8 | 6.29 | 6.29 | 46.51 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 12:00 | 55.48 | 6.61 | 6.61 | 48.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 13:00 | 56.48 | 5.69 | 5.69 | 50.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 14:00 | 57.07 | 3.91 | 3.91 | 53.16 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 15:00 | 57.4 | 1.78 | 1.78 | 55.62 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 16:00 | 57.01 | 0 | 0 | 57.01 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 17:00 | 57.3 | 0 | 0 | 57.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 18:00 | 54.8 | 0 | 0 | 54.8 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 19:00 | 52.83 | 0 | 0 | 52.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 20:00 | 51.96 | 0 | 0 | 51.96 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 21:00 | 49.42 | 0 | 0 | 49.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 22:00 | 48.55 | 0 | 0 | 48.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-10 23:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 01:00 | 43.42 | 0 | 0 | 43.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 02:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 03:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 04:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 05:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 06:00 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 07:00 | 45.04 | 0 | 0 | 45.04 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 08:00 | 46.21 | 3.7 | 3.7 | 42.51 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 09:00 | 49.86 | 10.26 | 10.26 | 39.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 10:00 | 51.58 | 3.68 | 3.68 | 47.91 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 11:00 | 53.7 | 13.61 | 13.61 | 40.09 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 12:00 | 54.77 | 22.77 | 22.77 | 32 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 13:00 | 56.5 | 24.66 | 24.66 | 31.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 14:00 | 57.72 | 21.18 | 21.18 | 36.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 15:00 | 57.94 | 10.05 | 10.05 | 47.89 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 16:00 | 58.02 | 0.73 | 0.73 | 57.29 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 17:00 | 57.34 | 0 | 0 | 57.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 18:00 | 56.75 | 0 | 0 | 56.75 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 19:00 | 53.78 | 0 | 0 | 53.78 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 20:00 | 52.27 | 0 | 0 | 52.27 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 21:00 | 49.15 | 0 | 0 | 49.15 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 22:00 | 46.64 | 0 | 0 | 46.64 | 0 | 0 | 32.45 | 0 | 0
2025-11-11 23:00 | 45.43 | 0 | 0 | 45.43 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 01:00 | 42.73 | 0 | 0 | 42.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 02:00 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 03:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 04:00 | 42.9 | 0 | 0 | 42.9 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 05:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 06:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 07:00 | 45.71 | 1.16 | 1.16 | 44.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 08:00 | 46.53 | 43.76 | 43.76 | 2.77 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 09:00 | 49.18 | 57.49 | 57.49 | 0 | 8.31 | 0 | 40.35 | 0 | 0
2025-11-12 10:00 | 49.98 | 45.12 | 45.12 | 0 | 0 | 4.85 | 35.24 | 0 | 0
2025-11-12 11:00 | 51.64 | 49.62 | 49.62 | 0 | 0 | 2.02 | 33.11 | 0 | 0
2025-11-12 12:00 | 53.42 | 49.28 | 49.28 | 3.51 | 0 | 0.63 | 32.45 | 0 | 0
2025-11-12 13:00 | 54.55 | 53.67 | 53.67 | 0.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 14:00 | 55.27 | 69.08 | 69.08 | 0 | 13.81 | 0 | 45.57 | 0 | 0
2025-11-12 15:00 | 55.06 | 77.54 | 77.54 | 0 | 22.48 | 0 | 66.93 | 0 | 0
2025-11-12 16:00 | 55.15 | 14.43 | 14.43 | 7.97 | 0 | 32.75 | 32.45 | 0 | 0
2025-11-12 17:00 | 54.63 | 0 | 0 | 54.63 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 18:00 | 53.34 | 0 | 0 | 53.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 19:00 | 51.84 | 0 | 0 | 51.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 20:00 | 49.62 | 0 | 0 | 49.62 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 21:00 | 48.93 | 0 | 0 | 48.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 22:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-12 23:00 | 45.05 | 0 | 0 | 45.05 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 | 44.34 | 0 | 0 | 44.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 01:00 | 41.88 | 0 | 0 | 41.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 02:00 | 42.72 | 0 | 0 | 42.72 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 03:00 | 41.65 | 0 | 0 | 41.65 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 04:00 | 42.06 | 0 | 0 | 42.06 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 05:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 06:00 | 42.87 | 0 | 0 | 42.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 07:00 | 45.08 | 0.68 | 0.68 | 44.4 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 08:00 | 47 | 45.31 | 45.31 | 1.69 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 09:00 | 48.99 | 54.07 | 54.07 | 0 | 5.08 | 0 | 37.28 | 0 | 0
2025-11-13 10:00 | 50.37 | 61.67 | 61.67 | 0 | 11.29 | 0 | 48.01 | 0 | 0
2025-11-13 11:00 | 51.08 | 55 | 55 | 0 | 3.92 | 0 | 51.73 | 0 | 0
2025-11-13 12:00 | 52.87 | 48.74 | 48.74 | 0 | 0 | 4.13 | 47.38 | 0 | 0
2025-11-13 13:00 | 55.79 | 47.27 | 47.27 | 0 | 0 | 8.53 | 38.41 | 0 | 0
2025-11-13 14:00 | 54.93 | 35.88 | 35.88 | 13.39 | 0 | 5.66 | 32.45 | 0 | 0
2025-11-13 15:00 | 56.43 | 23.31 | 23.31 | 33.12 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 16:00 | 55.01 | 3.52 | 3.52 | 51.49 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 17:00 | 54.68 | 0 | 0 | 54.68 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 18:00 | 53.95 | 0 | 0 | 53.95 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 19:00 | 51.77 | 0 | 0 | 51.77 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 20:00 | 51.27 | 0 | 0 | 51.27 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 21:00 | 48.69 | 0 | 0 | 48.69 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 22:00 | 47.07 | 0 | 0 | 47.07 | 0 | 0 | 32.45 | 0 | 0
2025-11-13 23:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 01:00 | 43.24 | 0 | 0 | 43.24 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 02:00 | 41.71 | 0 | 0 | 41.71 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 03:00 | 42.41 | 0 | 0 | 42.41 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 04:00 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 05:00 | 42.84 | 0 | 0 | 42.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 06:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 07:00 | 44.33 | 0 | 0 | 44.33 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 08:00 | 46.5 | 1.29 | 1.29 | 45.21 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 09:00 | 47.97 | 6.61 | 6.61 | 41.37 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 10:00 | 49.07 | 25.82 | 25.82 | 23.25 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 11:00 | 51.04 | 28.6 | 28.6 | 22.44 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 12:00 | 52.07 | 43.01 | 43.01 | 9.06 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 13:00 | 52.8 | 42.12 | 42.12 | 10.69 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 14:00 | 53.32 | 11.32 | 11.32 | 42 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 15:00 | 53.49 | 4.89 | 4.89 | 48.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 16:00 | 53.18 | 0.7 | 0.7 | 52.48 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 17:00 | 52.91 | 0 | 0 | 52.91 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 18:00 | 51.67 | 0 | 0 | 51.67 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 19:00 | 52.19 | 0 | 0 | 52.19 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 20:00 | 48.79 | 0 | 0 | 48.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 21:00 | 47.68 | 0 | 0 | 47.68 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 22:00 | 46.14 | 0 | 0 | 46.14 | 0 | 0 | 32.45 | 0 | 0
2025-11-14 23:00 | 45.88 | 0 | 0 | 45.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 01:00 | 42.55 | 0 | 0 | 42.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 02:00 | 41.78 | 0 | 0 | 41.78 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 03:00 | 41.59 | 0 | 0 | 41.59 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 04:00 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 05:00 | 42.95 | 0 | 0 | 42.95 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 06:00 | 43.23 | 0 | 0 | 43.23 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 07:00 | 45.06 | 0.33 | 0.33 | 44.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 08:00 | 45.84 | 23.22 | 23.22 | 22.62 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 09:00 | 48.84 | 52.96 | 52.96 | 0 | 4.11 | 0 | 36.36 | 0 | 0
2025-11-15 10:00 | 50.5 | 62.63 | 62.63 | 0 | 12.13 | 0 | 47.88 | 0 | 0
2025-11-15 11:00 | 52.84 | 51.12 | 51.12 | 0 | 0 | 1.72 | 46.07 | 0 | 0
2025-11-15 12:00 | 53.89 | 40.63 | 40.63 | 0.33 | 0 | 12.94 | 32.45 | 0 | 0
2025-11-15 13:00 | 56.36 | 46.06 | 46.06 | 10.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 14:00 | 56.21 | 66.14 | 66.14 | 0 | 9.93 | 0 | 41.88 | 0 | 0
2025-11-15 15:00 | 57.45 | 78.4 | 78.4 | 0 | 20.95 | 0 | 61.79 | 0 | 0
2025-11-15 16:00 | 56.45 | 9.74 | 9.74 | 18.84 | 0 | 27.87 | 32.45 | 0 | 0
2025-11-15 17:00 | 55.73 | 0 | 0 | 55.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 18:00 | 55.31 | 0 | 0 | 55.31 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 19:00 | 53.23 | 0 | 0 | 53.23 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 20:00 | 51.48 | 0 | 0 | 51.48 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 21:00 | 49.58 | 0 | 0 | 49.58 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 22:00 | 46.39 | 0 | 0 | 46.39 | 0 | 0 | 32.45 | 0 | 0
2025-11-15 23:00 | 45.71 | 0 | 0 | 45.71 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 | 42.47 | 0 | 0 | 42.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 01:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 02:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 04:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 05:00 | 42.66 | 0 | 0 | 42.66 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 06:00 | 43.66 | 0 | 0 | 43.66 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 07:00 | 44.58 | 0 | 0 | 44.58 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 08:00 | 45.93 | 37.26 | 37.26 | 8.67 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 09:00 | 47.54 | 22.44 | 22.44 | 25.1 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 10:00 | 48.74 | 42.77 | 42.77 | 5.97 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 11:00 | 50 | 46.41 | 46.41 | 3.59 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 12:00 | 50.75 | 21.76 | 21.76 | 28.99 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 13:00 | 51.73 | 18.69 | 18.69 | 33.03 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 14:00 | 50.89 | 1.59 | 1.59 | 49.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 15:00 | 51.77 | 2.8 | 2.8 | 48.97 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 16:00 | 51.01 | 0.82 | 0.82 | 50.19 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 17:00 | 51.44 | 0 | 0 | 51.44 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 18:00 | 51.47 | 0 | 0 | 51.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 19:00 | 49.5 | 0 | 0 | 49.5 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 20:00 | 48.66 | 0 | 0 | 48.66 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 21:00 | 47.66 | 0 | 0 | 47.66 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 22:00 | 44.83 | 0 | 0 | 44.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-16 23:00 | 44.21 | 0 | 0 | 44.21 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 | 43.34 | 0 | 0 | 43.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 01:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 02:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 03:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 04:00 | 41.91 | 0 | 0 | 41.91 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 05:00 | 42.26 | 0 | 0 | 42.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 06:00 | 43.6 | 0 | 0 | 43.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 07:00 | 44.71 | 0 | 0 | 44.71 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 08:00 | 46.61 | 8.43 | 8.43 | 38.18 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 09:00 | 48.09 | 17.22 | 17.22 | 30.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 10:00 | 50.28 | 29.37 | 29.37 | 20.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 11:00 | 51.81 | 40.77 | 40.77 | 11.04 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 12:00 | 54.43 | 18.25 | 18.25 | 36.19 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 13:00 | 55.87 | 62.34 | 62.34 | 0 | 6.46 | 0 | 38.59 | 0 | 0
2025-11-17 14:00 | 56.64 | 20.53 | 20.53 | 30.27 | 0 | 5.83 | 32.45 | 0 | 0
2025-11-17 15:00 | 56.03 | 0 | 0 | 56.03 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 16:00 | 55.47 | 0 | 0 | 55.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 17:00 | 55.75 | 0 | 0 | 55.75 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 18:00 | 54.07 | 0 | 0 | 54.07 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 19:00 | 52.29 | 0 | 0 | 52.29 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 20:00 | 49.91 | 0 | 0 | 49.91 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 21:00 | 48.46 | 0 | 0 | 48.46 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 22:00 | 45.79 | 0 | 0 | 45.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-17 23:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 | 43.65 | 0 | 0 | 43.65 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 01:00 | 42.75 | 0 | 0 | 42.75 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 02:00 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 03:00 | 40.38 | 0 | 0 | 40.38 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 04:00 | 41.39 | 0 | 0 | 41.39 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 05:00 | 43.01 | 0 | 0 | 43.01 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 06:00 | 42.53 | 0 | 0 | 42.53 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 07:00 | 44.27 | 0.18 | 0.18 | 44.09 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 08:00 | 46.54 | 53.4 | 53.4 | 0 | 6.86 | 0 | 38.97 | 0 | 0
2025-11-18 09:00 | 47.78 | 79.11 | 79.11 | 0 | 31.34 | 0 | 68.74 | 0 | 0
2025-11-18 10:00 | 50.33 | 70.82 | 70.82 | 0 | 20.5 | 0 | 88.21 | 0 | 0
2025-11-18 11:00 | 50.22 | 59.18 | 59.18 | 0 | 8.96 | 0 | 96.72 | 0 | 0
2025-11-18 12:00 | 51.36 | 57.37 | 57.37 | 0 | 6.01 | 0 | 102.43 | 0 | 0
2025-11-18 13:00 | 53.44 | 66.25 | 66.25 | 0 | 12.81 | 0 | 114.6 | 0 | 0
2025-11-18 14:00 | 52.84 | 74.62 | 74.62 | 0 | 21.78 | 0 | 135.28 | 0 | 0
2025-11-18 15:00 | 53.55 | 75.34 | 75.34 | 0 | 21.79 | 0 | 155.99 | 0 | 0
2025-11-18 16:00 | 53.4 | 3.74 | 3.74 | 0 | 0 | 49.66 | 103.71 | 0 | 0
2025-11-18 17:00 | 53.35 | 0 | 0 | 0 | 0 | 53.35 | 47.56 | 0 | 0
2025-11-18 18:00 | 52.16 | 0 | 0 | 37.81 | 0 | 14.35 | 32.45 | 0 | 0
2025-11-18 19:00 | 50.81 | 0 | 0 | 50.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 20:00 | 48.89 | 0 | 0 | 48.89 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 21:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 22:00 | 47.84 | 0 | 0 | 47.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-18 23:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 01:00 | 41.17 | 0 | 0 | 41.17 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 02:00 | 40.85 | 0 | 0 | 40.85 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 03:00 | 40.84 | 0 | 0 | 40.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 04:00 | 40.9 | 0 | 0 | 40.9 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 05:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 06:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 07:00 | 44.96 | 0 | 0 | 44.96 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 08:00 | 46.01 | 17.02 | 17.02 | 28.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 09:00 | 47.45 | 45.98 | 45.98 | 1.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 10:00 | 50.78 | 47.48 | 47.48 | 3.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 11:00 | 52.09 | 54.21 | 54.21 | 0 | 2.12 | 0 | 34.46 | 0 | 0
2025-11-19 12:00 | 53.03 | 50.53 | 50.53 | 0.59 | 0 | 1.91 | 32.45 | 0 | 0
2025-11-19 13:00 | 55.66 | 53.35 | 53.35 | 2.31 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 14:00 | 56.72 | 40.56 | 40.56 | 16.16 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 15:00 | 55.3 | 6.88 | 6.88 | 48.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 16:00 | 55.79 | 1 | 1 | 54.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 17:00 | 55.25 | 0 | 0 | 55.25 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 18:00 | 54.26 | 0 | 0 | 54.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 19:00 | 51.86 | 0 | 0 | 51.86 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 20:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 21:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 22:00 | 45.85 | 0 | 0 | 45.85 | 0 | 0 | 32.45 | 0 | 0
2025-11-19 23:00 | 44.6 | 0 | 0 | 44.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 | 42.17 | 0 | 0 | 42.17 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 01:00 | 41.02 | 0 | 0 | 41.02 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 02:00 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 03:00 | 40.96 | 0 | 0 | 40.96 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 04:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 05:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 06:00 | 42.33 | 0 | 0 | 42.33 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 07:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 08:00 | 45.01 | 26.2 | 26.2 | 18.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 09:00 | 48.23 | 59.6 | 59.6 | 0 | 11.36 | 0 | 43.25 | 0 | 0
2025-11-20 10:00 | 50.16 | 69.03 | 69.03 | 0 | 18.87 | 0 | 61.17 | 0 | 0
2025-11-20 11:00 | 51.74 | 62.24 | 62.24 | 0 | 10.5 | 0 | 71.15 | 0 | 0
2025-11-20 12:00 | 52.57 | 39.02 | 39.02 | 0 | 0 | 13.54 | 56.89 | 0 | 0
2025-11-20 13:00 | 53.75 | 52.56 | 52.56 | 0 | 0 | 1.19 | 55.64 | 0 | 0
2025-11-20 14:00 | 54.86 | 45.86 | 45.86 | 0 | 0 | 9 | 46.16 | 0 | 0
2025-11-20 15:00 | 54.59 | 48.79 | 48.79 | 0 | 0 | 5.8 | 40.06 | 0 | 0
2025-11-20 16:00 | 54.48 | 6.06 | 6.06 | 41.19 | 0 | 7.23 | 32.45 | 0 | 0
2025-11-20 17:00 | 54.49 | 0 | 0 | 54.49 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 18:00 | 53.24 | 0 | 0 | 53.24 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 19:00 | 50.79 | 0 | 0 | 50.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 20:00 | 49.84 | 0 | 0 | 49.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 21:00 | 47.83 | 0 | 0 | 47.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 22:00 | 46.53 | 0 | 0 | 46.53 | 0 | 0 | 32.45 | 0 | 0
2025-11-20 23:00 | 44.4 | 0 | 0 | 44.4 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 01:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 02:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 03:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 04:00 | 40.87 | 0 | 0 | 40.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 05:00 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 06:00 | 42.52 | 0 | 0 | 42.52 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 07:00 | 44.33 | 0 | 0 | 44.33 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 08:00 | 46.24 | 17.32 | 17.32 | 28.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 09:00 | 48.2 | 48.77 | 48.77 | 0 | 0.57 | 0 | 32.99 | 0 | 0
2025-11-21 10:00 | 50.14 | 23.17 | 23.17 | 26.46 | 0 | 0.51 | 32.45 | 0 | 0
2025-11-21 11:00 | 52.05 | 38.27 | 38.27 | 13.77 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 12:00 | 54.94 | 42.45 | 42.45 | 12.5 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 13:00 | 56.15 | 63.4 | 63.4 | 0 | 7.26 | 0 | 39.35 | 0 | 0
2025-11-21 14:00 | 56.48 | 60.74 | 60.74 | 0 | 4.26 | 0 | 43.4 | 0 | 0
2025-11-21 15:00 | 57.24 | 52.79 | 52.79 | 0 | 0 | 4.45 | 38.71 | 0 | 0
2025-11-21 16:00 | 56.12 | 3.04 | 3.04 | 47.13 | 0 | 5.95 | 32.45 | 0 | 0
2025-11-21 17:00 | 55.99 | 0 | 0 | 55.99 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 18:00 | 54.29 | 0 | 0 | 54.29 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 19:00 | 52.13 | 0 | 0 | 52.13 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 20:00 | 51.02 | 0 | 0 | 51.02 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 21:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 22:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 32.45 | 0 | 0
2025-11-21 23:00 | 45.2 | 0 | 0 | 45.2 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 | 42.99 | 0 | 0 | 42.99 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 01:00 | 41.42 | 0 | 0 | 41.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 02:00 | 40.25 | 0 | 0 | 40.25 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 03:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 04:00 | 40.61 | 0 | 0 | 40.61 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 05:00 | 41.1 | 0 | 0 | 41.1 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 06:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 07:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 08:00 | 45.36 | 0 | 0 | 45.36 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 09:00 | 47.43 | 4.29 | 4.29 | 43.14 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 10:00 | 48.41 | 21.86 | 21.86 | 26.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 11:00 | 50.44 | 49.94 | 49.94 | 0.5 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 12:00 | 52.25 | 49.09 | 49.09 | 3.17 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 13:00 | 53.45 | 33.62 | 33.62 | 19.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 14:00 | 55.24 | 57.32 | 57.32 | 0 | 2.09 | 0 | 34.43 | 0 | 0
2025-11-22 15:00 | 54.7 | 4.39 | 4.39 | 48.42 | 0 | 1.88 | 32.45 | 0 | 0
2025-11-22 16:00 | 53.51 | 1.74 | 1.74 | 51.78 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 17:00 | 53.76 | 0 | 0 | 53.76 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 18:00 | 52.61 | 0 | 0 | 52.61 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 19:00 | 50.72 | 0 | 0 | 50.72 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 20:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 21:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 22:00 | 44.87 | 0 | 0 | 44.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-22 23:00 | 44.12 | 0 | 0 | 44.12 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 01:00 | 41.59 | 0 | 0 | 41.59 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 02:00 | 41.55 | 0 | 0 | 41.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 03:00 | 40.77 | 0 | 0 | 40.77 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 04:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 05:00 | 41.85 | 0 | 0 | 41.85 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 06:00 | 41.89 | 0 | 0 | 41.89 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 07:00 | 43.41 | 0 | 0 | 43.41 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 08:00 | 43.89 | 37.79 | 37.79 | 6.1 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 09:00 | 45.21 | 67.53 | 67.53 | 0 | 22.32 | 0 | 53.65 | 0 | 0
2025-11-23 10:00 | 46.82 | 57.62 | 57.62 | 0 | 10.79 | 0 | 63.91 | 0 | 0
2025-11-23 11:00 | 47.88 | 44.27 | 44.27 | 0 | 0 | 3.61 | 60.11 | 0 | 0
2025-11-23 12:00 | 47.53 | 47.31 | 47.31 | 0 | 0 | 0.22 | 59.87 | 0 | 0
2025-11-23 13:00 | 49.11 | 61.03 | 61.03 | 0 | 11.91 | 0 | 71.19 | 0 | 0
2025-11-23 14:00 | 48.73 | 74.86 | 74.86 | 0 | 26.12 | 0 | 96.01 | 0 | 0
2025-11-23 15:00 | 49.87 | 68.79 | 68.79 | 0 | 18.91 | 0 | 113.98 | 0 | 0
2025-11-23 16:00 | 48.97 | 5.72 | 5.72 | 0 | 0 | 43.25 | 68.46 | 0 | 0
2025-11-23 17:00 | 48.3 | 0 | 0 | 14.1 | 0 | 34.21 | 32.45 | 0 | 0
2025-11-23 18:00 | 48.42 | 0 | 0 | 48.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 19:00 | 47.24 | 0 | 0 | 47.24 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 20:00 | 47.43 | 0 | 0 | 47.43 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 21:00 | 45.72 | 0 | 0 | 45.72 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 22:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 32.45 | 0 | 0
2025-11-23 23:00 | 43.62 | 0 | 0 | 43.62 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 01:00 | 40.54 | 0 | 0 | 40.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 02:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 03:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 04:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 05:00 | 41.6 | 0 | 0 | 41.6 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 06:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 07:00 | 42.75 | 0 | 0 | 42.75 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 08:00 | 44.51 | 3.59 | 3.59 | 40.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 09:00 | 45.91 | 22.64 | 22.64 | 23.27 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 10:00 | 48.78 | 8.72 | 8.72 | 40.06 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 11:00 | 49.77 | 22.27 | 22.27 | 27.5 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 12:00 | 50.33 | 27.16 | 27.16 | 23.17 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 13:00 | 51.77 | 46.92 | 46.92 | 4.85 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 14:00 | 51.39 | 71.88 | 71.88 | 0 | 20.49 | 0 | 51.92 | 0 | 0
2025-11-24 15:00 | 51.93 | 65.1 | 65.1 | 0 | 13.18 | 0 | 64.44 | 0 | 0
2025-11-24 16:00 | 52.12 | 1.83 | 1.83 | 19.9 | 0 | 30.39 | 32.45 | 0 | 0
2025-11-24 17:00 | 51.7 | 0 | 0 | 51.7 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 18:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 19:00 | 49.44 | 0 | 0 | 49.44 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 20:00 | 47.93 | 0 | 0 | 47.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 21:00 | 46.28 | 0 | 0 | 46.28 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 22:00 | 44.67 | 0 | 0 | 44.67 | 0 | 0 | 32.45 | 0 | 0
2025-11-24 23:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 | 42.07 | 0 | 0 | 42.07 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 01:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 02:00 | 40.57 | 0 | 0 | 40.57 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 03:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 04:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 05:00 | 41.25 | 0 | 0 | 41.25 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 06:00 | 42.69 | 0 | 0 | 42.69 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 07:00 | 43.16 | 0 | 0 | 43.16 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 08:00 | 44.12 | 0.32 | 0.32 | 43.8 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 09:00 | 45.69 | 0.96 | 0.96 | 44.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 10:00 | 46.18 | 1.84 | 1.84 | 44.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 11:00 | 48.42 | 7.85 | 7.85 | 40.57 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 12:00 | 48.67 | 8.52 | 8.52 | 40.15 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 13:00 | 48.83 | 43.67 | 43.67 | 5.15 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 14:00 | 49.43 | 52.03 | 52.03 | 0 | 2.6 | 0 | 34.92 | 0 | 0
2025-11-25 15:00 | 49.37 | 37.53 | 37.53 | 9.5 | 0 | 2.34 | 32.45 | 0 | 0
2025-11-25 16:00 | 50.17 | 1.2 | 1.2 | 48.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 17:00 | 49.06 | 0 | 0 | 49.06 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 18:00 | 48.65 | 0 | 0 | 48.65 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 19:00 | 48.05 | 0 | 0 | 48.05 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 20:00 | 46.38 | 0 | 0 | 46.38 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 21:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 22:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 32.45 | 0 | 0
2025-11-25 23:00 | 42.3 | 0 | 0 | 42.3 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 | 41.98 | 0 | 0 | 41.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 01:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 02:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 03:00 | 40.18 | 0 | 0 | 40.18 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 04:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 05:00 | 41.61 | 0 | 0 | 41.61 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 06:00 | 41.26 | 0 | 0 | 41.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 07:00 | 42.85 | 0 | 0 | 42.85 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 08:00 | 44.68 | 29.67 | 29.67 | 15.02 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 09:00 | 45.98 | 55.08 | 55.08 | 0 | 9.1 | 0 | 41.09 | 0 | 0
2025-11-26 10:00 | 47.33 | 61.87 | 61.87 | 0 | 14.54 | 0 | 54.9 | 0 | 0
2025-11-26 11:00 | 49.7 | 51.38 | 51.38 | 0 | 1.68 | 0 | 56.5 | 0 | 0
2025-11-26 12:00 | 49.67 | 46.69 | 46.69 | 0 | 0 | 2.97 | 53.37 | 0 | 0
2025-11-26 13:00 | 50.7 | 38.99 | 38.99 | 0 | 0 | 11.71 | 41.04 | 0 | 0
2025-11-26 14:00 | 50.46 | 52.3 | 52.3 | 0 | 1.83 | 0 | 42.78 | 0 | 0
2025-11-26 15:00 | 50.28 | 30.58 | 30.58 | 9.88 | 0 | 9.82 | 32.45 | 0 | 0
2025-11-26 16:00 | 50.46 | 1.09 | 1.09 | 49.36 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 17:00 | 50.49 | 0 | 0 | 50.49 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 18:00 | 49.56 | 0 | 0 | 49.56 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 19:00 | 48.53 | 0 | 0 | 48.53 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 20:00 | 46.99 | 0 | 0 | 46.99 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 21:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 22:00 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 32.45 | 0 | 0
2025-11-26 23:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 | 42.23 | 0 | 0 | 42.23 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 01:00 | 40.34 | 0 | 0 | 40.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 02:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 03:00 | 39.72 | 0 | 0 | 39.72 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 04:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 05:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 06:00 | 42.59 | 0 | 0 | 42.59 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 07:00 | 42.93 | 0 | 0 | 42.93 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 08:00 | 44.85 | 9.88 | 9.88 | 34.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 09:00 | 46.92 | 22.21 | 22.21 | 24.71 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 10:00 | 48.13 | 37.63 | 37.63 | 10.5 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 11:00 | 50.45 | 52.6 | 52.6 | 0 | 2.16 | 0 | 34.5 | 0 | 0
2025-11-27 12:00 | 52.07 | 46.44 | 46.44 | 3.68 | 0 | 1.95 | 32.45 | 0 | 0
2025-11-27 13:00 | 53.31 | 48.34 | 48.34 | 4.97 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 14:00 | 54.22 | 47.5 | 47.5 | 6.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 15:00 | 55.3 | 47.59 | 47.59 | 7.72 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 16:00 | 54.14 | 3.49 | 3.49 | 50.66 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 17:00 | 53.85 | 0 | 0 | 53.85 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 18:00 | 52.36 | 0 | 0 | 52.36 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 19:00 | 49.79 | 0 | 0 | 49.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 20:00 | 48.83 | 0 | 0 | 48.83 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 21:00 | 45.91 | 0 | 0 | 45.91 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 22:00 | 45.08 | 0 | 0 | 45.08 | 0 | 0 | 32.45 | 0 | 0
2025-11-27 23:00 | 42.88 | 0 | 0 | 42.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 | 41.64 | 0 | 0 | 41.64 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 01:00 | 40.06 | 0 | 0 | 40.06 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 02:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 03:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 04:00 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 05:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 06:00 | 41.87 | 0 | 0 | 41.87 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 07:00 | 43.11 | 0 | 0 | 43.11 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 08:00 | 43.13 | 35.85 | 35.85 | 7.28 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 09:00 | 46.98 | 76.71 | 76.71 | 0 | 29.73 | 0 | 60.7 | 0 | 0
2025-11-28 10:00 | 47.9 | 64.69 | 64.69 | 0 | 16.79 | 0 | 76.64 | 0 | 0
2025-11-28 11:00 | 49.58 | 49.3 | 49.3 | 0 | 0 | 0.28 | 76.35 | 0 | 0
2025-11-28 12:00 | 50.55 | 48.13 | 48.13 | 0 | 0 | 2.42 | 73.8 | 0 | 0
2025-11-28 13:00 | 50.79 | 54.48 | 54.48 | 0 | 3.69 | 0 | 77.31 | 0 | 0
2025-11-28 14:00 | 52.75 | 37.12 | 37.12 | 0 | 0 | 15.62 | 60.86 | 0 | 0
2025-11-28 15:00 | 52.37 | 5.43 | 5.43 | 19.94 | 0 | 26.99 | 32.45 | 0 | 0
2025-11-28 16:00 | 52.68 | 0.21 | 0.21 | 52.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 17:00 | 51.61 | 0 | 0 | 51.61 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 18:00 | 50.74 | 0 | 0 | 50.74 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 19:00 | 48.84 | 0 | 0 | 48.84 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 20:00 | 48.07 | 0 | 0 | 48.07 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 21:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 22:00 | 45.47 | 0 | 0 | 45.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-28 23:00 | 43.99 | 0 | 0 | 43.99 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 | 42.27 | 0 | 0 | 42.27 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 01:00 | 41.22 | 0 | 0 | 41.22 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 02:00 | 39.99 | 0 | 0 | 39.99 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 03:00 | 40.42 | 0 | 0 | 40.42 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 04:00 | 39.98 | 0 | 0 | 39.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 05:00 | 39.81 | 0 | 0 | 39.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 06:00 | 42.2 | 0 | 0 | 42.2 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 07:00 | 43.12 | 0 | 0 | 43.12 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 08:00 | 43.8 | 0.28 | 0.28 | 43.52 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 09:00 | 44.49 | 3 | 3 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 10:00 | 46.06 | 5.74 | 5.74 | 40.32 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 11:00 | 46.56 | 7.02 | 7.02 | 39.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 12:00 | 48.88 | 7.9 | 7.9 | 40.98 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 13:00 | 48.3 | 6.42 | 6.42 | 41.88 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 14:00 | 49.67 | 4.51 | 4.51 | 45.16 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 15:00 | 49.25 | 1.8 | 1.8 | 47.44 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 16:00 | 48.81 | 0 | 0 | 48.81 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 17:00 | 49.22 | 0 | 0 | 49.22 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 18:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 19:00 | 47.9 | 0 | 0 | 47.9 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 20:00 | 45.72 | 0 | 0 | 45.72 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 21:00 | 44.73 | 0 | 0 | 44.73 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 22:00 | 42.62 | 0 | 0 | 42.62 | 0 | 0 | 32.45 | 0 | 0
2025-11-29 23:00 | 41.47 | 0 | 0 | 41.47 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 | 42.21 | 0 | 0 | 42.21 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 01:00 | 41.51 | 0 | 0 | 41.51 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 02:00 | 39.97 | 0 | 0 | 39.97 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 03:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 04:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 05:00 | 40.9 | 0 | 0 | 40.9 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 06:00 | 41.06 | 0 | 0 | 41.06 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 07:00 | 42.5 | 0 | 0 | 42.5 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 08:00 | 43.56 | 0 | 0 | 43.56 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 09:00 | 44.49 | 4.08 | 4.08 | 40.41 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 10:00 | 45.65 | 37.02 | 37.02 | 8.63 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 11:00 | 47.06 | 24.37 | 24.37 | 22.69 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 12:00 | 47.24 | 21.5 | 21.5 | 25.74 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 13:00 | 48.55 | 28.78 | 28.78 | 19.76 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 14:00 | 48.45 | 41.9 | 41.9 | 6.54 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 15:00 | 48.87 | 45.52 | 45.52 | 3.34 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 16:00 | 49.37 | 0.67 | 0.67 | 48.71 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 17:00 | 48.24 | 0 | 0 | 48.24 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 18:00 | 48.19 | 0 | 0 | 48.19 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 19:00 | 46.02 | 0 | 0 | 46.02 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 20:00 | 45.68 | 0 | 0 | 45.68 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 21:00 | 44.79 | 0 | 0 | 44.79 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 22:00 | 44.53 | 0 | 0 | 44.53 | 0 | 0 | 32.45 | 0 | 0
2025-11-30 23:00 | 41.4 | 0 | 0 | 41.4 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 | 41.18 | 0 | 0 | 41.18 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 01:00 | 41.09 | 0 | 0 | 41.09 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 02:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 03:00 | 39.52 | 0 | 0 | 39.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 04:00 | 39.98 | 0 | 0 | 39.98 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 05:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 06:00 | 42.02 | 0 | 0 | 42.02 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 07:00 | 42.59 | 0 | 0 | 42.59 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 08:00 | 44.36 | 27.53 | 27.53 | 16.82 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 09:00 | 44.94 | 69.51 | 69.51 | 0 | 24.57 | 0 | 55.79 | 0 | 0
2025-12-01 10:00 | 46.17 | 65.44 | 65.44 | 0 | 19.27 | 0 | 74.1 | 0 | 0
2025-12-01 11:00 | 47.76 | 55.53 | 55.53 | 0 | 7.77 | 0 | 81.48 | 0 | 0
2025-12-01 12:00 | 48.44 | 33.58 | 33.58 | 0 | 0 | 14.85 | 65.84 | 0 | 0
2025-12-01 13:00 | 50.14 | 25.47 | 25.47 | 0 | 0 | 24.67 | 39.87 | 0 | 0
2025-12-01 14:00 | 50.26 | 1.23 | 1.23 | 41.98 | 0 | 7.05 | 32.45 | 0 | 0
2025-12-01 15:00 | 50.3 | 0 | 0 | 50.3 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 16:00 | 50.7 | 1.95 | 1.95 | 48.75 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 17:00 | 49.32 | 0 | 0 | 49.32 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 18:00 | 49.4 | 0 | 0 | 49.4 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 19:00 | 47.64 | 0 | 0 | 47.64 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 20:00 | 47.12 | 0 | 0 | 47.12 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 21:00 | 44.92 | 0 | 0 | 44.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 22:00 | 44.01 | 0 | 0 | 44.01 | 0 | 0 | 32.45 | 0 | 0
2025-12-01 23:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 | 41.43 | 0 | 0 | 41.43 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 01:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 02:00 | 38.88 | 0 | 0 | 38.88 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 03:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 04:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 05:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 06:00 | 41.4 | 0 | 0 | 41.4 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 07:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 08:00 | 42.75 | 12.74 | 12.74 | 30 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 09:00 | 44.66 | 69.63 | 69.63 | 0 | 24.97 | 0 | 56.17 | 0 | 0
2025-12-02 10:00 | 45.23 | 70 | 70 | 0 | 24.77 | 0 | 79.7 | 0 | 0
2025-12-02 11:00 | 46.76 | 56.85 | 56.85 | 0 | 10.09 | 0 | 89.28 | 0 | 0
2025-12-02 12:00 | 46.93 | 2.61 | 2.61 | 0 | 0 | 44.32 | 42.63 | 0 | 0
2025-12-02 13:00 | 48.05 | 14.35 | 14.35 | 24.04 | 0 | 9.67 | 32.45 | 0 | 0
2025-12-02 14:00 | 48.07 | 23.8 | 23.8 | 24.27 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 15:00 | 48.1 | 2.32 | 2.32 | 45.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 16:00 | 47.67 | 2.22 | 2.22 | 45.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 17:00 | 47.66 | 0 | 0 | 47.66 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 18:00 | 47.62 | 0 | 0 | 47.62 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 19:00 | 46.27 | 0 | 0 | 46.27 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 20:00 | 45.65 | 0 | 0 | 45.65 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 21:00 | 44.36 | 0 | 0 | 44.36 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 22:00 | 43.27 | 0 | 0 | 43.27 | 0 | 0 | 32.45 | 0 | 0
2025-12-02 23:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 01:00 | 40.17 | 0 | 0 | 40.17 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 02:00 | 39.71 | 0 | 0 | 39.71 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 03:00 | 39.07 | 0 | 0 | 39.07 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 04:00 | 39.52 | 0 | 0 | 39.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 05:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 06:00 | 41.38 | 0 | 0 | 41.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 07:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 08:00 | 42.64 | 1.8 | 1.8 | 40.84 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 09:00 | 44.92 | 6.22 | 6.22 | 38.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 10:00 | 45.58 | 10.59 | 10.59 | 34.99 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 11:00 | 46.2 | 11.99 | 11.99 | 34.2 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 12:00 | 48.25 | 14.2 | 14.2 | 34.04 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 13:00 | 48.98 | 10.9 | 10.9 | 38.07 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 14:00 | 48.78 | 5.48 | 5.48 | 43.3 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 15:00 | 49.15 | 2.36 | 2.36 | 46.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 16:00 | 49.04 | 0 | 0 | 49.04 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 17:00 | 48.94 | 0 | 0 | 48.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 18:00 | 47.94 | 0 | 0 | 47.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 19:00 | 46.03 | 0 | 0 | 46.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 20:00 | 46.63 | 0 | 0 | 46.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 21:00 | 44.96 | 0 | 0 | 44.96 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-03 23:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 01:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 02:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 03:00 | 39.7 | 0 | 0 | 39.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 05:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 06:00 | 41.07 | 0 | 0 | 41.07 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 07:00 | 41.72 | 0 | 0 | 41.72 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 08:00 | 43.38 | 15.74 | 15.74 | 27.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 09:00 | 44.06 | 9.59 | 9.59 | 34.47 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 10:00 | 46.05 | 16.52 | 16.52 | 29.53 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 11:00 | 47.9 | 19.85 | 19.85 | 28.05 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 12:00 | 49.03 | 53.12 | 53.12 | 0 | 4.09 | 0 | 36.34 | 0 | 0
2025-12-04 13:00 | 49.25 | 64.73 | 64.73 | 0 | 15.48 | 0 | 51.04 | 0 | 0
2025-12-04 14:00 | 49.64 | 69.63 | 69.63 | 0 | 19.99 | 0 | 70.03 | 0 | 0
2025-12-04 15:00 | 50.43 | 60.34 | 60.34 | 0 | 9.9 | 0 | 79.44 | 0 | 0
2025-12-04 16:00 | 50.51 | 0.62 | 0.62 | 5.24 | 0 | 44.64 | 32.45 | 0 | 0
2025-12-04 17:00 | 49.85 | 0 | 0 | 49.85 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 18:00 | 48.47 | 0 | 0 | 48.47 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 19:00 | 47.69 | 0 | 0 | 47.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 20:00 | 46.93 | 0 | 0 | 46.93 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 21:00 | 44.83 | 0 | 0 | 44.83 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 22:00 | 42.49 | 0 | 0 | 42.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-04 23:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 01:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 02:00 | 39.42 | 0 | 0 | 39.42 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 03:00 | 39.12 | 0 | 0 | 39.12 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 04:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 05:00 | 40.03 | 0 | 0 | 40.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 06:00 | 41.36 | 0 | 0 | 41.36 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 07:00 | 42 | 0 | 0 | 42 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 08:00 | 44 | 2.43 | 2.43 | 41.57 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 09:00 | 44.89 | 13.4 | 13.4 | 31.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 10:00 | 46.43 | 63.25 | 63.25 | 0 | 16.82 | 0 | 48.43 | 0 | 0
2025-12-05 11:00 | 47.88 | 56.42 | 56.42 | 0 | 8.53 | 0 | 56.53 | 0 | 0
2025-12-05 12:00 | 48.74 | 31.17 | 31.17 | 0 | 0 | 17.57 | 38.04 | 0 | 0
2025-12-05 13:00 | 50.92 | 17 | 17 | 28.61 | 0 | 5.31 | 32.45 | 0 | 0
2025-12-05 14:00 | 52.53 | 27.71 | 27.71 | 24.82 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 15:00 | 51.98 | 0 | 0 | 51.98 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 16:00 | 51.85 | 0 | 0 | 51.85 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 17:00 | 50.57 | 0 | 0 | 50.57 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 18:00 | 49.53 | 0 | 0 | 49.53 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 19:00 | 48.71 | 0 | 0 | 48.71 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 20:00 | 47.61 | 0 | 0 | 47.61 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 21:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 22:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-05 23:00 | 41.97 | 0 | 0 | 41.97 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 | 40.76 | 0 | 0 | 40.76 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 01:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 02:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 03:00 | 38.57 | 0 | 0 | 38.57 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 04:00 | 39.33 | 0 | 0 | 39.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 05:00 | 39.68 | 0 | 0 | 39.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 06:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 07:00 | 41.74 | 0 | 0 | 41.74 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 08:00 | 42.92 | 0 | 0 | 42.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 09:00 | 43.94 | 1.56 | 1.56 | 42.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 10:00 | 45.83 | 2.97 | 2.97 | 42.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 11:00 | 47.27 | 6.58 | 6.58 | 40.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 12:00 | 48.37 | 8.09 | 8.09 | 40.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 13:00 | 50.11 | 45.2 | 45.2 | 4.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 14:00 | 49.32 | 48.49 | 48.49 | 0.83 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 15:00 | 49.49 | 36.19 | 36.19 | 13.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 16:00 | 50.27 | 0.51 | 0.51 | 49.76 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 17:00 | 49.7 | 0 | 0 | 49.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 18:00 | 48.88 | 0 | 0 | 48.88 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 19:00 | 47.16 | 0 | 0 | 47.16 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 20:00 | 45.55 | 0 | 0 | 45.55 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 21:00 | 44.52 | 0 | 0 | 44.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 22:00 | 42.86 | 0 | 0 | 42.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-06 23:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 | 40.26 | 0 | 0 | 40.26 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 01:00 | 39.67 | 0 | 0 | 39.67 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 02:00 | 40.45 | 0 | 0 | 40.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 03:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 04:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 05:00 | 40.02 | 0 | 0 | 40.02 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 06:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 07:00 | 41.45 | 0 | 0 | 41.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 08:00 | 42.3 | 0.81 | 0.81 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 09:00 | 43.09 | 3.57 | 3.57 | 39.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 10:00 | 43.45 | 7.95 | 7.95 | 35.51 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 11:00 | 44.43 | 11.24 | 11.24 | 33.19 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 12:00 | 45.63 | 11.75 | 11.75 | 33.88 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 13:00 | 45.43 | 8.79 | 8.79 | 36.65 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 14:00 | 45.09 | 6.12 | 6.12 | 38.97 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 15:00 | 45.39 | 1.97 | 1.97 | 43.43 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 16:00 | 44.5 | 0 | 0 | 44.5 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 17:00 | 44.7 | 0 | 0 | 44.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 18:00 | 45.09 | 0 | 0 | 45.09 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 19:00 | 45.01 | 0 | 0 | 45.01 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 20:00 | 43.35 | 0 | 0 | 43.35 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 21:00 | 42.8 | 0 | 0 | 42.8 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 22:00 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 32.45 | 0 | 0
2025-12-07 23:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 | 41.32 | 0 | 0 | 41.32 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 01:00 | 39.72 | 0 | 0 | 39.72 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 02:00 | 39.24 | 0 | 0 | 39.24 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 03:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 04:00 | 39.58 | 0 | 0 | 39.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 05:00 | 40.29 | 0 | 0 | 40.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 06:00 | 39.9 | 0 | 0 | 39.9 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 07:00 | 41.29 | 0 | 0 | 41.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 08:00 | 43.17 | 5.55 | 5.55 | 37.62 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 09:00 | 43.99 | 7.12 | 7.12 | 36.87 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 10:00 | 45.18 | 3.51 | 3.51 | 41.67 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 11:00 | 47.22 | 17.79 | 17.79 | 29.44 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 12:00 | 48.39 | 20.01 | 20.01 | 28.39 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 13:00 | 48.48 | 32.84 | 32.84 | 15.65 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 14:00 | 49.36 | 24.34 | 24.34 | 25.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 15:00 | 48.84 | 4.05 | 4.05 | 44.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 16:00 | 48.81 | 0.04 | 0.04 | 48.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 17:00 | 48.77 | 0 | 0 | 48.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 18:00 | 47.86 | 0 | 0 | 47.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 19:00 | 46.23 | 0 | 0 | 46.23 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 20:00 | 45.07 | 0 | 0 | 45.07 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 21:00 | 43.53 | 0 | 0 | 43.53 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 22:00 | 42.94 | 0 | 0 | 42.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-08 23:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 | 39.79 | 0 | 0 | 39.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 01:00 | 38.58 | 0 | 0 | 38.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 02:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 03:00 | 37.95 | 0 | 0 | 37.95 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 04:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 05:00 | 40.33 | 0 | 0 | 40.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 06:00 | 41.13 | 0 | 0 | 41.13 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 07:00 | 40.41 | 0 | 0 | 40.41 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 08:00 | 42.66 | 12.51 | 12.51 | 30.15 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 09:00 | 43.3 | 33.35 | 33.35 | 9.95 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 10:00 | 44.49 | 8.56 | 8.56 | 35.93 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 11:00 | 46.23 | 14.13 | 14.13 | 32.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 12:00 | 47.94 | 25.88 | 25.88 | 22.07 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 13:00 | 48.43 | 35.95 | 35.95 | 12.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 14:00 | 48.27 | 66.16 | 66.16 | 0 | 17.89 | 0 | 49.44 | 0 | 0
2025-12-09 15:00 | 49.16 | 60.31 | 60.31 | 0 | 11.16 | 0 | 60.04 | 0 | 0
2025-12-09 16:00 | 47.51 | 1.87 | 1.87 | 19.42 | 0 | 26.21 | 32.45 | 0 | 0
2025-12-09 17:00 | 47.75 | 0 | 0 | 47.75 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 18:00 | 46.92 | 0 | 0 | 46.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 19:00 | 46.33 | 0 | 0 | 46.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 20:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 21:00 | 43.72 | 0 | 0 | 43.72 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 22:00 | 42.42 | 0 | 0 | 42.42 | 0 | 0 | 32.45 | 0 | 0
2025-12-09 23:00 | 41.33 | 0 | 0 | 41.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 | 40.47 | 0 | 0 | 40.47 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 01:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 02:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 03:00 | 38.96 | 0 | 0 | 38.96 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 04:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 05:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 06:00 | 40.17 | 0 | 0 | 40.17 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 07:00 | 41.81 | 0 | 0 | 41.81 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 08:00 | 41.9 | 15.38 | 15.38 | 26.53 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 09:00 | 44.69 | 36.51 | 36.51 | 8.19 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 10:00 | 44.48 | 33.48 | 33.48 | 11 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 11:00 | 46.26 | 9.01 | 9.01 | 37.26 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 12:00 | 47.09 | 40.82 | 40.82 | 6.27 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 13:00 | 49.53 | 18.92 | 18.92 | 30.61 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 14:00 | 48.74 | 39.35 | 39.35 | 9.39 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 15:00 | 48.93 | 46.36 | 46.36 | 2.57 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 16:00 | 48.8 | 1.51 | 1.51 | 47.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 17:00 | 48.48 | 0 | 0 | 48.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 18:00 | 47.4 | 0 | 0 | 47.4 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 19:00 | 46.37 | 0 | 0 | 46.37 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 20:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 21:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 22:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 32.45 | 0 | 0
2025-12-10 23:00 | 41.75 | 0 | 0 | 41.75 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 01:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 02:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 03:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 05:00 | 39.04 | 0 | 0 | 39.04 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 06:00 | 39.54 | 0 | 0 | 39.54 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 07:00 | 41.14 | 0 | 0 | 41.14 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 08:00 | 43.3 | 9.29 | 9.29 | 34.01 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 09:00 | 44.24 | 53.27 | 53.27 | 0 | 9.03 | 0 | 41.03 | 0 | 0
2025-12-11 10:00 | 46.54 | 37.5 | 37.5 | 0.89 | 0 | 8.15 | 32.45 | 0 | 0
2025-12-11 11:00 | 47.04 | 53.11 | 53.11 | 0 | 6.08 | 0 | 38.22 | 0 | 0
2025-12-11 12:00 | 49.39 | 32.9 | 32.9 | 11 | 0 | 5.48 | 32.45 | 0 | 0
2025-12-11 13:00 | 49.69 | 36.55 | 36.55 | 13.15 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 14:00 | 50.88 | 25.76 | 25.76 | 25.12 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 15:00 | 51.13 | 3.38 | 3.38 | 47.75 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 16:00 | 51.09 | 0.25 | 0.25 | 50.84 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 17:00 | 50.14 | 0 | 0 | 50.14 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 18:00 | 48.49 | 0 | 0 | 48.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 19:00 | 47.85 | 0 | 0 | 47.85 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 20:00 | 46.66 | 0 | 0 | 46.66 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 21:00 | 43.86 | 0 | 0 | 43.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 22:00 | 41.68 | 0 | 0 | 41.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-11 23:00 | 41.49 | 0 | 0 | 41.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 | 39.73 | 0 | 0 | 39.73 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 01:00 | 39.14 | 0 | 0 | 39.14 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 02:00 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 03:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 04:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 06:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 07:00 | 40.74 | 0 | 0 | 40.74 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 08:00 | 40.98 | 11.2 | 11.2 | 29.78 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 09:00 | 41.83 | 73.88 | 73.88 | 0 | 32.05 | 0 | 62.9 | 0 | 0
2025-12-12 10:00 | 43.21 | 67.45 | 67.45 | 0 | 24.24 | 0 | 85.93 | 0 | 0
2025-12-12 11:00 | 43.13 | 54.94 | 54.94 | 0 | 11.82 | 0 | 97.15 | 0 | 0
2025-12-12 12:00 | 43.31 | 50.5 | 50.5 | 0 | 7.19 | 0 | 103.99 | 0 | 0
2025-12-12 13:00 | 44.66 | 58.41 | 58.41 | 0 | 13.75 | 0 | 117.05 | 0 | 0
2025-12-12 14:00 | 44.82 | 68.25 | 68.25 | 0 | 23.43 | 0 | 139.31 | 0 | 0
2025-12-12 15:00 | 44.33 | 56.24 | 56.24 | 0 | 11.9 | 0 | 150.61 | 0 | 0
2025-12-12 16:00 | 44.62 | 0.66 | 0.66 | 0 | 0 | 43.96 | 104.34 | 0 | 0
2025-12-12 17:00 | 44.44 | 0 | 0 | 0 | 0 | 44.44 | 57.56 | 0 | 0
2025-12-12 18:00 | 44.39 | 0 | 0 | 20.53 | 0 | 23.86 | 32.45 | 0 | 0
2025-12-12 19:00 | 44 | 0 | 0 | 44 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 20:00 | 41.84 | 0 | 0 | 41.84 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 21:00 | 42.31 | 0 | 0 | 42.31 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 22:00 | 41.86 | 0 | 0 | 41.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-12 23:00 | 40.52 | 0 | 0 | 40.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 | 39.86 | 0 | 0 | 39.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 01:00 | 39.49 | 0 | 0 | 39.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 02:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 03:00 | 39.25 | 0 | 0 | 39.25 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 04:00 | 39.22 | 0 | 0 | 39.22 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 05:00 | 39.06 | 0 | 0 | 39.06 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 06:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 07:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 08:00 | 41.65 | 8.13 | 8.13 | 33.53 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 09:00 | 42.23 | 52.39 | 52.39 | 0 | 10.16 | 0 | 42.1 | 0 | 0
2025-12-13 10:00 | 44.08 | 56.58 | 56.58 | 0 | 12.5 | 0 | 53.97 | 0 | 0
2025-12-13 11:00 | 45.01 | 48.76 | 48.76 | 0 | 3.76 | 0 | 57.54 | 0 | 0
2025-12-13 12:00 | 46.08 | 44.83 | 44.83 | 0 | 0 | 1.24 | 56.23 | 0 | 0
2025-12-13 13:00 | 47.03 | 45.63 | 45.63 | 0 | 0 | 1.4 | 54.76 | 0 | 0
2025-12-13 14:00 | 46.69 | 45.2 | 45.2 | 0 | 0 | 1.48 | 53.2 | 0 | 0
2025-12-13 15:00 | 47.96 | 36.52 | 36.52 | 0 | 0 | 11.44 | 41.15 | 0 | 0
2025-12-13 16:00 | 46.82 | 0.59 | 0.59 | 37.96 | 0 | 8.27 | 32.45 | 0 | 0
2025-12-13 17:00 | 45.67 | 0 | 0 | 45.67 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 18:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 19:00 | 44.74 | 0 | 0 | 44.74 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 20:00 | 44.27 | 0 | 0 | 44.27 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 21:00 | 42.44 | 0 | 0 | 42.44 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 22:00 | 41.67 | 0 | 0 | 41.67 | 0 | 0 | 32.45 | 0 | 0
2025-12-13 23:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 | 39.56 | 0 | 0 | 39.56 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 01:00 | 39.44 | 0 | 0 | 39.44 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 02:00 | 38.89 | 0 | 0 | 38.89 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 03:00 | 39 | 0 | 0 | 39 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 04:00 | 38.41 | 0 | 0 | 38.41 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 05:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 06:00 | 39.1 | 0 | 0 | 39.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 07:00 | 40.08 | 0 | 0 | 40.08 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 08:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 09:00 | 43.26 | 0 | 0 | 43.26 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 10:00 | 45.19 | 2.57 | 2.57 | 42.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 11:00 | 45.56 | 10.81 | 10.81 | 34.76 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 12:00 | 46.74 | 7.61 | 7.61 | 39.13 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 13:00 | 47.74 | 45.81 | 45.81 | 1.93 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 14:00 | 48.69 | 54.42 | 54.42 | 0 | 5.74 | 0 | 37.9 | 0 | 0
2025-12-14 15:00 | 48.35 | 37.93 | 37.93 | 5.24 | 0 | 5.18 | 32.45 | 0 | 0
2025-12-14 16:00 | 48.13 | 0.49 | 0.49 | 47.64 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 17:00 | 47.17 | 0 | 0 | 47.17 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 18:00 | 46.69 | 0 | 0 | 46.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 19:00 | 46.45 | 0 | 0 | 46.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 20:00 | 44.64 | 0 | 0 | 44.64 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 21:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 22:00 | 42.58 | 0 | 0 | 42.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-14 23:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 | 40.32 | 0 | 0 | 40.32 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 01:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 02:00 | 38.52 | 0 | 0 | 38.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 03:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 04:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 05:00 | 39.13 | 0 | 0 | 39.13 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 06:00 | 39.45 | 0 | 0 | 39.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 07:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 08:00 | 41.69 | 0 | 0 | 41.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 09:00 | 42.88 | 0.95 | 0.95 | 41.93 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 10:00 | 42.69 | 1.73 | 1.73 | 40.97 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 11:00 | 43.85 | 2.88 | 2.88 | 40.97 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 12:00 | 43.61 | 6.16 | 6.16 | 37.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 13:00 | 44.89 | 42.42 | 42.42 | 2.47 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 14:00 | 44.75 | 47.84 | 47.84 | 0 | 3.09 | 0 | 35.39 | 0 | 0
2025-12-15 15:00 | 44.97 | 40.21 | 40.21 | 1.96 | 0 | 2.79 | 32.45 | 0 | 0
2025-12-15 16:00 | 44.69 | 0.59 | 0.59 | 44.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 17:00 | 44.43 | 0 | 0 | 44.43 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 18:00 | 43.76 | 0 | 0 | 43.76 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 19:00 | 44.08 | 0 | 0 | 44.08 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 20:00 | 43.77 | 0 | 0 | 43.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 21:00 | 41.95 | 0 | 0 | 41.95 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 22:00 | 41.62 | 0 | 0 | 41.62 | 0 | 0 | 32.45 | 0 | 0
2025-12-15 23:00 | 40.66 | 0 | 0 | 40.66 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 01:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 02:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 03:00 | 37.86 | 0 | 0 | 37.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 04:00 | 37.34 | 0 | 0 | 37.34 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 05:00 | 39.57 | 0 | 0 | 39.57 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 06:00 | 39.8 | 0 | 0 | 39.8 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 07:00 | 40.63 | 0 | 0 | 40.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 08:00 | 40.81 | 0.55 | 0.55 | 40.25 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 09:00 | 42.42 | 4.72 | 4.72 | 37.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 10:00 | 44.84 | 11.31 | 11.31 | 33.53 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 11:00 | 47.3 | 12.25 | 12.25 | 35.05 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 12:00 | 47.29 | 14.59 | 14.59 | 32.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 13:00 | 49.12 | 15.33 | 15.33 | 33.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 14:00 | 49.12 | 6.08 | 6.08 | 43.04 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 15:00 | 49.62 | 2.94 | 2.94 | 46.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 16:00 | 49.97 | 0 | 0 | 49.97 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 17:00 | 48.51 | 0 | 0 | 48.51 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 18:00 | 47.29 | 0 | 0 | 47.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 19:00 | 47.02 | 0 | 0 | 47.02 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 20:00 | 44.86 | 0 | 0 | 44.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 21:00 | 43.88 | 0 | 0 | 43.88 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 22:00 | 41.56 | 0 | 0 | 41.56 | 0 | 0 | 32.45 | 0 | 0
2025-12-16 23:00 | 41.35 | 0 | 0 | 41.35 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 | 39.62 | 0 | 0 | 39.62 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 01:00 | 38.99 | 0 | 0 | 38.99 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 02:00 | 38.39 | 0 | 0 | 38.39 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 03:00 | 37.92 | 0 | 0 | 37.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 04:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 05:00 | 38.55 | 0 | 0 | 38.55 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 06:00 | 39.96 | 0 | 0 | 39.96 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 07:00 | 40.32 | 0 | 0 | 40.32 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 08:00 | 40.79 | 0 | 0 | 40.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 09:00 | 41.91 | 35.16 | 35.16 | 6.74 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 10:00 | 43.11 | 1.7 | 1.7 | 41.42 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 11:00 | 45.45 | 56.46 | 56.46 | 0 | 11.01 | 0 | 42.91 | 0 | 0
2025-12-17 12:00 | 45.58 | 53.24 | 53.24 | 0 | 7.66 | 0 | 50.19 | 0 | 0
2025-12-17 13:00 | 47.09 | 61.55 | 61.55 | 0 | 14.46 | 0 | 63.93 | 0 | 0
2025-12-17 14:00 | 47.51 | 71.57 | 71.57 | 0 | 24.07 | 0 | 86.79 | 0 | 0
2025-12-17 15:00 | 47.58 | 61.09 | 61.09 | 0 | 13.51 | 0 | 99.63 | 0 | 0
2025-12-17 16:00 | 47.66 | 1.39 | 1.39 | 0 | 0 | 46.27 | 50.92 | 0 | 0
2025-12-17 17:00 | 47.02 | 0 | 0 | 29.47 | 0 | 17.55 | 32.45 | 0 | 0
2025-12-17 18:00 | 44.8 | 0 | 0 | 44.8 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 19:00 | 44.98 | 0 | 0 | 44.98 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 20:00 | 44.19 | 0 | 0 | 44.19 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 21:00 | 43.57 | 0 | 0 | 43.57 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 22:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-17 23:00 | 39.74 | 0 | 0 | 39.74 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 01:00 | 37.91 | 0 | 0 | 37.91 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 02:00 | 39.01 | 0 | 0 | 39.01 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 03:00 | 38.61 | 0 | 0 | 38.61 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 04:00 | 38.42 | 0 | 0 | 38.42 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 05:00 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 06:00 | 40.1 | 0 | 0 | 40.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 07:00 | 40.97 | 0 | 0 | 40.97 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 08:00 | 42.1 | 7.54 | 7.54 | 34.55 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 09:00 | 43.03 | 71.08 | 71.08 | 0 | 28.05 | 0 | 59.1 | 0 | 0
2025-12-18 10:00 | 43.95 | 65.23 | 65.23 | 0 | 21.28 | 0 | 79.32 | 0 | 0
2025-12-18 11:00 | 45.78 | 52.28 | 52.28 | 0 | 6.49 | 0 | 85.49 | 0 | 0
2025-12-18 12:00 | 46.93 | 47.87 | 47.87 | 0 | 0.93 | 0 | 86.37 | 0 | 0
2025-12-18 13:00 | 47.31 | 55.93 | 55.93 | 0 | 8.62 | 0 | 94.56 | 0 | 0
2025-12-18 14:00 | 47.8 | 65.34 | 65.34 | 0 | 17.55 | 0 | 111.23 | 0 | 0
2025-12-18 15:00 | 48.73 | 54.97 | 54.97 | 0 | 6.24 | 0 | 117.16 | 0 | 0
2025-12-18 16:00 | 48.8 | 0.81 | 0.81 | 0 | 0 | 47.99 | 66.64 | 0 | 0
2025-12-18 17:00 | 47.03 | 0 | 0 | 14.55 | 0 | 32.48 | 32.45 | 0 | 0
2025-12-18 18:00 | 46.39 | 0 | 0 | 46.39 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 19:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 20:00 | 44.37 | 0 | 0 | 44.37 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 21:00 | 42.54 | 0 | 0 | 42.54 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 22:00 | 42.46 | 0 | 0 | 42.46 | 0 | 0 | 32.45 | 0 | 0
2025-12-18 23:00 | 40.58 | 0 | 0 | 40.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 | 39.53 | 0 | 0 | 39.53 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 01:00 | 39.48 | 0 | 0 | 39.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 02:00 | 37.95 | 0 | 0 | 37.95 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 03:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 04:00 | 37.54 | 0 | 0 | 37.54 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 05:00 | 38.51 | 0 | 0 | 38.51 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 06:00 | 38.52 | 0 | 0 | 38.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 07:00 | 40.5 | 0 | 0 | 40.5 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 08:00 | 41.31 | 7.38 | 7.38 | 33.93 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 09:00 | 41.98 | 55.49 | 55.49 | 0 | 13.51 | 0 | 45.29 | 0 | 0
2025-12-19 10:00 | 43.05 | 37.82 | 37.82 | 0 | 0 | 5.23 | 39.78 | 0 | 0
2025-12-19 11:00 | 44.38 | 48.92 | 48.92 | 0 | 4.54 | 0 | 44.09 | 0 | 0
2025-12-19 12:00 | 44.17 | 15.04 | 15.04 | 18.07 | 0 | 11.06 | 32.45 | 0 | 0
2025-12-19 13:00 | 45.4 | 19.94 | 19.94 | 25.46 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 14:00 | 46 | 10.28 | 10.28 | 35.71 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 15:00 | 44.87 | 2.72 | 2.72 | 42.15 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 16:00 | 45.99 | 0.47 | 0.47 | 45.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 17:00 | 44.46 | 0 | 0 | 44.46 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 18:00 | 44.68 | 0 | 0 | 44.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 19:00 | 43.41 | 0 | 0 | 43.41 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 20:00 | 43.82 | 0 | 0 | 43.82 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 21:00 | 41.54 | 0 | 0 | 41.54 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 22:00 | 40.27 | 0 | 0 | 40.27 | 0 | 0 | 32.45 | 0 | 0
2025-12-19 23:00 | 40.19 | 0 | 0 | 40.19 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 | 39.02 | 0 | 0 | 39.02 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 01:00 | 37.78 | 0 | 0 | 37.78 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 02:00 | 38.36 | 0 | 0 | 38.36 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 03:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 04:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 05:00 | 38.24 | 0 | 0 | 38.24 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 06:00 | 39.63 | 0 | 0 | 39.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 07:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 08:00 | 41.83 | 6.94 | 6.94 | 34.89 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 09:00 | 42.45 | 57.74 | 57.74 | 0 | 15.29 | 0 | 46.97 | 0 | 0
2025-12-20 10:00 | 42.6 | 57.04 | 57.04 | 0 | 14.45 | 0 | 60.7 | 0 | 0
2025-12-20 11:00 | 45.24 | 50.14 | 50.14 | 0 | 4.9 | 0 | 65.35 | 0 | 0
2025-12-20 12:00 | 46.87 | 41.76 | 41.76 | 0 | 0 | 5.11 | 59.97 | 0 | 0
2025-12-20 13:00 | 47.6 | 50.76 | 50.76 | 0 | 3.16 | 0 | 62.97 | 0 | 0
2025-12-20 14:00 | 47.76 | 61.07 | 61.07 | 0 | 13.31 | 0 | 75.61 | 0 | 0
2025-12-20 15:00 | 47.13 | 44.41 | 44.41 | 0 | 0 | 2.72 | 72.75 | 0 | 0
2025-12-20 16:00 | 47.27 | 0.82 | 0.82 | 8.16 | 0 | 38.28 | 32.45 | 0 | 0
2025-12-20 17:00 | 47.96 | 0 | 0 | 47.96 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 18:00 | 45.43 | 0 | 0 | 45.43 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 19:00 | 44.47 | 0 | 0 | 44.47 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 20:00 | 44.28 | 0 | 0 | 44.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 21:00 | 42.31 | 0 | 0 | 42.31 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 22:00 | 40.69 | 0 | 0 | 40.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-20 23:00 | 40.92 | 0 | 0 | 40.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 | 39.38 | 0 | 0 | 39.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 01:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 02:00 | 37.45 | 0 | 0 | 37.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 03:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 04:00 | 38.01 | 0 | 0 | 38.01 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 05:00 | 39.15 | 0 | 0 | 39.15 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 06:00 | 39.59 | 0 | 0 | 39.59 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 07:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 08:00 | 40.96 | 6.32 | 6.32 | 34.64 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 09:00 | 43.22 | 51.06 | 51.06 | 0 | 7.84 | 0 | 39.9 | 0 | 0
2025-12-21 10:00 | 44.55 | 57.26 | 57.26 | 0 | 12.71 | 0 | 51.97 | 0 | 0
2025-12-21 11:00 | 44.17 | 51.15 | 51.15 | 0 | 6.99 | 0 | 58.61 | 0 | 0
2025-12-21 12:00 | 46.52 | 45.12 | 45.12 | 0 | 0 | 1.4 | 57.14 | 0 | 0
2025-12-21 13:00 | 47.08 | 46.26 | 46.26 | 0 | 0 | 0.82 | 56.28 | 0 | 0
2025-12-21 14:00 | 47.2 | 54.44 | 54.44 | 0 | 7.23 | 0 | 63.15 | 0 | 0
2025-12-21 15:00 | 48.05 | 43.47 | 43.47 | 0 | 0 | 4.57 | 58.33 | 0 | 0
2025-12-21 16:00 | 47.04 | 0.9 | 0.9 | 21.55 | 0 | 24.59 | 32.45 | 0 | 0
2025-12-21 17:00 | 46.91 | 0 | 0 | 46.91 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 18:00 | 45.85 | 0 | 0 | 45.85 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 19:00 | 44.85 | 0 | 0 | 44.85 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 20:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 21:00 | 41.99 | 0 | 0 | 41.99 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 22:00 | 42.01 | 0 | 0 | 42.01 | 0 | 0 | 32.45 | 0 | 0
2025-12-21 23:00 | 40.33 | 0 | 0 | 40.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 | 39.93 | 0 | 0 | 39.93 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 01:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 02:00 | 37.68 | 0 | 0 | 37.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 03:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 04:00 | 37.66 | 0 | 0 | 37.66 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 05:00 | 38.28 | 0 | 0 | 38.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 06:00 | 39.4 | 0 | 0 | 39.4 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 07:00 | 39.29 | 0 | 0 | 39.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 08:00 | 41.3 | 6.67 | 6.67 | 34.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 09:00 | 42.35 | 68.52 | 68.52 | 0 | 26.17 | 0 | 57.31 | 0 | 0
2025-12-22 10:00 | 43.82 | 64.47 | 64.47 | 0 | 20.65 | 0 | 76.93 | 0 | 0
2025-12-22 11:00 | 44.69 | 52.58 | 52.58 | 0 | 7.88 | 0 | 84.42 | 0 | 0
2025-12-22 12:00 | 45.81 | 30.65 | 30.65 | 0 | 0 | 15.17 | 68.45 | 0 | 0
2025-12-22 13:00 | 45.82 | 38.27 | 38.27 | 0 | 0 | 7.55 | 60.5 | 0 | 0
2025-12-22 14:00 | 45.89 | 62.67 | 62.67 | 0 | 16.78 | 0 | 76.44 | 0 | 0
2025-12-22 15:00 | 47.53 | 59.37 | 59.37 | 0 | 11.84 | 0 | 87.69 | 0 | 0
2025-12-22 16:00 | 45.56 | 2.11 | 2.11 | 0 | 0 | 43.45 | 41.95 | 0 | 0
2025-12-22 17:00 | 45.16 | 0 | 0 | 36.13 | 0 | 9.03 | 32.45 | 0 | 0
2025-12-22 18:00 | 45.45 | 0 | 0 | 45.45 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 19:00 | 45.06 | 0 | 0 | 45.06 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 20:00 | 43.28 | 0 | 0 | 43.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 21:00 | 42.56 | 0 | 0 | 42.56 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 22:00 | 39.94 | 0 | 0 | 39.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-22 23:00 | 39.66 | 0 | 0 | 39.66 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 | 38.02 | 0 | 0 | 38.02 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 01:00 | 38.68 | 0 | 0 | 38.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 03:00 | 37.1 | 0 | 0 | 37.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 04:00 | 38.14 | 0 | 0 | 38.14 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 05:00 | 38.83 | 0 | 0 | 38.83 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 06:00 | 38.87 | 0 | 0 | 38.87 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 07:00 | 40.1 | 0 | 0 | 40.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 08:00 | 41.11 | 0 | 0 | 41.11 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 09:00 | 41.83 | 30.36 | 30.36 | 11.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 10:00 | 42.51 | 1.39 | 1.39 | 41.11 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 11:00 | 44.39 | 39.99 | 39.99 | 4.39 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 12:00 | 45.32 | 45.52 | 45.52 | 0 | 0.21 | 0 | 32.65 | 0 | 0
2025-12-23 13:00 | 46.16 | 52.62 | 52.62 | 0 | 6.46 | 0 | 38.78 | 0 | 0
2025-12-23 14:00 | 46.31 | 60.86 | 60.86 | 0 | 14.55 | 0 | 52.6 | 0 | 0
2025-12-23 15:00 | 45.73 | 52.09 | 52.09 | 0 | 6.37 | 0 | 58.65 | 0 | 0
2025-12-23 16:00 | 46.5 | 2.39 | 2.39 | 19.22 | 0 | 24.89 | 32.45 | 0 | 0
2025-12-23 17:00 | 45.71 | 0 | 0 | 45.71 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 18:00 | 44.77 | 0 | 0 | 44.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 19:00 | 43.96 | 0 | 0 | 43.96 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 20:00 | 42.71 | 0 | 0 | 42.71 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 21:00 | 42.38 | 0 | 0 | 42.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 22:00 | 40.13 | 0 | 0 | 40.13 | 0 | 0 | 32.45 | 0 | 0
2025-12-23 23:00 | 39.32 | 0 | 0 | 39.32 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 | 38.71 | 0 | 0 | 38.71 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 01:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 02:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 04:00 | 38.49 | 0 | 0 | 38.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 05:00 | 38.9 | 0 | 0 | 38.9 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 06:00 | 38.29 | 0 | 0 | 38.29 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 07:00 | 38.47 | 0 | 0 | 38.47 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 08:00 | 40.71 | 0 | 0 | 40.71 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 09:00 | 42.4 | 0 | 0 | 42.4 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 10:00 | 43.74 | 1.5 | 1.5 | 42.24 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 11:00 | 43.56 | 2.49 | 2.49 | 41.07 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 12:00 | 45.78 | 2.61 | 2.61 | 43.17 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 13:00 | 44.49 | 33.87 | 33.87 | 10.62 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 14:00 | 45.86 | 35.06 | 35.06 | 10.81 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 15:00 | 45.99 | 27.93 | 27.93 | 18.06 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 16:00 | 46.62 | 0.77 | 0.77 | 45.85 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 17:00 | 46.25 | 0 | 0 | 46.25 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 18:00 | 45.38 | 0 | 0 | 45.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 19:00 | 43.32 | 0 | 0 | 43.32 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 20:00 | 43.38 | 0 | 0 | 43.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 21:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 22:00 | 39.91 | 0 | 0 | 39.91 | 0 | 0 | 32.45 | 0 | 0
2025-12-24 23:00 | 38.7 | 0 | 0 | 38.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 | 39.28 | 0 | 0 | 39.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 01:00 | 38.06 | 0 | 0 | 38.06 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 03:00 | 37.51 | 0 | 0 | 37.51 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 04:00 | 37.93 | 0 | 0 | 37.93 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 05:00 | 38.1 | 0 | 0 | 38.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 06:00 | 37.99 | 0 | 0 | 37.99 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 07:00 | 40.49 | 0 | 0 | 40.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 08:00 | 40.92 | 5.51 | 5.51 | 35.41 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 09:00 | 41.15 | 30.96 | 30.96 | 10.19 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 10:00 | 42.03 | 23.64 | 23.64 | 18.39 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 11:00 | 43.12 | 26.11 | 26.11 | 17 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 12:00 | 43 | 30.88 | 30.88 | 12.11 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 13:00 | 44.18 | 49.53 | 49.53 | 0 | 5.34 | 0 | 37.53 | 0 | 0
2025-12-25 14:00 | 43.64 | 56.96 | 56.96 | 0 | 13.32 | 0 | 50.18 | 0 | 0
2025-12-25 15:00 | 44.36 | 47.82 | 47.82 | 0 | 3.46 | 0 | 53.46 | 0 | 0
2025-12-25 16:00 | 43.72 | 2.47 | 2.47 | 21.29 | 0 | 19.96 | 32.45 | 0 | 0
2025-12-25 17:00 | 43.46 | 0 | 0 | 43.46 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 18:00 | 44.38 | 0 | 0 | 44.38 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 19:00 | 42.97 | 0 | 0 | 42.97 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 20:00 | 42.28 | 0 | 0 | 42.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 21:00 | 40.31 | 0 | 0 | 40.31 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 22:00 | 40.12 | 0 | 0 | 40.12 | 0 | 0 | 32.45 | 0 | 0
2025-12-25 23:00 | 39.77 | 0 | 0 | 39.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 | 38.81 | 0 | 0 | 38.81 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 01:00 | 37.01 | 0 | 0 | 37.01 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 02:00 | 37.79 | 0 | 0 | 37.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 03:00 | 37.74 | 0 | 0 | 37.74 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 04:00 | 38.33 | 0 | 0 | 38.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 05:00 | 37.76 | 0 | 0 | 37.76 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 06:00 | 37.59 | 0 | 0 | 37.59 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 07:00 | 39.03 | 0 | 0 | 39.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 08:00 | 39.92 | 4.49 | 4.49 | 35.43 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 09:00 | 41.84 | 50.98 | 50.98 | 0 | 9.14 | 0 | 41.13 | 0 | 0
2025-12-26 10:00 | 41.11 | 57.88 | 57.88 | 0 | 16.77 | 0 | 57.06 | 0 | 0
2025-12-26 11:00 | 43.17 | 48.67 | 48.67 | 0 | 5.5 | 0 | 62.29 | 0 | 0
2025-12-26 12:00 | 44.89 | 36.25 | 36.25 | 0 | 0 | 8.64 | 53.2 | 0 | 0
2025-12-26 13:00 | 44.78 | 28.2 | 28.2 | 0 | 0 | 16.58 | 35.74 | 0 | 0
2025-12-26 14:00 | 45.6 | 15.06 | 15.06 | 27.42 | 0 | 3.12 | 32.45 | 0 | 0
2025-12-26 15:00 | 44.46 | 6.19 | 6.19 | 38.27 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 16:00 | 44.36 | 0.84 | 0.84 | 43.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 17:00 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 18:00 | 44.23 | 0 | 0 | 44.23 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 19:00 | 43.44 | 0 | 0 | 43.44 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 20:00 | 41.91 | 0 | 0 | 41.91 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 21:00 | 41.52 | 0 | 0 | 41.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 22:00 | 39.89 | 0 | 0 | 39.89 | 0 | 0 | 32.45 | 0 | 0
2025-12-26 23:00 | 40.12 | 0 | 0 | 40.12 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 | 40 | 0 | 0 | 40 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 01:00 | 38.26 | 0 | 0 | 38.26 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 02:00 | 37.31 | 0 | 0 | 37.31 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 03:00 | 36.22 | 0 | 0 | 36.22 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 04:00 | 36.78 | 0 | 0 | 36.78 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 05:00 | 38.79 | 0 | 0 | 38.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 06:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 07:00 | 39.26 | 0 | 0 | 39.26 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 08:00 | 40.7 | 0 | 0 | 40.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 09:00 | 42.11 | 1.65 | 1.65 | 40.46 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 10:00 | 42.25 | 4.31 | 4.31 | 37.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 11:00 | 43.06 | 6 | 6 | 37.06 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 12:00 | 44.08 | 6.12 | 6.12 | 37.96 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 13:00 | 44.32 | 5.68 | 5.68 | 38.64 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 14:00 | 44.72 | 4.63 | 4.63 | 40.09 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 15:00 | 45.34 | 2.01 | 2.01 | 43.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 16:00 | 45.1 | 0 | 0 | 45.1 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 17:00 | 45.7 | 0 | 0 | 45.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 18:00 | 44.26 | 0 | 0 | 44.26 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 19:00 | 43.84 | 0 | 0 | 43.84 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 20:00 | 41.82 | 0 | 0 | 41.82 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 21:00 | 41.63 | 0 | 0 | 41.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 22:00 | 40.01 | 0 | 0 | 40.01 | 0 | 0 | 32.45 | 0 | 0
2025-12-27 23:00 | 39.64 | 0 | 0 | 39.64 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 | 38.93 | 0 | 0 | 38.93 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 01:00 | 37.98 | 0 | 0 | 37.98 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 02:00 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 03:00 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 04:00 | 38.16 | 0 | 0 | 38.16 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 05:00 | 38.34 | 0 | 0 | 38.34 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 06:00 | 39.47 | 0 | 0 | 39.47 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 07:00 | 38.69 | 0 | 0 | 38.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 08:00 | 41.07 | 1.27 | 1.27 | 39.8 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 09:00 | 40.96 | 7.21 | 7.21 | 33.75 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 10:00 | 42.26 | 24.56 | 24.56 | 17.7 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 11:00 | 43.85 | 35.14 | 35.14 | 8.71 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 12:00 | 45.08 | 24.58 | 24.58 | 20.5 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 13:00 | 44.58 | 23.44 | 23.44 | 21.14 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 14:00 | 45.34 | 13.97 | 13.97 | 31.37 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 15:00 | 45.79 | 0 | 0 | 45.79 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 16:00 | 45.5 | 0 | 0 | 45.5 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 17:00 | 45.58 | 0 | 0 | 45.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 18:00 | 46.18 | 0 | 0 | 46.18 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 19:00 | 43.78 | 0 | 0 | 43.78 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 20:00 | 42.17 | 0 | 0 | 42.17 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 21:00 | 40.81 | 0 | 0 | 40.81 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 22:00 | 40.23 | 0 | 0 | 40.23 | 0 | 0 | 32.45 | 0 | 0
2025-12-28 23:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 | 38.77 | 0 | 0 | 38.77 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 01:00 | 38.12 | 0 | 0 | 38.12 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 02:00 | 37.28 | 0 | 0 | 37.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 03:00 | 38.37 | 0 | 0 | 38.37 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 04:00 | 37.14 | 0 | 0 | 37.14 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 05:00 | 37.84 | 0 | 0 | 37.84 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 06:00 | 38.85 | 0 | 0 | 38.85 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 07:00 | 39.83 | 0 | 0 | 39.83 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 08:00 | 41.06 | 1.44 | 1.44 | 39.62 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 09:00 | 41.78 | 42.2 | 42.2 | 0 | 0.42 | 0 | 32.85 | 0 | 0
2025-12-29 10:00 | 43.29 | 52.54 | 52.54 | 0 | 9.25 | 0 | 41.63 | 0 | 0
2025-12-29 11:00 | 43.59 | 30.65 | 30.65 | 4.22 | 0 | 8.73 | 32.45 | 0 | 0
2025-12-29 12:00 | 45.41 | 26.19 | 26.19 | 19.22 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 13:00 | 46.21 | 21.87 | 21.87 | 24.34 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 14:00 | 47.04 | 7.55 | 7.55 | 39.49 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 15:00 | 45.62 | 1.11 | 1.11 | 44.51 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 16:00 | 45.82 | 0.49 | 0.49 | 45.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 17:00 | 46.17 | 0 | 0 | 46.17 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 18:00 | 43.63 | 0 | 0 | 43.63 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 19:00 | 44.17 | 0 | 0 | 44.17 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 20:00 | 43.3 | 0 | 0 | 43.3 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 21:00 | 41.28 | 0 | 0 | 41.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 22:00 | 40.2 | 0 | 0 | 40.2 | 0 | 0 | 32.45 | 0 | 0
2025-12-29 23:00 | 38.85 | 0 | 0 | 38.85 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 | 38.15 | 0 | 0 | 38.15 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 01:00 | 37.58 | 0 | 0 | 37.58 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 02:00 | 37.11 | 0 | 0 | 37.11 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 03:00 | 36.96 | 0 | 0 | 36.96 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 04:00 | 37.32 | 0 | 0 | 37.32 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 05:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 06:00 | 39.34 | 0 | 0 | 39.34 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 07:00 | 38.94 | 0 | 0 | 38.94 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 08:00 | 40.12 | 0.6 | 0.6 | 39.52 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 09:00 | 40.48 | 0 | 0 | 40.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 10:00 | 41.25 | 14.1 | 14.1 | 27.15 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 11:00 | 41.37 | 25.69 | 25.69 | 15.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 12:00 | 41.98 | 28.94 | 28.94 | 13.04 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 13:00 | 42.56 | 25.88 | 25.88 | 16.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 14:00 | 43.5 | 41.17 | 41.17 | 2.33 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 15:00 | 44.03 | 44.8 | 44.8 | 0 | 0.78 | 0 | 33.19 | 0 | 0
2025-12-30 16:00 | 42.52 | 4.24 | 4.24 | 37.57 | 0 | 0.7 | 32.45 | 0 | 0
2025-12-30 17:00 | 42.89 | 0 | 0 | 42.89 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 18:00 | 42.08 | 0 | 0 | 42.08 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 19:00 | 42.09 | 0 | 0 | 42.09 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 20:00 | 42.08 | 0 | 0 | 42.08 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 21:00 | 40.55 | 0 | 0 | 40.55 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 22:00 | 39.92 | 0 | 0 | 39.92 | 0 | 0 | 32.45 | 0 | 0
2025-12-30 23:00 | 39.86 | 0 | 0 | 39.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 | 38.6 | 0 | 0 | 38.6 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 01:00 | 37.4 | 0 | 0 | 37.4 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 02:00 | 37.48 | 0 | 0 | 37.48 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 03:00 | 36.86 | 0 | 0 | 36.86 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 04:00 | 37.61 | 0 | 0 | 37.61 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 05:00 | 38.03 | 0 | 0 | 38.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 06:00 | 37.69 | 0 | 0 | 37.69 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 07:00 | 39.23 | 0 | 0 | 39.23 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 08:00 | 39.98 | 3.92 | 3.92 | 36.06 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 09:00 | 41.27 | 39.39 | 39.39 | 1.88 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 10:00 | 42.37 | 44.25 | 44.25 | 0 | 1.88 | 0 | 34.23 | 0 | 0
2025-12-31 11:00 | 43.07 | 48.76 | 48.76 | 0 | 5.69 | 0 | 39.64 | 0 | 0
2025-12-31 12:00 | 43.43 | 42.22 | 42.22 | 0 | 0 | 1.22 | 38.36 | 0 | 0
2025-12-31 13:00 | 44.63 | 57.55 | 57.55 | 0 | 12.93 | 0 | 50.64 | 0 | 0
2025-12-31 14:00 | 44.08 | 69.02 | 69.02 | 0 | 24.94 | 0 | 74.33 | 0 | 0
2025-12-31 15:00 | 43.98 | 68.72 | 68.72 | 0 | 24.74 | 0 | 97.83 | 0 | 0
2025-12-31 16:00 | 42.92 | 6.19 | 6.19 | 0 | 0 | 36.73 | 59.16 | 0 | 0
2025-12-31 17:00 | 44.12 | 0 | 0 | 18.75 | 0 | 25.38 | 32.45 | 0 | 0
2025-12-31 18:00 | 43.17 | 0 | 0 | 43.17 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 19:00 | 43.03 | 0 | 0 | 43.03 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 20:00 | 40.97 | 0 | 0 | 40.97 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 21:00 | 40.68 | 0 | 0 | 40.68 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 22:00 | 40.28 | 0 | 0 | 40.28 | 0 | 0 | 32.45 | 0 | 0
2025-12-31 23:00 | 38.63 | 0 | 0 | 38.63 | 0 | 0 | 32.45 | 0 | 0